## SER 2 Review
Standard Number | R | Text of Requirement | Time Horizon | Status | Violation Risk Factors | SER Phase 1 Disposition | SER Phase 1 Justification (initial) | SER Phase 2 Disposition | SER Phase 2 Follow-up Review
BAL-001-2 | R1. | The Responsible Entity shall operate such that the Control Performance Standard 1 (CPS1), calculated in accordance with Attachment 1, is greater than or equal to 100 percent for the applicable Interconnection in which it operates for each preceding 12 consecutive calendar month period, evaluated monthly. | Real-time Operations | Active | MEDIUM | No Action | This requirement serves a reliability purpose. | No Action | No action recommended.
BAL-001-2 | R2. | Each Balancing Authority shall operate such that its clock-minute average of Reporting ACE does not exceed its clock-minute Balancing Authority ACE Limit (BAAL) for more than 30 consecutive clock-minutes, calculated in accordance with Attachment 2, for the applicable Interconnection in which the Balancing Authority operates. | Real-time Operations | Active | MEDIUM | No Action | This requirement serves a reliability purpose. | No Action | No action recommended.
BAL-002-2 | R1. | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: 1.1. within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of: • zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or, • its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. 1.2. document all Reportable Balancing Contingency Events using CR Form 1. 1.3. deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if: 1.3.1 the Responsible Entity: • is a Balancing Authority experiencing a Reliability Coordinator declared Energy Emergency Alert Level or is a Reserve Sharing Group whose member, or members, are experiencing a Reliability Coordinator declared Energy Emergency Alert level, and • is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and • has depleted its Contingency Reserve to a level below its Most Severe Single Contingency or, 1.3.2 the Responsible Entity experiences: • multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. | Real-time Operations | Future | HIGH | No Action | This requirement serves a reliability purpose. | No Action | No action recommended.
BAL-002-2 | R3. | R3. Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. | Real-time Operations | Future | MEDIUM | No Action | This requirement serves a reliability purpose. | No Action | No action recommended.
BAL-002-2(i) | R2. | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. | Operations Planning | Future | High | No Action | The industry did not provide input supporting retiring this requirement. Multiple entities did recommend retaining the requirement. | No Action | BAL-002-2(i) was superseded by BAL-002-3. This standard shows retired on 3-3-2019 Maintain BAL-002-3
BAL-003-1.1 | R1. | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation | Real-time Operations | Active | HIGH | No Action | This requirement serves a reliability purpose. | No Action | No action recommended.
BAL-003-1.1 | R2. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. | Operations Planning | Current | Medium | No Action | The industry did not provide input supporting retiring this requirement. Multiple entities did recommend retaining the requirement. | No Action | No action recommended.
BAL-003-1.1 | R3. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: 3.1 Less than zero at all times, and 3.2 Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. | Operations Planning | Current | Medium | No Action | The industry did not provide input supporting retiring this requirement. Multiple entities did recommend retaining the requirement. | No Action | No action recommended.
BAL-003-1.1 | R4. | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. | Operations Planning | Current | Medium | No Action | The industry did not provide input supporting retiring this requirement. Multiple entities did recommend retaining the requirement. | No Action | No action recommended.
BAL-005-1 | R1. | The Balancing Authority shall use a design scan rate of no more than six seconds in acquiring data necessary to calculate Reporting ACE. | Real-time Operations | Future | MEDIUM | Transfer | This can be transferred to Phase 2 Alternatives to Retirement. It maybe included in the Organization Certification. The acquisition of data, determination of the accuracy of data, and the mitigation of inaccuracies are essential components of BA functionality. The details of the tools and information retrieval are not needed in a reliability standard since the purpose of BA Organization Certification is to ensure that an entity has the tools and capabilities to be a BA, so this type of requirement would be a suitable inclusion in the Organization Certification process. This also applies to R3, R5, and R7. | Modify | Modify. Move requirement and associated Measure to BAL-001-2 as requirement R3. Closely related to BAL-001, R2. Keep VSLs the same. Should be considered by a Periodic Review Team.
BAL-005-1 | R2. | A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. | Real-time Operations | Future | MEDIUM | Transfer | Although this does have a reliability impact, all other requirements are recommended for transfer/retirement, so this can be incorporated into another standard such as EOP-008-1 or BAL-001-2. | PRT | Recommend for Periodic Review and if other modifications are needed, consider removing BAL-005-1 Requirement R2 and associated Measure M2 and placing it in BAL-001-2 as new Requirement R3 and Measure M3 as these requirements are closely related. Keep Violation Severity Limit the same.
BAL-005-1 | R3. | Each Balancing Authority shall use frequency metering equipment for the calculation of Reporting ACE: 3.1. that is available a minimum of 99.95% for each calendar year; and, 3.2. with a minimum accuracy of 0.001 Hz. | Real-time Operations | Future | MEDIUM | Transfer | This can be transferred to Phase 2 Alternatives to Retirement. It may be included in the Organization Certification. See comments for R1. | No Action | No action recommended.
BAL-005-1 | R4. | The Balancing Authority shall make available to the operator information associated with Reporting ACE including, but not limited to, quality flags indicating missing or invalid data. | Real-time Operations | Future | MEDIUM | Retirement | This is already duplicated in TOP-010-1(i) R2: “Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: 2.1. Criteria for evaluating the quality of Real-time data; 2.2. Provisions to indicate the quality of Real-time data to the System Operator; and 2.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions.” The BA is already required by TOP-010-1(i) R2 to have an Operating Process/Procedure to address quality of Real-time data (which would include Reporting ACE) which includes criteria to evaluate the data, provisions to indicate the quality of the data to the System Operator, and actions to address data quality issues with other entities. | Retire | Retire. Reporting ACE is part of the analysis and real-time monitoring function and should be covered in TOP-010-1(i), R2. Supported by NERC Glossary of Terms BA definition. The VRF of BAL-005, R4 is Medium and TOP-010, R2 is High because it is more comprehensive and all encompassing of data quality.
BAL-005-1 | R5. | Each Balancing Authority’s system used to calculate Reporting ACE shall be available a minimum of 99.5% of each calendar year. | Operations Assessment | Future | MEDIUM | Transfer | This can be transferred to Phase 2 Alternatives to Retirement. It may be included in the Organization Certification. See comments for R1. | No Action | No action recommended.
BAL-005-1 | R6. | Each Balancing Authority that is within a multiple Balancing Authority Interconnection shall implement an Operating Process to identify and mitigate errors affecting the accuracy of scan rate data used in the calculation of Reporting ACE for each Balancing Authority Area. | Same Day Operations | Future | MEDIUM | Retirement | This is already duplicated in TOP-010-1(i) R2: “Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: 2.1. Criteria for evaluating the quality of Real-time data; 2.2. Provisions to indicate the quality of Real-time data to the System Operator; and 2.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions.” The BA is already required by TOP-010-1(i) R2 to have an Operating Process/Procedure to address quality of Real-time data (which would include Reporting ACE) which includes criteria to evaluate the data, provisions to indicate the quality of the data to the System Operator, and actions to address data quality issues with other entities. The same logic applies since TOP-010-1(i) R2 requires an Operating Process/Procedure to include criteria to evaluate the data, provisions to indicate the quality of the data to the System Operator, and actions to address data quality issues with other entities. | Retire | Retire. ACE is an analysis and real-time monitoring function and should be covered in TOP-010-1(i), R2, part 2.3. Supported by NERC Glossary of Terms BA and BA Area definition. Real-time monitoring and analysis capabilities of the BA are core to the function (e.g., determining Reporting ACE). Multiple Balancing Authority is an exclusion for the ERCOT Interconnection, which is only one BA.
BAL-005-1 | R7. | Each Balancing Authority shall ensure that each Tie-Line, Pseudo-Tie, and Dynamic Schedule with an Adjacent Balancing Authority is equipped with: [Violation Risk Factor: 7.1. a common source to provide information to both Balancing Authorities for the scan rate values used in the calculation of Reporting ACE; and, 7.2. a time synchronized common source to determine hourly megawatt-hour values agreed-upon to aid in the identification and mitigation of errors. | Operations Planning | Future | MEDIUM | Transfer | This can be transferred to Phase 2 Alternatives to Retirement. It may be included in the Organization Certification. See comments for R1. | No Action | No action recommended.
COM-001-3 | R1. | Each Reliability Coordinator shall have Interpersonal Communication capability with the following entities (unless the Reliability Coordinator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): 1.1. All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. 1.2. Each adjacent Reliability Coordinator within the same Interconnection. | Real-time Operations | Active | HIGH | Transfer | See R7 | No Action | No action recommended.
COM-001-3 | R2. | Each Reliability Coordinator shall designate an Alternative Interpersonal Communication capability with the following entities: 2.1. All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. 2.2. Each adjacent Reliability Coordinator within the same Interconnection. | Real-time Operations | Active | HIGH | Transfer | See R7 | No Action | No action recommended.
COM-001-3 | R3. | Each Transmission Operator shall have Interpersonal Communication capability with the following entities (unless the Transmission Operator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): 3.1. Its Reliability Coordinator. 3.2. Each Balancing Authority within its Transmission Operator Area. 3.3. Each Distribution Provider within its Transmission Operator Area. 3.4. Each Generator Operator within its Transmission Operator Area. 3.5. Each adjacent Transmission Operator synchronously connected. 3.6. Each adjacent Transmission Operator asynchronously connected. | Real-time Operations | Active | HIGH | Transfer | See R7 | No Action | No action recommended.
COM-001-3 | R4. | Each Transmission Operator shall designate an Alternative Interpersonal Communication capability with the following entities: 4.1. Its Reliability Coordinator. 4.2. Each Balancing Authority within its Transmission Operator Area. 4.3. Each adjacent Transmission Operator synchronously connected. 4.4. Each adjacent Transmission Operator asynchronously connected. | Real-time Operations | Active | HIGH | Transfer | Votes to Retain = 4; Votes to Retire = 8. Industry Comments supporting retirement of COM-001-3 R4-R6 fell into 3 main arguments: (1) communication is a basic function of the TOP and BA and is covered elsewhere in standards and guidelines; (2) communication obligations should be verified through the NERC Certification Program as a basic utility function; and (3) communication obligations of this standard should be consolidated with other TOP and BA functions elsewhere in the standards. This Standard is not required and only enforces a compliance "got you" if your primary communication system fails. There is not a reliability benefit with COM-001-3, just administrative burden. COM-001-3 has zero SNOP entries. Given the standard adoption of a multitude of communication technologies, including cell phones, VoIP, radio, and satellite, voice communication requirements are no longer necessary. When financial and business priorities mitigate reliability risks there is no need for a reliability standard. | No Action | No action recommended.
COM-001-3 | R5. | Each Balancing Authority shall have Interpersonal Communication capability with the following entities (unless the Balancing Authority detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): 5.1. Its Reliability Coordinator. 5.2. Each Transmission Operator that operates Facilities within its Balancing Authority Area. 5.3. Each Distribution Provider within its Balancing Authority Area. 5.4. Each Generator Operator that operates Facilities within its Balancing Authority Area. 5.5. Each Adjacent Balancing Authority. | Real-time Operations | Active | HIGH | Transfer | Votes to Retain = 5; Votes to Retire = 12. Industry Comments supporting retirement of COM-001-3 R4-R6 fell into 3 main arguments: (1) communication is a basic function of the TOP and BA and is covered elsewhere in standards and guidelines; (2) communication obligations should be verified through the NERC Certification Program as a basic utility function; and (3) communication obligations of this standard should be consolidated with other TOP and BA functions elsewhere in the standards. This Standard is not required and only enforces a compliance "got you" if your primary communication system fails. There is not a reliability benefit with COM-001-3, just administrative burden. COM-001-3 has zero SNOP entries. Given the standard adoption of a multitude of communication technologies, including cell phones, VoIP, radio, and satellite, voice communication requirements are no longer necessary. When financial and business priorities mitigate reliability risks there is no need for a reliability standard. | No Action | No action recommended.
COM-001-3 | R6. | Each Balancing Authority shall designate an Alternative Interpersonal Communication capability with the following entities: 6.1. Its Reliability Coordinator. 6.2. Each Transmission Operator that operates Facilities within its Balancing Authority Area. 6.3. Each Adjacent Balancing Authority. | Real-time Operations | Active | HIGH | Transfer | Votes to Retain = 5; Votes to Retire = 12. Industry Comments supporting retirement of COM-001-3 R4-R6 fell into 3 main arguments: (1) communication is a basic function of the TOP and BA and is covered elsewhere in standards and guidelines; (2) communication obligations should be verified through the NERC Certification Program as a basic utility function; and (3) communication obligations of this standard should be consolidated with other TOP and BA functions elsewhere in the standards. This Standard is not required and only enforces a compliance "got you" if your primary communication system fails. There is not a reliability benefit with COM-001-3, just administrative burden. COM-001-3 has zero SNOP entries. Given the standard adoption of a multitude of communication technologies, including cell phones, VoIP, radio, and satellite, voice communication requirements are no longer necessary. When financial and business priorities mitigate reliability risks there is no need for a reliability standard. | No Action | No action recommended.
COM-001-3 | R7. | Each Distribution Provider shall have Interpersonal Communication capability with the following entities (unless the Distribution Provider detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): 7.1. Its Balancing Authority. 7.2. Its Transmission Operator. | Real-time Operations | Active | MEDIUM | Transfer | Compiled Notes - Note: Should be addressed in conjunction with IRO-001-4 … see comment #3014) - COM-001-3: Retire COM-001-3 R1, R2, R3, R4, R5, R6, R7, R8, R9 and R11. For Interpersonal Communications and Alternate Interpersonal Communications, merge R12 and R13 into one Requirement and modify R10 for loss of communications as a second Requirement. All should be verified through the NERC Certification Program as a basic utility function. Basic functionality. This should be part of the certification process for BAs, TOPs and RCs. For all other entities (DPs and GOs), it is not necessary to require communication to be proven as the RC, TOP or BA will assure that they can make contact with these entities and all entities have internal and external Interpersonal Communications Capabilities. This Standard basically states to have a primary and back up communications (a phone). - In today's world, basic, daily functionality necessitates multiple avenues of communications such as a land line phone, a cell phone, text messaging, a radio, satellite phone, etc. This Standard is not required and only enforces a compliance "got you" if your primary communication system fails. There is not a reliability benefit with COM-001-3, just administrative burden. Communications are a basic function of every Entity. The entire Standard should be retired. - Basic business functions require "Interpersonal Communications." - This Requirement is an unnecessary administrative burden and does not add anything to reliability. - Current definition of "Interpersonal Communication" is too broad and should be revised. - Communications is a basic function and a requirement to operate the electric grid reliably. The standard adds administrative burden without increased system reliability. COM-001-1 R1 has 3 low risk SNOP entries. COM-001-3 has zero SNOP entries. - Given the standard adoption of a multitude of communication technologies, including cell phones, VoIP, radio, and satellite, voice communication requirements are no longer necessary. When financial and business priorities mitigate reliability risks there is no need for a reliability standard. | No Action | No action recommended.
COM-001-3 | R8. | Each Generator Operator shall have Interpersonal Communication capability with the following entities (unless the Generator Operator detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): 8.1. Its Balancing Authority. 8.2. Its Transmission Operator. | Real-time Operations | Active | HIGH | Transfer | See R7 | No Action | No action recommended.
COM-001-3 | R9. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall test its Alternative Interpersonal Communication capability at least once each calendar month. If the test is unsuccessful, the responsible entity shall initiate action to repair or designate a replacement Alternative Interpersonal Communication capability within 2 hours. | Same Day Operations and Real-time Operations | Active | MEDIUM | Transfer | See R7 | PRT | Recommend for Periodic Review and if other modifications are needed as this could be combined with R7 by adding the following "Each Distribution Provider and Generator Operator shall have ….and verify with their Balancing Authority and Transmission Operator (check VRF) will need to modify R-11 to remove R8 reference.
COM-001-3 | R10. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall notify entities as identified in Requirements R1, R3, and R5, respectively within 60 minutes of the detection of a failure of its Interpersonal Communication capability that lasts 30 minutes or longer. | Real-time Operations | Active | MEDIUM | Transfer | See R7 | No Action | No action recommended.
COM-001-3 | R11. | Each Distribution Provider and Generator Operator that detects a failure of its Interpersonal Communication capability shall consult each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of its Interpersonal Communication capability. | Real-time Operations | Active | MEDIUM | Transfer | See R7 | No Action | No action recommended.
COM-001-3 | R12. | Each Reliability Coordinator, Transmission Operator, Generator Operator, and Balancing Authority shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between Control Centers within the same functional entity, and/or between a Control Center and field personnel. | Real-time Operations | Active | HIGH | Transfer | See R7 | No Action | No action recommended.
COM-001-3 | R13. | Each Distribution Provider shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between control centers within the same functional entity, and/or between a control center and field personnel. | Real-time Operations | Active | MEDIUM | Transfer | See R7 | No Action | No action recommended.
COM-002-4 | R1. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall develop documented communications protocols for its operating personnel that issue and receive Operating Instructions. The protocols shall, at a minimum: [Please see the standard for more information] | Long Term Planning | Active | LOWER | No Action | The Long-term Planning Team recommends that no action be taken on COM-002-4, R1. R1 requires documented protocols for personnel that issue and receive an Operating Instruction. Based on the responses received, there was little industry provided justification to retire (11%) or modify (3%) of R1. Also, the use of compliance monitoring tools (e.g., spot checks, self-certifications, etc.) is only applicable to requirements enforceable during the period of review, i.e., would not apply to retired requirements. An internal control evaluation is not mandatory, and applies to enforceable requirements. Entity controls, if any, may or may not address documented communication protocols in R5, R6 and/or R7, and will likely vary from entity to entity. | No Action | No action recommended.
COM-002-4 | R2. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall conduct initial training for each of its operating personnel responsible for the Real-time operation of the interconnected Bulk Electric System on the documented communications protocols developed in Requirement R1 prior to that individual operator issuing an Operating Instruction. | Long Term Planning | Active | LOWER | Retirement | This requirement should be retired because the related compliance activities are duplicative of the activities covered by the Systematic Approach to Training within the PER-005-2 Standard. The Long-term Planning Team recommends that no action be taken on COM-002-4, R2, which should not be retired. R2 requires conducting initial training of operating personnel for BAs, RCs, and TOPs prior to that operating personnel issuing an Operating Instruction1. Most respondents in favor of retiring and/or modifying R2 cited redundancy with PER-005, indicating that this initial training should be included on the BES company-specific Real-time reliability-related tasks. The Team does not believe that this is sufficient justification to retire R2. The Team further believes that an incorrect Operating Instruction1 (human error) has the ability to negatively impact BES system-wide reliability. 1 A command by operating personnel responsible for the Real-time operation of the interconnected Bulk Electric System to change or preserve the state, status, output, or input of an Element of the Bulk Electric System or Facility of the Bulk Electric System | No Action | 3-part communications is well known across the industry and should be part of the BA's, RC's and TOP's systematic approach to training as required by PER-005-2. COM-001, R1 requires a protocol (self-explanatory of the steps required), PER-005 should have the protocol identified as a "reliability related task," the ERO would be monitoring compliance that System Operators would be using 3-part communications, and COM-001, R4 requires ongoing entity monitoring of 3-part communication use.
COM-002-4 | R3. | Each Distribution Provider and Generator Operator shall conduct initial training for each of its operating personnel who can receive an oral two-party, person-to-person Operating Instruction prior to that individual operator receiving an oral two-party, person-to-person Operating Instruction to either: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or • Request that the issuer reissue the Operating Instruction. | Long Term Planning | Active | LOWER | Transfer | Longterm Planning recommends to transfer to PER-005 to keep all required System Operator training together. | No Action | No action. The DP and GOP plant operators are not required to have a Training Program covered in PER-005 and therefore would need to have this specific training required in the standard.
COM-002-4 | R4. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall at least once every twelve (12) calendar months: [Please see the standard for more information] 4.1. Assess adherence to the documented communications protocols in Requirement R1 by its operating personnel that issue and receive Operating Instructions, provide feedback to those operating personnel and take corrective action, as deemed appropriate by the entity, to address deviations from the documented protocols. 4.2. Assess the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions and modify its documented communication protocols, as necessary. | Operations Planning | Active | MEDIUM | Retirement | Course of Action: Retire Justification: The SER Operations Planning team believes this requirement should be retired because it describes internal control activities that can be utilized to support compliance with another Requirement (COM-002 R1). Some industry respondents suggested retiring/moving R4 to PER-005. However, the SER Operations Planning sub-team does not see a strong tie between R4 and PER-005 training related requirements. R4 assesses the effectiveness of and adherence to documented protocols required by R1. Training related to the protocols is required by R2 and R3. It has been suggested that assessment of adherence to the documented protocols and of the effectiveness of those protocols is a part of the ADDIE process related to the associated RRT in PER-005-2 Some industry respondents suggested modification of the assessment timeline. However, there was little industry provided justification to modify. Summary of Industry Comments: Most industry comments indicated that this requirement should not be retired. For those that provided a comment other than retaining the requirement, indicated it should either be moved to R1, moved to PER-005, or indicated it was a control and should not be an auditable item. Another comment was to expand the timeframe from 12 months to 15 months. | No Action | No action. The ADDIE process may not adequately cover assessing the effectiveness of the protocols in R1. 3-Part communications is technically required only in emergency situations. Retaining this requirement would ensure that the protocols are adhered to day-to-day.
COM-002-4 | R5. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: • Confirm the receiver’s response if the repeated information is correct (in accordance with Requirement R6). • Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver, or • Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. | Real-time Operations | Active | HIGH | Transfer | 3-part is part of the communication protocols in R1 and required to be used. Adherence to communication protocols is then assessed annually under R4. Recommend that R1 and R4 be retained and not retired as they are used for justification to retire R5, R6 and R7. Industry Comments: • Consider retirement or consolidating into TOP-001 for the TOP/BA and IRO-001 for the RC where the Operating Instruction requirements reside. • There should be no difference between an Operation Instruction under normal conditions and under Emergency conditions. R1 covers all Operating instructions. By imposing additional requirements on Operating Instructions that are issued during an emergency, R5 makes it necessary for entities to track whether each Operating Instruction was issued during an Emergency or during normal operations, in order to be able to demonstrate compliance. This administrative burden does not enhance reliability. • This is clearly a control. • Finding non-compliance over the form of communication, when there is no substantive BES impact if the underlying O/I is completed does not support reliability. • Furthermore, TOP-001-3 R2 requires BAs, IRO-001-4 R1 requires RCs, and TOP-001-3 R1 requires TOPs to maintain reliability by issuing O/Is. Presumably, if an entity does not maintain reliability, they are non-compliant. • As such, a judgment on failure to comply with COM-002 R5 is either not impactful to reliability as the O/I has been communicated and complied with or double jeopardy in the case when a reliability has not been maintained. • Additionally, this requirement has three challenging concepts/definitions that create significant ambiguity when considering communication between multiple entitles (entity defined Communications Protocols, During an Emergency, and Operational Instruction). It is likely that disparate entities have different protocols, define emergencies differently, and/or not have a common understanding of events constituting O/I. Attempting to create a North American wide common understanding of these three concepts/definitions does not support real-time operations. | No Action | No action. This is specific to Emergencies and is not flexible as non-emergency use of developed protocols.
COM-002-4 | R6. | Each Balancing Authority, Distribution Provider, Generator Operator, and Transmission Operator that receives an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or • Request that the issuer reissue the Operating Instruction. | Real-time Operations | Active | HIGH | Transfer | 3-part is part of the communication protocols in R1 and required to be used. Adherence to communication protocols is then assessed annually under R4. Recommend that R1 and R4 be retained and not retired as they are used for justification to retire R5, R6 and R7. Industry Comments: • Consider retirement or consolidating into TOP-001 for the TOP/BA and IRO-001 for the RC where the Operating Instruction requirements reside. • See R5 • This is clearly a control. • Finding non-compliance over the form of communication, when there is no substantive BES impact if the underlying O/I is completed does not support reliability. • Furthermore, IRO-001-4 R2 requires TOPs, BAs, GOPs, and DPs to comply with RC issued O/Is, TOP-001-3 R3 requires BAs, GOPs, and DPs to comply with TOP issued O/Is, and TOP-001-3 R5 requires TOPs, GOPs, and DPs to comply with BA issued O/Is. Presumably, if an entity does not comply, they are non-compliant. • As such, a judgment on failure to comply with COM-002 R6 is either not impactful to reliability as the O/I has been communicated and complied with or double jeopardy in the case when an entity fails to comply with an O/I. • Additionally, this requirement has three challenging concepts/definitions that create significant ambiguity when considering communication between multiple entitles (entity defined Communications Protocols, During an Emergency, and Operational Instruction). It is likely that disparate entities have different protocols, define emergencies differently, and/or not have a common understanding of events constituting O/I. Attempting to create a North American wide common understanding of these three concepts/definitions does not support real-time operations. | No Action | No action. This is specific to Emergencies and is not flexible as non-emergency use of developed protocols.
COM-002-4 | R7. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues a written or oral single-party to multiple-party burst Operating Instruction during an Emergency shall confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. | Real-time Operations | Active | HIGH | Transfer | Industry Comments: • Consider retirement or consolidating into TOP-001 for the TOP/BA and IRO-001 for the RC where the Operating Instruction requirements reside. • See R5 • This is clearly a control. • Finding non-compliance over the form of communication, when there is no substantive BES impact if the underlying O/I is completed does not support reliability. • Furthermore, IRO-001-4 R2 requires TOPs, BAs, GOPs, and DPs to comply with RC issued O/Is, TOP-001-3 R3 requires BAs, GOPs, and DPs to comply with TOP issued O/Is, and TOP-001-3 R5 requires TOPs, GOPs, and DPs to comply with BA issued O/Is. Presumably, if an entity does not comply, they are non-compliant. • As such, a judgment on failure to comply with COM-002 R7 is either not impactful to reliability as the O/I has been communicated and complied with or double jeopardy in the case when an entity fails to comply with an O/I. • Additionally, this requirement has three challenging concepts/definitions that create significant ambiguity when considering communication between multiple entitles (entity defined Communications Protocols, During an Emergency, and Operational Instruction). It is likely that disparate entities have different protocols, define emergencies differently, and/or not have a common understanding of events constituting O/I. Attempting to create a North American wide common understanding of these three concepts/definitions does not support real-time operations. | No Action | No action. This to ensure the message was received by at least one entity.
EOP-004-4 | R1. | Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-4 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | Operations Planning | Future | LOWER | No Action | Course of Action: No Action Justification: Following internal discussions and consideration of the comments received the EOP/COM sub team does not recommend action to R1 R2 or R3. (R3 is not in the Operations Planning horizon) Discussion: EOP-004 has never been intended to be a real time reporting Standard. Real time information sharing is distributed in other standards including many EOP, BAL, IRO, etc. Standards. BES reliability The Standard has been vetted via several SDT reviews, periodic reviews, and was included in Par 81 assessments. With regard to comments regarding benefit of a reporting standard the team recognizes the importance of event evaluation as part of a process to ensure BES reliability. We do recommend that during the next review the drafting team looks for a method to improve the process of reporting to be more consistent to the extent possible across the continent yet meet the needs of the U.S. based DOE activities. | No Action
EOP-004-4 | R2. | Each Responsible Entity shall report events specified in EOP-004-4 Attachment 1 to the entities specified per their Operating Plan by the later of 24 hours of recognition of meeting an event type threshold for reporting or by the end of the Responsible Entity’s next business day (4 p.m. local time will be considered the end of the business day). | Operations Assessment | Future | MEDIUM | No Action | Course of Action: No Action Justification: Following internal discussions and consideration of the comments received the EOP/COM sub team does not recommend action to R1 R2 or R3. (R3 is not in the Operations Planning horizon) Discussion: EOP-004 has never been intended to be a real time reporting Standard. Real time information sharing is distributed in other standards including many EOP, BAL, IRO, etc. Standards. BES reliability The Standard has been vetted via several SDT reviews, periodic reviews, and was included in Par 81 assessments. With regard to comments regarding benefit of a reporting standard the team recognizes the importance of event evaluation as part of a process to ensure BES reliability. We do recommend that during the next review the drafting team looks for a method to improve the process of reporting to be more consistent to the extent possible across the continent yet meet the needs of the U.S. based DOE activities. | No Action
EOP-005-3 | R1. | Each Transmission Operator shall have a restoration plan approved by its Reliability Coordinator. The restoration plan shall allow for restoring the Transmission Operator’s System following a Disturbance in which one or more areas of the Bulk Electric System (BES) shuts down and the use of Blackstart Resources is required to restore the shut down area to service, to a state whereby the choice of the next Load to be restored is not driven by the need to control frequency or voltage regardless of whether the Blackstart Resource is located within the Transmission Operator’s System. The restoration plan shall include: 1.1. Strategies for system restoration that are coordinated with the Reliability Coordinator’s high level strategy for restoring the Interconnection. 1.2. A description of how all Agreements or mutually agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. 1.3. Procedures for restoring interconnections with other Transmission Operators under the direction of the Reliability Coordinator. 1.4. Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. 1.5. Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. 1.6. Identification of acceptable operating voltage and frequency limits during restoration. 1.7. Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. 1.8. Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. 1.9. Operating Processes for transferring authority back to the Balancing Authority in accordance with the Reliability Coordinator’s criteria. | Real-time Operations | Future | HIGH | Modification | Moved to Ops Planning | No Action | R1 ensures that there are Operating procedures, processes or plans in place and coordinated (R2) in advance. R3-R7 do not adequately cover this as they cover real-time events. Considering the comments on R2, the Requirement 1 and 2 should be combined and R2 retired: R1. Each Reliability Coordinator shall have, implement, and maintain Operating Procedures, Operating Processes, or Operating Plans, for activities that require notification or coordination of actions that may impact adjacent Reliability Coordinator Areas, to support Interconnection reliability. These Operating Procedures, Operating Processes, or Operating Plans shall include, but are not limited to, the following: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same-Day Operations] 1.1. Criteria and processes for notifications. 1.2. Energy and capacity shortages. 1.3. Control of voltage, including the coordination of reactive resources. 1.4. Exchange of information including planned and unplanned outage information to support its Operational Planning Analyses and Real-time Assessments. 1.5. Provisions for periodic communications to support reliable operations. 1.6 Review and update annually with no more than 15 months between reviews. 1.7 Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. 1.8. Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. 1.9. Operating Processes for transferring operations back to the Balancing Authority in accordance with its Reliability Coordinator’s criteria.
EOP-005-3 | R10. | Each Transmission Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | Operations Planning | Future | MEDIUM | Modification | Course of Action: Modification Justification: The SER Operations Planning team agrees that this requirement was recently revised. However, this requirement is very similar to EOP-005-3, R16 and the two requirements should be merged accordingly. | PRT | Recommend for Periodic Review and if other modifications are needed, consider consolidating Requirement R16 (GO) with R10 (TO) as follows: "Each Transmission Operator and Generator Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator."
EOP-005-3 | R11. | Each Transmission Operator and each Generator Operator with a Blackstart Resource shall have written Blackstart Resource Agreements or mutually agreed upon procedures or protocols, specifying the terms and conditions of their arrangement. Such Agreements shall include references to the Blackstart Resource testing requirements. | Operations Planning | Future | MEDIUM | No Action | Course of Action: Leave as-is with no modification. Justification: The SER Operations Planning team agrees that this particular requirement was just revised and there is no need for further action. | No Action | No action recommended.
EOP-005-3 | R12. | Each Generator Operator with a Blackstart Resource shall have documented procedures for starting each Blackstart Resource and energizing a bus. | Operations Planning | Future | MEDIUM | No Action | Course of Action: Leave as-is with no modification. Justification: The SER Operations Planning team agrees that this particular requirement was just revised and there is no need for further action. | No Action | No action recommended.
EOP-005-3 | R13. | Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following such change. | Operations Planning | Future | MEDIUM | Modification | Course of Action: Modification Justification: The SER Operations Planning team agrees that this particular requirement was just revised, and it also agrees that the requirement's wording requires modification. For example, there could be an interpretation that the 24 hour timeline starts when the capability change occurred, regardless of when this change became known. The SER team recommends that this requirement be reworded from "within 24 hours following such change" to "within 24 hours of identifying such change" or "within 24 hours of the discovery of any changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan." | PRT | Recommend for Periodic Review and if other modifications are needed, consider clarifying expectation in EOP-005-3, Requirement R13 by adding "of identifying" or other clarifying language: "R13. Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following of identifying such change."
EOP-005-3 | R14. | Each Generator Operator with a Blackstart Resource shall perform Blackstart Resource tests, and maintain records of such testing, in accordance with the testing requirements set by the Transmission Operator to verify that the Blackstart Resource can perform as specified in the restoration plan. 14.1. Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R7. 14.2. Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. | Operations Planning | Future | MEDIUM | No Action | Course of Action: Leave as-is with no modification. Justification: The SER Operations Planning team agrees that this particular requirement was just revised and there is no need for further action. | No Action | No action recommended.
EOP-005-3 | R15. | Each Generator Operator with a Blackstart Resource shall provide a minimum of two hours of training every two calendar years to each of its operating personnel responsible for the startup of its Blackstart Resource generation units and energizing a bus. The training program shall include training on the following: 15.1. System restoration plan including coordination with the Transmission Operator. 15.2. The procedures documented in Requirement R12. | Operations Planning | Future | MEDIUM | No Action | Course of Action: No Action Justification: The SER Operations Planning team believes this requirement should be retained but the team also agrees that the requirement to provide at least two-hours of training is arbitrary and should be reviewed by the next Standard Review team. | No Action | No action recommended.
EOP-005-3 | R16. | Each Generator Operator shall participate in the Reliability Coordinator’s restoration drills, exercises, or simulations as requested by the Reliability Coordinator. | Operations Planning | Future | MEDIUM | Transfer | Course of Action: Transfer Justification: The SER Operations Planning team recommends this requirement text be merged into EOP-005-3 R10. The team agrees that this particular requirement was just revised. The team disagrees with the suggestion to change the applicability of this Requirement to from "Generator Operator" to "Generator Operator with a Blackstart Resource" because this Requirement could be applicable to more Generator Operators than just those with Blackstart Resources. R16 is intended to be more broadly applicable to any Generator Operator that has been requested to participate in its Reliability Coordinator’s restoration drills, exercises, or simulations [which could include a non-Blackstart generator (such as a cranked generator or a nuclear generator that relies on the system restoration plan to restore off-site power sources to it)]. A non-Blackstart generator (such as a cranked generator or a nuclear generator) could have a role to play in a restoration plan and, in accordance with EOP-005-3 R2, the Transmission Operator would provide the Generator Operators of such a facility with a description of their role(s) and specific task(s) in the plan. | Retire w/ modification | Combine R16 with R10 as follows: Each Transmission Operator and Generator Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. There is not much of a gain in efficiency to move the applicable entity to another similar requirement. The performance remains and it would be a burden for entities to update their internal processes.
EOP-005-3 | R2. | Each Transmission Operator shall provide the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the implementation date of the plan. | Operations Planning | Future | MEDIUM | No Action | Course of Action: Leave as-is with no modification. Justification: The SER Operations Planning team agrees that this particular requirement was just revised and there is no need for further action. | Retire w/ modification | R2 should be combined with R1. See R1 above.
EOP-005-3 | R3. | Each Transmission Operator shall review its restoration plan and submit it to its Reliability Coordinator annually on a mutually-agreed, predetermined schedule. | Operations Planning | Future | MEDIUM | No Action | Course of Action: No Action Justification: The SER Operations Planning team recommends that during the next Standard Review that EOP-005 and EOP-006 be reviewed for consistency between the standards. For example, the "review" requirements (EOP-005 R3 and EOP-006 R3). The SER teams does not agree that EOP-005-3, R3 is the same as EOP-011-1, R3 as suggested by one respondent. EOP-005-3, R3 is about reviewing the restoration plan (and contains no references to the NERC-defined "Emergency" term) and EOP-011-1, R3 is about the operating plan review of Operating Plan(s) to mitigate operating Emergencies [NERC Glossary definition of "Emergency" - Any abnormal system condition that requires automatic or immediate manual action to prevent or limit the failure of transmission facilities or generation supply that could adversely affect the reliability of the Bulk Electric System"]. Finally, the SER team does not believe this is a candidate for the NERC Certification Program. | No Action | No action recommended.
EOP-005-3 | R4. | Each Transmission Operator shall submit its revised restoration plan to its Reliability Coordinator for approval, when the revision would change its ability to implement its restoration plan, as follows: 4.1. Within 90 calendar days after identifying any unplanned permanent BES modifications. 4.2. Prior to implementing a planned permanent BES modification subject to its Reliability Coordinator approval requirements per EOP-006. | Operations Planning | Future | MEDIUM | No Action | Course of Action: No Action Justification: The SER Operations Planning team agrees that this requirement was recently revised and is important enough to be retained as-is with no modification. The team also discussed the possibility that EOP-005-3 R3 and R4 can be combined together and we recommend that this be further investigated by the Standard Review team. As noted in our comment for EOP-005-3 R3, the SER team does not agree with the comment that this requirement is redundant with EOP-011-1, R3. EOP-005-3, R4 deals with restoration, while EOP-011-1 R3 deals with Operating Plan(s) to mitigate operating Emergencies. The team disagrees with the suggestion to change the applicability in 4.1.2 from "Generator Operator" to "Generator Operator with a Blackstart Resource" because one of the EOP-005-3 Requirements (R16) could be applicable to more Generator Operators than just those with Blackstart Resources. Although the text of the Requirements R6 through R15 each specifies "each Generator Operator with a Blackstart Resource" -- R16 does not because it is intended to be more broadly applicable to any Generator Operator that has been requested to participate in its Reliability Coordinator’s restoration drills, exercises, or simulations [which could include a non-Blackstart generator (such as a cranked generator)]. | No Action | No action recommended.
EOP-005-3 | R5. | Each Transmission Operator shall have a copy of its latest Reliability Coordinator approved restoration plan within its primary and backup control rooms so that it is available to all of its System Operators prior to its effective date. | Operations Planning | Future | LOWER | No Action | Course of Action: No Action Justification: The SER Operations Planning team recommends that during the next Standard Review that EOP-005 and EOP-006 be reviewed for consistency between the standards. For example, EOP-005 R5 and EOP-006 R6. The SER Operations Planning team agrees that this requirement was recently revised, however the team does agree with those respondents who suggest that the availability of the restoration plan at the primary and backup control rooms should be part of the NERC Certification program and should remain in the Standard. For the same reason that we noted in our comments for EOP-005-3 R3 and R4, the SER team does not agree that this requirement should be added to the EOP-011-1 standard -- EOP-005-3 deals with restoration, while EOP-011-1 deals with Operating Plan(s) to mitigate operating Emergencies. Based on the majority of responses from the SER Matrix we recommend the following. Recommendations for EOP-005 R5 and EOP-006 R6 need to be consistent | No Action | No action recommended.
EOP-005-3 | R7. | Each Transmission Operator shall have Blackstart Resource testing requirements to verify that each Blackstart Resource is capable of meeting the requirements of its restoration plan. These Blackstart Resource testing requirements shall include: 7.1. The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. 7.2. A list of required tests including: 7.2.1. The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. 7.2.2. The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. 7.3. The minimum duration of each of the required tests. | Operations Planning | Future | MEDIUM | No Action | Course of Action: No Action Justification: The SER Operations Planning team agrees that this requirement was recently revised. The team believes the requirement is appropriately focused on Blackstart Resource Testing to assure that it is capable of meeting the requirements of is restoration plan and should not be expanded to include key facilities like batteries and synchroscope. | No Action | No action recommended.
EOP-005-3 | R8. | Each Transmission Operator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall include training on the following: 8.1. System restoration plan including coordination with the Reliability Coordinator and Generator Operators included in the restoration plan. 8.2. Restoration priorities. 8.3. Building of cranking paths. 8.4. Synchronizing (re-energized sections of the System). 8.5. Transition of Demand and resource balance within its area to the Balancing Authority. | Operations Planning | Future | MEDIUM | Retirement | Course of Action: Retirement Justification: The SER Operations Planning team believes this requirement should be retired because the related compliance activities are duplicative of the activities covered by the Systematic Approach to Training within the PER Standards. The team also agrees that the requirement to provide at least two-hours of training is arbitrary. The training objective should be to assure thorough training such that System Operators are certified and competent to perform restoration activities. At minimum, as noted in the SER Operations Planning team comments on EOP-005-3 R8, we agree that EOP-006-3 R7 requirement can be retired and the content from this requirement transferred into PER-005-2 (and eventually into PER-005-3 when PER-005-3 is approved and becomes mandatory). The SER teams believes that system restoration would certainly fall within an entity's systematic approach to developing and implementing a training program for its System Operators and system restoration would very likely be included within the entity's reliability-related task list. As a general matter, the SER Operations Planning team believes that having a training requirement embedded within another standard other than a PER standard creates the opportunity for confusion and administrative duplication. | No Action | Transfer this requirement to PER-005 to consolidate training requirements to be covered within an entity's systematic approach to training. This recommendation is central to Concept 4 currently being evaluated by the Phase 2 team. Consider holding pending the outcome of their decision.
EOP-005-3 | R9. | Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall provide a minimum of two hours of System restoration training every two calendar years to their field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks. | Operations Planning | Future | MEDIUM | No Action | Course of Action: No Action Justification: The SER Operations Planning team believes this requirement should be retained but the team also agrees that the requirement to provide at least two-hours of training is arbitrary and should be reviewed by the next Standard Review team. | No Action | No action recommended.
EOP-006-3 | R1. | Each Reliability Coordinator shall have a Reliability Coordinator Area restoration plan. The scope of the Reliability Coordinator’s restoration plan starts when Blackstart Resources are utilized to re-energize a shut down area of the Bulk Electric System (BES), or separation has occurred between neighboring Reliability Coordinators, or an energized island has been formed on the BES within the Reliability Coordinator Area. The scope of the Reliability Coordinator’s restoration plan ends when all of its Transmission Operators are interconnected and it its Reliability Coordinator Area is connected to all of its neighboring Reliability Coordinator Areas. The restoration plan shall include: 1.1. A description of the high-level strategy to be employed during restoration events for restoring the Interconnection, including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. 1.2. Criteria and conditions for re-establishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. 1.3. Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. 1.4. Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. 1.5. Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. 1.6. . Criteria for transferring operations and authority back to the Balancing Authority. | Operations Planning and Real-Time Operations | Future | HIGH | No Action | Although there may be opportunity for improvement through modifications of the requirement, there is minimal support or justification for retirement or consolidation of R1 into other requirements. Violation Risk Factor = High. The SER Operations Planning team disagrees with the comment that the part of the R1 requirement pertaining to when the implementation of the Reliability Coordinator's restoration is considered to be completed is too restrictive. The focus of the EOP-006-3 standard is "restoring the Interconnection" and so the statement within R1 that the "scope of the Reliability Coordinator’s restoration plan ends when all of its Transmission Operators are interconnected and its Reliability Coordinator Area is connected to all of its neighboring Reliability Coordinator Areas" is appropriate. Restoration plan objectives would always include restoring the Interconnection and could also include other objectives such as restoring off-site power to nuclear plants. After these stated objectives are achieved, restoration of any remaining unserved load within the Reliability Coordinator Area would continue. The implementation of the Reliability Coordinator's restoration plan is considered complete when the stated objectives have been met (not necessarily when all remaining unserved load is restored). | No Action | No action recommended.
EOP-006-3 | R2. | The Reliability Coordinator shall distribute its most recent Reliability Coordinator Area restoration plan to each of its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of creation or revision. | Operations Planning | Future | LOWER | No Action | There is minimal support or justification for retirement or consolidation into other requirements. The SER Operations Planning team does not believe this is a candidate for the NERC Certification Program. | No Action | No action recommended.
EOP-006-3 | R3. | Each Reliability Coordinator shall review its restoration plan within 13 calendar months of the last review. | Operations Planning | Future | MEDIUM | No Action | The SER Operations Planning team recommends that during the next Standard Review that EOP-005 and EOP-006 be reviewed for consistency between the standards. For example, the "review" requirements (EOP-005 R3 and EOP-006 R3). | No Action | No action recommended.
EOP-006-3 | R4. | Each Reliability Coordinator shall review its neighboring Reliability Coordinator’s restoration plans and provide written notification of any conflicts discovered during that review within 60 calendar days of receipt. 4.1. If a Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved within 30 calendar days of receipt of written notification. | Operations Planning | Future | MEDIUM | No Action | There is no support or justification for retirement or consolidation. | No Action | No action recommended.
EOP-006-3 | R5. | Each Reliability Coordinator shall review the restoration plans required by EOP-005 of the Transmission Operators within its Reliability Coordinator Area. 5.1. The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall approve or disapprove, with stated reasons, the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. | Operations Planning | Future | MEDIUM | No Action | There is minimal support or justification for retirement or consolidation into other requirements. The SER Operations Planning team does not agree that EOP-005-3 R5 is redundant with EOP-011-1 R3. EOP-005-3 deals with restoration, while EOP-011-1 deals with Operating Plan(s) to mitigate operating Emergencies. as described in the industry comment provided. | No Action | No action recommended.
EOP-006-3 | R6. | Each Reliability Coordinator shall have a copy of its latest restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area within its primary and backup control rooms so that it is available to all of its System Operators prior to the implementation date. | Operations Planning | Future | LOWER | No Action | The SER Operations Planning team recommends that during the next Standard Review that EOP-005 and EOP-006 be reviewed for consistency between the standards. For example, EOP-005 R5 and EOP-006 R6. | No Action | No action recommended.
EOP-006-3 | R7. | Each Reliability Coordinator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall address the following: 7.1. The coordination role of the Reliability Coordinator; and 7.2. Re-establishing the Interconnection. | Operations Planning | Future | MEDIUM | Retirement | The SER Operations Planning team believes this requirement should be retired because the related compliance activities are duplicative of the activities covered by the Systematic Approach to Training within the PER Standards. The SER teams believes that system restoration would certainly fall within an entity's systematic approach to developing and implementing a training program for its System Operators and system restoration would very likely be included within the entity's reliability-related task list. The attributes of the PER training should cover the tasks in EOP-006 R1. | No Action | Retain. Transfer this requirement to PER-005 to consolidate training requirements to be covered within an entity's systematic approach to training. This recommendation is central to Concept 4 currently being evaluated by the Phase 2 team. Consider holding pending the outcome of their decision.1.
EOP-006-3 | R8. | Each Reliability Coordinator shall conduct two System restoration drills, exercises, or simulations per calendar year, which shall include the Transmission Operators and Generator Operators as dictated by the particular scope of the drill, exercise, or simulation that is being conducted. 8.1. Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least once every two calendar years. | Operations Planning | Future | MEDIUM | No Action | There is minimal support or justification for retirement or consolidation into other requirements. The SER Operations Planning team after discussion does not agree that EOP-006-3 R8 is too broad, so we do not think that a modification is warranted -- it is appropriately scoped because all TOPs and GOPs identified in the plan would be expected to have certain roles or tasks. | No Action | No action recommended.
EOP-008-2 | R1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. This Operating Plan for backup functionality shall include the following, at a minimum: [See standard for what the Operating Plan shall include] | Operations Planning | Future | MEDIUM | Modification | Justification: The team recommends that this requirement be retained and considered for modification/ consolidation as outlined in R2 and R5 below. We have no objection to the SAR also addressing consistency as discussed in the comments to result in consistency in regard to: "Plans to be developed, maintained and implemented". (See R2 and R5 for potential modification) | No Action | Retain. No action recommended. See comments in R2 and R5. This recommendation is central to Concept 6 currently being evaluated by the Phase 2 team. Consider holding pending the outcome of their decision.
EOP-008-2 | R2. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a copy of its current Operating Plan for backup functionality available at its primary control center and at the location providing backup functionality. | Operations Planning | Future | LOWER | Transfer | Justification: The team recommends that this requirement be retired with the following modification to R1. Consolidation with R1 as described or similar language. Entities commented that R2 should be retired and/or become part of NERC Certification programs. The team is not convinced that transfer of requirements to the NERC Certification Program is in the best interest of the industry or reliability. SAR guidance: R2 can be eliminated by adding the following (in red) to R1: Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan, located in the Primary Control Center and at the location providing backup functionality describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. | Retire w/ modification | Recommend retiring with modification. Modify EOP-008-2, Requirement R1 to address having a copy of the current Operating Plan at the location providing the backup functionality. For example: "R1: Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan, located in the Primary Control Center and at the location providing backup functionality describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost." Update the VSL as necessary. Retire. The activities described in R2 are basic administrative expectations and implied within the requirement for an entity to have an Operating Plan. If necessary, these activities can be covered as part of the entity's Control Center reviews associated with the Organizational Certification and Registration Process and/or periodic on-site compliance audits. This recommendation is central to Concept 6 currently being evaluated by the Phase 2 team. Consider holding pending the outcome of their decision.
EOP-008-2 | R3. | Each Reliability Coordinator shall have a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards that depend on primary control center functionality. To avoid requiring a tertiary facility, a backup facility is not required during: [See standard for situations where a backup facility is not required] | Operations Planning | Future | HIGH | No Action | Justification: This requirement is applicable only to the RC with the nuance that a RC entity unlike other entities needs to maintain full control of the backup facility. Following review of comments the SER Sub group team recommends no changes. | No Action | No action recommended.
EOP-008-2 | R4. | Each Balancing Authority and Transmission Operator shall have backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) that includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that depend on a Balancing Authority and Transmission Operator’s primary control center functionality respectively. To avoid requiring tertiary functionality, backup functionality is not required during: [See standard for situations where a backup facility is not required] | Operations Planning | Future | HIGH | No Action | Justification: Following review of comments the SER Sub group team recommends no changes. | No Action | No action recommended.
EOP-008-2 | R5. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall annually review and approve its Operating Plan for backup functionality. [See standard for update and approval requirements] | Operations Planning | Future | MEDIUM | Transfer | Justification: The team recommends that this requirement be retired with the following modification to R1. Consolidation with R1 as described or via similar language. Entities commented that R2 should be retired and/or become part of NERC Certification programs. The team is not convinced that transfer of requirements to the NERC Certification Program is in the best interest of the industry or reliability. A number of entities believe R5 should be can be eliminated or combined with R1. SAR Guidance: The team recommends this requirement be included within R1 and not stand as a separate requirement by changing R1 as outlined here or similar. R1: Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current (reviewed annually at minimum) Operating Plan, located in the Primary Control Center and at the location providing backup functionality describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. | Retire w/ modification | Recommend retiring with modification. Modify EOP-008-2, Requirement R1 to address conducting an annual review and approval. For example, "R1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current (reviewed and approved within 60 days of a change and annually at minimum) Operating Plan, located in the Primary Control Center and at the location providing backup functionality describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. Update the VSL as needed. Retire. The activities described in R5 are basic administrative expectations and implied within the language of R1 for an entity to have a "current" Operating Plan, including the internal processes for addressing changes (Part 1.3).
EOP-008-2 | R6. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have primary and backup functionality that do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. | Operations Planning | Future | MEDIUM | No Action | Justification: Following review of comments the SER Sub group team recommends no changes. Entities suggested merging with R3. Although possible R3 only has within the requirement scope the Reliability Coordinator BUCC. We considered the change from "compliance with Reliability Standards" to "required to maintain reliability" (as suggested in comments). It is difficult to measure the latter in comparison to having capability to maintain compliance. | No Action | No action recommended.
EOP-008-2 | R7. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct and document results of an annual test of its Operating Plan that demonstrates: [See standard for what the annual test shall demonstrate] | Operations Planning | Future | MEDIUM | No Action | Justification: Following review of comments and the content, realizing that testing periodically is in the interest of BES reliability the SER Sub group team recommends no changes. | No Action | No action recommended.
EOP-008-2 | R8. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of its primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide a plan to its Regional Entity within six calendar months of the date when the functionality is lost, showing how it will re-establish primary or backup functionality. | Operations Planning | Future | MEDIUM | No Action | Justification: Following review of comments the SER Sub group team recommends no changes. | No Action | No action recommended.
EOP-010-1 | R1. | Each Reliability Coordinator shall develop, maintain, and implement a GMD Operating Plan that coordinates GMD Operating Procedures or Operating Processes within its Reliability Coordinator Area. At a minimum, the GMD Operating Plan shall include: [Please see the Standard for more information] | Long Term Planning, Operations Planning, Same Day Operations, and Real-time Operations | Active | MEDIUM | Modification | EOP-011-1, R1 requires TOPs to implement RC Operating Plans. Requirement R1 could be expanded to include that RC’s develop, maintain, and implement GMD Operating Plans. NOTE: Operations Planning SER Team recommended No Action be taken on this requirement as there was no or minimal support for retirement or consolidation. The SER Operations Planning team recommends EOP-010-1 R1 be transferred to EOP-011-1 R1 to consolidate operating plans into one standard. | No Action | No action. The industry suggested this requirement could be consolidated with EOP-011. However, the Phase 1 Operations Planning team recommended no action. I don't think it's worth the effort to pursue consolidation.
EOP-010-1 | R2. | Each Reliability Coordinator shall disseminate forecasted and current space weather information to functional entities identified as recipients in the Reliability Coordinator's GMD Operating Plan. | Same Day Operations and Real-time Operations | Active | MEDIUM | Transfer | Dissemination of forecasted and current space weather information to recipients of the RC GMD Operating Plan provides no reliability benefit as these entities can obtain this information from public sources such as NOAA. This obligation should be included as a sub-requirement of the GMD Operating Plan to be included in EOP-011-1. Industry Comments: MRO NSRF - This is for situational awareness only and may be a mitigating feature of R1. If one K warning is not sent out, it becomes a non compliance issue. This is also covered in EOP-011-1, R1.2.1. Recommend this Requirement be retired. Alternatively, impactful GMD events are well known and publicized. Clarify entities may show compliance by exception for high risk notifications only. There are many low risk events to track and few high risk events. Zero defect auditing could require entities track all space weather notifications. TAPS - This is for situational awareness only and may be a mitigating feature of R1. If one K warning is not sent out, it becomes a non compliance issue. This is also covered in EOP-011-1, R1.2.1. NOTE: GMD Task Force is working on EOP-010-1 and the TPL standards. | No Action | No action. The industry suggested EOP-010 R2 is not needed for reliability since it's public information. However, it's tied to the RC's emergency plan. Therefore, I'm not sure it's worth the effort to attempt retirement or consolidation. This topic is central to Concept 5 currently being evaluated by the Phase 2 team. Consider holding pending the outcome of their decision.
EOP-010-1 | R3. | Each Transmission Operator shall develop, maintain, and implement a GMD Operating Procedure or Operating Process to mitigate the effects of GMD events on the reliable operation of its respective system. At a minimum, the Operating Procedure or Operating Process shall include: [Please see the Standard for more information] | Long Term Planning, Operations Planning, Same Day Operations, and Real-time Operations | Active | MEDIUM | Modification | Sub-requirement EOP-011-1, R1.2 requires TOPs to develop processes to prepare for and mitigation Emergencies. Longterm Planning believes GMD events could be added to this sub-requirement. The SER Operations Planning team recommends EOP-010-1 R3 be transferred to EOP-011-1 R1 to consolidate operating plans into one standard. Industry Comments: City Utilities/Midwest Energy/SECI - This is a basic functional obligation of a TOP and could be retired and verified in a periodic review/spot check within the NERC Certification Program or consolidated with EOP-011 R1. Another recommendation is consolidating/combining with EOP-011-1 R1 (as a sub requirement 1.2.x) MRO NSRF - R3.1 is contained in R1. Alternatively, Clarify entities may show compliance by exception for high risk notifications only. There are many low risk events to track and few high risk events. Zero defect auditing could require entities prove a negative. This increases compliance burden without a corresponding increase in system reliability. TAPS - R3.1 is contained in R1. Per part 3.1, this will force the TOP to prove a negative if they did not receive any space weather information. Part 3.2 starts the mitigating processes for GMD events and part 3.3 concludes them. Part 3.1 is administrative in nature as alone does not accomplish anything, part 3.2 and part 3.3 mitigate the GMD. Recommend part 3.1 be retired. If not retired, part 3.1 should be modified to clearly state in the requirements or measures that proof of compliance is to show the steps only and entities are not required to prove a null set of data. NOTE: The SER Operations Planning team recommends EOP-010-1 R3 be transferred to EOP-011-1 R1 to consolidate operating plans into one standard. | No Action | No action. The industry and the Phase 1 Operations Planning team recommended EOP-010 R3 could be consolidated with EOP-011 R1.2. I'm not sure it's worth the effort to pursue consolidation given the topic.
EOP-011-1 | R1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: [Please see the Standard for more information] | Operations Planning | Active | HIGH | Modification | The SER Operations Planning team agrees that this particular requirement was just revised. The team recommends modification to include EOP-010-1 R1 and R3 as subrequirements of EOP-011-1 R1. Industry Comments: MRO NSRF/TAPS - R1.1 does not enhance or enforce reliability, it is only an auditable item. R1.2.2, R1.2.3, R1.2.4, R1.2.5, and R1.2.6 are all actions or event types that require actions. These are all event specific. The Operating plan will just say that the operator will do something to mitigate these event. Then it becomes an auditable item in the Operating Plan, only. R1 is simple enough. Have a plan for emergencies. Recommend sub-components be retired. NOTE: Operations Planning SER Team noted that EOP-011-1 was revised 11/19/15 and that Sub-requirement R1.2.5 should be modified to define the amount of overlap with automatic load shedding. | No Action | No action. See comments to EOP-010 R1 & R3.
EOP-011-1 | R1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: [Please see the Standard for more information] | Long Term Planning, Operations Planning, and Real-time Operations | Active | HIGH | No Action | Requirement R1 requires TOPs to develop, maintain, and implement Operating Plans to mitigate operating emergencies. Recommended that EOP-010-1, R1 and R3 be consolidated into EOP-011-1, R1 as well. Industry Comments: MRO NSRF/TAPS - R1.1 does not enhance or enforce reliability, it is only an auditable item. R1.2.2, R1.2.3, R1.2.4, R1.2.5, and R1.2.6 are all actions or event types that require actions. These are all event specific. The Operating plan will just say that the operator will do something to mitigate these event. Then it becomes an auditable item in the Operating Plan, only. R1 is simple enough. Have a plan for emergencies. Recommend sub-components be retired. NOTE: Operations Planning SER Team noted that EOP-011-1 was revised 11/19/15 and that Sub-requirement R1.2.5 should be modified to define the amount of overlap with automatic load shedding. | No Action | No action recommended.
EOP-011-1 | R2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: [Please see the Standard for more information] | Operations Planning | Active | HIGH | Modification | The SER Operations Planning team agrees that this particular requirement was just revised, however, based on entity feedback, the team agrees with the recommendation to Modify R2.2.8 to more clearly define the amount of acceptable overlap with automatic load shed. (i.e., Part 2.2.8 should specify the minimum percentage of total load within the Transmission Operator Area that must be addressed through operator-controlled manual load shedding that does not overlap with automatic load shedding). | PRT | Recommend for Periodic Review and if other modifications are needed, because EOP-011-1, Requirement R1, Part 1.2.5. uses the word "minimizes," which is not measurable. To correct, consider modifying EOP-011-1, Requirement R2, Part 2.2.8 to eliminate the word "minimizes" and in place requires identification of the acceptable amount of overlap with automatic load shed. For example, "2.5.8. Provisions for operator-controlled manual Load shedding that minimizes defines the acceptable amount of overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and"
EOP-011-1 | R2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: [Please see the Standard for more information] | Long Term Planning, Operations Planning, and Real-time Operations | Active | HIGH | No Action | Requirement R2 requires BAs to develop, maintain, and implement Operating Plans to mitigate Capacity Emergencies and Energy Emergencies within its BAA. These obligations support reliability. Industry Comments: MRO NSRF/TAPS - R2.1 does not enhance or enforce reliability, it is only an auditable item. R2.2.3 and its parts and R2.2.4, R2.2.5, R2.2.6, R2.2.7, R2.2.8 and R2.2.9 are all actions or event types that require actions. These are all event specific. The Operating plan will just say that the operator will do something to mitigate these events. Then it becomes an auditable item in the Operating Plan. R1 is simple enough. Have a plan for emergencies. Recommend sub components be retired. NOTE: Operations Planning SER Team noted that EOP-011-1 was revised 11/19/15 and that Sub-requirement R2.2.8 should be modified to define the amount of overlap with automatic load shedding. | No Action | No action recommended.
EOP-011-1 | R3 | The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. [Please see the Standard for more information] | Operations Planning | Active | HIGH | No Action | The SER Operations Planning team agrees that this particular requirement was just revised and there is no need for further action. Therefore, leave this requirement as-is with no modification and no retirement. The SER Operations Planning team does not agree with the suggestion to require that the BAs and TOPs follow the RC's Operating Plan. Although this option would always be available to BAs and TOPs if agreement on such a course of action was reached with the RC, it should not be required (the standard should not preclude the option of a BA or TOP developing its own Operating Plan). | No Action | No action recommended.
EOP-011-1 | R4 | Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. | Operations Planning | Active | HIGH | Modification | The SER Operations Planning team disagrees that EOP-011-1 R4 can be deleted. This requirement for the TOP and BA to address reliability risks identified by the RC is a necessary complement to EOP-011-1 R3 Part 3.1.3. The team recommends modifying the language of this requirement to clarify the ability for the TOP or BA to request additional time necessary to effectively respond to the RC's concerns. (See EEI comments) | No Action | No action. Although this could be clarified, it does not result in a reduction of requirements the expectations need to be clarified and allow flexibility for longer lead-time changes. For example, modify as follows: "R4. Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by mutually agreed upon with its Reliability Coordinator.
EOP-011-1 | R5. | Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. | Real-time Operations | Active | HIGH | Modification | Keep requirement, but remove 30 minute timeframe. Notification will occur within this timeframe, and it does not support reliability. RCIS is a blast notification and will occur quickly. 30 minute timeline does not support reliability and is more of an auditing function. Industry Comments: MRO_NSRF/TAPS - This is in line with R4, as this is common sense. The RC will act immediately on all emergency notifications. The time frame of 30 minutes only become an auditable point and does not support reliability. Recommend that the 30 minute mark be deleted at least. HydroQuebec - All notifications could be placed in a single standard. RCIS notification should exempt RC from EOP-004 reporting. | No Action | EOP-011 was revised by Cold Weather SDT;
EOP-011-1 | R6. | Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. | Real-time Operations | Active | HIGH | No Action | Industry Comments: HydroQuebec - All notifications could be placed in a single standard. RCIS notification should exempt RC from EOP-004 reporting. MRO_NSRF - The RC will act immediately on all emergency notifications. Recommend retirement of this Requirement. TAPS - This is clearly stated in the Functional model under Real Time actions and does not need to be contained here; the RC will act immediately on all emergency notifications. Recommend retirement of this Requirement. | No Action | No action recommended.
FAC-001-3 | R1. | Each Transmission Owner shall document Facility interconnection requirements, update them as needed, and make them available upon request. Each Transmission Owner’s Facility interconnection requirements shall address interconnection requirements for 1.1. generation Facilities; 1.2. transmission Facilities; and 1.3. end-user Facilities. | Long Term Planning | Future | LOWER | Transfer | This Requirement should be transferred to a potential TO certification program and as a required procedure; or in a reliability guideline. The requirement is administrative in nature and causes the TO to perform a minimal to no risk activity that does not contribute to reliable operations. | No Action | No action recommended.
FAC-001-3 | R2. | Each applicable Generator Owner shall document Facility interconnection requirements and make them available upon request within 45 calendar days of full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | Long Term Planning | Future | LOWER | Transfer | Proposed justification to be determined. Review industry feedback pertaining to this requirement. If this process or certification is used in a market area the market interconnection process will be used but if its not a market area there may be an issue. | No Action | No action recommended.
FAC-001-3 | R3. | Each Transmission Owner shall address the following items in its Facility interconnection requirements: [Please see the Standard for more information] | Long Term Planning | Future | LOWER | Transfer | This Requirement should be transferred to a potential TO certification program and as a required procedure; or in a reliability guideline. The requirement is administrative in nature and causes the TO to perform a minimal to no risk activity that does not contribute to reliable operations. | No Action | No action recommended.
FAC-001-3 | R4. | Each applicable Generator Owner shall address the following items in its Facility interconnection requirements: [Please see the Standard for more information] | Long Term Planning | Future | LOWER | Transfer | Proposed justification to be determined. Review industry feedback pertaining to this requirement. If this process or certification is used in a market area the market interconnection process will be used but if its not a market area there may be an issue. | No Action | No action recommended.
FAC-002-2 | R1. | Each Transmission Planner and each Planning Coordinator shall study the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities and (ii) materially modifying existing interconnections of generation, transmission, or electricity end-user Facilities. The following shall be studied: [Please see the Standard for more information] | Long Term Planning | Active | MEDIUM | Modification | Justification to be determined in phase two of the SER Project. | No Action | No action recommended.
FAC-002-2 | R2. | Each Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | Long Term Planning | Active | MEDIUM | No Action |  | No Action | No action recommended.
FAC-002-2 | R3. | Each Transmission Owner, each Distribution Provider, and each Load-Serving Entity seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4 | Long Term Planning | Active | MEDIUM | Modification | i. Remove Load Serving Entity from the applicable entities and other parts of the standard. | No Action | No action. Project 2018-03 will address the LSE. There is no appetite to open TPL-001. At a minimum: Remove the LSE from the Applicability and other parts of the standard. Options: 1. Recommend removing the LSE 2. Refer the LSE removal to the Standards Alignment with Registration Project 2018-03. 3. Consider augmenting TPL-001, which could lead to retirement of FAC-002.
FAC-002-2 | R4. | Each Transmission Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested new or materially modified interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | Long Term Planning | Active | MEDIUM | Modification | Consolidate R4 into R3 | No Action | No action. The only way to consolidate would be to say that each TO and DP will coordinate and cooperate with their TP or PC on studies regarding requested new or materially modified interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. But I presume that DPs would never have to cooperate on studies that do not pertain to their new or modified interconnection and this would make it sound like they do. Team agrees to not modify b/c R4 addresses other entities other than the requester.
FAC-002-2 | R5. | Each applicable Generator Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | Long Term Planning | Active | MEDIUM | No Action |  | No Action | No action recommended.
FAC-003-4 | R1. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the Minimum Vegetation Clearance Distance (MVCD) of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below [Please see the Standard for more information] | Real-time Operations | Active | HIGH | Consolidate | Merge FAC-003-4 R1 and R2. Commenters observed that the only difference between the two requirements was the acknowledgement of whether the transmission line was associated with an IROL or and element of a Major WECC Transfer Path. There was no difference in the way to measure compliance, however it could be expected that different enforcement actions may take place. This however should not have warranted a separate requirement. | Refer to Project 2015-09 | Consolidate. Merge R1 and R2 and remove references to whether the line is an element of an IROL or WECC Transfer Path. Project 2015-09 SDT retired Requirement R2 and R1 was retained.
FAC-003-4 | R2. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below [Please see the Standard for more information] | Real-time Operations | Active | HIGH | Consolidate | Merge FAC-003-4 R1 and R2. Commenters observed that the only difference between the two requirements was the acknowledgement of whether the transmission line was associated with an IROL or and element of a Major WECC Transfer Path. There was no difference in the way to measure compliance, however it could be expected that different enforcement actions may take place. This however should not have warranted a separate requirement. | Refer to Project 2015-09 | Recommend retiring with modification. Agree to merge R1 and R2 and remove references to whether the line is an element of an IROL or WECC Transfer Path and consolidate R1/R2. Project 2015-09 SDT retired R2.
FAC-003-4 | R3. | Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: [Please see the Standard for more information] | Long Term Planning | Active | LOWER | Retirement | R1 and R2 fulfil the purpose of the standard through measurable actions. R3 is merely a control and duplicative in nature. Removal of R3 does not pose a risk to BES as long as R1 & R2 remain. This requirement appear to be more administrative of Good Utility Practice for vegetation management inside the ROW and do not provide any further protection for BES reliability over what R1 and R2 does. | No Action | No action recommended.
FAC-003-4 | R4. | Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment | Real-time Operations | Active | MEDIUM | No Action | This Requirement does have reliability implications that should continued to be observed. | No Action | No action recommended.
FAC-003-4 | R5. | When an applicable Transmission Owner and an applicable Generator Owner are constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments | Operations Planning | Active | MEDIUM | Retirement | R1 and R2 fulfil the purpose of the standard through measurable actions. R5, R6, and R7 are merely controls and duplicative in nature. Removal of R5, R6, and R7 do not pose a risk to BES as long as R1 & R2 remain. These three requirements appear to be more administrative of Good Utility Practice for vegetation management inside the ROW and do not provide any further protection for BES reliability over what R1 and R2 does. Further the NERC ROP allows for Force Majeur consideration. | No Action | No action. due to industry wanting this as an alternative to not meeting the work plan. There was a lot of discussion during the initial meetings and there did not appear to be consensus that industry wanted these "get out of jail free cards" to go away. But in the end, I do see that they were put in the initial list for retirements. The Phase 1 team removed them from their final list.
FAC-003-4 | R6. | Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW | Operations Planning | Active | MEDIUM | Retirement | R1 and R2 fulfil the purpose of the standard through measurable actions. R5, R6, and R7 are merely controls and duplicative in nature. Removal of R5, R6, and R7 do not pose a risk to BES as long as R1 & R2 remain. These three requirements appear to be more administrative of Good Utility Practice for vegetation management inside the ROW and do not provide any further protection for BES reliability over what R1 and R2 does. | No Action | FAC-003-4 objective is to prevent vegetation encroachment and R6 is one element of how you do that, which is a control under Concept 6 of the efficiency concepts SER Phase II.
FAC-003-4 | R7. | Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). Examples of reasons for modification to annual plan may include [Please see the Standard for more information] | Operations Planning | Active | MEDIUM | Retirement | R1 and R2 fulfil the purpose of the standard through measurable actions. R5, R6, and R7 are merely controls and duplicative in nature. Removal of R5, R6, and R7 do not pose a risk to BES as long as R1 & R2 remain. These three requirements appear to be more administrative of Good Utility Practice for vegetation management inside the ROW and do not provide any further protection for BES reliability over what R1 and R2 does. | No Action | FAC-003-4 objective is to prevent vegetation encroachment and R7 is one element of how you do that, which is a control under Concept 6 of the efficiency concepts SER Phase II.
FAC-008-3 | R1. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. [See standard for documentation requirements] | Long Term Planning | Active | LOWER | No Action |  | No Action | No action recommended.
FAC-008-3 | R2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. [See standard for methodology requirements] | Long Term Planning | Active | MEDIUM | No Action |  | No Action | No action recommended.
FAC-008-3 | R3. | Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: [See standard for methodology requirements] | Long Term Planning | Active | MEDIUM | No Action |  | No Action | No action recommended.
FAC-008-3 | R6. | Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. | Operations Planning | Active | MEDIUM | Modification | R6 is implied by the fact that via MOD-032 and other standards, the TO and GO will have to provide the facility ratings thus you do not need a requirement explicitly stating that the TO and GO have to have facility ratings. TOP-003 and IRO-010 data specifications can also require that the data be provided to the TOP/RC | No Action | Retain. This requirement is the only place where the application of the methodology is applied. R7/R8, where the actual redundant sharing is cited is already slated for retirement in Phase 1. MOD-032 is an all-encompassing ask of model data. It is not practical to add "ratings developed according to methodology" to just these values. R6 does not involve providing data to anyone, so TOP-003 and IRO-010 are not suitable justifications.
FAC-008-3 | R7. | Each Generator Owner shall provide Facility Ratings (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities. | Operations Planning | Active | MEDIUM | Retirement | FAC-008-3 R7 is redundant in nature when compared to other data sharing standards such as MOD-032, IRO-010, and TOP-003. In order for the RC and TOP to comply with FAC-014 data must be shared between the GO and RC/TOP and between the TO and RC/TOP. FAC-008-3 R7 can be retired without negatively impacting the reliability of the BES. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
FAC-008-3 | R8. | Each Transmission Owner (and each Generator Owner subject to Requirement R2) shall provide requested information as specified below (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s): [See standard for requirements of providing requested information] | Operations Planning | Active | MEDIUM | Retirement | FAC-008-3 R8 are redundant in nature when compared to other data sharing standards such as MOD-032, IRO-010, and TOP-003. In order for the RC and TOP to comply with FAC-014 data must be shared between the GO and RC/TOP and between the TO and RC/TOP. FAC-008-3 R8 can be retired without negatively impacting the reliability of the BES. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
FAC-010-3 | R1. | The Planning Authority shall have a documented SOL Methodology for use in developing SOLs within its Planning Authority Area. This SOL Methodology shall: [Please see the Standard for more information] | Long Term Planning | Active | LOWER | Retirement | Project 2015-09 SDT is proposing to retire FAC-010-3. Recommend we defer to the SDT's recommendation | Refer to Project 2015-09 | No action. Project 2015-09 Retiring
FAC-010-3 | R2. | The Planning Authority’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: [Please see the Standard for more information] | Long Term Planning | Active | HIGH | Retirement | Project 2015-09 SDT is proposing to retire FAC-010-3. Recommend we defer to the SDT's recommendation | Refer to Project 2015-09 | No action. Project 2015-09 Retiring
FAC-010-3 | R3. | The Planning Authority’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: [Please see the Standard for more information] | Long Term Planning | Active | LOWER | Retirement | Project 2015-09 SDT is proposing to retire FAC-010-3. Recommend we defer to the SDT's recommendation | Refer to Project 2015-09 | No action. Project 2015-09 Retiring
FAC-010-3 | R4. | The Planning Authority shall issue its SOL Methodology, and any change to that methodology, to all of the following prior to the effectiveness of the change: [Please see the Standard for more information] | Long Term Planning | Active | LOWER | Retirement | Project 2015-09 SDT is proposing to retire FAC-010-3. Recommend we defer to the SDT's recommendation | Refer to Project 2015-09 | No action. Project 2015-09 Retiring
FAC-011-3 | R1. | The Reliability Coordinator shall have a documented methodology for use in developing SOLs (SOL Methodology) within its Reliability Coordinator Area. This SOL Methodology shall: [Please see the Standard for more information] | Long Term Planning | Active | LOWER | Transfer | The SDT is currently reviewing this standard we propose to defer to the recommendations of Project 2015-09 SDT | Refer to Project 2015-09 | No action. Deferring to the team of Project 2015-09.
FAC-011-3 | R2. | The Reliability Coordinator’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: [Please see the Standard for more information] | Long Term Planning | Active | NONE | Transfer | The SDT is currently reviewing this standard we propose to defer to the recommendations of Project 2015-09 SDT | Refer to Project 2015-09 | No action. Deferring to the team of Project 2015-09.
FAC-011-3 | R3. | The Reliability Coordinator’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: [Please see the Standard for more information] | Long Term Planning | Active | MEDIUM | Transfer | The SDT is currently reviewing this standard we propose to defer to the recommendations of Project 2015-09 SDT | Refer to Project 2015-09 | No action. Deferring to the team of Project 2015-09.
FAC-011-3 | R4. | The Reliability Coordinator shall issue its SOL Methodology and any changes to that methodology, prior to the effectiveness of the Methodology or of a change to the Methodology, to all of the following: [Please see the Standard for more information] | Long Term Planning | Active | LOWER | Transfer | The SDT is currently reviewing this standard we propose to defer to the recommendations of Project 2015-09 SDT | Refer to Project 2015-09 | No action. Deferring to the team of Project 2015-09.
FAC-013-2 | R1. | Each Planning Coordinator shall have a documented methodology it uses to perform an annual assessment of Transfer Capability in the Near-Term Transmission Planning Horizon (Transfer Capability methodology). The Transfer Capability methodology shall include, at a minimum, the following information: [Please see the Standard for more information] | Long Term Planning | Active | MEDIUM | Retirement | FAC-013 duplicates the general purpose of the TPL standard – to determine whether an entity has enough resources and capacity to adequately serve its load in the planning horizon. A Transfer Capability analysis is valuable in the operations horizon, which is currently covered by MOD-001 for operations. FAC-013 tries to parallel what is done in the operations timeframe into the planning timeframe. But there is not a need or value for this in the planning timeframe because the TPL study is already analyzing the system ability to support load and contractual transfers. Having two Standards requiring the same activity or task does little, if anything, to benefit or protect the reliable operation of the BES because it is duplicative. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
FAC-013-2 | R2. | Each Planning Coordinator shall issue its Transfer Capability methodology, and any revisions to the Transfer Capability methodology, to the following entities subject to the following: [Please see the Standard for more information] | Long Term Planning | Active | LOWER | Retirement | FAC-013 duplicates the general purpose of the TPL standard – to determine whether an entity has enough resources and capacity to adequately serve its load in the planning horizon. A Transfer Capability analysis is valuable in the operations horizon, which is currently covered by MOD-001 for operations. FAC-013 tries to parallel what is done in the operations timeframe into the planning timeframe. But there is not a need or value for this in the planning timeframe because the TPL study is already analyzing the system ability to support load and contractual transfers. Having two Standards requiring the same activity or task does little, if anything, to benefit or protect the reliable operation of the BES because it is duplicative. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
FAC-013-2 | R4. | During each calendar year, each Planning Coordinator shall conduct simulations and document an assessment based on those simulations in accordance with its Transfer Capability methodology for at least one year in the Near-Term Transmission Planning Horizon. | Long Term Planning | Active | MEDIUM | Retirement | FAC-013 duplicates the general purpose of the TPL standard – to determine whether an entity has enough resources and capacity to adequately serve its load in the planning horizon. A Transfer Capability analysis is valuable in the operations horizon, which is currently covered by MOD-001 for operations. FAC-013 tries to parallel what is done in the operations timeframe into the planning timeframe. But there is not a need or value for this in the planning timeframe because the TPL study is already analyzing the system ability to support load and contractual transfers. Having two Standards requiring the same activity or task does little, if anything, to benefit or protect the reliable operation of the BES because it is duplicative. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
FAC-013-2 | R5. | Each Planning Coordinator shall make the documented Transfer Capability assessment results available within 45 calendar days of the completion of the assessment to the recipients of its Transfer Capability methodology pursuant to Requirement R2, Parts 2.1 and Part 2.2. However, if a functional entity that has a reliability related need for the results of the annual assessment of the Transfer Capabilities makes a written request for such an assessment after the completion of the assessment, the Planning Coordinator shall make the documented Transfer Capability assessment results available to that entity within 45 calendar days of receipt of the request | Long Term Planning | Active | LOWER | Retirement | FAC-013 duplicates the general purpose of the TPL standard – to determine whether an entity has enough resources and capacity to adequately serve its load in the planning horizon. A Transfer Capability analysis is valuable in the operations horizon, which is currently covered by MOD-001 for operations. FAC-013 tries to parallel what is done in the operations timeframe into the planning timeframe. But there is not a need or value for this in the planning timeframe because the TPL study is already analyzing the system ability to support load and contractual transfers. Having two Standards requiring the same activity or task does little, if anything, to benefit or protect the reliable operation of the BES because it is duplicative. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
FAC-013-2 | R6. | If a recipient of a documented Transfer Capability assessment requests data to support the assessment results, the Planning Coordinator shall provide such data to that entity within 45 calendar days of receipt of the request. The provision of such data shall be subject to the legal and regulatory obligations of the Planning Coordinator’s area regarding the disclosure of confidential and/or sensitive information. | Long Term Planning | Active | LOWER | Retirement | FAC-013 duplicates the general purpose of the TPL standard – to determine whether an entity has enough resources and capacity to adequately serve its load in the planning horizon. A Transfer Capability analysis is valuable in the operations horizon, which is currently covered by MOD-001 for operations. FAC-013 tries to parallel what is done in the operations timeframe into the planning timeframe. But there is not a need or value for this in the planning timeframe because the TPL study is already analyzing the system ability to support load and contractual transfers. Having two Standards requiring the same activity or task does little, if anything, to benefit or protect the reliable operation of the BES because it is duplicative. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
FAC-014-2 | R1. | The Reliability Coordinator shall ensure that SOLs, including Interconnection Reliability Operating Limits (IROLs), for its Reliability Coordinator Area are established and that the SOLs (including Interconnection Reliability Operating Limits) are consistent with its SOL Methodology. | Long Term Planning | Active | MEDIUM | Transfer | The SDT is currently reviewing this standard we propose to defer to the recommendations of Project 2015-09 SDT | Refer to Project 2015-09 | No action. Deferring to the team of Project 2015-09.
FAC-014-2 | R2. | The Transmission Operator shall establish SOLs (as directed by its Reliability Coordinator) for its portion of the Reliability Coordinator Area that are consistent with its Reliability Coordinator’s SOL Methodology. | Long Term Planning | Active | MEDIUM | Transfer | The SDT is currently reviewing this standard we propose to defer to the recommendations of Project 2015-09 SDT | Refer to Project 2015-09 | No action. Deferring to the team of Project 2015-09.
FAC-014-2 | R3. | The Planning Authority shall establish SOLs, including IROLs, for its Planning Authority Area that are consistent with its SOL Methodology. | Long Term Planning | Active | MEDIUM | Transfer | The SDT is currently reviewing this standard we propose to defer to the recommendations of Project 2015-09 SDT | Refer to Project 2015-09 | No action. Deferring to the team of Project 2015-09.
FAC-014-2 | R4. | The Transmission Planner shall establish SOLs, including IROLs, for its Transmission Planning Area that are consistent with its Planning Authority’s SOL Methodology. | Long Term Planning | Active | MEDIUM | Transfer | The SDT is currently reviewing this standard we propose to defer to the recommendations of Project 2015-09 SDT | Refer to Project 2015-09 | No action. Deferring to the team of Project 2015-09.
FAC-014-2 | R5. | The Reliability Coordinator, Planning Authority and Transmission Planner shall each provide its SOLs and IROLs to those entities that have a reliability-related need for those limits and provide a written request that includes a schedule for delivery of those limits as follows: [Please see the Standard for more information] | Long Term Planning | Active | HIGH | Transfer | The SDT is currently reviewing this standard we propose to defer to the recommendations of Project 2015-09 SDT | Refer to Project 2015-09 | No action. Deferring to the team of Project 2015-09.
FAC-014-2 | R6. | The Planning Authority shall identify the subset of multiple contingencies (if any), from Reliability Standard TPL-003 which result in stability limits. [Please see the Standard for more information] | Long Term Planning | Active | MEDIUM | Transfer | The SDT is currently reviewing this standard we propose to defer to the recommendations of Project 2015-09 SDT | Refer to Project 2015-09 | No action. Deferring to the team of Project 2015-09.
INT-004-3.1 | R1. | Each Purchasing-Selling Entity that secures energy to serve Load via a Dynamic Schedule or Pseudo-Tie shall ensure that a Request for Interchange is submitted as an on-time Arranged Interchange to the Sink Balancing Authority for that Dynamic Schedule or Pseudo-Tie, unless the information about the Pseudo-Tie is included in congestion management procedure(s) via an alternate method. (see footnote on standard) | Operations Planning and Same Day Operations | Active | LOWER | Retirement | This requirement is no longer enforceable as the Purchasing Selling Entity is no longer a NERC registered function. The INT Periodic Review Team completed their analysis and determined the requirement is duplicative of the NAESB business practice standards. Covered in existing NAESB WEQ-004-1 and WEQ-004-5 and in proposed NAESB WEQ-004-1.8. Requirement R1: (1) IERP recommended for retirement and (2) duplicative because (a) language leading to the submittal of all RFI, which includes Dynamic Schedules and Pseudo-Ties, is contained in existing NAESB WEQ-004-1 and WEQ-004-5; and (b) the remaining element of Requirement R1, when Pseudo-Ties may be excluded, is contained in the NAESB proposed WEQ-004-1.8. The Independent Expert Review Team recommended the requirement be retired. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
INT-004-3.1 | R2. | R2. The Purchasing-Selling Entity that submits a Request for Interchange in accordance with Requirement R1 shall ensure the Confirmed Interchange associated with that Dynamic Schedule or Pseudo-Tie is updated for future hours in order to support congestion management procedures if any one of the following occurs: 2.1. For Confirmed Interchange greater than 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 10% for that hour and that deviation is expected to persist. 2.2. For Confirmed Interchange less than or equal to 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 25 MW for that hour and that deviation is expected to persist. 2.3. The Purchasing-Selling Entity receives notification from a Reliability Coordinator or Transmission Operator to update the Confirmed Interchange. | Operations Planning, Same Day Operations, and Real-time Operations | Active | LOWER | Retirement | This requirement is no longer enforceable as the Purchasing Selling Entity is no longer a NERC registered function. The INT Periodic Review Team completed their analysis and determined the requirement is duplicative of a currently proposed revision to the NAESB. duplicative as the language in R2 that requires Confirmed Interchange associated with Dynamic Schedules or Pseudo-Ties be updated for future hours when any of the three the conditions cited in the requirement occur is contained almost verbatim in the proposed NAESB WEQ-004-23. business practice standards. The Independent Expert Review Team recommended the requirement be retired. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
INT-004-3.1 | R3. | Each Balancing Authority shall only implement or operate a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication in order to support congestion management procedures. | Operations Planning | Active | LOWER | Retirement | The SER Team and industry comments support the conclusion of the INT Periodic Review Team who concluded this requirement should be retired. This requirement qualifies for Paragraph 81 retirement as it obligates entities to report to NAESB, an industry forum for wholesale electric standards, on activities which have no discernible impact on promoting the reliable operation of the BES and if the entity failed to meet this requirement there would be little reliability impact. The pseudo-tie coordination is already guided and more clearly explained within the NERC Pseudo-Tie Coordination Reference Document. RC visibility to Pseudo-Ties is allowed under existing NERC Reliability Standard IRO-010-2 Requirement R2. Therefore, this requirement is redundant and does little, if anything, to benefit or protect the reliable operation of the BES. Additionally, it is contained on the list of standards not commonly identified through an IRA process. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
INT-006-4 | R1. | Each Balancing Authority shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. 1.1. Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. 1.2. Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. | Operations Planning, Same Day Operations, and Real-time Operations | Active | LOWER | Modification | The undefined and ambiguous terms “emergency” and “on-time” in Requirements R1 can be removed from the requirements as they bring no reliability benefit to the requirement. In addition, the term “Reliability Assessment” be reintegrated into the requirement as it is the reliability task being performed in these requirements, as noted in the Purpose, not merely the task of approving or denying the Arranged Interchange. INT-006-4 R1 could also be combined with INT-006-4 R2 and INT-009-2.1 R1 for a single requirement on approved interchanges. NOTE: Ops Planning - The SER Team and industry comments support the conclusion of the INT Periodic Review Team to retain this requirement and make minimal modifications listed in that team's report. | PRT | Recommend for Periodic Review and if other modifications are needed, because the tables make no distinction on "emergency" Arranged Interchange. For example, "R1. Each Balancing Authority shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B." Keep Requirement R1, Parts 1.1 and 1.2.
INT-006-4 | R2. | Each Transmission Service Provider shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. [Please see the standard for more information] | Operations Planning, Same Day Operations, and Real-time Operations | Active | LOWER | Modification | The undefined and ambiguous terms “emergency” and “on-time” in Requirements R2 can be removed from the requirements as they bring no reliability benefit to the requirement. In addition, the term “Reliability Assessment” be reintegrated into the requirement as it is the reliability task being performed in these requirements, as noted in the Purpose, not merely the task of approving or denying the Arranged Interchange. INT-006-4 R1 could also be combined with INT-006-4 R2 and INT-009-2.1 R1 for a single requirement on approved interchanges. | PRT | Recommend for Periodic Review and if other modifications are needed, because the tables make no distinction on "emergency" Arranged Interchange. For example, "R1. Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it responded to each request for its approval to transition an Arranged Interchange to a Confirmed Interchange within the time defined in Attachment 1, Column B." Keep Requirement R2, Part 2.1.
INT-006-4 | R3. | The Source Balancing Authority and the Sink Balancing Authority receiving a Reliability Adjustment Arranged Interchange shall approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B. 3.1. If a Balancing Authority denies a Reliability Adjustment Arranged Interchange, the Balancing Authority must communicate that fact to its Reliability Coordinator no more than 10 minutes after the denial. | Operations Planning, Same Day Operations, and Real-time Operations | Active | LOWER | Modification | This will need to be updated to reflect the retirement of Requirement R3, Part 3.1 The SER Ops Planning Team and industry comments support the conclusion of the INT Periodic Review Team to retain requirement R3. | Modify | Modify. Each Balancing Authority shall agree with each of its Adjacent Balancing Authorities that its Composite Confirmed Interchange with that Adjacent Balancing Authority, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo-Ties is: 1.1. Identical in magnitude to that of the Adjacent Balancing Authority, and 1.2. Opposite in sign or direction to that of the Adjacent Balancing Authority.
INT-006-4 | R3.1 | If a Balancing Authority denies a Reliability Adjustment Arranged Interchange, the Balancing Authority must communicate that fact to its Reliability Coordinator no more than 10 minutes after the denial. | Operations Planning | Active | LOWER | Retirement | The SER Team and industry comments support the conclusion of the INT Periodic Review Team who concluded this requirement should be retired. The INT PRT found little to no effect on reliability in requiring the RC being notified when a Reliability Adjustment Arranged Interchange has been denied. Additionally, RCs are notified via the electronic tag when a Reliability Adjustment Arranged Interchange is denied, as required in the NAESB e-Tagging Specifications. Therefore, this requirement is redundant and requires Responsible Entities to conduct an activity that does little, if anything, to benefit or protect the reliable operation of the BES. Additionally, it is contained on the list of standards not commonly identified through an IRA process. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
INT-006-4 | R4. | Each Sink Balancing Authority shall confirm that none of the following conditions exist prior to transitioning an Arranged Interchange to Confirmed Interchange: [Please see the standard for more information] | Operations Planning | Active | LOWER | Retirement | The SER Team and industry comments support the conclusion of the INT Periodic Review Team who concluded this requirement should be retired as it is duplicative of the NAESB e-Tagging Specifications and is not a reliability related task performed by a Responsible Entity. Additionally, it is contained on the list of standards not commonly identified through an IRA process. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
INT-006-4 | R5. | For each Arranged Interchange that is transitioned to Confirmed Interchange, the Sink Balancing Authority shall notify the following entities of the on-time Confirmed Interchange such that the notification is delivered in time to be incorporated into scheduling systems prior to ramp start as specified in Attachment 1, Column D: [Please see the standard for more information] | Operations Planning | Active | LOWER | Retirement | The SER Team and industry comments support the conclusion of the INT Periodic Review Team who concluded this requirement should be retired as it is duplicative of the NAESB e-Tagging Specifications and is not a reliability related task performed by a Responsible Entity. Covered in NAESB e-Tagging specifications, Section 1.6.4. Additionally, it is contained on the list of standards not commonly identified through an IRA process. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
INT-009-2.1 | R1. | R1. Each Balancing Authority shall agree with each of its Adjacent Balancing Authorities that its Composite Confirmed Interchange with that Adjacent Balancing Authority, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange per INT-010-2 not yet captured in the Composite Confirmed Interchange, is: 1.1. Identical in magnitude to that of the Adjacent Balancing Authority, and 1.2. Opposite in sign or direction to that of the Adjacent Balancing Authority. | Real-time Operations | Active | MEDIUM | Modification | Requirement R1 would need to be revised to remove references to INT-010-2.1 and develop language to address interchange transactions that are related to reliability events but are not yet Confirmed Interchange. INT-006-4 R1 could also be combined with INT-006-4 R2 and INT-009-2.1 R1 for a single requirement on approved interchanges, a recommendation of the PRT on Project 2017-04. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
INT-009-2.1 | R2. | The Attaining Balancing Authority and the Native Balancing Authority shall use a dynamic value emanating from an agreed upon common source to account for the Pseudo-Tie in the Actual Net Interchange (NIA) term of their respective control ACE (or alternate control process). | Real-time Operations | Active | MEDIUM | Retirement | This can be retired under Paragraph 81 criteria, as the requirement is redundant with approved NERC Reliability Standard BAL-005-1, Requirement R7. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
INT-009-2.1 | R3. | Each Balancing Authority in whose area the high-voltage direct current tie is controlled shall coordinate the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. | Operations Planning and Real-Time Operations | Active | MEDIUM | No Action | The SER Team and industry comments support the conclusion of the INT Periodic Review Team to retain requirement R3. | No Action | No action recommended.
INT-010-2.1 | R1. | The Balancing Authority that experiences a loss of resources covered by an energy sharing agreement or other reliability needs covered by an energy sharing agreement shall ensure that a Request for Interchange (RFI) is submitted with a start time no more than 60 minutes beyond the resource loss. If the use of the energy sharing agreement does not exceed 60 minutes from the time of the resource loss, no RFI is required. | Real-time Operations | Active | LOWER | Retirement | INT-010-2.1, R1 may be retired under Paragraph 81 Criteria B6 and B7, due to their inclusion in the NAESB Business Practice Standards with more stringent tagging requirements already exist in NAESB WEQ-004-1. Therefore, this requirement is duplicative and does little, if anything, to benefit or protect the reliable operation of the BES. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
INT-010-2.1 | R2. | Each Sink Balancing Authority shall ensure that a Reliability Adjustment Arranged Interchange reflecting a modification is submitted within 60 minutes of the start of the modification if a Reliability Coordinator directs the modification of a Confirmed Interchange or Implemented Interchange for actual or anticipated reliability-related reasons. | Real-time Operations | Active | LOWER | Retirement | INT-010-2.1, R2 may be retired under Paragraph 81 Criteria B6 and B7, due to their inclusion in the NAESB Business Practice Standards with more stringent tagging requirements already exist in NAESB WEQ-004-8. Therefore, this requirement is duplicative and does little, if anything, to benefit or protect the reliable operation of the BES. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
INT-010-2.1 | R3. | Each Sink Balancing Authority shall ensure that a Request for Interchange is submitted reflecting that Interchange Schedule within 60 minutes of the start of the scheduled Interchange if a Reliability Coordinator directs the scheduling of Interchange for actual or anticipated reliability-related reasons. | Real-time Operations | Active | LOWER | Retirement | INT-010-2.1, R3 may be retired under Paragraph 81 Criteria B6 and B7, due to their inclusion in the NAESB Business Practice Standards with more stringent tagging requirements already exist in NAESB WEQ-004-1. Therefore, this requirement is duplicative and does little, if anything, to benefit or protect the reliable operation of the BES. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
IRO-001-4 | R1. | Each Reliability Coordinator shall act to address the reliability of its Reliability Coordinator Area via direct actions or by issuing Operating Instructions | Same Day Operations and Real-time Operations | Active | HIGH | No Action | 2 comments support retirement based on "basic functionality" argument 5 comments supporting non-retirement | No Action | No action recommended.
IRO-001-4 | R2. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall comply with its Reliability Coordinator’s Operating Instructions unless compliance with the Operating Instructions cannot be physically implemented or unless such actions would violate safety, equipment, regulatory, or statutory requirements. | Same Day Operations and Real-time Operations | Active | HIGH | Modification | 2 votes supporting retirement 6 votes nay RCs do not communicate directly with DPs nor, typically w/ GOPs. ADDRESS IN CONJUNCTION WITH COM-001-3. Does not align with COM-001-3, R1-R6. If it is intended that the RC have Interpersonal Communication capability with the TOP and BA, and (in turn) the TOP and BA have Interpersonal Communication capability with the DP and GOP, consider deleting the DP and GOP from IRO-001-4. Alternatively, require the RC to have Interpersonal Communication capability with the DP and GOP under COM-001-3, R1 and the DP and GOP to have Interpersonal Communication capability with the RC under COM-001-3, R7 and R8. | Modify | Recommend modifying. Remove the DP and GOP applicable entities from IRO-001-4, Requirement R2 since TOP-001-4, Requirement, R3 requires that the DP and GOP comply with Operating Instructions from the TOP. This also aligns with COM-001-3 for communications capability. May not be supported, IRO is RC and TOP is TOP/BA, TOP-001 doesn't say RC.
IRO-001-4 | R3. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall inform its Reliability Coordinator of its inability to perform the Operating Instruction issued by its Reliability Coordinator in Requirement R1. | Same Day Operations and Real-time Operations | Active | HIGH | Modification | Concerns about double jeopardy when entity issuing OI is registered both RC and BA. Also, R3 is implicit in R2. One comment concerned that the receiving entity is responsible for informing if not able to perform the instruction ADDRESS IN CONJUNCTION WITH COM-001-3. Does not align with COM-001-3, R1-R6. If it is intended that the RC have Interpersonal Communication capability with the TOP and BA, and (in turn) the TOP and BA have Interpersonal Communication capability with the DP and GOP, consider deleting the DP and GOP from IRO-001-4. Alternatively, require the RC to have Interpersonal Communication capability with the DP and GOP under COM-001-3, R1 and the DP and GOP to have Interpersonal Communication capability with the RC under COM-001-3, R7 and R8. | Modify | Recommend modifying. Remove the DP and GOP applicable entities from IRO-001-4, Requirement R3 since TOP-001-4, Requirement, R3 requires that the DP and GOP comply with Operating Instructions from the TOP. This also aligns with COM-001-3 for communications capability. May not be supported, IRO is RC and TOP is TOP/BA, TOP-001 doesn't say RC.
IRO-002-5 | R1. | Each Reliability Coordinator shall have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | Operations Planning | Active | MEDIUM | Retirement | The requirement is solely a control for aiding compliance with IRO-008-2 R1 related to the performance of an Operational Planning Analysis (OPA) and it is duplicative to requirements R3 in IRO-010-2. The NERC Glossary of Terms definition of OPA requires certain data to be used for the analysis performed under IRO-008-2 R1 and standard IRO-010-2 requires the RC to identify the data it needs to perform its OPA (R1), which entities need to provide such data (R2), and then obligates those registered entities to then supply the data (R3). For an entity to fulfill IRO-010-2 R3, it must be able to exchange data with the requesting RC. Additionally, to comply with IRO-008-2 R1, the RC must have received all of the data it needs to perform the OPA. Finally, the measure (M1) for IRO-002-5 R1 states that an entity merely needs to show a piece of paper describing its data exchange capabilities with other entities, which is solely administrative in nature. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
IRO-002-5 | R2. | Each Reliability Coordinator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing its Real-time monitoring and Real-time Assessments. | Same Day Operations and Real-time Operations | Active | HIGH | Modification | 2 comments for Retirement/4 votes nay ... 3 votes for Modify/3 votes nay. "diversely routed" is not defined and has led to confusion between entities and RE compliance auditing personnel. While the Rationale stated by the SDT seems clear, Compliance personnel in different regions appear to be applying varying criteria in their assessments. The term "diversely routed" should be clarified and added either to the glossary or the Requirement could be modified to clarify the concept. NOTE - this needs to be coordinated with TOP-001-4 R20 and IRO-002-5 R3 "MODIFY ""diversely routed"" is not defined and has led to confusion between entities and RE compliance auditing personnel. Not a lot of support for retirement" | No Action | CMEP practice guide posted on the NERC site named Determination of "Redundant" and "Diversely Routed"
IRO-002-5 | R3. | Each Reliability Coordinator shall test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Reliability Coordinator shall init | Operations Planning | Active | MEDIUM | Transfer | Full group discussion needed. Discussed at 4/3/18 meeting. IRO sub-team reviewing further. R3 of IRO-002-5 acts as a control for R2 of IRO-002-5. Requirement R3 should be moved into the Certification process and the certification process should confirm that the entity has internal controls to (1) monitor the health and status of its data exchange capabilities and/or (2) test and recover its data exchange. Note that, by requiring entities to test every 90 days, the requirement does not protect real time reliability because a loss of redundancy event can occur between the 90 day tests. In such an event, the RC would need to recover from the event quickly to continue operation, regardless of this requirement. | No Action | No action recommended.
IRO-002-5 | R4. | Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Operations Planning, Same Day Operations, and Real-time Operations | Active | HIGH | Retirement | This authority is inherent in IRO-017-1. If there is concern about a gap in coverage of that Standard, a Requirement could be added to IRO-017-x to include this category in the outage coordination Process This requirement can be retired because the authority to approve/deny outages to any equipment, whether load carrying or not, is a fundamental attribute of the system operator role. This was recognized by NERC and FERC in Project 2007-03 where the authority language in former Standard TOP-001-1 R1 was removed from the revised TOP standards approved by both NERC and FERC. Developed because of 2011 Southwest blackout concerns. Perhaps instead make a capability-based attribute for certification. VSL is binary. Further this requirement does not address the problem noted in relationship to the 2011 blackout; could potentially be addressed in IRO-018. Need to check the Issues and Directives related to earlier version IRO-002-2 RETIRE in Phase 1 - in Phase 2 ... figure out what's actually needed, | No Action | No action recommended.
IRO-002-5 | R5. | Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Real-time Operations | Active | HIGH | No Action | There was a comment recommending modification, but no real justification. This Requirement seems clear with no justification for action. MODIFY possible clarity to be gained in scope of monitoring neighboring RC Area although it would appear to read that monitoring scope would be limited to what would impact IROLs within the RC's own Area. | No Action | No action recommended.
IRO-002-5 | R6. | Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | Real-time Operations | Active | HIGH | Retirement | This is covered in R5 & R2. The requirement to monitor (R5) pre-supposes the ability (tools) to do so. "Redundant infrastructure" is captured in R2. EMS and other tools are evaluated during the RC Certification and re-certification process. (5 industry comments supporting this position, 3 opposed to retirement) RETIRE covered in R5 supra | No Action | No action recommended.
IRO-006-5 | R1. | Each Reliability Coordinator and Balancing Authority that receives a request pursuant to an Interconnection-wide transmission loading relief procedure (such as Eastern Interconnection TLR, WECC Unscheduled Flow Mitigation, or congestion management procedures from the ERCOT Protocols) from any Reliability Coordinator, Balancing Authority, or Transmission Operator in another Interconnection to curtail an Interchange Transaction that crosses an Interconnection boundary shall comply with the request, unless it provides a reliability reason to the requestor why it cannot comply with the request. | Real-time Operations | Active | HIGH | Retirement | The communication and coordination aspects of this Requirement are covered in IRO-014 R1, R3, R4, R5, and especially R6 & R7. RCs across interconnection boundaries could direct BAs (since IRO-014 is RC only). NOTE IRO-006-EAST, -TRE, & -WECC should remain active (modified as appropriate?). RETIRE covered in IRO-014 R1, R6, & R7 as well as IRO-006-EAST; -TRE; -WECC | PRT | Was not Retired as part of the initial Project 2018-03 SER Retirements
IRO-008-2 | R1. | Each Reliability Coordinator shall perform an Operational Planning Analysis that will allow it to assess whether the planned operations for the next-day will exceed System Operating Limits (SOLs) and Interconnection Operating Reliability Limits (IROLs) within its Wide Area. | Operations Planning | Active | MEDIUM | No action | Retain as is | No Action | No action recommended.
IRO-008-2 | R2. | Each Reliability Coordinator shall have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational | Operations Planning | Active | MEDIUM | No action | Retain as is | No Action | No action recommended.
IRO-008-2 | R3. | Each Reliability Coordinator shall notify impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). | Operations Planning | Active | MEDIUM | Modification | The coordination of Operating Plans due to the OPA will occur as a result of R2. The purpose of the standard is fulfilled in other requirements of IRO-008. R3 could be considered "How" when performing an OPA where R2 is the "What". By "coordinating" in R2, the RC is essentially "notifying"; can you coordinate without notifying? | No Action | No action recommended.
IRO-008-2 | R4. | Each Reliability Coordinator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | Same Day Operations and Real-time Operations | Active | HIGH | Transfer | This Requirement pertains to basic functionality of Reliability Coordinator, and it can be covered by process review in NERC certification program. In addition, performing real-time assessment without the assurance of good quality will less likely enhance the reliability of the Bulk Electric System. The enforcement of IRO-018-1 R2 “Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments” would ensure both the interval and quality of real-time assessments. Highlights of industry comments: • Entergy, HydroQuebec, and TAPS: Requirement is a candidate for coverage in NERC certification program • Duke Energy: we do not believe that there is sufficient justification for this timeframe from a transmission risk perspective when alternative measures must be taken…. The expectations of these standards also appear to conflict with the current NERC EOP-008-1 R1.5 allowing up to two hours to activate a backup upon the loss of primary control center functionality • MidwestEnergy: IRO-018-1 R2 when implemented will address RTA quality. The quality process could also assure RTA activity in accordance with utility practice (RTA, RTA backup, etc) without a hard Requirement 30 minute compliance threshold. Candidate for NERC certification program. | No Action | No action recommended.
IRO-008-2 | R5. | Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the results of a Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. | Same Day Operations and Real-time Operations | Active | HIGH | No Action | Highlights of industry comments: • Entergy, MidwestEnergy, TAPS, and MISO: Requirement is a candidate for coverage in NERC Certification Program • ISO New England, NPCC, and OntarioIESO: Retain the requirement • HydroQuebec: IRO-014 also has requirements for notifying RC in potential or actual emergency situations. | No Action | No action recommended.
IRO-008-2 | R6. | Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. | Same Day Operations and Real-time Operations | Active | MEDIUM | Retirement | This requirement is more of administrative nature and would not provide any justifiable benefits to system reliability. Alternatively, it can be incorporated into the process review in NERC certification program. Highlights of industry comments: • Entergy: Requirement is a candidate for coverage in NERC certification program • MidwestEnergy, TAPS: This requirement supports R2 and process can be verified through NERC Certification (process review). It could be merged with R2. • ISO New England, OntarioIESO: Retain the requirement • HydroQuebec: IRO-014 also has requirements for notifying RC in potential or actual emergency situations. • MISO: This requirement is an administrative retrospective historical lookback, overly burdensome to comply with, and does nothing to ensure reliability during the operational next-day planning nor real-time operating time horizons and therefore should be retired | No Action | No action recommended.
IRO-009-2 | R1. | For each IROL (in its Reliability Coordinator Area) that the Reliability Coordinator identifies one or more days prior to the current day, the Reliability Coordinator shall have one or more Operating Processes, Procedures, or Plans that identify actions the Reliability Coordinator shall take or actions the Reliability Coordinator shall direct others to take (up to and including load shedding): 1.1. That can be implemented in time to prevent the identified IROL exceedance. 1.2. To mitigate the magnitude and duration of an IROL exceedance such that the IROL exceedance is relieved within the IROL’s Tv. | Operations Planning and Same Day Operations | Active | MEDIUM | Modification | As IRO-008-2 R1 and R2 already cover the identification of IROL exceedances and development of corresponding Operating Plans(s) for next-day operations, IRO-009-2 R1 is redundant. The necessity of acting on projected IROL exceedances multiple days prior to the current day needs to be evaluated by the standard drafting team. It shall be combined with IRO-008 R1 and R2 Highlights of industry comments: • Entergy: Requirement is a candidate for coverage in NERC Certification Program • ISO New England, NPCC, OntarioIESO: Retain the requirement • HydroQuebec: First paragraph could be divided in 2 shorter sentences. • PJM: Documentation and administrative procedure • ERCOT: IRO-009-2 R1 is redundant with IRO-008-2 R2... However, it is not clear that these projected IROL exceedances need to be acted upon ahead of the OPA... In any case, at a minimum, the two requirements could be combined. The main issue with IRO-009 is the interpretation that pre-contingency load shedding is mandated prior to exceeding an N-(x) calculated IROL limit... Definitions of "SOL exceedance" and "IROL exceedance" should be developed to provide much-needed clarity. • MISO: Since IRO-008-2 was extended include SOLs and not just IROLs, there is no reason to have a separate IRO-009 standard that just addresses IROLs. The IROL specific requirements can be included in an all-encompassing standard that requires a quality RTA, that must be performed periodically, and the results of that RTA must be communicated and acted upon by the RC. This could all be done in IRO-018-1, or more realistically, IRO-018, IRO-008, and IRO-009 should all be combined into a new standard. IRO-009-2 R1 should be combined with IRO-008-2 R1. | PRT | Recommend for Periodic Review and if other modifications are needed, combine with IRO-008-2, Requirement R1. For example IRO0-008-2, R1. Each Reliability Coordinator shall preform an Operational Planning Analysis that will allow it to asses whether the planned operations for the next-day will exceed System Operating Limits (SOL) and Interconnection Operating Reliability Limits (IROLs) within its Wide Area and shall have Operating Processes, Procedures, or Plans that will mitigate the IROL and or SOL.
IRO-009-2 | R2. | Each Reliability Coordinator shall initiate one or more Operating Processes, Procedures, or Plans (not limited to the Operating Processes, Procedures, or Plans developed for Requirement R1) that are intended to prevent an IROL exceedance, as identified in the Reliability Coordinator’s Real-time monitoring or Real-time Assessment. | Real-time Operations | Active | HIGH | Modification | IRO-008-2 R5 shall include more actions for Reliability Coordinator to take to cover IRO-009-2 R2. It shall include the action of initiating Operating Processes, Procedures, or Plans to mitigate or prevent IROLs exceedance in addition to notifying the impacted Transmission Operators, Balancing Authorities, and other impacted Reliability Coordinators. The proposed changes would allow for the consolidation of IRO-009-2 R2 and IRO-008-2 R5. Highlights of industry comments: • Entergy: Requirement is a candidate for coverage in NERC Certification Program • ISO New England: It is not possible to implement an Operating Process to "prevent an exceedance;" the exceedance needs to actually occur before it is cleared. In the instance of this Standard, R1 and R3 are sufficient and this requirement is confusing and unnecessary • NPCC, OntarioIESO: Retain • ERCOT: IRO-009-2 R2 should be moved into IRO-008-2 for continuity. Also, as explained under R1, it is unclear whether this requirement is necessary given IRO-008. Definitions of "SOL exceedance" and "IROL exceedance" should be developed to provide much-needed clarity. • MISO: Since IRO-008-2 was extended include SOLs and not just IROLs, there is no reason to have a separate IRO-009 standard that just addresses IROLs. The IROL specific requirements can be included in an all-encompassing standard that requires a quality RTA, that must be performed periodically, and the results of that RTA must be communicated and acted upon by the RC. This could all be done in IRO-018-1, or more realistically, IRO-018, IRO-008, and IRO-009 should all be combined into a new standard. IRO-009-2 R2 should be combined with IRO-008-2 R2. | PRT | Recommend for Periodic Review and if other modifications are needed, combine IRO-009-2, Requirement R2 with IRO-008-2, Requirement R5. For example, Each Reliability Coordinator shall initiate its Operating Processes, Procedures, or Plans developed in R1 and notify impacted Reliability Coordinators, Transmission Operators and Balancing Authorities when the results of a Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within it Wide Area.
IRO-009-2 | R3. | Each Reliability Coordinator shall act or direct others to act so that the magnitude and duration of an IROL exceedance is mitigated within the IROL’s Tv, as identified in the Reliability Coordinator’s Real-time monitoring or Real-time Assessment. | Real-time Operations | Active | HIGH | Modification | Acting or directing other to act to mitigate IROL exceedance is the responsibility of Reliability Coordinator as specified by IRO-001-4 and shall be combined with IRO-008-2 R5 so that the expected actions after the initiation of Operating Processes, Operating Procedures, or Operating Plans by Reliability Coordinators can be specified more clearly. It shall be combined with IRO-008-2 R5 Highlights of industry comments: • Entergy: Requirement is a candidate for coverage in NERC Certification Program • ISO New England, NPCC, OntarioIESO, and SER: Retain • ERCOT: There is a level of redundancy with IRO-001-4 R1 and IRO-008-2 R5, R6. This should also be considered under one IRO-008 umbrella vs a separate standard. • MISO: Since IRO-008-2 was extended include SOLs and not just IROLs, there is no reason to have a separate IRO-009 standard that just addresses IROLs ... IRO-009-2 R3 should be combined with IRO-008-2 R5 | PRT | Recommend for Periodic Review and if other modifications are needed, combine with IRO-008-2, Requirement R5 with IRO-009-2, Requirement. For example in IRO-008-2, R3. Each Reliability Coordinator shall act or direct others to act when the results of a Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operation Limit (SOL) or Interconnection Reliability operating Limit (IROL) exceedance within it Wide Area.
IRO-009-2 | R4. | Each Reliability Coordinator shall operate to the most limiting IROL and Tv in instances where there is a difference in an IROL or its Tv between Reliability Coordinators that are responsible for that Facility (or group of Facilities). | Real-time Operations | Active | HIGH | Modification | Operating to the most limiting IROL and Tv when conflicts exist is considered as a part of neighboring Reliability Coordinators’ coordination process. Therefore, IRO-009-2 R4 suits better under IRO-014-3. Highlights of industry comments: • Entergy: Requirement is a candidate for coverage in NERC Certification Program • NPCC, OntarioIESO: Retain • ERCOT: This requirement is no longer necessary. Coordination between limits including IROLs should be addressed within the FAC standards as well as in IRO-010, TOP-003, and IRO-014. While this was necessary prior to the current standards, coordination limits makes this unnecessary. Essentially every IROL should have one owner that distributes that limits to others. The connotation of more than one IROL creates reliability concerns. • MISO: This requirement should be added to IRO-014-3 which designates the responsibilities between Reliability Coordinators. | PRT | Recommend for Periodic Review and if other modifications are needed, retire IRO-009-2, Requirement R4 and move it to IRO-014-3, Requirement R1. For example, create a new IRO-0014-3, Requirement R1, Part "1.6. Shall operate to the most limiting IROL and Tv in instances where there is a difference between reliability Coordinators."
IRO-010-2 | R1. | The Reliability Coordinator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include but not be limited to: | Operations Planning | Active | LOWER | No Action | No comments raised by industry. SER Team did not identify any justification for retiring or modifying this standard and requirement. | Modify | Recommend for Periodic Review and if other modifications are needed, consider combining the language in IRO-010-2, Requirement R2 with IRO-010-2, Requirement R1 to simplify the standard. For example, modification would eliminate a requirement and create "R1. Each RC shall maintain AND DISTRIBUTE a documented specification…"
IRO-010-2 | R2. | The Reliability Coordinator shall distribute its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Operations Planning | Active | LOWER | Transfer | This requirement is better suited for inclusion in the ERO Certification and Review Procedure. This fundamental organization requirement, ensures each operating entity has the ability to perform reliability tasks to meet basic obligations and maintain BPS reliability. This requirement is purely administrative. Combine the language with R1 by adding "Each RC shall maintain AND DISTRIBUTE a documented specification…". R2 would then be retired. | Retire w/ modification | Retire with Modification and if other modifications are needed, consider combining IRO-010-2, Requirement R2 with Requirement R1. For example a modified Requirement R1 could be, "The Reliability Coordinator shall maintain and distribute to entities that have data required by the Reliability Coordinator, a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include but not be limited to: (Time Horizon: Operations Planning)" Does not see an immediate efficiency gain by consolidating these requirements.
IRO-010-2 | R3. | Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall satisfy the obligations of the documented specifications using: [Please see the standard for more information] | Operations Planning, Same Day Operations, and Real-time Operations | Active | LOWER | Transfer | The requirement regulates a high volume of low risk activity, and it doesn’t has any significant justifiable benefits for reliability. It can be included in certification program as it is a fundamental organization requirement to enable Reliability Coordinator to perform its reliability tasks to meet its basic obligations. The proposed change would ensure the data needed for situational awareness and/or real-time assessment can be made available to Reliability Coordinators. In addition, IRO-018-1(i) “Reliability Coordinator Real-time Reliability Monitoring and Analysis Capabilities” can act as a control to support the data specification requirement on a continuous basis. Highlights of industry comments: • ACES, ATC, Entergy, HydroQuebec, MRO_NSRF, TAPS: Requirement regulates a high volume of Low Risk activity • PJM: Documentation and administrative procedure • NPCC, ACES, HydroQuebec, SouthernCo: LSE should be removed. • HydroQuebec: Should include a delay when new or revised data are required by RC. If R2 is retired, rewording of R3 is required. • MidwestEnergy, OklahomaGE, SECI: NERC should combine IRO-010-2 and TOP-003-3/4. Some RTOs are registered as both a BA and a RC. If the RTO provides just one specification (as a BA and RC), it creates a double jeopardy situation for the registered entities. • MRO: Requirement is a candidate for coverage in NERC Certification • OntraioIESO: This requirement is more suited for inclusion in the ERO Certification and Review Procedure instead of a Reliability Standard as it is a fundamental organization requirement to enable the operating entity to perform its reliability tasks to meet its basic obligations. • XcelEnergy: Clarify process for 3.1-3.3 to account for reliability impacts • WAPA: TOP-010, TOP-003 redundancy • ISO New England: Retain • NEI: NEI-NITF contends that this requirement is difficult to provide evidence for an audit without a requirement that the RC provides specifications directly to the GO/GOP or an attestation that specifications have not been provided | No Action | No action recommended.
IRO-014-3 | R1. | Each Reliability Coordinator shall have and implement Operating Procedures, Operating Processes, or Operating Plans, for activities that require notification or coordination of actions that may impact adjacent Reliability Coordinator Areas, to support Interconnection reliability. These Operating Procedures, Operating Processes, or Operating Plans shall include, but are not limited to, the following: 1.1. Criteria and processes for notifications. 1.2. Energy and capacity shortages. 1.3. Control of voltage, including the coordination of reactive resources. 1.4. Exchange of information including planned and unplanned outage information to support its Operational Planning Analyses and Real-time Assessments. 1.5. Provisions for periodic communications to support reliable operations. | Operations Planning and Same Day Operations | Active | MEDIUM | Modification | Incorporate R 2.1, 2.3 into R1 as a sub requirement. The requirement should be retired as it is only administrative in nature. Requirements R3 through R7 of this standard contain the results-based requirements to maintain reliability. NEEDS FURTHER DISCUSSION Phase I Justification: The SDT believes this requirement should be retained for the following reasons: The reliability objective of “notification” is mandated as a part of the RC having and implementing Operating Procedures, Operating Processes, or Operating Plans that include criteria and processes for notifications (Requirement R1, Part 1.1), this ensures RC operations are coordinated to maintain reliability of the BES. As such, a separate requirement for ensuring notifications are made to impacted RCs is duplicative. However, IRO-014-3, Requirement R1 time horizon would need to be revised to a time horizon of “Real-time” if Requirement R3 were to be retired. Revision of Requirement R1 is outside the scope of the project, so retirement of IRO-014-3, Requirement R3 is not being sought during this phase of the project. SER Phase I team will communicate with the Standards Efficiency Review Phase II team regarding Requirement R3 of IRO-014-3 to determine if there is opportunity for revision to IRO-014-3, Requirement R1 that would satisfy the revision of the time horizon to “Real-time.” If the Standards Efficiency Review Phase II team takes an approach for such determinations and then finds that there is that opportunity, then Requirements R3 of IRO-014-3 may be able to be looked at for retirement within that project or within a future project. | No Action | See IRO-014-3, Requirement R2.
IRO-014-3 | R2. | Each Reliability Coordinator shall maintain its Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 as follows: 2.1. Review and update annually with no more than 15 months between reviews. 2.2. Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. 2.3. Distribute to all Reliability Coordinators that are required | Operations Planning and Same Day Operations | Active | LOWER | Modification | Part of this Requirement is administrative in nature. Requirement 2.1 and 2.3 can be moved into R1. For other NERC Requirements that call for a process or procedures, there is no requirement for obtaining and tracking written agreements. Then R2 can be retired. The requirement should be retired as it is only administrative in nature. Requirements R3 through R7 of this standard contain the results-based requirements to maintain reliability. NEEDS FURTHER DISCUSSION | PRT | Recommend for Periodic Review and if other modifications are needed, Requirement R2 could be retired with the following changes in red to Requirement R1. R1 ensures that there are Operating procedures, processes or plans in place and coordinated (R2) in advance. R3-R7 do not adequately cover this as they cover real-time events. Considering the comments on Requirement R2, the Requirements R1 and R2 should be combined and Requirement R2 retired: R1. Each Reliability Coordinator shall have, implement, and maintain Operating Procedures, Operating Processes, or Operating Plans, for activities that require notification or coordination of actions that may impact adjacent Reliability Coordinator Areas, to support Interconnection reliability. These Operating Procedures, Operating Processes, or Operating Plans shall include, but are not limited to, the following: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same-Day Operations] 1.1. Criteria and processes for notifications. 1.2. Energy and capacity shortages. 1.3. Control of voltage, including the coordination of reactive resources. 1.4. Exchange of information including planned and unplanned outage information to support its Operational Planning Analyses and Real-time Assessments. 1.5. Provisions for periodic communications to support reliable operations. 1.6 Review and update annually with no more than 15 months between reviews. 1.7 Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update.
IRO-014-3 | R3. | Each Reliability Coordinator, upon identification of an expected or actual Emergency in its Reliability Coordinator Area, shall notify other impacted Reliability Coordinators. | Operations Planning, Same Day Operations, and Real-time Operations | Active | MEDIUM | No Action | Notification is part of R1, 1.1 (Ops Planning said retain as is). | No Action | No action recommended.
IRO-014-3 | R4. | Each impacted Reliability Coordinator shall operate as though the Emergency exists during each instance where Reliability Coordinators disagree on the existence of an Emergency. | Operations Planning, Same Day Operations, and Real-time Operations | Active | HIGH | No action | Retain as is | PRT | Recommend for Periodic Review and if other modifications are needed, combine with IRO-014-3, Requirement R4 and R6. For example, "Each Reliability Coordinator that identifies an Emergency shall develop and implement and operate to resolve…." Does not see an immediate efficiency gain by consolidating these requirements.
IRO-014-3 | R5. | Each Reliability Coordinator that Identifies an Emergency in its Reliability Coordinator Area shall develop an action plan to resolve the Emergency during those instances where impacted Reliability Coordinators disagree on the existence of an Emergency. | Operations Planning, Same Day Operations, and Real-time Operations | Active | HIGH | No action | Retain as is | No Action | No action recommended.
IRO-014-3 | R6. | Each impacted Reliability Coordinator shall implement the action plan developed by the Reliability Coordinator that identifies the Emergency during those instances where Reliability Coordinators disagree on the existence of an Emergency, unless such actions would violate safety, equipment, regulatory, or statutory requirements. | Operations Planning, Same Day Operations, and Real-time Operations | Active | HIGH | No action | Retain as is | PRT | Recommend for Periodic Review and if other modifications are needed, combine with IRO-014-3, Requirement R4 and R6. For example, "Each Reliability Coordinator that identifies an Emergency shall develop and implement and operate to resolve…." Does not see an immediate efficiency gain by consolidating these requirements.
IRO-014-3 | R7. | Each Reliability Coordinator shall assist Reliability Coordinators, if requested and able, provided that the requesting Reliability Coordinator has implemented its emergency procedures, unless such actions cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Real-time Operations | Active | HIGH | No Action |  | No Action | No action recommended.
IRO-017-1 | R1. | Each Reliability Coordinator shall develop, implement, and maintain an outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. The outage coordination process shall: 1.1. Identify applicable roles and | Operations Planning | Active | MEDIUM | No action | Retain as is | No Action | No action recommended.
IRO-017-1 | R2. | Each Transmission Operator and Balancing Authority shall perform the functions specified in its Reliability Coordinator’s outage coordination process. | Operations Planning | Active | MEDIUM | Modification | The R2 requirement applies only to Transmission Operators and Balancing Authorities. However, the outage coordination process requires input from, at a minimum, Generator Operators as well. The requirement should be modified to either replace ‘Balancing Authority’ with Generator Operator or the Generator Operator should be listed as well. | PRT | Recommend for Periodic Review and if other modifications are needed, as this is potentially a gap. The Generator Operator should be considered being added to the requirement and that an SME team should review, for example: "R2. Each Transmission Operator, Balancing Authority, and Generator Operator shall perform the functions specified in its Reliability Coordinator’s outage coordination process."
IRO-017-1 | R3. | Each Planning Coordinator and Transmission Planner shall provide its Planning Assessment to impacted Reliability Coordinators. | Long Term Planning | Active | MEDIUM | Retirement | Requirement R3 could be retired due to similar language in TPL-001-4, R8, regarding distribution of the report of the results of the analysis. TPL-001-4, R8, could be modified to include “Reliability Coordinator” in the list of entities in the distribution list. | No Action | Requirement R3 could retired be to similar language in TPL-001-4, R8, regarding distribution of the report of the results of the analysis. TPL-001-4, R8, could be modified to include “Reliability Coordinator” in the list of entities in the distribution list. [Leave as is, IRO-017 relates to the Operations Planning time frame and TPL-001 is based on a Long Term Planning time frame]
IRO-017-1 | R4. | Each Planning Coordinator and Transmission Planner shall jointly develop solutions with its respective Reliability Coordinator(s) for identified issues or conflicts with planned outages in its Planning Assessment for the Near-Term Transmission Planning Horizon. | Long Term Planning | Active | MEDIUM | No Action |  | No Action | No action recommended.
IRO-018-1(i) | R1. | R1. Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: 1.1. Criteria for evaluating the quality of Real-time data; 1.2. Provisions to indicate the quality of Real-time data to the System Operator; and 1.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | Real-time Operations | Future | HIGH | No Action |  | No Action | New Standard
IRO-018-1(i) | R2. | R2. Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] 2.1. Criteria for evaluating the quality of analysis used in its Real-time Assessments; 2.2. Provisions to indicate the quality of analysis used in its Real-time Assessments; and 2.3. Actions to address analysis quality issues affecting its Real-time Assessments. | Real-time Operations | Future | MEDIUM | No Action |  | No Action | New Standard
IRO-018-1(i) | R3. | R3. Each Reliability Coordinator shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | Real-time Operations | Future | MEDIUM | No Action |  | No Action | New Standard
MOD-001-2 | R1 | Each Transmission Operator that determines Total Flowgate Capability (TFC) or Total Transfer Capability (TTC) shall develop a written methodology (or methodologies) for determining TFC or TTC values. The methodology (or methodologies) shall reflect the Transmission Operator’s current practices for determining TFC or TTC values. [Please see the standard for more information] | Operations Planning | Future | LOWER | Retirement | The Operations Planning Team recommends the retirement of MOD-001-1 as adopted by the NERC BOT and filed with FERC in February 2014. Additionally, the Operations Planning Team recommends retiring/revoking MOD-001-2 as adopted by the NERC BOT and filed with FERC in February 2014. The filing notes that ATC/AFC are commercially-based values used to facilitate a market for unused transmission capacity in an open access environment and that the values do not directly control the operation of the BPS. It further acknowledges that TOPs are ultimately responsible for operating the grid in a reliable manner consistent with System Operating Limits, not ATC/AFC values. Nevertheless, the filing proposes MOD-001-2 for approval by FERC indicating ATC/AFC values have the potential to influence Real-time conditions on the Bulk-Power System and impact Real-time operations. Although, ATC/AFC values have the potential to influence Real-Time conditions, the Operations Planning Team recommends retirement of the entire MOD-001-2 standard because ATC/AFC are commercially based values, do not directly control the operation of the BPS, and there are a number of approved Reliability Standards to address potential impacts to Real-time operations and operation of the grid in a reliable manner consistent with System Operation Limits. This includes TOP Reliability Standard improvements that have been filed and approved since the MOD-001-2 filing in February 2014. | Project 2018-03 Retiring | Was not Retired as part of the initial Project 2018-03 SER Retirements
MOD-001-2 | R2 | Each Transmission Service Provider that determines Available Flowgate Capability (AFC) or Available Transfer Capability (ATC) shall develop an Available Transfer Capability Implementation Document (ATCID) that describes the methodology (or methodologies) for determining AFC or ATC values. The methodology (or methodologies) shall reflect the Transmission Service Provider’s current practices for determining AFC or ATC values. | Operations Planning | Future | LOWER | Retirement | The Operations Planning Team recommends the retirement of MOD-001-1 as adopted by the NERC BOT and filed with FERC in February 2014. Additionally, the Operations Planning Team recommends retiring/revoking MOD-001-2 as adopted by the NERC BOT and filed with FERC in February 2014. The filing notes that ATC/AFC are commercially-based values used to facilitate a market for unused transmission capacity in an open access environment and that the values do not directly control the operation of the BPS. It further acknowledges that TOPs are ultimately responsible for operating the grid in a reliable manner consistent with System Operating Limits, not ATC/AFC values. Nevertheless, the filing proposes MOD-001-2 for approval by FERC indicating ATC/AFC values have the potential to influence Real-time conditions on the Bulk-Power System and impact Real-time operations. Although, ATC/AFC values have the potential to influence Real-Time conditions, the Operations Planning Team recommends retirement of the entire MOD-001-2 standard because ATC/AFC are commercially based values, do not directly control the operation of the BPS, and there are a number of approved Reliability Standards to address potential impacts to Real-time operations and operation of the grid in a reliable manner consistent with System Operation Limits. This includes TOP Reliability Standard improvements that have been filed and approved since the MOD-001-2 filing in February 2014. | Project 2018-03 Retiring | Was not Retired as part of the initial Project 2018-03 SER Retirements
MOD-001-2 | R3 | Each Transmission Service Provider that determines Capacity Benefit Margin (CBM) values shall develop a Capacity Benefit Margin Implementation Document (CBMID) that describes its method for determining CBM values. The method described in the CBMID shall reflect the Transmission Service Provider’s current practices for determining CBM values. | Operations Planning | Future | LOWER | Retirement | The Operations Planning Team recommends the retirement of MOD-001-1 as adopted by the NERC BOT and filed with FERC in February 2014. Additionally, the Operations Planning Team recommends retiring/revoking MOD-001-2 as adopted by the NERC BOT and filed with FERC in February 2014. The filing notes that ATC/AFC are commercially-based values used to facilitate a market for unused transmission capacity in an open access environment and that the values do not directly control the operation of the BPS. It further acknowledges that TOPs are ultimately responsible for operating the grid in a reliable manner consistent with System Operating Limits, not ATC/AFC values. Nevertheless, the filing proposes MOD-001-2 for approval by FERC indicating ATC/AFC values have the potential to influence Real-time conditions on the Bulk-Power System and impact Real-time operations. Although, ATC/AFC values have the potential to influence Real-Time conditions, the Operations Planning Team recommends retirement of the entire MOD-001-2 standard because ATC/AFC are commercially based values, do not directly control the operation of the BPS, and there are a number of approved Reliability Standards to address potential impacts to Real-time operations and operation of the grid in a reliable manner consistent with System Operation Limits. This includes TOP Reliability Standard improvements that have been filed and approved since the MOD-001-2 filing in February 2014. | Project 2018-03 Retiring | Was not Retired as part of the initial Project 2018-03 SER Retirements
MOD-001-2 | R4 | Each Transmission Operator that determines Transmission Reliability Margin (TRM) values shall develop a Transmission Reliability Margin Implementation Document (TRMID) that describes its method for determining TRM values. The method described in the TRMID shall reflect the Transmission Operator’s current practices for determining TRM values. | Operations Planning | Future | LOWER | Retirement | The Operations Planning Team recommends the retirement of MOD-001-1 as adopted by the NERC BOT and filed with FERC in February 2014. Additionally, the Operations Planning Team recommends retiring/revoking MOD-001-2 as adopted by the NERC BOT and filed with FERC in February 2014. The filing notes that ATC/AFC are commercially-based values used to facilitate a market for unused transmission capacity in an open access environment and that the values do not directly control the operation of the BPS. It further acknowledges that TOPs are ultimately responsible for operating the grid in a reliable manner consistent with System Operating Limits, not ATC/AFC values. Nevertheless, the filing proposes MOD-001-2 for approval by FERC indicating ATC/AFC values have the potential to influence Real-time conditions on the Bulk-Power System and impact Real-time operations. Although, ATC/AFC values have the potential to influence Real-Time conditions, the Operations Planning Team recommends retirement of the entire MOD-001-2 standard because ATC/AFC are commercially based values, do not directly control the operation of the BPS, and there are a number of approved Reliability Standards to address potential impacts to Real-time operations and operation of the grid in a reliable manner consistent with System Operation Limits. This includes TOP Reliability Standard improvements that have been filed and approved since the MOD-001-2 filing in February 2014. | Project 2018-03 Retiring | Was not Retired as part of the initial Project 2018-03 SER Retirements
MOD-001-2 | R5 | Within 45 calendar days of receiving a written request that references this specific requirement from a Planning Coordinator, Reliability Coordinator, Transmission Operator, Transmission Planner, Transmission Service Provider, or any other registered entity that demonstrates a reliability need, each Transmission Operator or Transmission Service Provider shall provide: [Please see the standard for more information] | Operations Planning | Future | LOWER | Retirement | The Operations Planning Team recommends the retirement of MOD-001-1 as adopted by the NERC BOT and filed with FERC in February 2014. Additionally, the Operations Planning Team recommends retiring/revoking MOD-001-2 as adopted by the NERC BOT and filed with FERC in February 2014. The filing notes that ATC/AFC are commercially-based values used to facilitate a market for unused transmission capacity in an open access environment and that the values do not directly control the operation of the BPS. It further acknowledges that TOPs are ultimately responsible for operating the grid in a reliable manner consistent with System Operating Limits, not ATC/AFC values. Nevertheless, the filing proposes MOD-001-2 for approval by FERC indicating ATC/AFC values have the potential to influence Real-time conditions on the Bulk-Power System and impact Real-time operations. Although, ATC/AFC values have the potential to influence Real-Time conditions, the Operations Planning Team recommends retirement of the entire MOD-001-2 standard because ATC/AFC are commercially based values, do not directly control the operation of the BPS, and there are a number of approved Reliability Standards to address potential impacts to Real-time operations and operation of the grid in a reliable manner consistent with System Operation Limits. This includes TOP Reliability Standard improvements that have been filed and approved since the MOD-001-2 filing in February 2014. | Project 2018-03 Retiring | Was not Retired as part of the initial Project 2018-03 SER Retirements
MOD-001-2 | R6 | Each Transmission Operator or Transmission Service Provider that receives a written request from another Transmission Operator or Transmission Service Provider for data related to AFC, ATC, TFC, or TTC determinations that (1) references this specific requirement, and (2) specifies that the requested data is for use in the requesting party’s AFC, ATC, TFC, or TTC determination shall take one of the actions below. | Operations Planning | Future | LOWER | Retirement | The Operations Planning Team recommends the retirement of MOD-001-1 as adopted by the NERC BOT and filed with FERC in February 2014. Additionally, the Operations Planning Team recommends retiring/revoking MOD-001-2 as adopted by the NERC BOT and filed with FERC in February 2014. The filing notes that ATC/AFC are commercially-based values used to facilitate a market for unused transmission capacity in an open access environment and that the values do not directly control the operation of the BPS. It further acknowledges that TOPs are ultimately responsible for operating the grid in a reliable manner consistent with System Operating Limits, not ATC/AFC values. Nevertheless, the filing proposes MOD-001-2 for approval by FERC indicating ATC/AFC values have the potential to influence Real-time conditions on the Bulk-Power System and impact Real-time operations. Although, ATC/AFC values have the potential to influence Real-Time conditions, the Operations Planning Team recommends retirement of the entire MOD-001-2 standard because ATC/AFC are commercially based values, do not directly control the operation of the BPS, and there are a number of approved Reliability Standards to address potential impacts to Real-time operations and operation of the grid in a reliable manner consistent with System Operation Limits. This includes TOP Reliability Standard improvements that have been filed and approved since the MOD-001-2 filing in February 2014. | Project 2018-03 Retiring | Was not Retired as part of the initial Project 2018-03 SER Retirements
MOD-004-1 | R1. | The Transmission Service Provider that maintains CBM shall prepare and keep current a “Capacity Benefit Margin Implementation Document” (CBMID) that includes, at a minimum, the following information: [Please see the standard for more information] | Long Term Planning and Operations Planning | Active | MEDIUM | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-004-1 standard. All the requirements within MOD-004-1 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-004-1 | R10. | The Load-Serving Entity or Balancing Authority shall request to import energy over firm Transfer Capability set aside as CBM only when experiencing a declared NERC Energy Emergency Alert (EEA) 2 or higher. [Time Horizon: Same-day Operations] | Same Day Operations | Active | LOWER | Retirement | 1. Project 2012-05, Pending Regulatory Approval, retires this requirement with the following description, "The applicability of the proposed Reliability Standard has been changed so that the LSE or Balancing Authority (BA) are not applicable registered entities within the Reliability Standard". 2. Project 2012-05 industry comments and SER Project industry comments suggest appropriate location is in NAESB (WEQ023 Modeling and/or may be included in WEQ013 Oasis Implementation). 3. Also suggest retirement because its inherent in the definition of CBM, "The amount of firm transmission transfer capability preserved by the transmission provider for Load-Serving Entities (LSEs), whose loads are located on that Transmission Service Provider’s system, to enable access by the LSEs to generation from interconnected systems to meet generation reliability requirements. Preservation of CBM for an LSE allows that entity to reduce its installed generating capacity below that which may otherwise have been necessary without interconnections to meet its generation reliability requirements. The transmission transfer capability preserved as CBM is intended to be used by the LSE only in times of emergency generation deficiencies." | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-004-1 | R11. | When reviewing an Arranged Interchange using CBM, all Balancing Authorities and Transmission Service Providers shall waive, within the bounds of reliable operation, any Real-time timing and ramping requirements. [Time Horizon: Same-day Operations] | Same Day Operations | Active | MEDIUM | Retirement | 1. From the 2012-05 Mapping Document: Maps to MOD-001-2 R3 - Each Transmission Service Provider that determines Capacity Benefit Margin (CBM) values shall develop a Capacity Benefit Margin Implementation Document (CBMID) that describes its method for determining CBM values. The method described in the CBMID shall reflect the Transmission Service Provider's current practices for determining CBM values. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning]. That project justification is, "The proposed Reliability Standard will require entities that use CBM to have a CBMID but does not dictate what must be included or how it is calculated." (BA applicability was removed. Time Horizon changes to Ops Planning) 2. Project 2012-05 industry comments and SER Project industry comments suggest appropriate location is in NAESB (WEQ023 Modeling and/or may be included in WEQ013 Oasis Implementation). | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-004-1 | R12. | The Transmission Service Provider that maintains CBM shall approve, within the bounds of reliable operation, any Arranged Interchange using CBM that is submitted by an “energy deficient entity ” under an EEA 2 if: [Please see the standard for more information] | Same Day Operations | Active | MEDIUM | Retirement | 1. From the Project 2012-05 Mapping Document: Maps to MOD-001-2 R3 Time Horizon changes to Ops Planning (which is not EEA2 related), applicable to TSP. EOP standards only apply to BA, RC, TOP (not TSP). 2. Project 2012-05 industry comments and SER Project industry comments suggest appropriate location is in NAESB (WEQ023 Modeling and/or may be included in WEQ013 Oasis Implementation). | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-004-1 | R2. | The Transmission Service Provider that maintains CBM shall make available its current CBMID to the Transmission Operators, Transmission Service Providers, Reliability Coordinators, Transmission Planners, Resource Planners, and Planning Coordinators that are within or adjacent to the Transmission Service Provider’s area, and to the Load Serving Entities and Balancing Authorities within the Transmission Service Provider’s area, and notify those entities of any changes to the CBMID prior to the effective date of the change. [Time Horizon: Operations Planning] | Operations Planning | Active | MEDIUM | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-004-1 standard. All the requirements within MOD-004-1 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-004-1 | R3. | Each Load-Serving Entity determining the need for Transmission capacity to be set aside as CBM for imports into a Balancing Authority Area shall determine that need by:[Please see the standard for more information] | Operations Planning | Active | MEDIUM | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-004-1 standard. All the requirements within MOD-004-1 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-004-1 | R4. | Each Resource Planner determining the need for Transmission capacity to be set aside as CBM for imports into a Balancing Authority Area shall determine that need by: [Please see the standard for more information] | Operations Planning | Active | MEDIUM | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-004-1 standard. All the requirements within MOD-004-1 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-004-1 | R5. | At least every 13 months, the Transmission Service Provider that maintains CBM shall establish a CBM value for each ATC Path or Flowgate to be used for ATC or Available Flowgate Capability (AFC) calculations during the 13 full calendar months (months 2-14) following the current month (the month in which the Transmission Service Provider is establishing the CBM values). This value shall: [Please see the standard for more information] | Operations Planning | Active | MEDIUM | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-004-1 standard. All the requirements within MOD-004-1 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-004-1 | R6. | At least every 13 months, the Transmission Planner shall establish a CBM value for each ATC Path or Flowgate to be used in planning during each of the full calendar years two through ten following the current year (the year in which the Transmission Planner is establishing the CBM values). This value shall: [Please see the standard for more information] | Long Term Planning | Active | MEDIUM | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-004-1 standard. All the requirements within MOD-004-1 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-004-1 | R7. | Less than 31 calendar days after the establishment of CBM, the Transmission Service Provider that maintains CBM shall notify all the Load-Serving Entities and Resource Planners that determined they had a need for CBM on the Transmission Service Provider’s system of the amount of CBM set aside. [Time Horizon: Operations Planning] | Operations Planning | Active | MEDIUM | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-004-1 standard. All the requirements within MOD-004-1 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-004-1 | R8. | Less than 31 calendar days after the establishment of CBM, the Transmission Planner shall notify all the Load-Serving Entities and Resource Planners that determined they had a need for CBM on the system being planned by the Transmission Planner of the amount of CBM set aside. [Time Horizon: Operations Planning] | Operations Planning | Active | MEDIUM | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-004-1 standard. All the requirements within MOD-004-1 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-004-1 | R9. | The Transmission Service Provider that maintains CBM and the Transmission Planner shall each provide (subject to confidentiality and security requirements) copies of the applicable supporting data, including any models, used for determining CBM or allocating CBM over each ATC Path or Flowgate to the following: [Please see the standard for more information] | Long Term Planning and Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-004-1 standard. All the requirements within MOD-004-1 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-008-1 | R1. | Each Transmission Operator shall prepare and keep current a TRM Implementation Document (TRMID) that includes, as a minimum, the following information: [Please see the standard for more information] | Operations Planning | Active | MEDIUM | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-008-1 standard. All the requirements within MOD-008-1 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-008-1 | R2. | Each Transmission Operator shall only use the components of uncertainty from R1.1 to establish TRM, and shall not include any of the components of Capacity Benefit Margin (CBM). Transmission capacity set aside for reserve sharing agreements can be included in TRM. [Time Horizon: Operations Planning] | Operations Planning | Active | MEDIUM | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-008-1 standard. All the requirements within MOD-008-1 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-008-1 | R3. | Each Transmission Operator shall make available its TRMID, and if requested, underlying documentation (if any) used to determine TRM, in the format used by the Transmission Operator, to any of the following who make a written request no more than 30 calendar days after receiving the request. [Time Horizon: Operations Planning] • Transmission Service Providers • Reliability Coordinators • Planning Coordinators • Transmission Planner • Transmission Operators | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-008-1 standard. All the requirements within MOD-008-1 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-008-1 | R4. | Each Transmission Operator that maintains TRM shall establish TRM values in accordance with the TRMID at least once every 13 months. [Time Horizon: Operations Planning] | Operations Planning | Active | MEDIUM | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-008-1 standard. All the requirements within MOD-008-1 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-008-1 | R5. | The Transmission Operator that maintains TRM shall provide the TRM values to its Transmission Service Provider(s) and Transmission Planner(s) no more than seven calendar days after a TRM value is initially established or subsequently changed. [Time Horizon: Operations Planning] | Operations Planning | Active | MEDIUM | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-008-1 standard. All the requirements within MOD-008-1 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-020-0 | R1. | The Load-Serving Entity, Transmission Planner, and Resource Planner shall each make known its amount of interruptible demands and Direct Control Load Management (DCLM) to Transmission Operators, Balancing Authorities, and Reliability Coordinators on request within 30 calendar days. |  | Active | LOWER | Retirement | Retire as R1. LSE is no longer applicable. This is a duplication of data provision for MOD-031. As part of load data request entities are required to provide Interruptible Demand and Load Management | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-025-2 | R1. | Each Generator Owner shall provide its Transmission Planner with verification of the Real Power capability of its applicable Facilities as follows: 1.1. Verify the Real Power capability of its generating units in accordance with Attachment 1. 1.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Long Term Planning | Active | MEDIUM | Modification | Modification: GAP Issue with Generator Owner without direct relationship to a known Transmission Planner for their facility. GO provides their information to the TO who is NOT an identified TP. | No Action | No action recommended.
MOD-025-2 | R2. | Each Generator Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: 2.1. Verify, in accordance with Attachment 1, (i) the Reactive Power capability of its generating units and (ii) the Reactive Power capability of its synchronous condenser units. 2.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Long Term Planning | Active | MEDIUM | Modification | Modification: GAP Issue with Generator Owner without direct relationship to a known Transmission Planner for their facility. GO provides their information to the TO who is NOT an identified TP. | No Action | No action recommended.
MOD-025-2 | R3. | Each Transmission Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: 3.1. Verify, in accordance with Attachment 1, the Reactive Power capability of its synchronous condenser units. 3.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Long Term Planning | Active | MEDIUM | Modification | Modification: GAP Issue with Generator Owner without direct relationship to a known Transmission Planner for their facility. GO provides their information to the TO who is NOT an identified TP. | No Action | No action recommended.
MOD-026-1 | R1. | Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request : • Instructions on how to obtain the list of excitation control system or plant volt/var control function models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic excitation control system or plant volt/var control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific excitation control system or plant volt/var control function contained in the Transmission Planner’s dynamic database from the current (in-use) models, including generator MVA base. | Operations Planning | Active | LOWER | Transfer | From MOD-032 background item, The action “consolidation of standards” was a significant recommendation driven by both NERC and FERC. These standards and their requirements as applied in both MOD-026 and MOD-027 are redundant in their administrative functions and fitting that these be retired since these are covered by requirements in MOD-032 for the data submittal per R1 and R2. Upon notification of technical concerns per MOD-032 R3 the focus entity (GO) is directed to act, making this redundant in both MOD-026 and MOD-027 for model and data associated with a generator control equipment. When data is not usable, the technical concerns focus on the model and applied data to which the GO will perform the reverification and submittal of data, delivered on a requirement date schedule or as agreed upon, that supports the need of and use of the correct control model data for any of the unit’s control responses and validation. Or GO shall provide a technical basis for model and data use. DEFER TO PHASE 2 | No Action | No action recommended.
MOD-026-1 | R2. | Each Generator Owner shall provide for each applicable unit, a verified generator excitation control system or plant volt/var control function model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-026 Attachment 1. 2.1. Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s), or both. Each verification shall include the following: 2.1.1. Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance, 2.1.2. Manufacturer, model number (if available), and type of the excitation control system including, but not limited to static, AC brushless, DC rotating, and/or the plant volt/var control function (if installed), 2.1.3. Model structure and data including, but not limited to reactance, time constants, saturation factors, total rotational inertia, or equivalent data for the generator, 2.1.4. Model structure and data for the excitation control system, including the closed loop voltage regulator if a closed loop voltage regulator is installed or the model structure and data for the plant volt/var control function system, 2.1.5. Compensation settings (such as droop, line drop, differential compensation), if used, and 2.1.6. Model structure and data for power system stabilizer, if so equipped. | Long Term Planning | Active | MEDIUM | Modification | Modification: GAP Issue with Generator Owner without direct relationship to a known Transmission Planner for their facility. GO provides their information to the TO who is NOT an identified TP | No Action | No action recommended.
MOD-026-1 | R3. | Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit: • Written notification from its Transmission Planner (in accordance with Requirement R6) that the excitation control system or plant volt/var control function model is not usable, • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the excitation control system or plant volt/var control function model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated excitation control system or plant volt/var control function model response did not match the recorded response to a transmission system event. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). | Operations Planning | Active | LOWER | Transfer | From MOD-032 background item, The action “consolidation of standards” was a significant recommendation driven by both NERC and FERC. These standards and their requirements as applied in both MOD-026 and MOD-027 are redundant in their administrative functions and fitting that these be retired since these are covered by requirements in MOD-032 for the data submittal per R1 and R2. Upon notification of technical concerns per MOD-032 R3 the focus entity (GO) is directed to act, making this redundant in both MOD-026 and MOD-027 for model and data associated with a generator control equipment. When data is not usable, the technical concerns focus on the model and applied data to which the GO will perform the reverification and submittal of data, delivered on a requirement date schedule or as agreed upon, that supports the need of and use of the correct control model data for any of the unit’s control responses and validation. Or GO shall provide a technical basis for model and data use. DEFER TO PHASE 2 GENERALLY RLATED TO MOD-026 / MOD-027 - Ops Planning and Long Term Planning do not fully agree on the disposition MOD-032 builds the models - 26 and 27 define how TPs verify those models. MOD-026, 27, and 32 perhaps need to be considered as a body to assure that all concerns are addressed once ... and only once. | No Action | No action recommended.
MOD-026-1 | R4. | Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the excitation control system or plant volt/var control function that alter the equipment response characteristic. | Operations Planning | Active | LOWER | Transfer | From MOD-032 background item, The action “consolidation of standards” was a significant recommendation driven by both NERC and FERC. These standards and their requirements as applied in both MOD-026 and MOD-027 are redundant in their administrative functions and fitting that these be retired since these are covered by requirements in MOD-032 for the data submittal per R1 and R2. Upon notification of technical concerns per MOD-032 R3 the focus entity (GO) is directed to act, making this redundant in both MOD-026 and MOD-027 for model and data associated with a generator control equipment. When data is not usable, the technical concerns focus on the model and applied data to which the GO will perform the reverification and submittal of data, delivered on a requirement date schedule or as agreed upon, that supports the need of and use of the correct control model data for any of the unit’s control responses and validation. Or GO shall provide a technical basis for model and data use. DEFER TO PHASE 2 | No Action | No action. In the current state, there is no efficiency to be gained by transferring MOD-026 R4 to MOD-032. Consider including in SER Phase II, Concept 5, Data Sharing. R4 is inexplicably tied to R2/R3. This level of model information as spelled out in R2 would have to be brought into MOD-032 in order for R4 to follow suit. Not sure given the current design of MOD-032 that would be practical or "efficient". Also, why is the concern with R4 in MOD-026 and R5 with MOD-027?
MOD-026-1 | R5. | Each Generator Owner shall provide a written response to its Transmission Planner, within 90 calendar days following receipt of a technically justified unit request from the Transmission Planner to perform a model review of a unit or plant that includes one of the following: • Details of plans to verify the model (in accordance with Requirement R2), or • Corrected model data including the source of revised model data such as discovery of manufacturer test values to replace generic model data or updating of data parameters based on an on-site review of the equipment. | Operations Planning | Active | LOWER | Transfer | From MOD-032 background item, The action “consolidation of standards” was a significant recommendation driven by both NERC and FERC. These standards and their requirements as applied in both MOD-026 and MOD-027 are redundant in their administrative functions and fitting that these be retired since these are covered by requirements in MOD-032 for the data submittal per R1 and R2. Upon notification of technical concerns per MOD-032 R3 the focus entity (GO) is directed to act, making this redundant in both MOD-026 and MOD-027 for model and data associated with a generator control equipment. When data is not usable, the technical concerns focus on the model and applied data to which the GO will perform the reverification and submittal of data, delivered on a requirement date schedule or as agreed upon, that supports the need of and use of the correct control model data for any of the unit’s control responses and validation. Or GO shall provide a technical basis for model and data use. DEFER TO PHASE 2 | No Action | No action recommended.
MOD-026-1 | R6. | Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the verified excitation control system or plant volt/var control function model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 6.1 through 6.3) or is not usable. 6.1. The excitation control system or plant volt/var control function model initializes to compute modeling data without error, 6.2. A no-disturbance simulation results in negligible transients, and 6.3. For an otherwise stable simulation, a disturbance simulation results in the excitation control and plant volt/var control function model exhibiting positive damping. If the model is not usable, the Transmission Planner shall provide a technical description of why the model is not usable. | Operations Planning | Active | MEDIUM | Transfer | From MOD-032 background item, The action “consolidation of standards” was a significant recommendation driven by both NERC and FERC. These standards and their requirements as applied in both MOD-026 and MOD-027 are redundant in their administrative functions and fitting that these be retired since these are covered by requirements in MOD-032 for the data submittal per R1 and R2. Upon notification of technical concerns per MOD-032 R3 the focus entity (GO) is directed to act, making this redundant in both MOD-026 and MOD-027 for model and data associated with a generator control equipment. When data is not usable, the technical concerns focus on the model and applied data to which the GO will perform the reverification and submittal of data, delivered on a requirement date schedule or as agreed upon, that supports the need of and use of the correct control model data for any of the unit’s control responses and validation. Or GO shall provide a technical basis for model and data use. DEFER TO PHASE 2 | No Action | No action recommended.
MOD-027-1 | R1. | Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: • Instructions on how to obtain the list of turbine/governor and load control or active power/frequency control system models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic turbine/governor and load control or active power/frequency control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific turbine/governor and load control or active power/frequency control system contained in the Transmission Planner’s dynamic database from the current (in-use) models. | Operations Planning | Active | LOWER | Transfer | From MOD-032 background item, The action “consolidation of standards” was a significant recommendation driven by both NERC and FERC. These standards and their requirements as applied in both MOD-026 and MOD-027 are redundant in their administrative functions and fitting that these be retired since these are covered by requirements in MOD-032 for the data submittal per R1 and R2. Upon notification of technical concerns per MOD-032 R3 the focus entity (GO) is directed to act, making this redundant in both MOD-026 and MOD-027 for model and data associated with a generator control equipment. When data is not usable, the technical concerns focus on the model and applied data to which the GO will perform the reverification and submittal of data, delivered on a requirement date schedule or as agreed upon, that supports the need of and use of the correct control model data for any of the unit’s control responses and validation. Or GO shall provide a technical basis for model and data use. DEFER TO PHASE 2 | No Action | No action recommended.
MOD-027-1 | R2. | Each Generator Owner shall provide, for each applicable unit, a verified turbine/governor and load control or active power/frequency control model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-027 Attachment 1. 2.1. Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units rated less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s) or both. Each verification shall include the following: 2.1.1. Documentation comparing the applicable unit’s MW model response to the recorded MW response for either: • A frequency excursion from a system disturbance that meets MOD-027 Attachment 1 Note 1 with the applicable unit on-line, • A speed governor reference change with the applicable unit on-line, or • A partial load rejection test, 2.1.2. Type of governor and load control or active power control/frequency control1 equipment, 2.1.3. A description of the turbine (e.g. for hydro turbine - Kaplan, Francis, or Pelton; for steam turbine - boiler type, normal fuel type, and turbine type; for gas turbine - the type and manufacturer; for variable energy plant - type and manufacturer), 2.1.4. Model structure and data for turbine/governor and load control or active power/frequency control, and 2.1.5. Representation of the real power response effects of outer loop controls (such as operator set point controls, and load control but excluding AGC control) that would override the governor response (including blocked or nonfunctioning governors or modes of operation that limit Frequency Response), if applicable. | Long Term Planning | Active | MEDIUM | Modification | Modification: GAP Issue with Generator Owner without direct relationship to a known Transmission Planner for their facility. GO provides their information to the TO who is NOT an identified TP | No Action | No action recommended.
MOD-027-1 | R3. | Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit. • Written notification, from its Transmission Planner (in accordance with Requirement R5) that the turbine/governor and load control or active power/frequency control model is not “usable,” • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the turbine/governor and load control or active power/frequency control model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated turbine/governor and load control or active power/frequency control response did not approximate the recorded response for three or more transmission system events. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). | Operations Planning | Active | LOWER | Transfer | From MOD-032 background item, The action “consolidation of standards” was a significant recommendation driven by both NERC and FERC. These standards and their requirements as applied in both MOD-026 and MOD-027 are redundant in their administrative functions and fitting that these be retired since these are covered by requirements in MOD-032 for the data submittal per R1 and R2. Upon notification of technical concerns per MOD-032 R3 the focus entity (GO) is directed to act, making this redundant in both MOD-026 and MOD-027 for model and data associated with a generator control equipment. When data is not usable, the technical concerns focus on the model and applied data to which the GO will perform the reverification and submittal of data, delivered on a requirement date schedule or as agreed upon, that supports the need of and use of the correct control model data for any of the unit’s control responses and validation. Or GO shall provide a technical basis for model and data use. DEFER TO PHASE 2 | No Action | No action recommended.
MOD-027-1 | R4. | Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the turbine/governor and load control or active power/frequency control system that alter the equipment response characteristic | Operations Planning | Active | LOWER | Transfer | From MOD-032 background item, The action “consolidation of standards” was a significant recommendation driven by both NERC and FERC. These standards and their requirements as applied in both MOD-026 and MOD-027 are redundant in their administrative functions and fitting that these be retired since these are covered by requirements in MOD-032 for the data submittal per R1 and R2. Upon notification of technical concerns per MOD-032 R3 the focus entity (GO) is directed to act, making this redundant in both MOD-026 and MOD-027 for model and data associated with a generator control equipment. When data is not usable, the technical concerns focus on the model and applied data to which the GO will perform the reverification and submittal of data, delivered on a requirement date schedule or as agreed upon, that supports the need of and use of the correct control model data for any of the unit’s control responses and validation. Or GO shall provide a technical basis for model and data use. DEFER TO PHASE 2 | No Action | No action recommended.
MOD-027-1 | R5. | Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the turbine/governor and load control or active power/frequency control system verified model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 5.1 through 5.3) or is not usable. 5.1. The turbine/governor and load control or active power/frequency control function model initializes to compute modeling data without error, 5.2. A no-disturbance simulation results in negligible transients, and 5.3. For an otherwise stable simulation, a disturbance simulation results in the turbine/governor and load control or active power/frequency control model exhibiting positive damping. If the model is not usable, the Transmission Planner shall provide a technical description of why the model is not usable. | Operations Planning | Active | MEDIUM | Transfer | From MOD-032 background item, The action “consolidation of standards” was a significant recommendation driven by both NERC and FERC. These standards and their requirements as applied in both MOD-026 and MOD-027 are redundant in their administrative functions and fitting that these be retired since these are covered by requirements in MOD-032 for the data submittal per R1 and R2. Upon notification of technical concerns per MOD-032 R3 the focus entity (GO) is directed to act, making this redundant in both MOD-026 and MOD-027 for model and data associated with a generator control equipment. When data is not usable, the technical concerns focus on the model and applied data to which the GO will perform the reverification and submittal of data, delivered on a requirement date schedule or as agreed upon, that supports the need of and use of the correct control model data for any of the unit’s control responses and validation. Or GO shall provide a technical basis for model and data use. DEFER TO PHASE 2 | No Action | In the current state, there is no efficiency to be gained by transferring MOD-027 R5 to MOD-032. Consider including in SER Phase II, Concept 5, Data Sharing. R5 is inexplicably tied to R2/R3. This level of model information as spelled out in R2 would have to be brought into MOD-032 in order for R5 to follow suit. Given the current design of MOD-032 may not be practical or "efficient".
MOD-028-2 | R1. | Each Transmission Service Provider shall include in its Available Transfer Capability Implementation Document (ATCID), at a minimum, the following information relative to its methodology for determining Total Transfer Capability (TTC): [Please see the standard for more information] | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-028-2 standard. All the requirements within MOD-028-2 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-028-2 | R10. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall utilize the following algorithm: ATCF = TTC – ETCF – CBM – TRM + PostbacksF + counterflowsF Where: ATCF is the firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. CBM is the Capacity Benefit Margin for the ATC Path during that period. TRM is the Transmission Reliability Margin for the ATC Path during that period. PostbacksF¬ are changes to firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsF are adjustments to firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-028-2 standard. All the requirements within MOD-028-2 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-028-2 | R11. | When calculating non-firm ATC for a ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: ATCNF = TTC – ETCF - ETCNF – CBMS – TRMU + PostbacksNF + counterflowsNF Where: ATCNF is the non-firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. ETCNF is the sum of existing non-firm Transmission commitments for the ATC Path during that period. CBMS is the Capacity Benefit Margin for the ATC Path that has been scheduled without a separate reservation during that period. TRMU is the Transmission Reliability Margin for the ATC Path that has not been released for sale (unreleased) as non-firm capacity by the Transmission Service Provider during that period. PostbacksNF¬ are changes to non-firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsNF are adjustments to non-firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-028-2 standard. All the requirements within MOD-028-2 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-028-2 | R2. | When calculating TTC for ATC Paths, the Transmission Operator shall use a Transmission model that contains all of the following: [Please see the standard for more information] | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-028-2 standard. All the requirements within MOD-028-2 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-028-2 | R3. | When calculating TTCs for ATC Paths, the Transmission Operator shall include the following data for the Transmission Service Provider’s area. The Transmission Operator shall also include the following data associated with Facilities that are explicitly represented in the Transmission model, as provided by adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed: [Please see the standard for more information] | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-028-2 standard. All the requirements within MOD-028-2 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-028-2 | R4. | When calculating TTCs for ATC Paths, the Transmission Operator shall meet all of the following conditions: [Please see the standard for more information] | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-028-2 standard. All the requirements within MOD-028-2 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-028-2 | R5. | Each Transmission Operator shall establish TTC for each ATC Path as defined below: [Please see the standard for more information] | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-028-2 standard. All the requirements within MOD-028-2 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-028-2 | R6. | Each Transmission Operator shall establish TTC for each ATC Path using the following process: [Please see the standard for more information] | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-028-2 standard. All the requirements within MOD-028-2 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-028-2 | R7. | The Transmission Operator shall provide the Transmission Service Provider of that ATC Path with the most current value for TTC for that ATC Path no more than: [Please see the standard for more information] | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-028-2 standard. All the requirements within MOD-028-2 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-028-2 | R8. | When calculating Existing Transmission Commitments (ETCs) for firm commitments (ETCF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCF = NITSF + GFF + PTPF + RORF + OSF Where: NITSF is the firm capacity set aside for Network Integration Transmission Service (including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) on ATC Paths that serve as interfaces with other Balancing Authorities. GFF is the firm capacity set aside for Grandfathered Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPF is the firm capacity reserved for confirmed Point-to-Point Transmission Service. RORF is the capacity reserved for roll-over rights for Firm Transmission Service contracts granting Transmission Customers the right of first refusal to take or continue to take Transmission Service when the Transmission Customer’s Transmission Service contract expires or is eligible for renewal. OSF is the firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-028-2 standard. All the requirements within MOD-028-2 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-028-2 | R9. | When calculating ETC for non-firm commitments (ETCNF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCNF = NITSNF + GFNF + PTPNF + OSNF Where: NITSNF is the non-firm capacity set aside for Network Integration Transmission Service (i.e., secondary service , including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) reserved on ATC Paths that serve as interfaces with other Balancing Authorities. GFNF is the non-firm capacity reserved for Grandfathered Non-Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPNF is non-firm capacity reserved for confirmed Point-to-Point Transmission Service. OSNF is the non-firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Non-Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-028-2 standard. All the requirements within MOD-028-2 address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-029-2a | R1. | When calculating TTCs for ATC Paths, the Transmission Operator shall use a Transmission model which satisfies the following requirements: [Please see the standard for more information] | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-029-2a standard. All the requirements within MOD-029-2a address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-029-2a | R2. | The Transmission Operator shall use the following process to determine TTC: [Please see the standard for more information] | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-029-2a standard. All the requirements within MOD-029-2a address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-029-2a | R3. | Each Transmission Operator shall establish the TTC at the lesser of the value calculated in R2 or any System Operating Limit (SOL) for that ATC Path. | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-029-2a standard. All the requirements within MOD-029-2a address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-029-2a | R4. | Within seven calendar days of the finalization of the study report, the Transmission Operator shall make available to the Transmission Service Provider of the ATC Path, the most current value for TTC and the TTC study report documenting the assumptions used and steps taken in determining the current value for TTC for that ATC Path. | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-029-2a standard. All the requirements within MOD-029-2a address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-029-2a | R5. | When calculating ETC for firm Existing Transmission Commitments (ETCF) for a specified period for an ATC Path, the Transmission Service Provider shall use the algorithm below: See standard for formula | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-029-2a standard. All the requirements within MOD-029-2a address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-029-2a | R6. | When calculating ETC for non-firm Existing Transmission Commitments (ETCNF) for all time horizons for an ATC Path the Transmission Service Provider shall use the following algorithm: See standard for formula | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-029-2a standard. All the requirements within MOD-029-2a address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-029-2a | R7. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See Standard for Formula | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-029-2a standard. All the requirements within MOD-029-2a address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-029-2a | R8. | When calculating non-firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: See standard for formula | Operations Planning | Active | LOWER | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-029-2a standard. All the requirements within MOD-029-2a address commercial issues, not reliability issues. This requirement was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-030-3 | R1. | The Transmission Service Provider shall include in its “Available Transfer Capability Implementation Document” [Please see the standard for more information] | Operations Planning | Active | To Be Determined | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-030-3 standard. All the requirements within MOD-030-3 address commercial issues, not reliability issues. Version 2 of this standard was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. Version 3 was approved by FERC on November 19, 2015, but retains the same elements as Version 2. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-030-3 | R10. | Each Transmission Service Provider shall recalculate AFC, utilizing the updated models described in R3.2, R3.3, and R5, at a minimum on the following frequency, unless none of the calculated values identified in the AFC equation have changed: [See standard for additional information.] | Operations Planning | Active | To Be Determined | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-030-3 standard. All the requirements within MOD-030-3 address commercial issues, not reliability issues. Version 2 of this standard was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. Version 3 was approved by FERC on November 19, 2015, but retains the same elements as Version 2. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-030-3 | R11. | When converting Flowgate AFCs to ATCs for ATC Paths, the Transmission Service Provider shall convert those values based on the following algorithm: [See standard for additional information.] | Operations Planning | Active | To Be Determined | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-030-3 standard. All the requirements within MOD-030-3 address commercial issues, not reliability issues. Version 2 of this standard was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. Version 3 was approved by FERC on November 19, 2015, but retains the same elements as Version 2. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-030-3 | R2. | The Transmission Operator shall perform the following: [Please see the standard for more information] | Operations Planning | Active | To Be Determined | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-030-3 standard. All the requirements within MOD-030-3 address commercial issues, not reliability issues. Version 2 of this standard was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. Version 3 was approved by FERC on November 19, 2015, but retains the same elements as Version 2. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-030-3 | R3. | The Transmission Operator shall make available to the Transmission Service Provider a Transmission model to determine Available Flowgate Capability (AFC) that meets the following criteria: [Please see the standard for more information] | Operations Planning | Active | To Be Determined | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-030-3 standard. All the requirements within MOD-030-3 address commercial issues, not reliability issues. Version 2 of this standard was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. Version 3 was approved by FERC on November 19, 2015, but retains the same elements as Version 2. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-030-3 | R4. | When calculating AFCs, the Transmission Service Provider shall represent the impact of Transmission Service as follows: [See standard for additional information.] | Operations Planning | Active | To Be Determined | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-030-3 standard. All the requirements within MOD-030-3 address commercial issues, not reliability issues. Version 2 of this standard was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. Version 3 was approved by FERC on November 19, 2015, but retains the same elements as Version 2. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-030-3 | R5. | When calculating AFCs, the Transmission Service Provider shall: [Please see the standard for more information] | Operations Planning | Active | To Be Determined | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-030-3 standard. All the requirements within MOD-030-3 address commercial issues, not reliability issues. Version 2 of this standard was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. Version 3 was approved by FERC on November 19, 2015, but retains the same elements as Version 2. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-030-3 | R6. | When calculating the impact of ETC for firm commitments (ETCFi) for all time periods for a Flowgate, the Transmission Service Provider shall sum the following: [Please see the standard for more information] | Operations Planning | Active | To Be Determined | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-030-3 standard. All the requirements within MOD-030-3 address commercial issues, not reliability issues. Version 2 of this standard was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. Version 3 was approved by FERC on November 19, 2015, but retains the same elements as Version 2. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-030-3 | R7. | When calculating the impact of ETC for non-firm commitments (ETCNFi) for all time periods for a Flowgate the Transmission Service Provider shall sum: [Please see the standard for more information] | Operations Planning | Active | To Be Determined | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-030-3 standard. All the requirements within MOD-030-3 address commercial issues, not reliability issues. Version 2 of this standard was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. Version 3 was approved by FERC on November 19, 2015, but retains the same elements as Version 2. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-030-3 | R8. | When calculating firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): [See standard for additional information.] | Operations Planning | Active | To Be Determined | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-030-3 standard. All the requirements within MOD-030-3 address commercial issues, not reliability issues. Version 2 of this standard was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. Version 3 was approved by FERC on November 19, 2015, but retains the same elements as Version 2. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-030-3 | R9. | When calculating non-firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): [See standard for additional information.] | Operations Planning | Active | To Be Determined | Retirement | The Operations Planning Team recommends the retirement of the entire MOD-030-3 standard. All the requirements within MOD-030-3 address commercial issues, not reliability issues. Version 2 of this standard was identified for retirement through Project 2012-05 ATC Revisions (MOD A) (http://www.nerc.com/pa/Stand/Pages/Project201205MODAAvailableTransferCapability.aspx), to be replaced by MOD-001-2. This was adopted by the NERC BOT and filed with FERC in February 2014. Version 3 was approved by FERC on November 19, 2015, but retains the same elements as Version 2. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
MOD-031-2 | R1. | Each Planning Coordinator or Balancing Authority that identifies a need for the collection of Total Internal Demand, Net Energy for Load, and Demand Side Management data shall develop and issue a data request to the applicable entities in its area. The data request shall include: [See standard for additional information.] | Long Term Planning | Active | MEDIUM | Modification | Modification: Could be recommended for modification: FERC approved removal of Load-Serving Entity (LSE) as a functional registration category, therefore LSE should be removed from the Applicability section. | No Action | No action recommended.
MOD-031-2 | R2. | Each Applicable Entity identified in a data request shall provide the data requested by its Planning Coordinator or Balancing Authority in accordance with the data request issued pursuant to Requirement R1. | Long Term Planning | Active | MEDIUM | Modification | Modification: Could be recommended for modification: FERC approved removal of Load-Serving Entity (LSE) as a functional registration category, therefore LSE should be removed from the Applicability section. | No Action | No action recommended.
MOD-031-2 | R3. | The Planning Coordinator or the Balancing Authority shall provide the data listed under Requirement R1 Parts 1.3 through 1.5 for their area to the applicable Regional Entity within 75 calendar days of receiving a request for such data, unless otherwise agreed upon by the parties. | Long Term Planning | Active | MEDIUM | Modification | Modification: Could be recommended for modification: FERC approved removal of Load-Serving Entity (LSE) as a functional registration category, therefore LSE should be removed from the Applicability section. | No Action | No action recommended.
MOD-031-2 | R4. | R4. Any Applicable Entity shall, in response to a written request for the data included in parts 1.3-1.5 of Requirement R1 from a Planning Coordinator, Balancing Authority, Transmission Planner or Resource Planner with a demonstrated need for such data in order to conduct reliability assessments of the Bulk Electric System, provide or otherwise make available that data to the requesting entity. This requirement does not modify an entity’s obligation pursuant to Requirement R2 to respond to data requests issued by its Planning Coordinator or Balancing Authority pursuant to Requirement R1. Unless otherwise agreed upon, the Applicable Entity: • shall not be required to alter the format in which it maintains or uses the data; • shall provide the requested data within 45 calendar days of the written request, subject to part 4.1 of this requirement; unless providing the requested data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements 4.1. If the Applicable Entity does not provide data requested because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. | Long Term Planning | Active | MEDIUM | Modification | Modification: Could be recommended for modification: FERC approved removal of Load-Serving Entity (LSE) as a functional registration category, therefore LSE should be removed from the Applicability section. | No Action | No action recommended.
MOD-032-1 | R1. | Each Planning Coordinator and each of its Transmission Planners shall jointly develop steady‐state, dynamics, and short circuit modeling data requirements and reporting procedures for the Planning Coordinator’s planning area that include: [Please see the standard for more information] | Long Term Planning | Active | LOWER | Modification | Efficiency opportunity- recommended modification: FERC approved removal of Load-Serving Entity (LSE) as a functional registration category; therefore LSE should be removed from the Applicability section. Look at duplication of MOD-025. | No Action | No action recommended.
MOD-032-1 | R2. | Each Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, and Transmission Service Provider shall provide steady‐state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s) according to the data requirements and reporting procedures developed by its Planning Coordinator and Transmission Planner in Requirement R1. For data that has not changed since the last submission, a written confirmation that the data has not changed is sufficient. | Long Term Planning | Active | MEDIUM | Modification | Efficiency opportunity- recommended modification: FERC approved removal of Load-Serving Entity (LSE) as a functional registration category; therefore LSE should be removed from the Applicability section. Look at duplication of MOD-025. | No Action | No action recommended.
MOD-032-1 | R3. | Upon receipt of written notification from its Planning Coordinator or Transmission Planner regarding technical concerns with the data submitted under Requirement R2, including the technical basis or reason for the technical concerns, each notified Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider shall respond to the notifying Planning Coordinator or Transmission Planner as follows: [Please see the standard for more information] | Long Term Planning | Active | LOWER | Modification | Efficiency opportunity- recommended modification: FERC approved removal of Load-Serving Entity (LSE) as a functional registration category; therefore LSE should be removed from the Applicability section. Look at duplication of MOD-025. | No Action | No action recommended.
MOD-032-1 | R4. | Each Planning Coordinator shall make available models for its planning area reflecting data provided to it under Requirement R2 to the Electric Reliability Organization (ERO) or its designee to support creation of the Interconnection‐wide case(s) that includes the Planning Coordinator’s planning area. | Long Term Planning | Active | MEDIUM | Modification | Efficiency opportunity- recommended modification: FERC approved removal of Load-Serving Entity (LSE) as a functional registration category; therefore LSE should be removed from the Applicability section. Look at duplication of MOD-025. | No Action | No action recommended.
MOD-033-1 | R1. | Each Planning Coordinator shall implement a documented data validation process that includes the following attributes: [Please see the standard for more information] | Long Term Planning | Active | MEDIUM | Modification | Modification: Could be recommended for modification: FERC approved removal of Load-Serving Entity (LSE) as a functional registration category, therefore LSE should be removed from the Applicability section. | No Action | No action recommended.
MOD-033-1 | R2. | Each Reliability Coordinator and Transmission Operator shall provide actual system behavior data (or a written response that it does not have the requested data) to any Planning Coordinator performing validation under Requirement R1 within 30 calendar days of a written request, such as, but not limited to, state estimator case or other Real‐time data (including disturbance data recordings) necessary for actual system response validation. | Long Term Planning | Active | LOWER | Modification | Modification: Could be recommended for modification: FERC approved removal of Load-Serving Entity (LSE) as a functional registration category, therefore LSE should be removed from the Applicability section. | No Action | No action recommended.
NUC-001-3 | R1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt. | Long Term Planning | Active | MEDIUM | Retirement | Administrative in nature; R1 actions are inherent in R2 since each entity 'shall have in effect' an agreement | Retire w/ modification | Recommend retirement with modification. Requirement R2 more than covers the need for NPIRs in Requirement R1 to be shared because it requires they be agreed upon in Requirement R2. Requirement R1 is administrative in nature and only includes the "proposed" NPIRs and not the "mutually agreed upon" ones in Requirement R2.
NUC-001-3 | R2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements[1] that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. | Long Term Planning | Active | MEDIUM | Modification | This requirement is needed for reliability. The SER LTP team recommends referencing R9 elements into a newly created Attachment. | Modify | Recommend modifying to move Requirement R1 to Requirement R2 and to move the Requirement R9 elements to Requirement R2 and retire Requirements R1 and R9.
NUC-001-3 | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator.: | Long Term Planning | Active | MEDIUM | No Action | This requirement is needed for reliability. | No Action | No action recommended.
NUC-001-3 | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: 4.1. Incorporate the NPIRs into their operating analyses of the electric system. 4.2. Operate the electric system to meet the NPIRs. 4.3. Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | Operations Planning and Real-Time Operations | Active | HIGH | No Action | Retain as is | No Action | No action recommended.
NUC-001-3 | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: (please see standard for sub-req's) | Operations Planning and Real-Time Operations | Active | HIGH | No Action |  | No Action | No action recommended.
NUC-001-3 | R5. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall operate the nuclear plant to meet the NPIRs. | Operations Planning and Real-Time Operations | Active | HIGH | No Action | Retain as is | No Action | No action recommended.
NUC-001-3 | R5. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall operate the nuclear plant to meet the NPIRs. | Operations Planning and Real-Time Operations | Active | HIGH | No Action | This requirement was transferred to the Long Term Planning Team and it was determined that it is needed for reliability. | No Action | No action recommended.
NUC-001-3 | R6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. | Operations Planning | Active | MEDIUM | No Action | Retain as is | No Action | No action recommended.
NUC-001-3 | R7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | Long Term Planning | Active | HIGH | No Action | This requirement is needed for reliability. | No Action | No action recommended.
NUC-001-3 | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | Long Term Planning | Active | HIGH | No Action | This requirement is needed for reliability. | No Action | No action recommended.
NUC-001-3 | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. • Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. • Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity. (please see standard for sub-req's) | Long Term Planning | Active | MEDIUM | Modification | The SER LTP team recommends retiring R9 after the attachment for R2 is created. On its own, R9 is purely administrative to achieve R2. It is recommended that the elements of R9 be rolled into a newly created Attachment referenced from R2. | Retire w/ modification | Recommend retirement with modification. The elements in Requirement R9 are part and parcel to this requirement and should simply be referenced here. Additionally, recommend creating an Attachment 1, which should list all of the elements currently listed in Requirement R9. Then add to the end of Requirement R2, "The Agreement(s) shall include the elements in aggregate cited in Attachment 1." Then Attachment 1 should list all of the elements currently listed in Requirement R9.
PER-003-1 | R1. | Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate: 1.1. Areas of Competency 1.1.1. Resource and demand balancing 1.1.2. Transmission operations 1.1.3. Emergency preparedness and operations 1.1.4. System operations 1.1.5. Protection and control 1.1.6. Voltage and reactive 1.1.7. Interchange scheduling and coordination 1.1.8. Interconnection reliability operations and coordination | Real-time Operations | Active | HIGH | Transfer | Transfer to Certification/Controls Review for PER-005 R3 (see Alternatives to Retirement Guideline) | No Action | No action recommended.
PER-003-1 | R2. | Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates: 2.1. Areas of Competency 2.1.1. Transmission operations 2.1.2. Emergency preparedness and operations 2.1.3. System operations 2.1.4. Protection and control 2.1.5. Voltage and reactive 2.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator | Real-time Operations | Active | HIGH | Transfer | Transfer to Certification/Controls Review for PER-005 R3 (see Alternatives to Retirement Guideline) | No Action | No action recommended.
PER-003-1 | R3. | Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates: 3.1. Areas of Competency 3.1.1. Resources and demand balancing 3.1.2. Emergency preparedness and operations 3.1.3. System operations 3.1.4. Interchange scheduling and coordination 3.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator | Real-time Operations | Active | HIGH | Transfer | Transfer to Certification/Controls Review for PER-005 R3 (see Alternatives to Retirement Guideline) | No Action | No action recommended.
PER-004-2 | R1. | Each Reliability Coordinator shall be staffed with adequately trained and NERC-certified Reliability Coordinator operators, 24 hours per day, seven days per week. | Real-time Operations | Active | HIGH | Transfer | Transfer to Certification/Controls Review for PER-005 R3 (see Alternatives to Retirement Guideline) | No Action | No action recommended.
PER-004-2 | R2. | Reliability Coordinator operating personnel shall place particular attention on SOLs and IROLs and inter-tie facility limits. The Reliability Coordinator shall ensure protocols are in place to allow Reliability Coordinator operating personnel to have the best available information at all times. | Real-time Operations | Active | HIGH | Transfer | Transfer to Certification/Controls Review for PER-005 R3 (see Alternatives to Retirement Guideline) | No Action | No action recommended.
PER-005-2 | R1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement a training program for its System Operators as follows: [Please see the standard for more information] | Long Term Planning | Active | MEDIUM | Transfer | PER-005-2 Requirements 1, 2, instruct the applicable Registered Entities (RE) to “use a systematic approach to develop and implement a training program” based on a predetermined list of BES company-specific Real-time reliability-related tasks, its employees perform. It is apparent to the industry that there are administrative inefficiencies having these competency-based requirements within the CMEP. The entities' capability/readiness to address the associated BES risk could be evaluated during a certification and/or controls review for the performance-based requirement (e.g., PER-005-2 R3). | No Action | No action recommended.
PER-005-2 | R2. | Each Transmission Owner shall use a systematic approach to develop and implement a training program for its personnel identified in Applicability Section 4.1.4.1 of this standard as follows: [Please see the standard for more information] | Long Term Planning | Active | MEDIUM | Transfer | PER-005-2 Requirements 1, 2, instruct the applicable Registered Entities (RE) to “use a systematic approach to develop and implement a training program” based on a predetermined list of BES company-specific Real-time reliability-related tasks, its employees perform. It is apparent to the industry that there are administrative inefficiencies having these competency-based requirements within the CMEP. The entities' capability/readiness to address the associated BES risk could be evaluated during a certification and/or controls review for the performance-based requirement (e.g., PER-005-2 R3). | No Action | No action recommended.
PER-005-2 | R3. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify, at least once, the capabilities of its personnel, identified in Requirement R1 or Requirement R2, assigned to perform each of the BES company‐specific Real‐time reliability‐related tasks identified under Requirement R1 part 1.1 or Requirement R2 part 2.1. [Please see the standard for more information] | Long Term Planning | Active | HIGH | No Action |  | No Action | No action recommended.
PER-005-2 | R4. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner that (1) has operational authority or control over Facilities with established Interconnection Reliability Operating Limits (IROLs), or (2) has established protection systems or operating guides to mitigate IROL violations, shall provide its personnel identified in Requirement R1 or Requirement R2 with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES. [Please see the standard for more information] | Long Term Planning | Active | MEDIUM | No Action |  | No Action | No action recommended.
PER-005-2 | R5. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement training for its identified Operations Support Personnel on how their job function(s) impact those BES company‐specific Real‐time reliability‐related tasks identified by the entity pursuant to Requirement R1 part 1.1. [Please see the standard for more information] | Long Term Planning | Active | MEDIUM | Transfer | Requirement 5 could be retired outright, because the industry stakeholders believe it is excessive to require a systematic approach to training for Operations Support Personnel on how their jobs impact real-time operations, particularly for ratings engineers. There is little value in training people on a topic they already understand quite well due to very nature of their jobs. | No Action | No action recommended.
PER-005-2 | R6. | Each Generator Operator shall use a systematic approach to develop and implement training to its personnel identified in Applicability Section 4.1.5.1 of this standard, on how their job function(s) impact the reliable operations of the BES during normal and emergency operations. [Please see the standard for more information] | Long Term Planning | Active | MEDIUM | Transfer | Requirement 6 could be retired outright because for most generation, the BA staff performs central dispatching and associated risks are addressed by PER-005-2. For all other generation, the risks are addressed by TOP and VAR standards. Operations Support Personnel know their impact to reliability and the task list. The prep and training used for OSP and the trainers is better spent for their job duties in support of reliability. | No Action | No action recommended.
PRC-002-2 | R1. | Each Transmission Owner shall: 1.1. Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-2, Attachment 1. 1.2. Notify other owners of BES Elements connected to those BES buses, if any, within 90-calendar days of completion of Part 1.1, that those BES Elements require SER data and/or FR data. 1.3. Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners, if any, in accordance with Part 1.2, and implement the re-evaluated list of BES buses as per the Implementation Plan. | Long Term Planning | Active | LOWER | No Action |  | No Action | No action recommended.
PRC-002-2 | R10. | Each Transmission Owner and Generator Owner shall time synchronize all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to meet the following: 10.1 Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. 10.2 Synchronized device clock accuracy within ± 2 milliseconds of UTC. | Long Term Planning | Active | LOWER | Modification | Again, overly prescriptive and if needed to stay could perhaps be combined with the recording requirement R8 and stipulate that the DME device have continuous monitoring capabilities and be time synchronized. | PRT | Recommend for periodic review and if other modifications are needed as some gains could be achieved moving parts around, but may not be practical.
PRC-002-2 | R11. | Each Transmission Owner and Generator Owner shall provide, upon request, all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to the Responsible Entity, Regional Entity, or NERC in accordance with the following: 11.1 Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. 11.2 Data subject to Part 11.1 will be provided within 30-calendar days of a request unless an extension is granted by the requestor. 11.3 SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. 11.4 FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. 11.5 Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. | Long Term Planning | Active | LOWER | No Action |  | No Action | No action recommended.
PRC-002-2 | R12. | Each Transmission Owner and Generator Owner shall, within 90-calendar days of the discovery of a failure of the recording capability for the SER, FR or DDR data, either: • Restore the recording capability, or • Submit a Corrective Action Plan (CAP) to the Regional Entity and implement | Long Term Planning | Active | LOWER | Transfer | This used to be a maintenance requirement under PRC-018-1, R6 and I don't know why the SDT didn't recommend that this requirement move to PRC-005-6 with it's own table similar to alarming paths and monitoring (Table 2). The argument is that PRC-005-6 addresses specific maintenance around Protection Systems but DME's address the event logging to determine post mortem analysis of Protection Systems. The construct is already there for PRC-005-6 and governs the maintenance of assets that are being used for alarming and monitoring (Table 2). | No Action | Retain. Moving to PRC-005 would increase the obligations set forth in PRC-002.
PRC-002-2 | R2. | Each Transmission Owner and Generator Owner shall have SER data for circuit breaker position (open/close) for each circuit breaker it owns connected directly to the BES buses identified in Requirement R1 and associated with the BES Elements at those BES buses. | Long Term Planning | Active | LOWER | No Action |  | No Action | No action recommended.
PRC-002-2 | R3. | Each Transmission Owner and Generator Owner shall have FR data to determine the following electrical quantities for each triggered FR for the BES Elements it owns connected to the BES buses identified in Requirement R1: 3.1 Phase-to-neutral voltage for each phase of each specified BES bus. 3.2 Each phase current and the residual or neutral current for the following BES Elements: 3.2.1 Transformers that have a low-side operating voltage of 100kV or above. 3.2.2 Transmission Lines. | Long Term Planning | Active | LOWER | No Action |  | No Action | No action recommended.
PRC-002-2 | R4. | Each Transmission Owner and Generator Owner shall have FR data as specified in Requirement R3 that meets the following: 4.1 A single record or multiple records that include: • A pre-trigger record length of at least two cycles and a total record length of at least 30-cycles for the same trigger point, or • At least two cycles of the pre-trigger data, the first three cycles of the post-trigger data, and the final cycle of the fault as seen by the fault recorder. 4.2 A minimum recording rate of 16 samples per cycle. 4.3 Trigger settings for at least the following: 4.3.1 Neutral (residual) overcurrent. 4.3.2 Phase undervoltage or overcurrent. | Long Term Planning | Active | LOWER | No Action |  | No Action | No action recommended.
PRC-002-2 | R5. | Each Responsible Entity shall: 5.1 Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: 5.1.1 Generating resource(s) with: 5.1.1.1 Gross individual nameplate rating greater than or equal to 500 MVA. 5.1.1.2 Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. 5.1.2 Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). 5.1.3 Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter. 5.1.4 One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). 5.1.5 Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. 5.2 Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: 5.2.1 One BES Element; and 5.2.2 One BES Element per 3,000 MW of the Responsible Entity’s historical simultaneous peak System Demand. 5.3 Notify all owners of identified BES Elements, within 90-calendar days of completion of Part 5.1, that their respective BES Elements require DDR data when requested. 5.4 Re-evaluate all BES Elements at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3 to implement the re-evaluated list of BES Elements as per the Implementation Plan. | Long Term Planning | Active | LOWER | No Action |  | No Action | No action recommended.
PRC-002-2 | R6. | Each Transmission Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: 6.1 One phase-to-neutral or positive sequence voltage. 6.2 The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. 6.3 Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. 6.4 Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. | Long Term Planning | Active | LOWER | No Action |  | No Action | No action recommended.
PRC-002-2 | R7. | Each Generator Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: 7.1 One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. 7.2 The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. 7.3 Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. 7.4 Frequency of at least one of the voltages in Requirement R7, Part 7.1. | Long Term Planning | Active | LOWER | No Action |  | No Action | No action recommended.
PRC-002-2 | R8. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have continuous data recording and storage. If the equipment was installed prior to the effective date of this standard and is not capable of continuous recording, triggered records must meet the following: 8.1 Triggered record lengths of at least three minutes. 8.2 At least one of the following three triggers: • Off nominal frequency trigger set at: Low High o Eastern Interconnection <59.75 Hz >61.0 Hz o Western Interconnection <59.55 Hz >61.0 Hz o ERCOT Interconnection <59.35 Hz >61.0 Hz o Hydro-Quebec Interconnection <58.55 Hz >61.5 Hz • Rate of change of frequency trigger set at: o Eastern Interconnection < -0.03125 Hz/sec > 0.125 Hz/sec o Western Interconnection < -0.05625 Hz/sec > 0.125 Hz/sec o ERCOT Interconnection < -0.08125 Hz/sec > 0.125 Hz/sec o Hydro-Quebec Interconnection < -0.18125 Hz/sec > 0.1875 Hz/sec • Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. | Long Term Planning | Active | LOWER | Modification | This was a variation from the original requirement in PRC-018-1, R5. This seems to be overly prescriptive and needs to be simplified by requiring that entities continuously monitor only. Most entities aren't going to have DME's already installed in locations stipulated per R5 of this standard. | PRT | Recommend for periodic review and if other modifications are needed, this requirement is prescriptive and would require further technical discussion and expertise.
PRC-002-2 | R9. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have DDR data that meet the following: 9.1 Input sampling rate of at least 960 samples per second. 9.2 Output recording rate of electrical quantities of at least 30 times per second. | Long Term Planning | Active | LOWER | No Action |  | No Action | No action recommended.
PRC-004-5(i) | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: 1.1 The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and 1.2 The BES interrupting device owner owns all or part of the Composite Protection System; and 1.3 The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | Operations Assessment, Operations Planning | Active | HIGH | Modification | While it is critical that any BES interrupting device operation be evaluated to determine whether it operated properly, and also if it caused a Misoperation, it may be possible to consolidate Requirements R1, R2, and R3. | No Action | No action recommended.
PRC-004-5(i) | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] 2.1 For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: 2.1.1 The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and 2.1.2 The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and 2.1.3 The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. 2.2 For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | Operations Assessment, Operations Planning | Active | HIGH | Modification | While it is critical that any BES interrupting device operation be evaluated to determine whether it operated properly, and also if it caused a Misoperation, it may be possible to consolidate Requirements R1, R2, and R3. | No Action | No action recommended.
PRC-004-5(i) | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. | Operations Assessment, Operations Planning | Active | HIGH | Modification | While it is critical that any BES interrupting device operation be evaluated to determine whether it operated properly, and also if it caused a Misoperation, it may be possible to consolidate Requirements R1, R2, and R3. | No Action | No action recommended.
PRC-004-5(i) | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | Operations Planning and Operations Assessment | Active | HIGH | Retirement | An entity should always endeavor to determine the cause of a Misoperation, although doing so may take extended time if equipment outages are necessary. However, if an entity is unable to determine the cause, further investigations are unlikely to lead to additional observations unless additional misoperations occur. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
PRC-004-5(i) | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | Long Term Planning and Operations Planning | Active | HIGH | No Action | In order to minimize the potential for cascading outages, it is essential that CAPs be developed to correct both the proximate cause and root cause of the Misoperation. | No Action | No action recommended.
PRC-004-5(i) | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. | Long Term Planning and Operations Planning | Active | HIGH | No Action | In order to minimize the potential for cascading outages, it is essential that CAPs be implemented as expeditiously as possible. | No Action | No action recommended.
PRC-005-1.1b | R1. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: R1.1. Maintenance and testing intervals and their basis. R1.2. Summary of maintenance and testing procedures. |  | Active |  | No Action | • PRC-005-1.1b has been superseded by PRC-005-2 and beyond versions. • PRC-005-1.1b retirement has already been approved by FERC and is in gradual phase-out due to the long implementation plan of standard PRC-005-6. This is necessary to ensure compliance of equipment for which maintenance activities have not yet been performed under revised PRC-005-6 criteria. | Superseded | Superseded.
PRC-005-1.1b | R2. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Entity on request (within 30 calendar days). The documentation of the program implementation shall include: R2.1. Evidence Protection System devices were maintained and tested within the defined intervals. R2.2. Date each Protection System device was last tested/maintained. |  | Active |  | No Action | • PRC-005-1.1b has been superseded by PRC-005-2 and beyond versions. • PRC-005-1.1b retirement has already been approved by FERC and is in gradual phase-out due to the long implementation plan of standard PRC-005-6. This is necessary to ensure compliance of equipment for which maintenance activities have not yet been performed under revised PRC-005-6 criteria. | Superseded | Superseded.
PRC-005-6 | R1 | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. The PSMP shall: 1.1. Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. 1.2. Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. | Operations Planning | Active | MEDIUM | Transfer | Retire R1 but transfer to tables at the end of PRC-005-6 Standard. Modify Table 1.4 to add a line specifying that battery maintenance cannot be performance-based. Justification: • The Protection System Maintenance Program (PSMP) acts as a control for the performance-based requirements R3 and R4. Entities are required to perform maintenance on Protection Systems (PS) as specified in requirements R3 and R4. Establishing a PSMP identifying maintenance methods and applicable monitored component attributes, as indicated in R1, is a prerequisite to maintenance activities that does not need not to be formalized in a standard. - Experts on PRC-005 drafting teams determined that battery maintenance should be time-based. This requirement (second half of R1.1) must be maintained for reliability purposes but could be inserted as an additional line or note in PRC-005-6 Table 1.4 (Also refer to recommendation for R4 whereby our team is recommending adding a line to all tables for performance-based maintenance.) | No Action | Retain. R1 establishes the PSMP and it would need to be included in another requirement to retire R1. Including Lithium-Ion batteries will require technical expertise and SAR for such modifications. Moving the line specifying that battery maintenance cannot be performance-based is not a sufficient gain in efficiency (Part 1.1).
PRC-005-6 | R2 | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | Operations Planning | Active | MEDIUM | Transfer | Retire R2 and transfer info to Tables at the end of PRC-005-6 standard. Justification • R4 implements performance-based maintenance program and R2 specifies the criteria to establish this maintenance program. R2 could be retired and a line could be added in each of the Tables at the end of the standard (except for batteries see R1) to allow for performance-based maintenance as per Attachment A. | No Action | The recommended change requires significant work and would not result in a quick efficiency gain. May require a SAR and technical work.
PRC-005-6 | R3 | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5. | Operations Planning | Active | HIGH | Consolidate | Modify R3 to take into account Unresolved Maintenance Issues. And consolidate R3 and R4. • Maintenance on Protection Systems is necessary for reliability. • An Unresolved Maintenance Issue (UMI) should not lead to non-compliance with R3 because all maintenance activities could not be completed during the maintenance interval. Thus, the requirement should be worded to take into account UMI exceptions. • R3 and R4 can be consolidated and refer to Tables at the end of the standard as long as Tables are augmented to each include a line for performance-based maintenance. • Note: The standard allows two maintenance methods: time-based and performance-based. Entitles that suggest modifying time intervals for Sudden Pressure Relays (SPR) maintenance can use the performance-based method. | No Action | The recommended change requires significant work and would not result in a quick efficiency gain. May require a SAR and technical work.
PRC-005-6 | R4 | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performance-based program(s). | Operations Planning | Active | HIGH | Consolidate | Modify R4 to take into account Unresolved Maintenance Issues. Consolidate R3 and R4. • Maintenance on Protection Systems is necessary for reliability. • R4 provides an alternative to time-based maintenance. • R3 and R4 can be consolidated and simply refer to Tables at the end of the standard as long as tables are augmented to each include a line for performance-based maintenance. The component column could, for example for Table 1.1, read " Protective Relays that utilize performance based maintenance with all attributes of Attachment A". Whereas the Maximum Maintenance Interval would be " As determined by performance-based maintenance" • An Unresolved Maintenance Issue (UMI) should not lead to non-compliance with R4 because all maintenance activities could not be completed during the maintenance interval. Thus, the requirement should be worded to take into account UMI exceptions. | No Action | The recommended change requires significant work and would not result in a quick efficiency gain. May require a SAR and technical work.
PRC-005-6 | R5 | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | Operations Planning | Active | MEDIUM | No action | Justification • R5 provides an exception to full compliance with R3 and R4 and thus reduces self-reporting or self-logging. • Notes: a) Some entities view R5 as a compliance burden and do not want to prove a null set of data. M5 or the RSAW could be modified to specify that successful completion of the maintenance program demonstrates that R5 is not applicable. b) MRO-NSRF raised the possibility of double jeopardy of non-compliance for R3 and R5. This has led to a recommendation of rewording for R3 and R4. | No Action | No action recommended.
PRC-006-3 | D.B.1. | Each Planning Coordinator shall participate in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that develops and documents criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES) that may form islands. | Long Term Planning | Active | MEDIUM | No Action |  | No Action | No action recommended.
PRC-006-3 | D.B.2. | Each Planning Coordinator shall identify one or more islands from the regional review (per D.B.1) to serve as a basis for designing a region-wide coordinated UFLS program including: [Please see the standard for more information] | Long Term Planning | Active | MEDIUM | No Action |  | No Action | No action recommended.
PRC-006-3 | D.B.3. | Each Planning Coordinator shall adopt a UFLS program, coordinated across the WECC Regional Entity area, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). [Please see the standard for more information] | Long Term Planning | Active | HIGH | No Action |  | No Action | No action recommended.
PRC-006-3 | D.B.4. | Each Planning Coordinator shall participate in and document a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2. The simulation shall model each of the following: [Please see the standard for more information] | Long Term Planning | Active | HIGH | No Action |  | No Action | No action recommended.
PRC-006-3 | R1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. | Long Term Planning | Active | MEDIUM | Transfer | The goal is to eventually retire R1 as the PRC-006, R2 is modified in Stage 2 to include criteria to identify potential islands. | No Action | Retain. No significant gain by combining elements of R1 into R2.
PRC-006-3 | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | Long Term Planning | Active | HIGH | No Action |  | No Action | No action recommended.
PRC-006-3 | R11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment within one year of actuation 11.1. The performance of the UFLS equipment, 11.2. The effectiveness of the UFLS program. | Operations Assessment | Active | MEDIUM | No Action | This requirement ensures that the PC performs analysis to evaluate the effectiveness of the UFLS program to maintain reliable operation, mitigate emergencies and meet system performance requirements. UFLS is usually the final effort taken to maintain system stability and PC needs to validate that the program is effective. This also assures that the study model and system behaviors match with real-time model and system performances | No Action | No action recommended.
PRC-006-3 | R12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | Operations Assessment | Active | MEDIUM | No Action | This requirement enables the PC to correct any inconsistencies identified in the existing UFLS program to avoid future operational deficiencies to maintain reliable operation, mitigate emergencies and meet system performance requirements. Failure to properly design, implement, and maintain UFLS could result in the UFLS not being deployed correctly, which could result in system instability conditions. | No Action | No action recommended.
PRC-006-3 | R13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following:  Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or  Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or  Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | Operations Assessment | Active | MEDIUM | No Action | UFLS is not a local system issue and coordination with other PCs is necessary to implement the most effective program. | No Action | No action recommended.
PRC-006-3 | R14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following [Please see the standard for more information] | Long Term Planning | Active | LOWER | Modification | The response to the written comments is administrative and could be moved to an information/Data request process. Or the requirement could be combined into PRC-006-2 R3 and/or R5 to include UFLS entities and Transmission Owners as a part of the coordination process with PCs. | Retire w/ modification | The response to the written comments is administrative and could be moved to an information/Data request process. Or the requirement could be combined into PRC-006-2 R3 and/or R5 to include UFLS entities and Transmission Owners as a part of the coordination process with PCs.
PRC-006-3 | R15. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. [Please see the standard for more information] | Long Term Planning | Active | HIGH | No Action |  | No Action | No action recommended.
PRC-006-3 | R2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: [Please see the standard for more information] | Long Term Planning | Active | MEDIUM | Modification | Section 2.1 of this requirement should be modified to include the criteria language from R1. | No Action | Retain. No significant gain by combining elements of R1 into R2.
PRC-006-3 | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). [Please see the standard for more information] | Long Term Planning | Active | HIGH | No Action |  | No Action | No action recommended.
PRC-006-3 | R4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: [Please see the standard for more information] | Long Term Planning | Active | HIGH | No Action |  | No Action | No action recommended.
PRC-006-3 | R5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | Long Term Planning | Active | HIGH | No Action |  | No Action | No action recommended.
PRC-006-3 | R6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | Long Term Planning | Active | LOWER | Transfer | This requirement (partially or wholly) could be consolidated into a list of required items that an entity must provide if requested. | No Action | This could be included in Phase concept #5 - Data Exchange
PRC-006-3 | R7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | Long Term Planning | Active | LOWER | Transfer | This requirement (partially or wholly) could be consolidated into a list of required items that an entity must provide if requested. | No Action | This could be included in Phase concept #5 - Data Exchange
PRC-006-3 | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | Long Term Planning | Active | LOWER | No Action |  | No Action | No action recommended.
PRC-006-3 | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | Long Term Planning | Active | HIGH | No Action |  | No Action | No action recommended.
PRC-010-2 | R1. | Each Planning Coordinator or Transmission Planner that is developing a UVLS Program shall evaluate its effectiveness and subsequently provide the UVLS Program’s specifications and implementation schedule to the UVLS entities responsible for implementing the UVLS Program. The evaluation shall include, but is not limited to, studies and analyses that show: [Please see the standard for more information] | Long Term Planning | Active | HIGH | No Action |  | No Action | No action recommended.
PRC-010-2 | R2. | Each UVLS entity shall adhere to the UVLS Program specifications and implementation schedule determined by its Planning Coordinator or Transmission Planner associated with UVLS Program development per Requirement R1 or with any Corrective Action Plans per Requirement R5. | Long Term Planning | Active | HIGH | No Action |  | No Action | No action recommended.
PRC-010-2 | R3. | Each Planning Coordinator or Transmission Planner shall perform a comprehensive assessment to evaluate the effectiveness of each of its UVLS Programs at least once every 60 calendar months. Each assessment shall include, but is not limited to, studies and analyses that evaluate whether: [Please see the standard for more information] | Long Term Planning | Active | MEDIUM | No Action |  | No Action | No action recommended.
PRC-010-2 | R4. | Each Planning Coordinator or Transmission Planner shall, within 12 calendar months of an event that resulted in a voltage excursion for which its UVLS Program was designed to operate, perform an assessment to evaluate: 4.1. Whether its UVLS Program resolved the undervoltage issues associated with the event, and 4.2. The performance (i.e., operation and non-operation) of the UVLS Program equipment. | Operations Planning | Active | MEDIUM | No Action | A comprehensive evaluation of the UVLS operation will help to identify any current/potential deficiencies of the program and will assist the entities to be proactive and incorporate modifications to be prepared for similar circumstances in the future. Event analysis will also identify effectiveness of the system model used in the simulated study analysis by assessing the difference between the expected system behavior versus the actual system behavior during the event. Therefore, no modification to the existing requirement is necessary. | No Action | No action recommended.
PRC-010-2 | R5. | Each Planning Coordinator or Transmission Planner that identifies deficiencies during an assessment performed in either Requirement R3 or R4 shall develop a Corrective Action Plan to address the deficiencies and subsequently provide the Corrective Action Plan, including an implementation schedule, to UVLS entities within three calendar months of completing the assessment. | Operations Planning | Active | MEDIUM | No Action | It is prudent to correct any inconsistencies identified during the event analysis per requirements R3 or R4. This will prevent future operational deficiencies, minimize risks and enhance system reliability. Therefore, no modification to the existing requirement is necessary. | No Action | No action recommended.
PRC-010-2 | R6. | Each Planning Coordinator that has a UVLS Program in its area shall update a database containing data necessary to model the UVLS Program(s) in its area for use in event analyses and assessments of the UVLS Program at least once each calendar year. | Operations Planning | Active | LOWER | Transfer | Provision and maintenance of databases to support reliability studies/analysis could be bundled into a model data submission and collection standard that apply to all registered entities and to avoid similar requirement in each standard. MOD-032-1 Standard has established consistent modeling data requirements, reporting procedures and data exchange schedules for developing planning horizon cases necessary to support reliability analysis of the interconnected transmission system. Data submitted to meet MOD-032-1 requirement is periodically checked and updated to maintain accuracy. Requirements also establish a feedback loop and time-frames to address data concerns between parties. MOD standards support the level of TPL-001-4 reliability standard modeling and all devices and equipment in the electric grid must be modeled correctly to capture how the equipment or program performs under specific system analysis. UVLS Program data submission can be added to MOD-032-01- Attachment 1: Data Reporting Requirements. | No Action | This could be included in Phase concept #5 - Data Exchange
PRC-010-2 | R7. | Each UVLS entity shall provide data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of a UVLS Program database. | Operations Planning | Active | LOWER | Transfer | Provision and maintenance of databases to support reliability studies/analysis could be bundled into a model data submission and collection standard that apply to all registered entities and to avoid similar requirement in each standard. MOD-032-1 Standard has established consistent modeling data requirements, reporting procedures and data exchange schedules for developing planning horizon cases necessary to support reliability analysis of the interconnected transmission system. Data submitted to meet MOD-032-1 requirement is periodically checked and updated to maintain accuracy. Requirements also establish a feedback loop and time-frames to address data concerns between parties. MOD standards support the level of TPL-001-4 reliability standard modeling and all devices and equipment in the electric grid must be modeled correctly to capture how the equipment or program performs under specific system analysis. UVLS Program data submission can be added to MOD-032-01- Attachment 1: Data Reporting Requirements. | No Action | This could be included in Phase concept #5 - Data Exchange
PRC-010-2 | R8. | Each Planning Coordinator that has a UVLS Program in its area shall provide its UVLS Program database to other Planning Coordinators and Transmission Planners within its Interconnection, and other functional entities with a reliability need, within 30 calendar days of a written request. | Operations Planning | Active | LOWER | Transfer | Provision and maintenance of databases to support reliability studies/analysis could be bundled into a model data submission and collection standard that apply to all registered entities and to avoid similar requirement in each standard. MOD-032-1 Standard has established consistent modeling data requirements, reporting procedures and data exchange schedules for developing planning horizon cases necessary to support reliability analysis of the interconnected transmission system. Data submitted to meet MOD-032-1 requirement is periodically checked and updated to maintain accuracy. Requirements also establish a feedback loop and time-frames to address data concerns between parties. MOD standards support the level of TPL-001-4 reliability standard modeling and all devices and equipment in the electric grid must be modeled correctly to capture how the equipment or program performs under specific system analysis. UVLS Program data submission can be added to MOD-032-01- Attachment 1: Data Reporting Requirements. Exchange of system model data between entities within an Interconnection is already being managed pursuant to MOD-032-1, R4 requirement. | No Action | This could be included in Phase concept #5 - Data Exchange
PRC-012-2 | R1. | Prior to placing a new or functionally modified RAS in service or retiring an existing RAS, each RAS-entity shall provide the information identified in Attachment 1 for review to the Reliability Coordinator(s) where the RAS is located. | Operations Planning | Future | MEDIUM | No Action | SER – Operational Planning Team suggest this requirement be unchanged until such time after its enforcement (2021) and use that the industry has had time to discern issues associated to it based on the database of RAS schemes provided to the Reliability Coordinator(s). Recommendation is thus “No Action”. | No Action | No action recommended.
PRC-012-2 | R2. | Each Reliability Coordinator that receives Attachment 1 information pursuant to Requirement R1 shall, within four full calendar months of receipt or on a mutually agreed upon schedule, perform a review of the RAS in accordance with Attachment 2, and provide written feedback to each RAS-entity. | Operations Planning | Future | MEDIUM | No Action | SER – Operational Planning Team suggest this requirement be unchanged until such time after its enforcement (2021) and use that the industry has had time to discern issues associated to it based on the database of RAS schemes provided to the Reliability Coordinator(s). Recommendation is thus “No Action”. | No Action | No action recommended.
PRC-012-2 | R3. | Prior to placing a new or functionally modified RAS in service or retiring an existing RAS, each RAS‐entity that receives feedback from the reviewing Reliability Coordinator(s) identifying reliability issue(s) shall resolve each issue to obtain approval of the RAS from each reviewing Reliability Coordinator. | Operations Planning | Future | MEDIUM | No Action | SER – Operational Planning Team suggest this requirement be unchanged until such time after its enforcement (2021) and use that the industry has had time to discern issues associated to it based on the database of RAS schemes provided to the Reliability Coordinator(s). Recommendation is thus “No Action”. | No Action | No action recommended.
PRC-012-2 | R5. | Each RAS-entity, within 120 full calendar days of a RAS operation or a failure of its RAS to operate when expected, or on a mutually agreed upon schedule with its reviewing Reliability Coordinator(s), shall: 5.1. Participate in analyzing the RAS operational performance to determine whether: 5.1.1. The System events and/or conditions appropriately triggered the RAS. 5.1.2. The RAS responded as designed. 5.1.3. The RAS was effective in mitigating BES performance issues it was designed to address. 5.1.4. The RAS operation resulted in any unintended or adverse BES response. 5.2. Provide the results of RAS operational performance analysis that identified any deficiencies to its reviewing Reliability Coordinator(s). | Operations Planning | Future | MEDIUM | No Action | SER – Operational Planning Team suggest this requirement be unchanged until such time after its enforcement (2021) and use that the industry has had time to discern issues associated to it based on the database of RAS schemes provided to the Reliability Coordinator(s). Recommendation is thus “No Action”. | No Action | No action recommended.
PRC-012-2 | R6. | Each RAS-entity shall participate in developing a Corrective Action Plan (CAP) and submit the CAP to its reviewing Reliability Coordinator(s) within six full calendar months of: • Being notified of a deficiency in its RAS pursuant to Requirement R4, or • Notifying the Reliability Coordinator of a deficiency pursuant to Requirement R5, Part 5.2, or • Identifying a deficiency in its RAS pursuant to Requirement R8. | Long Term Planning and Operations Planning | Future | MEDIUM | No Action | SER – Operational Planning Team suggest this requirement be unchanged until such time after its enforcement (2021) and use that the industry has had time to discern issues associated to it based on the database of RAS schemes provided to the Reliability Coordinator(s). Recommendation is thus “No Action”. | No Action | No action recommended.
PRC-012-2 | R7. | Each RAS-entity shall, for each of its CAPs developed pursuant to Requirement R6: 7.1. Implement the CAP. 7.2. Update the CAP if actions or timetables change. 7.3. Notify each reviewing Reliability Coordinator if CAP actions or timetables change and when the CAP is completed. | Long Term Planning and Operations Planning | Future | MEDIUM | No Action | SER – Operational Planning Team suggest this requirement be unchanged until such time after its enforcement (2021) and use that the industry has had time to discern issues associated to it based on the database of RAS schemes provided to the Reliability Coordinator(s). Recommendation is thus “No Action”. | No Action | No action recommended.
PRC-012-2 | R9. | Each Reliability Coordinator shall update a RAS database containing, at a minimum, the information in Attachment 3 at least once every twelve full calendar months. | Operations Planning | Future | LOWER | Transfer | This Requirement could be transferred to the RC certification program and made a required procedure . The requirement is administrative in nature and causes the RC to perform a minimal to no risk activity that does not contribute to reliable operations. | No Action | Originally considered for certification
PRC-017-1 | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place. The program(s) shall include: [Please see the standard for more information] |  | Active | HIGH | No Action | • PRC-017 maintenance has been superseded by PRC-005-2 and beyond versions. RAS maintenance is included in PRC-005-6 applicability section 4.2.4 • PRC-017 testing will be superseded by PRC-012-2 – Remedial Action Schemes, Requirement R8. • PRC-017-0 retirement has already been approved by FERC and is in gradual phase-out due to the long implementation plan of standards PRC-005-6. This is necessary to ensure compliance of equipment for which maintenance activities have not yet been performed under revised PRC-005-6 criteria. | Superseded | Superseded.
PRC-017-1 | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall provide documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). |  | Active | LOWER | No Action | • PRC-017 maintenance has been superseded by PRC-005-2 and beyond versions. RAS maintenance is included in PRC-005-6 applicability section 4.2.4 • PRC-017 testing will be superseded by PRC-012-2 – Remedial Action Schemes, Requirement R8. • PRC-017-0 retirement has already been approved by FERC and is in gradual phase-out due to the long implementation plan of standards PRC-005-6. This is necessary to ensure compliance of equipment for which maintenance activities have not yet been performed under revised PRC-005-6 criteria. | Superseded | Superseded.
PRC-018-1 | R1. | Each Transmission Owner and Generator Owner required to install DMEs by its Regional Reliability Organization (reliability standard PRC-002 Requirements 1-3) shall have DMEs installed that meet the following requirements: [Please see the standard for more information] |  | Active | LOWER | No Action | This requirement requires a TO or GO to ensure that DME's installed per PRC-002-1 and meet specific criteria. PRC-002-1 was never approved by FERC but PRC-018 was approved on the basis that each RRO would establish a DME program and that even if PRC-002-1 were not approved, PRC-018 could be enforced per the RRO program. Most RRO's have retired their programs which establish the scope of DME's for this standard. | Superseded | Will retire in 2022, tied to PRC-002
PRC-018-1 | R2. | The Transmission Owner and Generator Owner shall each install DMEs in accordance with its Regional Reliability Organization’s installation requirements (reliability standard PRC-002 Requirements 1 through 3). |  | Active | LOWER | No Action | This requirement requires a TO or GO to ensure that DME's installed per PRC-002-1 and meet specific criteria. PRC-002-1 was never approved by FERC but PRC-018 was approved on the basis that each RRO would establish a DME program and that even if PRC-002-1 were not approved, PRC-018 could be enforced per the RRO program. Most RRO's have retired their programs which establish the scope of DME's for this standard. | Superseded | Will retire in 2022, tied to PRC-002
PRC-018-1 | R3. | The Transmission Owner and Generator Owner shall each maintain, and report to its Regional Reliability Organization on request, the following data on the DMEs installed to meet that region’s installation requirements (reliability standard PRC-002 Requirements1.1, 2.1 and 3.1): [Please see the standard for more information] |  | Active | LOWER | No Action | This requirement requires a TO or GO to ensure that DME's installed per PRC-002-1 and meet specific criteria. PRC-002-1 was never approved by FERC but PRC-018 was approved on the basis that each RRO would establish a DME program and that even if PRC-002-1 were not approved, PRC-018 could be enforced per the RRO program. Most RRO's have retired their programs which establish the scope of DME's for this standard. | Superseded | Will retire in 2022, tied to PRC-002
PRC-018-1 | R4. | The Transmission Owner and Generator Owner shall each provide Disturbance data (recorded by DMEs) in accordance with its Regional Reliability Organization’s requirements (reliability standard PRC-002 Requirement 4). |  | Active | LOWER | No Action | This requirement requires a TO or GO to ensure that DME's installed per PRC-002-1 and meet specific criteria. PRC-002-1 was never approved by FERC but PRC-018 was approved on the basis that each RRO would establish a DME program and that even if PRC-002-1 were not approved, PRC-018 could be enforced per the RRO program. Most RRO's have retired their programs which establish the scope of DME's for this standard. | Superseded | Will retire in 2022, tied to PRC-002
PRC-018-1 | R5. | The Transmission Owner and Generator Owner shall each archive all data recorded by DMEs for Regional Reliability Organization-identified events for at least three years. |  | Active | LOWER | No Action | This requirement requires a TO or GO to ensure that DME's installed per PRC-002-1 and meet specific criteria. PRC-002-1 was never approved by FERC but PRC-018 was approved on the basis that each RRO would establish a DME program and that even if PRC-002-1 were not approved, PRC-018 could be enforced per the RRO program. Most RRO's have retired their programs which establish the scope of DME's for this standard. | Superseded | Will retire in 2022, tied to PRC-002
PRC-018-1 | R6. | Each Transmission Owner and Generator Owner that is required by its Regional Reliability Organization to have DMEs shall have a maintenance and testing program for those DMEs that includes: [Please see the standard for more information] |  | Active | LOWER | No Action | This requirement requires a TO or GO to ensure that DME's installed per PRC-002-1 and meet specific criteria. PRC-002-1 was never approved by FERC but PRC-018 was approved on the basis that each RRO would establish a DME program and that even if PRC-002-1 were not approved, PRC-018 could be enforced per the RRO program. Most RRO's have retired their programs which establish the scope of DME's for this standard. | Superseded | Will retire in 2022, tied to PRC-002
PRC-019-2 | R1. | At a maximum of every five calendar years, each Generator Owner and Transmission Owner with applicable Facilities shall coordinate the voltage regulating system controls, (including in-service limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. 1.1. Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: 1.1.1. The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. 1.1.2. The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. | Long Term Planning | Active | MEDIUM | Retirement | There is no reliability benefit from performing the coordination every five years. R2 already requires that any change that impacts the voltage regulating coordination be performed within 90 days of changes. If this requirement is followed, the five year coordination is an unnecessary paper exercise with no benefit. Doing this every five years adds little to reliability, suggest changing the cycle to 10 years. Informational: FERC Approved 5/29/15; RD15-3-000, NERC Project 2014-01 | Refer to Project 2021-01 | Defer to SPCS or other group that is actively looking at modifications to the standard.
PRC-019-2 | R2. | Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, each Generator Owner and Transmission Owner with applicable Facilities shall perform the coordination as described in Requirement R1. These possible systems, equipment or settings changes include, but are not limited to the following: • Voltage regulating settings or equipment changes; • Protection System settings or component changes; • Generating or synchronous condenser equipment capability changes; or • Generator or synchronous condenser step-up transformer changes. | Long Term Planning | Active | MEDIUM | No Action |  | Refer to Project 2021-01 | Defer to SPCS or other group that is actively looking at modifications to the standard.
PRC-023-4 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. See standard for Criteria. | Long Term Planning | Active | HIGH | No Action | Requirement should be retained to ensure transmission system loadability is not limited and thereby negatively adversely affecting reliability. | No Action | No action recommended.
PRC-023-4 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. | Long Term Planning | Active | HIGH | No Action | Requirement should be retained to ensure transmission system loadability is not limited and thereby negatively adversely affecting reliability. | Refer to SPCS SAR on PRC-023 | Refer to SPCS SAR on PRC-023
PRC-023-4 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. | Long Term Planning | Active | MEDIUM | Modification | FAC-008 R6 already obligates TOs and GOs to have facility ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. If the GO or TO uses PRC-023-4 R1 criterion for its calculated circuit capability that criterion becomes the methodology or documentation that must be used for its facility ratings, their compliance obligation for FAC-008-3 R6 would default to the PRC-023-4 R1 criterion. The SDT would also have to address any gaps that would present themselves due to the retirement of the requirement, such as applicability to all of the registered entities that are impacted or have to comply with the standard. | No Action | This could go forward with the inclusion of the Distribution Provider in FAC-008 as an applicable entity.
PRC-023-4 | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. | Long Term Planning | Active | LOWER | Modification | This requirement could be retired and covered within the data specifications for MOD-032 if the applicable entity list is modified to include Distribution Provider. More specifically, MOD-032-1 R1 obligates the PC and TPs within its area to develop the data requirements and reporting procedures relative to steady state, dynamics and short circuit modeling using Attachment 1 or additional criteria it deems necessary. IRO-010 and TOP-003 standards have established data specification and collection requirements that could be utilized to fulfill the intent of this requirement. Additionally, this requirement has no reliability benefit. This is simply one of the options for setting the relays, and whether the entity chooses to use a lower margin for the maximum short-term seasonal rating or a higher margin for the maximum long-term seasonal rating is immaterial. | No Action | A 15-minute (thermal) rating is an element of Facility Ratings. A relay loadability of 115% of this value is above the actual Facility Rating, and therefore imposes no additional planning or operating restrictions. This requirement is to provide a list of the applicable circuits to the other specified entities without the actual relay loadability of those circuits nor a specified reliability goal for the use of that data. Therefore, this requirement may be retired with no impact on reliability. Conflict: FAC-008 R7/R8 that require the GO/TO provide Facility Ratings to the TOP/RC/PC/TP is being retired by Project 2018-03. Due to the PC/TP being in that requirement and not included in the justification of R7/R8 being covered by the data specification in IRO-010 and TOP-003, this requirement should be retained.
PRC-023-4 | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. | Long Term Planning | Active | LOWER | Modification | During the Paragraph 81 initiative an Independent Expert Review Panel's (IERP) suggested NERC retire the requirement as "P81. Administrative/Documentation". It’s not clear what the risk to reliability is if the entity doesn’t report that information to the Regions. If this requirement is maintained, perhaps data could be provided on request by way of some other mechanism, rather than automatically. | PRT | Retire/PRT. Needs to be reviewed for reliability justification.
PRC-023-4 | R6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: 6.1 Maintain a list of circuits subject to PRC-023-4 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-4, Attachment B applies. 6.2 Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. | Long Term Planning | Active | HIGH | Modification | The Paragraph 81 initiative suggested that the Regional Entities do not use the data being requested in this requirement and R6.2 should be retired. There is also an opportunity to reduce the evaluation criteria to only evaluate elements not included in the Remedial Action Schemes. | Modify | Modify. Remove the entity "Regional Entities" from part 6.2. Refer to SPCS SAR on PRC-023. 6.2 Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. The opportunity to reduce the evaluation criteria to only evaluate elements not included in the Remedial Action Schemes is beyond the scope of the review.
PRC-024-2 | R1. | Each Generator Owner shall provide its applicable generator protection trip settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated unit within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested trip settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of relay setting changes is not required. | Operations Planning | Active | LOWER | Transfer | MOD-032-1 Standard has established consistent modeling data requirements, reporting procedures and data exchange schedules for developing planning horizon cases necessary to support reliability analysis of the interconnected transmission system. Data submitted to meet MOD-032-1 requirement is periodically checked and updated to maintain accuracy. Requirements also establish a feedback loop and time-frames to address data concerns between parties. MOD standards support the level of TPL-001-4 reliability standard modeling and all devices and equipment in the electric grid must be modeled correctly to capture how the equipment or program performs under specific system analysis. Generator Frequency and Voltage protective relay settings data submission can be added to MOD-032-01- Attachment 1: Data Reporting Requirements. Longterm Planning noted (Reliability is dependent on ensuring Generator Owners set their generator protective relays such that generating units remain connected during defined frequency and voltage excursions.) | No Action | Standard is being modified under NERC Project 2020-02
PRC-024-2 | R2. | Each Generator Owner that has generator voltage protective relaying activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2. If the Transmission Planner allows less stringent voltage relay settings than those required to meet PRC-024 Attachment 2, then the Generator Owner shall set its protective relaying within the voltage recovery characteristics of a location-specific Transmission Planner’s study. Requirement R2 is subject to the following exceptions: [See footnote] • Generating unit(s) may trip in accordance with a Special Protection System (SPS) or Remedial Action Scheme (RAS). • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip by action of protective functions (such as out-of-step functions or loss-of-field functions) that operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 2 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | Long Term Planning | Active | MEDIUM | No Action | Reliability is dependent on ensuring Generator Owners set their generator protective relays such that generating units remain connected during defined frequency and voltage excursions. | No Action | Standard is being modified under NERC Project 2020-02
PRC-024-2 | R3. | Each Generator Owner shall document each known regulatory or equipment limitation that prevents an applicable generating unit with generator frequency or voltage protective relays from meeting the relay setting criteria in Requirements R1 or R2 including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. [See footnote] [Please see the standard for more information] | Long Term Planning | Active | LOWER | Transfer | This documentation activity could be transferred to a certification process and the applicable performance activity of setting the relays remain in Rs 1and 2. | No Action | Standard is being modified under NERC Project 2020-02
PRC-025-1 | R1. | Each Generator Owner, Transmission Owner, and Distribution Provider shall apply settings that are in accordance with PRC-025-1 – Attachment 1: Relay Settings, on each load-responsive protective relay while maintaining reliable fault protection. | Long Term Planning | Active | HIGH | No Action |  | No Action | No action recommended.
PRC-026-1 | R1. | Each Planning Coordinator shall, at least once each calendar year, provide notification of each generator, transformer, and transmission line BES Element in its area that meets one or more of the following criteria, if any, to the respective Generator Owner and Transmission Owner: 1. Generator(s) where an angular stability constraint exists that is addressed by a System Operating Limit (SOL) or a Remedial Action Scheme (RAS) and those Elements terminating at the Transmission station associated with the generator(s). 2. An Element that is monitored as part of an SOL identified by the Planning Coordinator’s methodology based on an angular stability constraint. 3. An Element that forms the boundary of an island in the most recent underfrequency load shedding (UFLS) design assessment based on application of the Planning Coordinator’s criteria for identifying islands, only if the island is formed by tripping the Element due to angular instability. 4. An Element identified in the most recent annual Planning Assessment where relay tripping occurs due to a stable or unstable power swing during a simulated disturbance. | Long Term Planning | Active | MEDIUM | No Action | This requirement obligates the PC to send data to the identified entities and while the information being sent contributes to reliability, that action alone does not ensure reliability. It is the subsequent actions that are taken by the entities that receive the data that ensure reliability. Consider transferring to Certification process. The Planning Coordinator has a wide-area view and is in the position to identify generator, transformer, and transmission line BES Elements which meet the criteria, if any. The criteria-based approach is consistent with the NERC System Protection and Control Subcommittee (SPCS) technical document Protection System Response to Power Swings, August 2013 (“PSRPS Report”),31 which recommends a focused approach to determine an at-risk BES Element. | Refer to Project 2015-09 | Send recommendations to Project 2015-09 SDT
PRC-026-1 | R2. | Each Generator Owner and Transmission Owner shall: 2.1 Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-1 – Attachment B criteria has not been performed in the last five calendar years. 2.2 Within 12 full calendar months of becoming aware of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B. | Operations Planning | Active | HIGH | No Action | The requirement to review power-swing-responsive protection systems on BES Facilities that have been determined to be applicable under R1 to determine if the criteria appurtenant to this standard are met, does have a reliability benefit. Further, there were no industry comments recommending any action. | Refer to Project 2015-09 | Send recommendations to Project 2015-09 SDT
PRC-026-1 | R3. | Each Generator Owner and Transmission Owner shall, within six full calendar months of determining a load-responsive protective relay does not meet the PRC-026-1 – Attachment B criteria pursuant to Requirement R2, develop a Corrective Action Plan (CAP) to meet one of the following: • The Protection System meets the PRC-026-1 – Attachment B criteria, while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element); or • The Protection System is excluded under the PRC-026-1 – Attachment A criteria (e.g., modifying the Protection System so that relay functions are supervised by power swing blocking or using relay systems that are immune to power swings), while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element). | Operations Planning | Active | MEDIUM | No Action | Refer to Long-Term Planning Team for final response; the Operations Planning team recommends no action, in that it is imperative that CAPs be implemented as expeditiously as possible. | Refer to Project 2015-09 | Send recommendations to Project 2015-09 SDT
PRC-026-1 | R4. | Each Generator Owner and Transmission Owner shall implement each CAP developed pursuant to Requirement R3 and update each CAP if actions or timetables change until all actions are complete. | Long Term Planning | Active | MEDIUM | No Action |  | Refer to Project 2015-09 | Send recommendations to Project 2015-09 SDT
PRC-027-1 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a process for developing new and revised Protection System settings for BES Elements, such that the Protection Systems operate in the intended sequence during Faults. The process shall include: 1.1. A review and update of short-circuit model data for the BES Elements under study. 1.2. A review of the developed Protection System settings. 1.3. For Protection System settings applied on BES Elements that electrically join Facilities owned by separate functional entities (Transmission Owners, Generator Owners, and Distribution Providers), provisions to: 1.3.1. Provide the proposed Protection System settings to the owner(s) of the electrically joined Facilities. 1.3.2. Respond to any owner(s) that provided its proposed Protection System settings pursuant to Requirement R1, Part 1.3.1 by identifying any coordination issue(s) or affirming that no coordination issue(s) were identified. 1.3.3. Verify that identified coordination issue(s) associated with the proposed Protection System settings for the associated BES Elements are addressed prior to implementation. 1.3.4. Communicate with the other owner(s) of the electrically joined Facilities regarding revised Protection System settings resulting from unforeseen circumstances that arise during implementation or commissioning, Misoperation investigations, maintenance activities, or emergency replacements required as a result of Protection System component failure. | Long Term Planning | Active | MEDIUM | No Action |  | No Action | No action recommended.
PRC-027-1 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall, for each BES Element with Protection System functions identified in Attachment A: • Option 1: Perform a Protection System Coordination Study in a time interval not to exceed six-calendar years; or • Option 2: Compare present Fault current values to an established Fault current baseline and perform a Protection System Coordination Study when the comparison identifies a 15 percent or greater deviation in Fault current values (either three phase or phase to ground) at a bus to which the BES Element is connected, all in a time interval not to exceed six-calendar years; or, • Option 3: Use a combination of the above. | Long Term Planning | Active | MEDIUM | No Action |  | No Action | No action recommended.
PRC-027-1 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider shall utilize its process established in Requirement R1 to develop new and revised Protection System settings for BES Elements. | Operations Planning | Active | HIGH | No Action | Requirement R3 mandates that an entity utilize the process established in accordance with Requirement R1. Established process for setting Protection Systems must be implemented to properly coordinate and minimize the number of BES Elements removed from service and protect equipment from damage. | No Action | No action recommended.
TOP-001-4 | R1. | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Same Day Operations and Real-time Operations | Future | HIGH | Modification | Establishes the requirement to maintain reliability. Industry- 1) Basic functionality of a TOP is to operate or direct operation of equipment to maintain reliability. COM-002-4 clearly indicates that the TOP will be using Operating Instructions. 2) Restates routine operational actions pertaining to basic functionality as a Transmission Operator. 3) This authority Real-time action is also outlined in the Functional model. This is what an RC is charged to do as being an RC. Recommend this Standard be retired. 4) Inherently required as a TOP Functional Entity as outlined in the NERC Reliability Functional Model Function Definitions and Functional Entities Version 5. | No Action | No action recommended.
TOP-001-4 | R10. | R10. Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: 10.1. Monitor Facilities within its Transmission Operator Area; 10.2. Monitor the status of Remedial Action Schemes within its Transmission Operator Area; 10.3. Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; 10.4. Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; 10.5. Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and 10.6. Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. | Real-time Operations | Future | HIGH | Modification | Modify wording to add clarity and remove ambiguous language, Specifically as it applies to non-BES facilities. | No Action | Retain. This was a response to a FERC directive.
TOP-001-4 | R11. | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Real-time Operations | Future | HIGH | Modification | One industry response was to transfer to the BAL standards or retire due to IRO-010. | PRT | Recommend for periodic review and if other modifications are needed consider whether or not the BA sufficiently monitors its BA Area by virtue of DCS and CPS along with its requirement to have a data specification to address real-time monitoring and RAS (TOP-003).
TOP-001-4 | R12. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | Real-time Operations | Future | HIGH | No Action |  | No Action | No action recommended.
TOP-001-4 | R13. | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | Real-time Operations | Future | HIGH | Modification | Modification of the measure as administratively burdensome with IRO-008 and TOP-010. Perhaps move them to the Certification process. | No Action | No action recommended.
TOP-001-4 | R14. | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | Real-time Operations | Future | HIGH | No Action |  | No Action | No action recommended.
TOP-001-4 | R15. | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. | Real-time Operations | Future | MEDIUM | Modification | Modify wording due to current implications of the latitude granted to TOPs. Burdensome with IRO-10 or/and the Operating Plan. | No Action | No action recommended.
TOP-001-4 | R16. | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Same Day Operations, and Real-time Operations | Future | HIGH | Retirement | This requirement can be retired because the authority to approve/deny outages to any equipment, whether load carrying or not, is a fundamental attribute of the system operator role. This was recognized by NERC and FERC in Project 2007-03 where the authority language in former Standard TOP-001-1 R1 was removed from the revised TOP standards approved by both NERC and FERC. This requirement is redundant to PER-005-2. | Retire | Retire. The “authority” is inherent in “acting to maintain the reliability of its TOP/BA Area via its own actions or by issuing Operating Instructions.” Being able to approve outages of equipment in and of itself does not provide any reliability benefit. Other requirements, such as R13 are already in place which demand an extremely high availability of EMS functionality, EMS & IT staff should be well aware that unplanned outages impacting the ability to view and solve contingency analysis.
TOP-001-4 | R17. | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Operations Planning, Same Day Operations, and Real-time Operations | Future | HIGH | Retirement | This requirement can be retired because the authority to approve/deny outages to any equipment, whether load carrying or not, is a fundamental attribute of the system operator role. This was recognized by NERC and FERC in Project 2007-03 where the authority language in former Standard TOP-001-1 R1 was removed from the revised TOP standards approved by both NERC and FERC. This logic also applies to the BA operator. This requirement is redundant to PER-005-2. | Retire | Retire. The “authority” is inherent in “acting to maintain the reliability of its TOP/BA Area via its own actions or by issuing Operating Instructions.” Being able to approve outages of equipment in and of itself does not provide any reliability benefit. Other requirements, such as R13 are already in place which demand an extremely high availability of EMS functionality, EMS & IT staff should be well aware that unplanned outages impacting the ability to view and solve contingency analysis.
TOP-001-4 | R18. | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | Operations Planning, Same Day Operations, and Real-time Operations | Future | HIGH | No Action | Doesn't seem necessary, "difference" language could be added to R15. Industry - keep/no comment | No Action | No action recommended.
TOP-001-4 | R19. | Each Transmission Operator shall have data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. | Operations Planning | Future | MEDIUM | Retirement | The requirement is solely a control for aiding compliance with TOP-002-4 R1 related to the performance of an Operational Planning Analysis (OPA) and it is duplicative to requirements R5 in TOP-003-3. The NERC Glossary of Terms definition of OPA requires certain data to be used for the analysis performed under TOP-002-4 R1 and standard TOP-003-3 requires the TOP to identify the data it needs to perform its OPA (R1), which entities need to provide such data (R3), and then obligates those registered entities to then supply the data (R5). For an entity to fulfill TOP-003-3 R5, it must be able to exchange data with the requesting TOP. Additionally, to comply with TOP-002-4 R1, the TOP must have received all of the data it needs to perform the OPA. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
TOP-001-4 | R2. | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Same Day Operations and Real-time Operations | Future | HIGH | Modification | Establishes the requirement to maintain reliability. Industry -Restates routine operational actions pertaining to basic functionality as a Transmission Operator. | No Action | No action recommended.
TOP-001-4 | R20. | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. | Same Day Operations and Real-time Operations | Future | HIGH | Modification | Overly prescriptive. Industry - does not apply to all Control Center configurations | No Action | No action recommended.
TOP-001-4 | R21. | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. | Operations Planning | Future | MEDIUM | Transfer | Full group discussion needed. Discussed at 4/3/18 meeting. IRO sub-team reviewing further. R21 of TOP-001-4 acts as a control for R20 of TOP-001-4. Requirement R21 should be moved into the Certification process and the certification process should confirm that the entity has internal controls to (1) monitor the health and status of its data exchange capabilities and/or (2) test and recover its data exchange. Note that, by requiring entities to test every 90 days, the requirement does not protect real time reliability because a loss of redundancy event can occur between the 90 day tests. In such an event, the TOP would need to recover from the event quickly to continue operation, regardless of this requirement. | No Action | No action recommended.
TOP-001-4 | R22. | Each Balancing Authority shall have data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. | Operations Planning | Future | MEDIUM | Retirement | The requirement is solely a control for aiding compliance with TOP-002-4 R4 related to preparing Operating Plans and it is duplicative to requirement R5 in TOP-003-3. Standard TOP-003-3 requires the BA to identify the data it needs to perform its analysis functions (R2), which entities need to provide such data (R4), and then obligates those registered entities to then supply the data (R5). For an entity to fulfill TOP-003-3 R5, it must be able to exchange data with the requesting BA. Additionally, to comply with TOP-002-4 R4, the BA must have received all of the data it needs to perform its analysis functions. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
TOP-001-4 | R23. | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. | Same Day Operations and Real-time Operations | Future | HIGH | Modification | Overly prescriptive. Industry - does not apply to all Control Center configurations | No Action | No action recommended.
TOP-001-4 | R24. | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. | Operations Planning | Future | MEDIUM | Transfer | Full group discussion needed. Discussed at 4/3/18 meeting. IRO sub-team reviewing further. R24 of TOP-001-4 acts as a control for R23 of TOP-001-4. Requirement R24 should be moved into the Certification process and the certification process should confirm that the entity has internal controls to (1) monitor the health and status of its data exchange capabilities and/or (2) test and recover its data exchange. Note that, by requiring entities to test every 90 days, the requirement does not protect real time reliability because a loss of redundancy event can occur between the 90 day tests. In such an event, the BA would need to recover from the event quickly to continue operation, regardless of this requirement. | No Action | No action recommended.
TOP-001-4 | R3. | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | Same Day Operations and Real-time Operations | Future | HIGH | No Action | Provides the TOP with the authority to issue Operating Instructions by requiring the BA, GOP, and DP to comply. | No Action | No action recommended.
TOP-001-4 | R4. | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Same Day Operations and Real-time Operations | Future | HIGH | Transfer | This requirement is currently covered by TOP-001-4 R3's, " unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements." Additionally, communications protocols would facilitate the inability to comply. | No Action | Retain. Without the notification requirement in R3, the TOP will not have an ability to compensatory action.
TOP-001-4 | R5. | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | Same Day Operations and Real-time Operations | Future | HIGH | No Action | Provides the BA with the authority to issue Operating Instructions by requiring the TOP, GOP, and DP to comply. | No Action | No action recommended.
TOP-001-4 | R6. | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | Same Day Operations and Real-time Operations | Future | HIGH | Transfer | This requirement is currently covered by TOP-001-4 R5's, " unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements." Additionally, communications protocols would facilitate the inability to comply. | No Action | Retain. Without the notification requirement in R5, the TOP will not have an ability to compensatory action.
TOP-001-4 | R7. | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Real-time Operations | Future | HIGH | Transfer | Each TOP can only monitor and control facilities it has operational control over. A notification of operations resulting in an Emergency per TOP-001-4 R8 can include a request for assistance. | Retire w/ modification | Retire TOP-001-4, Requirement R7 and modify IRO-001-4, Requirement R2 to include the clause "provided that the requesting Transmission Operator has implemented its comparable Emergency procedures." IRO-001-4, Requirements R1, R2, and R3 require the RC to direct (R1) the TOP to take actions (R2) and the TOP to inform when Operating Instructions cannot be implemented (R3). During an Emergency, the RC is notified and will have greater visibility regarding mitigating actions. The only caveat not addressed is the "provided that the requesting Transmission Operator has implemented its comparable Emergency procedures."
TOP-001-4 | R8. | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. | Operations Planning, Same Day Operations, and Real-time Operations | Future | HIGH | Modification | Requirement R8 should be modified to remove "or expected" and "or could result in" since TOP-002-4 R3 covers the Operations Planning time horizon. Time horizon would as need to be modified to remove "Operations Planning". Notification of operations that could result in an Emergency serve as situational awareness for impacted entities. | No Action | No action recommended.
TOP-001-4 | R9. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. | Operations Planning, Same Day Operations, and Real-time Operations | Future | MEDIUM | Transfer | Outage communication and coordination is best consolidated under one standard, which would be IRO-017. Notifications to other entities would be covered through the RC's outage planning process documented under that standard. Transfer to IRO-010 and is redundant with TOP-010 and TOP-003 which necessitates the transfer. Industry is also open to retirement due to redundant requirements. | No Action | Could be pulled to another standard (e.g., IRO-017) to address outage related activities.
TOP-002-4 | R1. | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). | Operations Planning | Active | MEDIUM | No action | Retain as is | No Action | No action recommended.
TOP-002-4 | R2. | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. | Operations Planning | Active | MEDIUM | No action | Retain as is | No Action | No action recommended.
TOP-002-4 | R3. | Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). | Operations Planning | Active | MEDIUM | No action | The R3 requirement is adequate as written but the issue is the definition of "Operating Plan". Operating Plan, as described in the Associated Documents section F of the standard, is very broad and may not promote the type of notifications expected by the SW Blackout FERC-NERC recommendation #1. Industry would benefit from additional guidance from NERC such as a whitepaper. | No Action | No action recommended.
TOP-002-4 | R4. | Each Balancing Authority shall have an Operating Plan(s) for the next-day that addresses: 4.1 Expected generation resource commitment and dispatch 4.2 Interchange scheduling 4.3 Demand patterns 4.4 Capacity and energy reserve requirements, including deli | Operations Planning | Active | MEDIUM | No action | Retain as is | No Action | No action recommended.
TOP-002-4 | R5. | Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). | Operations Planning | Active | MEDIUM | No action | The R5 requirement is adequate as written but the issue is the definition of "Operating Plan". Operating Plan, as described in the Associated Documents section F of the standard, is very broad and may not promote the type of notifications expected by the SW Blackout FERC-NERC recommendation #1. Industry would benefit from additional guidance from NERC such as a whitepaper. | No Action | No action recommended.
TOP-002-4 | R6. | Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. | Operations Planning | Active | MEDIUM | No action | The R6 requirement is adequate as written but the issue is the definition of "Operating Plan". Operating Plan, as described in the Associated Documents section F of the standard, is very broad and may not promote the type of notifications expected by the SW Blackout FERC-NERC recommendation #1. Industry would benefit from additional guidance from NERC such as a whitepaper. | No Action | No action recommended.
TOP-002-4 | R7. | Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. | Operations Planning | Active | MEDIUM | No action | The R7 requirement is adequate as written but the issue is the definition of "Operating Plan". Operating Plan, as described in the Associated Documents section F of the standard, is very broad and may not promote the type of notifications expected by the SW Blackout FERC-NERC recommendation #1. Industry would benefit from additional guidance from NERC such as a whitepaper. | No Action | No action recommended.
TOP-003-3 | R1. | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: | Operations Planning | Active | LOWER | Modification | Combine the language with R3 to simplify the standard. TOP would create data specification and distribution. Modification of requirement would be adding "Each TOP shall maintain AND DISTRIBUTE a documented specification…" | PRT | Recommend for Periodic Review and if other modifications are needed, consider combining the language in TOP-003-3, Requirement R3 with TOP-003-3, Requirement R1 to simplify the standard. For example, modification would eliminate a requirement and create "R1. Each TO shall maintain AND DISTRIBUTE a documented specification…"
TOP-003-3 | R2. | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: 2.1. A list of data and information | Operations Planning | Active | LOWER | Modification | Combine the language with R4 to simplify the standard. TOP would create data specification and distribution. Modification of requirement would be adding "Each TOP shall maintain AND DISTRIBUTE a documented specification…" | PRT | Recommend for Periodic Review and if other modifications are needed, consider combining the language in TOP-003-3, Requirement R4 with TOP-003-3, Requirement R2 to simplify the standard. For example, modification would eliminate a requirement and create "R2. Each BA shall maintain AND DISTRIBUTE a documented specification…" No immediate efficiency gain by consolidating these requirements.
TOP-003-3 | R3. | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. | Operations Planning | Active | LOWER | Transfer | Combine the language with R1 by adding "Each TOP shall maintain AND DISTRIBUTE a documented specification…". R3 would then be retired. | No Action | No action recommended.
TOP-003-3 | R4. | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | Operations Planning | Active | LOWER | Transfer | Combine the language with R2, by adding "Each TOP shall maintain AND DISTRIBUTE a documented specification…". R4 would then be retired. | PRT | Recommend for Periodic Review and if other modifications are needed, consider combining the language in TOP-003-3, Requirement R4 with TOP-003-3, Requirement R2 to simplify the standard. For example, modification would eliminate a requirement and create "R2. Each BA shall maintain AND DISTRIBUTE a documented specification…" No immediate efficiency gain by consolidating these requirements.
TOP-003-3 | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: 5.1. A mutually agreeable format 5.2. A mutually agreeable process for resolving data conflicts 5.3. A mutually agreeable security protocol | Operations Planning, Same Day Operations, and Real-time Operations | Active | MEDIUM | Transfer | This requirement should either be retained as is or moved into the certification process, which may be a more appropriate location. The certification process would require Registered Entities to abide by data specifications laid out by the RC, TOP and BA, which is very important, but the requirement is very burdensome on the Registered Entities showing compliance. For example, if the RC has 75+ individual data spec requirements, then this is essentially 75+ added individual requirements the Registered Entities have to maintain compliance. | No Action | No action recommended.
TOP-010-1(i) | R1. | R1. Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: 1.1. Criteria for evaluating the quality of Real-time data; 1.2. Provisions to indicate the quality of Real-time data to the System Operator; and 1.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | Real-time Operations | Future | HIGH | No Action |  | No Action | No action recommended.
TOP-010-1(i) | R2. | R2. Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: 2.1. Criteria for evaluating the quality of Real-time data; 2.2. Provisions to indicate the quality of Real-time data to the System Operator; and 2.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. | Real-time Operations | Future | HIGH | No Action |  | No Action | No action recommended.
TOP-010-1(i) | R3. | R3. Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: 3.1. Criteria for evaluating the quality of analysis used in its Real-time Assessments; 3.2. Provisions to indicate the quality of analysis used in its Real-time Assessments; and 3.3. Actions to address analysis quality issues affecting its Real-time Assessments. | Real-time Operations | Future | MEDIUM | No Action | Keep as is. Industry - Consolidate with TOP-001-3/4. Only one comment. | No Action | No action recommended.
TOP-010-1(i) | R4. | R4. Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred | Real-time Operations | Future | MEDIUM | No Action | Keep as is. Industry - This requirement is more suited for inclusion in the ERO Certification and Review Procedure instead of a Reliability Standard as it is a fundamental organization requirement to enable the operating entity to perform its reliability tasks to meet its basic obligations. Only one comment. | No Action | No action recommended.
TPL-001-4 | R1. | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. [See standard for further information regarding R1] | Long Term Planning | Active | HIGH | Modification | The changes to the references to MOD-010 and MOD-012 are already in the scope of the TPL-004-5 SDT efforts (Project 2015-10). | No Action | No action. Recommended changes are included in TPL-001-5, which is filed and pending regulatory approval.
TPL-001-4 | R2. | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. [See standard for further information regarding R2] | Long Term Planning | Active | HIGH | Modification | Justification to be determined in phase two of the SER Project. | PRT | Defer to a technical team for more investigation. Modify to allow flexibility when stability performance requirements cannot be mitigated fast enough using load shed as an interim solution.
TPL-001-4 | R3. | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. [See standard for further information regarding R3] | Long Term Planning | Active | MEDIUM | Modification | Justification to be determined in phase two of the SER Project; discussion about how sensitivity analysis are included in this requirement. | PRT | Defer to a technical team for more investigation. Modify Part 3.2 to say “except for sensitivity case(s) conditions in Part 2.1.4”.
TPL-001-4 | R4. | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. [See standard for further information regarding R4] | Long Term Planning | Active | MEDIUM | Modification | Justification to be determined in phase two of the SER Project; discussion about how sensitivity analysis are included in this requirement. | PRT | Defer to a technical team for more investigation. Modify Part 4.2 to say “except for sensitivity case(s) conditions in Part 2.1.4”.
TPL-001-4 | R5. | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. | Long Term Planning | Active | MEDIUM | Modification | Justification to be determined in phase two of the SER Project. | PRT | Defer to a technical team for more investigation for more clarification and/or possible combining with R6. Clarify the phrase "post-Contingency Voltage deviation" to ensure consistent application across all planning regions.
TPL-001-4 | R6. | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. | Long Term Planning | Active | MEDIUM | Modification | Justification to be determined in phase two of the SER Project. | PRT | Defer to a technical team for more investigation for more clarification and/or possible combining with R5.
TPL-001-4 | R7. | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. | Long Term Planning | Active | LOWER | Modification | Justification to be determined in phase two of the SER Project. | No Action | In accordance with the recommendation from Paragraph 81 and the Standards Independent Experts Review Project, retire this requirement due to the administrative nature of the activity. An option could be to move this to the Applicability. For example: 4. Applicability: 4.1 Planning Coordinator having individual and mutual responsibilities as jointly determined with each of its Transmission Planners for performing the required studies for the Planning Assessment. 4.2 Transmission Planning having individual and mutual responsibilities as jointly determined with its Planning Coordinator for performing the required studies for the Planning Assessment.
TPL-001-4 | R8. | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. [See standard for further information regarding R8] | Long Term Planning | Active | MEDIUM | Modification | Add RC to the list of entities included in the distribution list | No Action | No action recommended.
TPL-007-1 | R1. | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s). | Long Term Planning | Active | Lower | No Action |  | No Action | No action recommended.
TPL-007-1 | R2. | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | Long Term Planning | Active | High | No Action |  | No Action | No action recommended.
TPL-007-1 | R3. | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the benchmark GMD event described in Attachment 1. | Long Term Planning | Active | Medium | No Action |  | No Action | No action recommended.
TPL-007-1 | R4. | Each responsible entity, as determined in Requirement R1, shall complete a GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon once every 60 calendar months. This GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. (please see standard for sub-req's) | Long Term Planning | Active | High | No Action |  | No Action | No action recommended.
TPL-007-1 | R5. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the transformer thermal impact assessment specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: (please see standard for sub-req's) | Long Term Planning | Active | Medium | No Action |  | No Action | No action recommended.
TPL-007-1 | R6. | Each Transmission Owner and Generator Owner shall conduct a thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A per phase or greater. The thermal impact assessment shall: (please see standard for sub-req's) | Long Term Planning | Active | Medium | No Action |  | No Action | No action recommended.
TPL-007-1 | R7. | Each responsible entity, as determined in Requirement R1, that concludes, through the GMD Vulnerability Assessment conducted in Requirement R4, that their System does not meet the performance requirements of Table 1 shall develop a Corrective Action Plan addressing how the performance requirements will be met. The Corrective Action Plan shall: (please see standard for sub-req's) | Long Term Planning | Active | High | No Action |  | No Action | No action recommended.
VAR-001-5 | E.A.13. | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A | Operations Planning and Same Day Operations | Active | MEDIUM | No action | This standard and requirement was not reviewed by the NERC SER team because it is not continent-wide. This requirement should be reviewed by a team of the entities within the region due to their local expertise to determine if any modification or retirement should be pursued. | No Action | No action recommended.
VAR-001-5 | E.A.14. | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The poin | Operations Planning and Same Day Operations | Active | MEDIUM | No action | This standard and requirement was not reviewed by the NERC SER team because it is not continent-wide. This requirement should be reviewed by a team of the entities within the region due to their local expertise to determine if any modification or retirement should be pursued. | No Action | No action recommended.
VAR-001-5 | E.A.15. | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system | Operations Planning and Same Day Operations | Active | MEDIUM | No action | This standard and requirement was not reviewed by the NERC SER team because it is not continent-wide. This requirement should be reviewed by a team of the entities within the region due to their local expertise to determine if any modification or retirement should be pursued. | No Action | No action recommended.
VAR-001-5 | E.A.15. | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system | Operations Planning and Same Day Operations | Active | MEDIUM | Retirement | VAR-001-5 E.A. 15 is applicable to WECC only. The same requirement exists in VAR-002-4.1 R2.3 that is applicable to the ERO. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
VAR-001-5 | E.A.16. | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. | Operations Planning | Active | LOWER | No action | This standard and requirement was not reviewed by the NERC SER team because it is not continent-wide. This requirement should be reviewed by a team of the entities within the region due to their local expertise to determine if any modification or retirement should be pursued. | No Action | No action recommended.
VAR-001-5 | E.A.17. | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion | Operations Planning | Active | LOWER | No action | This standard and requirement was not reviewed by the NERC SER team because it is not continent-wide. This requirement should be reviewed by a team of the entities within the region due to their local expertise to determine if any modification or retirement should be pursued. | No Action | No action recommended.
VAR-001-5 | E.A.18. | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: [Please see the standard for more information] | Real-time Operations | Active | MEDIUM | No Action |  | No Action | No action recommended.
VAR-001-5 | R1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. 1.1. Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. | Operations Planning | Active | HIGH | Modification | Retain R1 and retire R1.1. R1.1 can be adequately covered by the data specifications created by the RC and the TOP in standards IRO-010 and TOP-003, respectively. | Retire w/ modification | Retire with Modification. Requirement R1, Part R1.1 is administrative and can be adequately covered by the data specifications created by the RC and the TOP in standards IRO-010 and TOP-003, respectively.
VAR-001-5 | R2. | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | Operations Planning, Same Day Operations, and Real-time Operations | Active | HIGH | Transfer | VAR-001-5 R2 ensures the system stays within its SOLs (and IROLs). TOP-001-3/TOP-1-4 R1, R10, R12, R13, R14 and TOP-002-4 R1, R2 require TOPs to assess operation within SOLs and operate within these limits. If R2 and R3 are maintained, time horizons should be differentiated. | Project 2018-03 Retiring | No action. Project 2018-03 Retiring
VAR-001-5 | R3. | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | Operations Planning, Same Day Operations, and Real-time Operations | Active | HIGH | Retirement | The language of requirement R3 of VAR-001-5 is adequately covered by the following existing NERC standard requirements: 1. The actions taken by the registered TOP under R3 are the same actions required of the TOP under TOP-001-4 R1, which states that the TOP "shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions." The requirement to "act" using all available actions, whether by "its own actions" or by the actions of others via "issuing Operating Instructions" is the same as "operate or direct ... operation of devices to regulate ... voltage and reactive flow." 2. The purpose of the actions taken by the TOP under R3 is the same purpose accomplished by TOP-001-4 R1, R10, R12, R13 and R14 by acting to operate within limits (SOLs and IROLs) to maintain reliability of its transmission system. Coordinate with Real-Time Ops Team recommendation. In addition, per NERC' certification language, TOPs are "responsible for the reliability of its local transmission system", which is equivalent to R3's "regulate[ing] transmission voltage and reactive flow as necessary", and TOPs accomplish this action by "operate[ing] or direct[ing] the operations of the transmission Facilities", which is equivalent to R3's "operate or direct the Real-time operation of devices". (Real-Time Ops noted: Duplicative of TOP-001-3/TOP-001-4 R1, R12 and R14 are also referenced. Should be retired if those requirements are retained. Removing this requirement would also make VAR-001 more focused on specifying voltage schedules. If R3 is retained, time horizons should be differentiated. | Retire | Retire. TOP-001-4, R1 requires the TOP to maintain reliability by acting to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions.
VAR-001-5 | R4. | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from ha | Operations Planning | Active | LOWER | No action | Retain as is | No Action | No action recommended.
VAR-001-5 | R5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Tra | Operations Planning | Active | MEDIUM | No Action | Retain as is | No Action | No action recommended.
VAR-001-5 | R6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe | Operations Planning | Active | LOWER | No Action | Retain as is | No Action | No action recommended.
VAR-002-4.1 | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up, shutdown, or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | Real-time Operations | Active | MEDIUM | Transfer | This requirement can be combined with R3 of this standard to require notification when not in preferred mode of control specified by the TOP. | No Action | No action. "Notification" requirements are central to Concept 5 currently being evaluated by the Phase 2 team. Consider holding pending the outcome of their decision.
VAR-002-4.1 | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within each generating Facility’s capabilities ) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. 2.1. When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. 2.2. When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. 2.3. Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | Real-time Operations | Active | MEDIUM | Modification | The TOP should determine a voltage schedule tolerance band based on reliability limits, not ease of administration/determination. Notification requirements to the TOP should be addressed and considered during the review of this standard. Should be considered for modification to a results-based (performance, competency, or risk based) standard. | Retire w/ modification | Retire with modification. Remove Part 2.2. Instructions to modify voltage are within the scope of Operating Instructions, R2.2. is sufficiently covered and/or redundant with TOP-001-4 R3 & R4.
VAR-002-4.1 | R3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. | Real-time Operations | Active | MEDIUM | Modification | Review in light of proposed combination with R1. Also, somewhat duplicative of other notification requirements (IRO-010). The 30 minute administrative clock is too short in many cases to provide the GOP sufficient time to resolve the issue before notifying the TOP of the status change. Therefore, we believe that the risks associated with the 30-minute time clock causing numerous focusing efforts on reporting rather resolving needlessly incurred low-risk violations, due to inadequate time provided in this standard, far outweigh the risks to BES reliability. Moreover, we understand that status changes in AVR, and/or untimely notification of those changes have not been shown to have caused actual BES outage reliability impacts such as lost BES elements, load, or generation. For this reason, we ask NERC to consider either retiring this requirement or possibly providing additional time to resolve the issue rather than focus on reporting. We also ask NERC to consider that the reliability gap from units not being operated normally in AVR during the 2003 blackout is fully covered under R1. | Refer to Project 2021-02
VAR-002-4.1 | R4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | Real-time Operations | Active | MEDIUM | Modification | The 30 minute period is too short in many cases to provide the GOP sufficient time to resolve the issue before notifying the TOP of the status change. Therefore, we believe that the risks associated with the 30-minute time clock causing numerous focusing efforts on reporting rather resolving needlessly incurred low-risk violations, due to inadequate time provided in this standard, far outweigh the risks to BES reliability. Moreover, we understand that status changes in AVR, and/or untimely notification of those changes have not been shown to have caused actual BES outage reliability impacts such as lost BES elements, load, or generation. For this reason, we ask NERC to consider either retiring this requirement or possibly providing additional time to resolve the issue rather than focus on reporting. We also ask NERC to consider that the reliability gap from units not being operated normally in AVR during the 2003 blackout is fully covered under R1. | Refer to Project 2021-02
VAR-002-4.1 | R5. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. 5.1. For generator step-up and auxiliary transformers5 with primary voltages equal to or greater than the generator terminal voltage: 5.1.1. Tap settings. 5.1.2. Available fixed tap ranges. 5.1.3. Impedance data. | Real-time Operations | Active | LOWER | Transfer | Duplicative of other standards. Standards cited include TOP-003 and MOD-032. | Refer to Project 2021-02 | Could be retired since transformer specifications are within the scope of modeling data necessary for all planning horizons, R5 is sufficiently covered in TOP-003 & MOD-032 (Attachment 1, Steady State #3f) standards. If retained, the Time Horizon needs to be corrected to Ops Planning or longer
VAR-002-4.1 | R6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. 6.1. If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. | Real-time Operations | Active | LOWER | Modification | May be duplicative of TOP-003. It was noted that this is an administrative requirement. All entities keep transformer data on BES transformers. There is not a need for a mandatory standard to keep tap data. | Refer to Project 2021-02 | Could be retired. This requirement is applicable to the Real-time Operations horizon. Therefore, this requirement appears to only apply to transformers capable of changing tap position under load in Real-time. Therefore, that activity is within the scope of Operating Instructions and sufficiently covered in TOP-001 R3 & R4. If retained, the Time Horizon needs to be corrected to Ops Planning or longer
Note on G34: Chris Larson: Incorporate into Phase 2
Note on H159: Chris Larson: relation to TOP-003
Note on H368: Charles W. Rogers: Look at revisions to IRO-002-5
Note on H369: Charles W. Rogers: Look at changes to IRO-002-5

## List (hidden)
Course_of_Action
Consolidate
Modification
No Action
Retirement
Transfer