## VRF_VSL Matrix
Status | Family | Standard Version | Requirement Number | Requirement Text | Effective Date of Requirement | Inactive Date of Requirement | Violation Risk Factor (VRF) | Violation Severity Level (Lower) | Violation Severity Level (Moderate) | Violation Severity Level (High) | Violation Severity Level (Severe) | Public Notes | BA | DP | DP-UFLS | FRSG | GO | GOP | IA | LSE | NERC | PCPA | PSE | RC | RE | RP | RRO | RRSG | RSG | TO | TOP | TP | TSP
Inactive | BAL | BAL-001-0 | R1. | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. See Standard for Formula. The equation for ACE is: ACE = (NIA - NIS) - 10B (FA - FS) - IME where: · NIA is the algebraic sum of actual flows on all tie lines. · NIS is the algebraic sum of scheduled flows on all tie lines. · B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. · FA is the actual frequency. · FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. | 2007-06-18 | 2008-08-26 | Low | The Balancing Authority Area’s value of CPS1 is less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 is less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 is less than 85%. |  | BA
Inactive | BAL | BAL-001-0 | R2. | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. See Standard for Formula. | 2007-06-18 | 2008-08-26 | Low | The Balancing Authority Area’s value of CPS2 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS2 is less than 85% but greater than or equal to 80%. | The Balancing Authority Area’s value of CPS2 is less than 80% but greater than or equal to 75%. | The Balancing Authority Area’s value of CPS2 is less than 75%. |  | BA
Inactive | BAL | BAL-001-0 | R3. | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. | 2007-06-18 | 2008-08-26 | Low |  |  |  | The Balancing Authority providing Overlap Regulation Service failed to use a combined ACE and frequency bias. |  | BA
Inactive | BAL | BAL-001-0 | R4. | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). | 2007-06-18 | 2008-08-26 | Low | [5 empty] | BA
Inactive | BAL | BAL-001-0.1a | R1. | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. The equation for ACE is: ACE = (NIA - NIS) - 10B (FA - FS) - IME where: · NIA is the algebraic sum of actual flows on all tie lines. · NIS is the algebraic sum of scheduled flows on all tie lines. · B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. · FA is the actual frequency. · FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. · IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. | 2009-05-13 | 2014-03-31 | Medium | The Balancing Authority Area’s value of CPS1 is less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 is less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 is less than 85%. |  | BA
Inactive | BAL | BAL-001-0.1a | R2. | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. ?10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, ?10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. | 2009-05-13 | 2014-03-31 | Medium | The Balancing Authority Area’s value of CPS2 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS2 is less than 85% but greater than or equal to 80%. | The Balancing Authority Area’s value of CPS2 is less than 80% but greater than or equal to 75%. | The Balancing Authority Area’s value of CPS2 is less than 75%. |  | BA
Inactive | BAL | BAL-001-0.1a | R3. | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. | 2009-05-13 | 2014-03-31 | Low |  |  |  | The Balancing Authority providing Overlap Regulation Service failed to use a combined ACE and frequency bias. |  | BA
Inactive | BAL | BAL-001-0.1a | R4. | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). | 2009-05-13 | 2014-03-31 | Low |  |  |  | The Balancing Authority receiving Overlap Regulation Service failed to ensure that control performance was being evaluated in a manner consistent with the calculation methodology as described in BAL-001-01 R3. |  | BA
Inactive | BAL | BAL-001-0a | R1. | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit ??? is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. See standard for equation. The equation for ACE is: ACE = (NIA - NIS) - 10B (FA - FS) - IME where: · NIA is the algebraic sum of actual flows on all tie lines. · NIS is the algebraic sum of scheduled flows on all tie lines. · B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. · FA is the actual frequency. · FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. | 2008-08-27 | 2009-05-12 |  | The Balancing Authority Area’s value of CPS1 is less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 is less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 is less than 85%. |  | BA
Inactive | BAL | BAL-001-0a | R2. | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. See standard for formula. E10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, e10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. | 2008-08-27 | 2009-05-12 |  | The Balancing Authority Area’s value of CPS2 is less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS2 is less than 85% but greater than or equal to 80%. | The Balancing Authority Area’s value of CPS2 is less than 80% but greater than or equal to 75%. | The Balancing Authority Area’s value of CPS2 is less than 75%. |  | BA
Inactive | BAL | BAL-001-0a | R3. | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement M1 (i.e., Control Performance Standard 1 or CPS1) and Requirement M2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. | 2008-08-27 | 2009-05-12 |  |  |  |  | The Balancing Authority providing Overlap Regulation Service failed to use a combined ACE and frequency bias. |  | BA
Inactive | BAL | BAL-001-0a | R4. | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). | 2008-08-27 | 2009-05-12 |  |  |  |  | The Balancing Authority receiving Overlap Regulation Service failed to ensure that control performance was being evaluated in a manner consistent with the calculation methodology as described in BAL-001-01 R3. |  | BA
Inactive | BAL | BAL-001-1 | E.B.1. | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit e-1-2 is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee.(please see standard for formulas) | 2014-04-01 | 2016-06-30 | Medium | The Balancing Authority Area’s value of CPS1 was less than 100% but greater than or equal to 95%. | The Balancing Authority Area’s value of CPS1 was less than 95% but greater than or equal to 90%. | The Balancing Authority Area’s value of CPS1 was less than 90% but greater than or equal to 85%. | The Balancing Authority Area’s value of CPS1 was less than 85%. |  | BA
Inactive | BAL | BAL-001-1 | E.B.2. | Each Balancing Authority shall limit the absolute value of I-ATEC, the Automatic Time Error Correction term as follows:(please see standard for formula) | 2014-04-01 | 2016-06-30 | Medium | N/A | N/A | N/A | The Balancing Authority Area’s absolute value for IATEC was greater than L-max |  | BA
Inactive | BAL | BAL-001-1 | E.B.3. | Each Balancing Authority shall set L-max within the limits as follows:(please see standard for formula) | 2014-04-01 | 2016-06-30 | Medium | N/A | N/A | N/A | The Balancing Authority did not set L-max to within the limits in E.B.3 (please see standard for formula) |  | BA
Inactive | BAL | BAL-001-1 | R1. | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit ??? is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. (See standard for formulas) The equation for ACE is: ACE = (NIA − NIS) − 10B (FA − FS) − IME where: • NIA is the algebraic sum of actual flows on all tie lines. • NIS is the algebraic sum of scheduled flows on all tie lines. • B is the Frequency Bias Setting (MW/0.1 Hz) for the Balancing Authority. The constant factor 10 converts the frequency setting to MW/Hz. • FA is the actual frequency. • FS is the scheduled frequency. FS is normally 60 Hz but may be offset to effect manual time error corrections. • IME is the meter error correction factor typically estimated from the difference between the integrated hourly average of the net tie line flows (NIA) and the hourly net interchange demand measurement (megawatt-hour). This term should normally be very small or zero. | 2014-04-01 | 2016-06-30 | Medium | [5 empty] | BA
Inactive | BAL | BAL-001-1 | R2. | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. (See standard for formulas) ?10 is a constant derived from the targeted frequency bound. It is the targeted root-mean-square (RMS) value of ten-minute average Frequency Error based on frequency performance over a given year. The bound, ?10, is the same for every Balancing Authority Area within an Interconnection, and Bs is the sum of the Frequency Bias Settings of the Balancing Authority Areas in the respective Interconnection. For Balancing Authority Areas with variable bias, this is equal to the sum of the minimum Frequency Bias Settings. | 2014-04-01 | 2016-06-30 | Medium | [5 empty] | BA
Inactive | BAL | BAL-001-1 | R3. | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. | 2014-04-01 | 2016-06-30 | Low | [5 empty] | BA
Inactive | BAL | BAL-001-1 | R4. | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). | 2014-04-01 | 2016-06-30 | Low | [5 empty] | BA
Mandatory Subject to Enforcement | BAL | BAL-001-2 | R1. | The Responsible Entity shall operate such that the Control Performance Standard 1 (CPS1), calculated in accordance with Attachment 1, is greater than or equal to 100 percent for the applicable Interconnection in which it operates for each preceding 12 consecutive calendar month period, evaluated monthly. | 2016-07-01 |  | Medium | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 100 percent but greater than or equal to 95 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 95 percent, but greater than or equal to 90 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 90 percent, but greater than or equal to 85 percent for the applicable Interconnection. | The CPS 1 value of the Responsible Entity, for the preceding 12 consecutive calendar month period, is less than 85 percent for the applicable Interconnection. |  | BA | [14 empty] | RRSG
Mandatory Subject to Enforcement | BAL | BAL-001-2 | R2. | Each Balancing Authority shall operate such that its clock-minute average of Reporting ACE does not exceed its clock-minute Balancing Authority ACE Limit (BAAL) for more than 30 consecutive clock-minutes, calculated in accordance with Attachment 2, for the applicable Interconnection in which the Balancing Authority operates. | 2016-07-01 |  | Medium | The Balancing Authority exceeded its clock-minute BAAL for more than 30 consecutive clock minutes but for 45 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 45 consecutive clock minutes but for 60 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 60 consecutive clock minutes but for 75 consecutive clock-minutes or less for the applicable Interconnection. | The Balancing Authority exceeded its clock-minute BAAL for greater than 75 consecutive clock-minutes for the applicable Interconnection. |  | BA
Inactive | BAL | BAL-001-TRE-1 | R1. | The BA shall identify Frequency Measurable Events (FMEs), and within 14 calendar days after each FME the BA shall notify the Compliance Enforcement Authority and make FME information (time of FME (t(0)), pre-perturbation average frequency, post- perturbation average frequency) publicly available. | 2014-04-01 | 2020-06-30 | Low | The BA reported an FME more than 14 days but less than 31 days after identification of the event. | The BA reported an FME more than 30 days but less than 51 days after identification of the event. | The BA reported an FME more than 50 days but less than 71 days after identification of the event. | The BA reported an FME more than 70 days after identification of the event. |  | BA |  |  |  | GO | GOP
Inactive | BAL | BAL-001-TRE-1 | R2. | The BA shall calculate the Primary Frequency Response of each generating unit/generating facility in accordance with this standard and the Primary Frequency Response Reference Document. This calculation shall provide a 12-month rolling average of initial and sustained Primary Frequency Response performance. This calculation shall be completed each month for the preceding 12 calendar months. [Please see the standard for more information] | 2014-04-01 | 2020-06-30 | Low | The BA submitted a monthly report more than one month but less than 51 days after the end of the reporting month. | The BA submitted a monthly report more than 50 days but less than 71 days after the end of the reporting month. | The BA submitted a monthly report more than 70 days but less than 91 days after the end of the reporting month. | The BA failed to submit a monthly report within 90 days after the end of the reporting month. |  | BA |  |  |  | GO | GOP
Inactive | BAL | BAL-001-TRE-1 | R3. | The BA shall determine the Interconnection minimum Frequency Response (IMFR) in December of each year for the following year, and make the IMFR, the methodology for calculation and the criteria for determination of the IMFR publicly available. | 2014-04-01 | 2020-06-30 | Low | The BA did not make the calculation and criteria for determination of the IMFR publicly available. | The BA did not make the IMFR publicly available. | The BA did not calculate the IMFR for the following year in December. | The BA did not calculate the IMFR for a calendar year. |  | BA |  |  |  | GO | GOP
Inactive | BAL | BAL-001-TRE-1 | R4. | After each calendar month in which one or more FMEs occurs, the BA shall determine and make publicly available the Interconnection’s combined Frequency Response performance for a rolling average of the last six (6) FMEs by the end of the following calendar month. | 2014-04-01 | 2020-06-30 | Medium | N/A | N/A | The BA did not make public the six-FME rolling average Interconnection combined Frequency Response by the end of the following month. | The BA did not calculate the six-FME rolling average Interconnection combined Frequency Response for any month in which an FME occurred. |  | BA |  |  |  | GO | GOP
Inactive | BAL | BAL-001-TRE-1 | R5. | Following any FME that causes the Interconnection’s six-FME rolling average combined Frequency Response performance to be less than the IMFR, the BA shall direct any necessary actions to improve Frequency Response, which may include, but are not limited to, directing adjustment of Governor deadband and/or droop settings. | 2014-04-01 | 2020-06-30 | Medium | N/A | N/A | N/A | The BA did not take action to improve Frequency Response when the Interconnection’s rolling-average combined Frequency Response performance was less than the IMFR. |  | BA |  |  |  | GO | GOP
Inactive | BAL | BAL-001-TRE-1 | R6. | Each GO shall set its Governor parameters as follows: [Please see the standard for more information] | 2014-04-01 | 2020-06-30 | Medium | Any Governor parameter setting was > 10% and = 20% outside setting range specified in R6. | Any Governor parameter setting was > 20% and = 30% outside setting range specified in R6. | Any Governor parameter setting was > 30% and = 40% outside setting range specified in R6. | Any Governor parameter setting was > 40% outside setting range specified in R6, – OR – an electronic or digital Governor was set to step into the droop curve. |  | BA |  |  |  | GO | GOP
Inactive | BAL | BAL-001-TRE-1 | R7. | Each GO shall operate each generating unit/generating facility that is connected to the interconnected transmission system with the Governor in service and responsive to frequency when the generating unit/generating facility is online and released for dispatch, unless the GO has a valid reason for operating with the Governor not in service and the GOP has been notified that the Governor is not in service. | 2014-04-01 | 2020-06-30 | Medium | N/A | N/A | N/A | The GO operated with its Governor out of service and did not notify the GOP upon discovery of its Governor out of service. |  | BA |  |  |  | GO | GOP
Inactive | BAL | BAL-001-TRE-1 | R8. | Each GOP shall notify the BA as soon as practical but within 30 minutes of the discovery of a status change (in service, out of service) of a Governor. | 2014-04-01 | 2020-06-30 | Medium | The GOP notified the BA of a change in Governor status between 31 minutes and one hour after the GOP was notified of the discovery of the change. | The GOP notified the BA of a change in Governor status more than 1 hour but within 4 hours after the GOP was notified of the discovery of the change. | The GOP notified the BA of a change in Governor status more than 4 hours but within 24 hours after the GOP was notified of the discovery of the change. | The GOP failed to notify the BA of a change in Governor status within 24 hours after the GOP was notified of the discovery of the change. |  | BA |  |  |  | GO | GOP
Inactive | BAL | BAL-001-TRE-1 | R9. | Each GO shall meet a minimum 12-month rolling average initial Primary Frequency Response performance of 0.75 on each generating unit/generating facility, based on participation in at least eight FMEs. [Please see the standard for more information] | 2014-04-01 | 2020-06-30 | Medium | A GO’s rolling average initial Primary Frequency Response performance per R9 was < 0.75 and = 0.65. | A GO’s rolling average initial Primary Frequency Response performance per R9 was < 0.65 and = 0.55. | A GO’s rolling average initial Primary Frequency Response performance per R9 was < 0.55 and = 0.45. | A GO’s rolling average initial Primary Frequency Response performance per R9 was < 0.45. |  | BA |  |  |  | GO | GOP
Inactive | BAL | BAL-001-TRE-1 | R10. | Each GO shall meet a minimum 12-month rolling average sustained Primary Frequency Response performance of 0.75 on each generating unit/generating facility, based on participation in at least eight FMEs. [Please see the standard for more information] | 2014-04-01 | 2020-06-30 | Medium | A GO’s rolling average sustained Primary Frequency Response performance per R10 was < 0.75 and = 0.65. | A GO’s rolling average sustained Primary Frequency Response performance per R10 was < 0.65 and = 0.55. | A GO’s rolling average sustained Primary Frequency Response performance per R10 was < 0.55 and = 0.45. | A GO’s rolling average sustained Primary Frequency Response performance per R10 was < 0.45. |  | BA |  |  |  | GO | GOP
Mandatory Subject to Enforcement | BAL | BAL-001-TRE-2 | R1. | The Balancing Authority shall identify Frequency Measurable Events (FMEs), and within 14 calendar days after each FME the Balancing Authority shall notify the Compliance Enforcement Authority and make FME information (time of FME (t(0)), pre-perturbation average frequency, post- perturbation average frequency) publicly available. | 2020-07-01 |  | Low | The Balancing Authority reported an FME more than 14 days but less than 31 days after identification of the event. | The Balancing Authority reported an FME more than 30 days but less than 51 days after identification of the event. | The Balancing Authority reported an FME more than 50 days but less than 71 days after identification of the event. | The Balancing Authority reported an FME more than 70 days after identification of the event. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-001-TRE-2 | R2. | The Balancing Authority shall calculate the Primary Frequency Response of each generating unit/generating facility in accordance with this standard and the Primary Frequency Response Reference Document. This calculation shall provide a 12-month rolling average of initial and sustained Primary Frequency Response performance. This calculation shall be completed each month for the preceding 12 calendar months. The Primary Frequency Response Reference Document contains the calculations that the Balancing Authority will use to determine Primary Frequency Response performance of generating units/generating facilities. This reference document is a Texas RE-controlled document that is subject to revision by the Texas RE Board of Directors. | 2020-07-01 |  | Low | The Balancing Authority submitted a monthly report more than one month but less than 51 days after the end of the reporting month. | The Balancing Authority submitted a monthly report more than 50 days but less than 71 days after the end of the reporting month. | The Balancing Authority submitted a monthly report more than 70 days but less than 91 days after the end of the reporting month. | The Balancing Authority failed to submit a monthly report within 90 days after the end of the reporting month. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-001-TRE-2 | R3. | The Balancing Authority shall determine the Interconnection minimum Frequency Response (IMFR) in December of each year for the following year, and make the IMFR, the methodology for calculation and the criteria for determination of the IMFR publicly available. | 2020-07-01 |  | Low | The Balancing Authority did not make the calculation and criteria for determination of the IMFR publicly available. | The Balancing Authority did not make the IMFR publicly available. | The Balancing Authority did not calculate the IMFR for the following year in December. | The Balancing Authority did not calculate the IMFR for a calendar year. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-001-TRE-2 | R4. | After each calendar month in which one or more FMEs occurs, the Balancing Authority shall determine and make publicly available the Interconnection’s combined Frequency Response performance for a rolling average of the last six (6) FMEs by the end of the following calendar month. | 2020-07-01 |  | Medium | N/A | N/A | The Balancing Authority did not make public the six-FME rolling average Interconnection combined Frequency Response by the end of the following month. | The Balancing Authority did not calculate the six-FME rolling average Interconnection combined Frequency Response for any month in which an FME occurred. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-001-TRE-2 | R5. | Following any FME that causes the Interconnection’s six-FME rolling average combined Frequency Response performance to be less than the IMFR, the Balancing Authority shall direct any necessary actions to improve Frequency Response, which may include, but are not limited to, directing adjustment of Governor deadband and/or droop settings. | 2020-07-01 |  | Medium | N/A | N/A | N/A | The Balancing Authority did not take action to improve Frequency Response when the Interconnection’s rolling-average combined Frequency Response performance was less than the IMFR. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-001-TRE-2 | R6. | Each Generator Owner shall set its Governor parameters as follows: [Please see the standard for more information] | 2020-07-01 |  | Medium | Any Governor parameter setting was > 10% and = 20% outside setting range specified in R6. | Any Governor parameter setting was > 20% and = 30% outside setting range specified in R6. | Any Governor parameter setting was > 30% and = 40% outside setting range specified in R6. | Any Governor parameter setting was > 40% outside setting range specified in R6, – OR – an electronic or digital Governor was set to step into the droop curve. | [5 empty] | GO
Mandatory Subject to Enforcement | BAL | BAL-001-TRE-2 | R7. | Each Generator Owner shall operate each generating unit/generating facility that is connected to the interconnected transmission system with the Governor in service and responsive to frequency when the generating unit/generating facility is online and released for dispatch, unless the Generator Owner has a valid reason for operating with the Governor not in service and the Generator Operator has been notified that the Governor is not in service. | 2020-07-01 |  | Medium | N/A | N/A | N/A | The Generator Owner operated with its Governor out of service and did not notify the Generator Operator upon discovery of its Governor out of service. | [5 empty] | GO
Mandatory Subject to Enforcement | BAL | BAL-001-TRE-2 | R8. | Each Generator Operator shall notify the Balancing Authority as soon as practical but within 30 minutes of the discovery of a status change (in service, out of service) of a Governor. | 2020-07-01 |  | Medium | The Generator Operator notified the Balancing Authority of a change in Governor status between 31 minutes and one hour after the General Operator was notified of the discovery of the change. | The General Operator notified the Balancing Authority of a change in Governor status more than 1 hour but within 4 hours after the Generator Operator was notified of the discovery of the change. | The Generator Operator notified the Balancing Authority of a change in Governor status more than 4 hours but within 24 hours after the Generator Operator was notified of the discovery of the change. | The Generator Operator failed to notify the Balancing Authority of a change in Governor status within 24 hours after the Generator Operator was notified of the discovery of the change. | [6 empty] | GOP
Mandatory Subject to Enforcement | BAL | BAL-001-TRE-2 | R9. | Each Generator Owner shall meet a minimum 12-month rolling average initial Primary Frequency Response performance of 0.75 on each generating unit/generating facility, based on participation in at least eight FMEs. [Please see the standard for more information] | 2020-07-01 |  | Medium | A Generator Owner’s rolling average initial Primary Frequency Response performance per R9 was < 0.75 and = 0.65. | A Generator Owner’s rolling average initial Primary Frequency Response performance per R9 was < 0.65 and = 0.55. | A Generator Owner’s rolling average initial Primary Frequency Response performance per R9 was < 0.55 and = 0.45. | A Generator Owner’s rolling average initial Primary Frequency Response performance per R9 was < 0.45. | [5 empty] | GO
Mandatory Subject to Enforcement | BAL | BAL-001-TRE-2 | R10. | Each Generator Owner shall meet a minimum 12-month rolling average sustained Primary Frequency Response performance of 0.75 on each generating unit/generating facility, based on participation in at least eight FMEs. [Please see the standard for more information] | 2020-07-01 |  | Medium | A Generator Owner’s rolling average sustained Primary Frequency Response performance per R10 was < 0.75 and = 0.65. | A Generator Owner’s rolling average sustained Primary Frequency Response performance per R10 was < 0.65 and = 0.55. | A Generator Owner’s rolling average sustained Primary Frequency Response performance per R10 was < 0.55 and = 0.45. | A Generator Owner’s rolling average sustained Primary Frequency Response performance per R10 was < 0.45. | [5 empty] | GO
Inactive | BAL | BAL-002-0 | R1. | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. | 2007-06-18 | 2012-03-31 | High |  |  |  | The Balancing Authority does not have access to and/or operate Contingency Reserve to respond to Disturbances. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-0 | R2. | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: | 2007-06-18 | 2012-03-31 | Low | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 1 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 2 or 3 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 4 or 5 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify all 6 of the following sub-requirements. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-0 | R3. | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. | 2007-06-18 | 2012-03-31 | High | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 100% but greater than or equal to 95%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 95% but greater than or equal to 90%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 90% but greater than or equal to 85%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 85%. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-0 | R4. | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: | 2007-06-18 | 2012-03-31 | Low | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 90% and less than 100% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-0 | R5. | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: | 2007-06-18 | 2012-03-31 | Low | The Reserve Sharing Group met the DCS requirement for more than 90% and less than 100% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-0 | R6. | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. | 2007-06-18 | 2012-03-31 | Medium | The Balancing Authority or Reserve Sharing Group restored less than 100% but greater than 90% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 90% but greater than 80% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 80% but greater than or equal to 70% of its Contingency Reserve during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than 70% of its Contingency Reserves during the Contingency Reserve Restoration Period. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-1 | R1. | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. | 2012-04-01 | 2017-12-31 | High | [5 empty] | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-1 | R2. | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: | 2012-04-01 | 2017-12-31 | Medium | [5 empty] | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-1 | R3. | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. | 2012-04-01 | 2017-12-31 | High | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 100% but greater than or equal to 95%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 95% but greater than or equal to 90%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 90% but greater than or equal to 85%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 85%. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-1 | R4. | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: | 2012-04-01 | 2017-12-31 | Medium | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 90% and less than 100% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-1 | R5. | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: | 2012-04-01 | 2017-12-31 | Low | The Reserve Sharing Group met the DCS requirement for more than 90% and less than 100% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-1 | R6. | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. | 2012-04-01 | 2017-12-31 | Medium | The Balancing Authority or Reserve Sharing Group restored less than 100% but greater than 90% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 90% but greater than 80% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 80% but greater than or equal to 70% of its Contingency Reserve during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than 70% of its Contingency Reserves during the Contingency Reserve Restoration Period. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-1a | R1. | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. |  | 2017-02-17 | High | N/A | N/A | N/A | The Balancing Authority does not have access to and/or operate Contingency Reserve to respond to Disturbances. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-1a | R2. | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: |  | 2017-02-17 | Medium | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 1 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 2 or 3 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify 4 or 5 of the following sub-requirements. | The Regional Reliability Organization, sub-Regional Reliability Organization, or Reserve Sharing Group has failed to specify all 6 of the following sub-requirements. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-1a | R3. | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. |  | 2017-02-17 | High | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 100% but greater than or equal to 95%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 95% but greater than or equal to 90%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 90% but greater than or equal to 85%. | The Balancing Authority or Reserve Sharing Group’s Average Percent Recovery per the NERC DCS quarterly report was less than 85%. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-1a | R4. | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: |  | 2017-02-17 | Medium | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 90% and less than 100% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Balancing Authority or Reserve Sharing Group met the Disturbance Recovery Criterion within the Disturbance Recovery Period for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-1a | R5. | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: |  | 2017-02-17 | Low | The Reserve Sharing Group met the DCS requirement for more than 90% and less than 100% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 80% and less than or equal to 90% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 70% and less than or equal to 80% of Reportable Disturbances. | The Reserve Sharing Group met the DCS requirements for more than 0% and less than or equal to 70% of Reportable Disturbances. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-1a | R6. | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. |  | 2017-02-17 | Medium | The Balancing Authority or Reserve Sharing Group restored less than 100% but greater than 90% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 90% but greater than 80% of its contingency reserves during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than or equal to 80% but greater than or equal to 70% of its Contingency Reserve during the Contingency Reserve Restoration Period. | The Balancing Authority or Reserve Sharing Group restored less than 70% of its Contingency Reserves during the Contingency Reserve Restoration Period. |  | BA | [13 empty] | RRO |  | RSG
Inactive | BAL | BAL-002-2 | R1. | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: |  | 2017-12-31 | High | The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event. | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-2 | R2. | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. |  | 2017-12-31 | High | The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process. | N/A | The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process. | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-2 | R3. | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. |  | 2017-12-31 | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-2(i) | R1. | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: | 2018-01-01 | 2019-03-31 | High | The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event. | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-2(i) | R2. | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. | 2018-01-01 | 2019-03-31 | High | The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process. | N/A | The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process. | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-2(i) | R3. | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. | 2018-01-01 | 2019-03-31 | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. |  | BA | [15 empty] | RSG
Mandatory Subject to Enforcement | BAL | BAL-002-3 | R1. | The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: | 2019-04-01 |  | High | The Responsible Entity achieved less than 100% but at least 90% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period OR The Responsible Entity failed to use CR Form 1 to document a Reportable Balancing Contingency Event. | The Responsible Entity achieved less than 90% but at least 80% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 80% but at least 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. | The Responsible Entity achieved less than 70% of required recovery from a Reportable Balancing Contingency Event during the Contingency Event Recovery Period. |  | BA | [15 empty] | RSG
Mandatory Subject to Enforcement | BAL | BAL-002-3 | R2. | Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. | 2019-04-01 |  | High | The Responsible Entity developed and implemented an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to maintain annually the Operating Process. | N/A | The Responsible Entity developed an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency but failed to implement the Operating Process. | The Responsible Entity failed to develop an Operating Process to determine its Most Severe Single Contingency and to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency. |  | BA | [15 empty] | RSG
Mandatory Subject to Enforcement | BAL | BAL-002-3 | R3. | Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. | 2019-04-01 |  | Medium | The Responsible Entity restored less than 100% but at least 90% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 90% but at least 80% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 80% but at least 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. | The Responsible Entity restored less than 70% of required Contingency Reserve following a Reportable Balancing Contingency Event during the Contingency Event Restoration Period. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-WECC-1 | R1. | Each Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group shall maintain as a minimum Contingency Reserve that is the sum of the following: |  | 2010-11-26 | Medium | There shall be a Lower Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Contingency Reserve is less than 100% but greater than or equal to 90% of the required Contingency Reserve. | There shall be a Moderate Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Contingency Reserve is less than 90% but greater than or equal to 80% of the required Contingency Reserve. | There shall be a High Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Contingency Reserve is less than 80% but greater than or equal to 70% of the required Contingency Reserve. | There shall be a Severe Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Contingency Reserve is less than 70% of the required Contingency Reserve. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-WECC-1 | R2. | Each Reserve Sharing Group or Balancing Authority that is not a member of a Reserve Sharing Group shall maintain at least half of the Contingency Reserve in R1.1 as Spinning Reserve. Any Spinning Reserve specified in R1 shall meet the following requirements. |  | 2010-11-26 | High | There shall be a Lower Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Spinning Reserve is less than 100% but greater than or equal to 90% of the required Spinning Reserve. | There shall be a Moderate Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Spinning Reserve is less than 90% but greater than or equal to 80% of the required Spinning Reserve. | There shall be a High Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Spinning Reserve is less than 80% but greater than or equal to 70% of the required Spinning Reserve. | There shall be a Severe Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority's or the Reserve Sharing Group's Spinning Reserve is less than 70% of the required Spinning Reserve. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-WECC-1 | R3. | Each Reserve Sharing Group or Balancing Authority shall use the following acceptable types of reserve which must be fully deployable within 10 minutes of notification to meet R1: |  | 2010-11-26 | Medium | N/A | N/A | There shall be a High Level of non-compliance if there is one hour during a calendar month in which the Balancing Authority or Reserve Sharing Group used unacceptable resources for Contingency Reserves. | N/A |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-WECC-2 | R1. | Each Balancing Authority and each Reserve Sharing Group shall maintain a minimum amount of Contingency Reserve, except within the first sixty minutes following an event requiring the activation of Contingency Reserve, that is: | 2014-10-01 | 2017-01-23 | High | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-WECC-2 | R2. | Each Balancing Authority and each Reserve Sharing Group shall maintain at least half of its minimum amount of Contingency Reserve identified in Requirement R1, as Operating Reserve – Spinning that meets both of the following reserve characteristics. | 2014-10-01 | 2017-01-23 | High | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 100% but greater than or equal to 90% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 90% but greater than or equal to 80% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 80% but greater than or equal to 70% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 70% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-WECC-2 | R3. | Each Sink Balancing Authority and each sink Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | 2014-10-01 | 2017-01-23 | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R3. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-WECC-2 | R4. | Each Source Balancing Authority and each source Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve amounts identified in Requirement R1, equal to the amount and type of Operating Reserves for any Operating Reserve transactions for which it is the Source Balancing Authority or source Reserve Sharing Group. | 2014-10-01 | 2017-01-23 | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R4. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-WECC-2a | R1. | Each Balancing Authority and each Reserve Sharing Group shall maintain a minimum amount of Contingency Reserve, except within the first sixty minutes following an event requiring the activation of Contingency Reserve, that is: | 2017-01-24 | 2021-06-27 | High | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-WECC-2a | R2. | Each Balancing Authority and each Reserve Sharing Group shall maintain at least half of its minimum amount of Contingency Reserve identified in Requirement R1, as Operating Reserve – Spinning that meets both of the following reserve characteristics. | 2017-01-24 | 2021-06-27 | High | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 100% but greater than or equal to 90% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 90% but greater than or equal to 80% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 80% but greater than or equal to 70% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve Operating Reserve - Spinning is less than 70% of the required Operating Reserve–Spinning amount specified in Requirement R2, and both characteristics were met. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-WECC-2a | R3. | Each Sink Balancing Authority and each sink Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | 2017-01-24 | 2021-06-27 | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R3. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-002-WECC-2a | R4. | Each Source Balancing Authority and each source Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve amounts identified in Requirement R1, equal to the amount and type of Operating Reserves for any Operating Reserve transactions for which it is the Source Balancing Authority or source Reserve Sharing Group. | 2017-01-24 | 2021-06-27 | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R4. |  | BA | [15 empty] | RSG
Mandatory Subject to Enforcement | BAL | BAL-002-WECC-3 | R1. | Each Balancing Authority and each Reserve Sharing Group shall maintain a minimum amount of Contingency Reserve, except within the first sixty minutes following an event requiring the activation of Contingency Reserve, that is: | 2021-06-28 |  | High | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. | The Balancing Authority or the Reserve Sharing Group that incurs one Clock Hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Contingency Reserve amount, with the characteristics specified in Requirement R1. |  | BA | [15 empty] | RSG
Mandatory Subject to Enforcement | BAL | BAL-002-WECC-3 | R2. | Reserved. | 2021-06-28
Mandatory Subject to Enforcement | BAL | BAL-002-WECC-3 | R3. | Each Sink Balancing Authority and each sink Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve in Requirement R1, equal to the amount of Operating Reserve–Supplemental for any Interchange Transaction designated as part of the Source Balancing Authority’s Operating Reserve–Supplemental or source Reserve Sharing Group’s Operating Reserve–Supplemental, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. | 2021-06-28 |  | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R3. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R3. |  | BA | [15 empty] | RSG
Mandatory Subject to Enforcement | BAL | BAL-002-WECC-3 | R4. | Each Source Balancing Authority and each source Reserve Sharing Group shall maintain an amount of Operating Reserve, in addition to the minimum Contingency Reserve amounts identified in Requirement R1, equal to the amount and type of Operating Reserves for any Operating Reserve transactions for which it is the Source Balancing Authority or source Reserve Sharing Group. | 2021-06-28 |  | High | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 100% but greater than or equal to 90% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 90% but greater than or equal to 80% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 80% but greater than or equal to 70% of the required Operating Reserve amount specified in Requirement R4. | The Balancing Authority or the Reserve Sharing Group that incurs one hour, during a calendar month, in which Contingency Reserve Operating Reserve is less than 70% of the required Operating Reserve amount specified in Requirement R4. |  | BA | [15 empty] | RSG
Inactive | BAL | BAL-003-0 | R1. | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. | 2007-06-18 | 2008-08-26 | Low | [5 empty] | BA
Inactive | BAL | BAL-003-0 | R2. | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: | 2007-06-18 | 2008-08-26 | Low | [5 empty] | BA
Inactive | BAL | BAL-003-0 | R3. | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. | 2007-06-18 | 2008-08-26 | Low | [5 empty] | BA
Inactive | BAL | BAL-003-0 | R4. | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. | 2007-06-18 | 2008-08-26 | Low | [5 empty] | BA
Inactive | BAL | BAL-003-0 | R5. | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. | 2007-06-18 | 2008-08-26 | Low | [5 empty] | BA
Inactive | BAL | BAL-003-0 | R6. | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. | 2007-06-18 | 2008-08-26 | Medium | [5 empty] | BA
Inactive | BAL | BAL-003-0.1a | R1. | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. | 2009-05-13 | 2009-06-28 | [6 empty] | BA
Inactive | BAL | BAL-003-0.1a | R2. | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: | 2009-05-13 | 2009-06-28 | [6 empty] | BA
Inactive | BAL | BAL-003-0.1a | R3. | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. | 2009-05-13 | 2009-06-28 | [6 empty] | BA
Inactive | BAL | BAL-003-0.1a | R4. | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. | 2009-05-13 | 2009-06-28 | [6 empty] | BA
Inactive | BAL | BAL-003-0.1a | R5. | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. | 2009-05-13 | 2009-06-28 | [6 empty] | BA
Inactive | BAL | BAL-003-0.1a | R6. | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. | 2009-05-13 | 2009-06-28 | [6 empty] | BA
Inactive | BAL | BAL-003-0.1b | R1. | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. | 2009-06-29 | 2015-03-31 | Low | [5 empty] | BA
Inactive | BAL | BAL-003-0.1b | R2. | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: | 2009-06-29 | 2015-03-31 | Medium | [5 empty] | BA
Inactive | BAL | BAL-003-0.1b | R3. | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. | 2009-06-29 | 2015-03-31 | Medium | [5 empty] | BA
Inactive | BAL | BAL-003-0.1b | R4. | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. | 2009-06-29 | 2015-03-31 | Low | [5 empty] | BA
Inactive | BAL | BAL-003-0.1b | R5. | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. | 2009-06-29 | 2015-03-31 | Medium | [5 empty] | BA
Inactive | BAL | BAL-003-0.1b | R6. | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. | 2009-06-29 | 2015-03-31 | Medium | [5 empty] | BA
Inactive | BAL | BAL-003-0a | R1. | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. | 2008-08-27 | 2009-05-12 | [6 empty] | BA
Inactive | BAL | BAL-003-0a | R2. | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: | 2008-08-27 | 2009-05-12 | [6 empty] | BA
Inactive | BAL | BAL-003-0a | R3. | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. | 2008-08-27 | 2009-05-12 | [6 empty] | BA
Inactive | BAL | BAL-003-0a | R4. | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. | 2008-08-27 | 2009-05-12 | [6 empty] | BA
Inactive | BAL | BAL-003-0a | R5. | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. | 2008-08-27 | 2009-05-12 | [6 empty] | BA
Inactive | BAL | BAL-003-0a | R6. | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. | 2008-08-27 | 2009-05-12 | [6 empty] | BA
Inactive | BAL | BAL-003-0b | R1. | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. |  | 2009-06-28 | [6 empty] | BA
Inactive | BAL | BAL-003-0b | R2. | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: |  | 2009-06-28 | [6 empty] | BA
Inactive | BAL | BAL-003-0b | R3. | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability |  | 2009-06-28 | [6 empty] | BA
Inactive | BAL | BAL-003-0b | R4. | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. |  | 2009-06-28 | [6 empty] | BA
Inactive | BAL | BAL-003-0b | R5. | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. |  | 2009-06-28 | [6 empty] | BA
Inactive | BAL | BAL-003-0b | R6. | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. |  | 2009-06-28 | [6 empty] | BA
Inactive | BAL | BAL-003-1 | R1. | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. | 2015-04-01 | 2015-11-12 | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO |  | BA |  |  | FRSG
Inactive | BAL | BAL-003-1 | R2. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. | 2015-04-01 | 2015-11-12 | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. |  | BA |  |  | FRSG
Inactive | BAL | BAL-003-1 | R3. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: 1.1 Less than zero at all times, and 1.2 Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. | 2015-04-01 | 2015-11-12 | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%. |  | BA |  |  | FRSG
Inactive | BAL | BAL-003-1 | R4. | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. | 2015-04-01 | 2015-11-12 | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. |  | BA |  |  | FRSG
Inactive | BAL | BAL-003-1.1 | R1. | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. | 2016-04-01 | 2020-11-30 | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 1% but by at most 30% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% or by more than 15 MW/0.1 Hz, whichever is the greater deviation from its FRO |  | BA |  |  | FRSG
Inactive | BAL | BAL-003-1.1 | R2. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. | 2015-11-13 | 2020-11-30 | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. |  | BA |  |  | FRSG
Inactive | BAL | BAL-003-1.1 | R3. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: | 2015-11-13 | 2020-11-30 | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%.. |  | BA |  |  | FRSG
Inactive | BAL | BAL-003-1.1 | R4. | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. | 2015-11-13 | 2020-11-30 | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. |  | BA |  |  | FRSG
Mandatory Subject to Enforcement | BAL | BAL-003-2 | R1. | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. | 2020-10-01 |  | High | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by at most 15% or 15 MW/0.1 Hz, whichever one is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 15% but by at most 30% or 30 MW/0.1 Hz, whichever is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 30% but by at most 45% or 45 MW/0.1 Hz, whichever one is the greater deviation from its FRO. | The Balancing Authority’s, or Frequency Response Sharing Group’s, FRM was less negative than its FRO by more than 45% or by more than 45 MW/0.1 Hz, whichever is the greater deviation from its FRO. |  | BA |  |  | FRSG
Mandatory Subject to Enforcement | BAL | BAL-003-2 | R2. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. | 2020-10-01 |  | Medium | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting failed to implement the validated Frequency Bias Setting value into its ACE calculation within the implementation period specified but did so within 5 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 5 calendar days but less than or equal to 15 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting implemented the validated Frequency Bias Setting value into its ACE calculation in more than 15 calendar days but less than or equal to 25 calendar days from the implementation period specified by the ERO. | The Balancing Authority in a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting did not implement the validated Frequency Bias Setting value into its ACE calculation in more than 25 calendar days from the implementation period specified by the ERO. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-003-2 | R3. | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: | 2020-10-01 |  | Medium | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 1% but by at most 10%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 10% but by at most 20%. | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response Obligation by more than 20% but by at most 30%. | The Balancing Authority that is a multiple Balancing Authority Interconnection and not receiving Overlap Regulation Service and uses a variable Frequency Bias Setting average Frequency Bias Setting during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was less negative than its Frequency Response obligation by more than 30%. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-003-2 | R4. | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. | 2020-10-01 |  | Medium | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error less than or equal to 10% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 10% but less than or equal to 20% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 20% but less than or equal to 30% of the validated or calculated value. | The Balancing Authority incorrectly changed the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services with combined footprint setting-error more than 30% of the validated or calculated value. OR The Balancing Authority failed to change the Frequency Bias Setting value used in its ACE calculation when providing Overlap Regulation Services. |  | BA
Inactive | BAL | BAL-004-0 | R1. | Only a Reliability Coordinator shall be eligible to act as Interconnection Time Monitor. A single Reliability Coordinator in each Interconnection shall be designated by the NERC Operating Committee to serve as Interconnection Time Monitor. | 2007-06-18 | 2017-04-01 | Low |  |  |  | The responsible entity has designated more than one interconnection time monitor for a single interconnection. |  | BA | [10 empty] | RC
Inactive | BAL | BAL-004-0 | R2. | The Interconnection Time Monitor shall monitor Time Error and shall initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. | 2007-06-18 | 2017-04-01 | Low |  |  |  | The RC serving as the Interconnection Time Monitor failed to initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. |  | BA | [10 empty] | RC
Inactive | BAL | BAL-004-0 | R3. | Each Balancing Authority, when requested, shall participate in a Time Error Correction by one of the following methods: | 2007-06-18 | 2017-04-01 | Low | The Balancing Authority participated in more than 75% and less than 100% of requested Time Error Corrections for the calendar year. | The Balancing Authority participated in more than 50% and less than or equal to 75% of requested Time Error Corrections for the calendar year. | The Balancing Authority participated in more than 25% and less than or equal to 50% of requested Time Error Corrections for the calendar year. | The Balancing Authority participated in less than or equal to 25% of requested Time Error Corrections for the calendar year. |  | BA | [10 empty] | RC
Inactive | BAL | BAL-004-0 | R4. | Any Reliability Coordinator in an Interconnection shall have the authority to request the Interconnection Time Monitor to terminate a Time Error Correction in progress, or a scheduled Time Error Correction that has not begun, for reliability considerations. | 2007-06-18 | 2017-04-01 | Low |  |  |  | The RC serving as the Interconnection Time Monitor failed to initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. |  | BA | [10 empty] | RC
Inactive | BAL | BAL-004-1 | R1. | Only a Reliability Coordinator shall be eligible to act as Interconnection Time Monitor. |  | 2012-08-16 | [6 empty] | BA | [10 empty] | RC
Inactive | BAL | BAL-004-1 | R2. | Each Balancing Authority, when requested, shall participate in a Time Error Correction by one of the following methods: |  | 2012-08-16 | [6 empty] | BA | [10 empty] | RC
Inactive | BAL | BAL-004-1 | R3. | Any Reliability Coordinator in an Interconnection shall have the authority to request the Interconnection Time Monitor to terminate a Time Error Correction in progress, or a scheduled Time Error Correction that has not begun, for reliability considerations. |  | 2012-08-16 | [6 empty] | BA | [10 empty] | RC
Inactive | BAL | BAL-004-WECC-01 | R1. | Each BA that operates synchronously to the Western Interconnection shall continuously operate utilizing Automatic Time Error Correction (ATEC) in its Automatic Generation Control (AGC) system. (See standard for formulas.) | 2009-07-01 | 2014-03-31 | Low | [5 empty] | BA
Inactive | BAL | BAL-004-WECC-01 | R2. | Each BA that is synchronously connected to the Western Interconnection and operates in any AGC operating mode other than ATEC shall notify all other BAs of its operating mode through the designated Interconnection communication system. Each BA while synchronously connected to the Western Interconnection will be allowed to have ATEC out of service for a maximum of 24 hours per calendar quarter, for reasons including maintenance and testing. [Risk Factor: Lower] | 2009-07-01 | 2014-03-31 | Low | [5 empty] | BA
Inactive | BAL | BAL-004-WECC-01 | R3. | BAs in the Western Interconnection shall be able to change their AGC operating mode between Flat Frequency (for blackout restoration); Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; Tie Line Bias plus Time Error control (used in ATEC mode). The ACE used for NERC reports shall be the same ACE as the AGC operating mode in use. | 2009-07-01 | 2014-03-31 | Low | [5 empty] | BA
Inactive | BAL | BAL-004-WECC-01 | R4. | Regardless of the AGC operating mode each BA in the Western Interconnection shall compute its hourly Primary Inadvertent Interchange when hourly checkout is complete. If hourly checkout is not complete by 50 minutes after the hour, compute Primary Inadvertent Interchange with best available data. This hourly value shall be added to the appropriate accumulated Primary Inadvertent Interchange balance for either On-Peak or Off-Peak periods. | 2009-07-01 | 2014-03-31 | Low | [5 empty] | BA
Inactive | BAL | BAL-004-WECC-02 | R1. | Following the conclusion of each month each Balancing Authority shall verify that the absolute value of its Accumulated Primary Inadvertent Interchange (PII-accum) for both the monthly On-Peak period and the monthly Off-Peak period are each individually less than or equal to: | 2014-04-01 | 2018-09-30 | Medium | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 150%, but was less than or equal to 160% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 160%, but was less than or equal to 170% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 170%, but was less than or equal to 180% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 180% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. |  | BA
Inactive | BAL | BAL-004-WECC-02 | R2. | Each Balancing Authority shall, upon discovery of an error in the calculation of PII-hourly, recalculate within 90 days, the value of PII-hourly and adjust the PII-accum from the time of the error. | 2014-04-01 | 2018-09-30 | Medium | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 90 days of the discovery of the error; but made the required recalculations and adjustments within 120 days. | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 120 days of the discovery of the error; but made the required recalculations and adjustments within 150 days. | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 150 days of the discovery of the error; but made the required recalculations and adjustments within 180 days. | The Balancing Authority did not recalculate PIIhourly and adjust PIIaccum within 180 days of the discovery of the error. |  | BA
Inactive | BAL | BAL-004-WECC-02 | R3. | Each Balancing Authority shall keep its Automatic Time Error Correction (ATEC) in service, with an allowable exception period of less than or equal to an accumulated 24 hours per calendar quarter for ATEC to be out of service. | 2014-04-01 | 2018-09-30 | Medium | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 24 hours, but less than or equal to 72 hours. | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 72 hours, but less than or equal to 120 hours. | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 120 hours, but less than or equal to 168 hours | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 168 hours. |  | BA
Inactive | BAL | BAL-004-WECC-02 | R4. | Each Balancing Authority shall compute the following by 50 minutes after each hour: | 2014-04-01 | 2018-09-30 | Medium | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within 50 minutes, but made the required calculations in less than or equal to two hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within two hours, but made the required calculations in less than or equal to four hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within four hours, but made the required calculations in less than or equal to six hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within six hours. |  | BA
Inactive | BAL | BAL-004-WECC-02 | R5. | Each Balancing Authority shall be able to change its Automatic Generation Control operating mode between Flat Frequency (for blackout restoration); Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; and Tie Line Bias plus Time Error Control (used in ATEC mode), to correspond to current operating conditions. | 2014-04-01 | 2018-09-30 | Medium | N/A | N/A | N/A | The Balancing Authority is not able to change its AGC operating mode between Flat Frequency (for blackout restoration; Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; or Tie Line Bias plus Time Error control (used in ATEC mode). |  | BA
Inactive | BAL | BAL-004-WECC-02 | R6. | Each Balancing Authority shall recalculate the PIIhourly and PIIaccum for the On-Peak and Off-Peak periods whenever adjustments are made to hourly Inadvertent Interchange or ?TE. | 2014-04-01 | 2018-09-30 | Medium | N/A | N/A | N/A | When making adjustments to hourly Inadvertent Interchange or ?TE, the Balancing Authority did not recalculate the PIIhourly and the PIIaccum for the On-Peak and Off-Peak periods. |  | BA
Inactive | BAL | BAL-004-WECC-02 | R7. | Each Balancing Authority shall make the same adjustment to the PII-accum as it did for any month-end meter reading adjustments to Inadvertent Interchange. | 2014-04-01 | 2018-09-30 | Medium | N/A | N/A | N/A | When making any month-end meter reading adjustments to Inadvertent Interchange, the Balancing Authority did not make the same adjustment to the PIIaccum. |  | BA
Inactive | BAL | BAL-004-WECC-02 | R8. | Each Balancing Authority shall payback Inadvertent Interchange using ATEC rather than bilateral and unilateral payback. | 2014-04-01 | 2018-09-30 | Medium | N/A | N/A | N/A | The Balancing Authority paid back Inadvertent Interchange using bilateral and unilateral payback rather than using ATEC. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-004-WECC-3 | R1. | Each Balancing Authority shall operate its system such that, following the conclusion of each month, the month-end absolute value of its On-Peak and Off-Peak, Accumulated Primary Inadvertent Interchange (PIIaccum), as calculated by the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, are each individually less than or equal to: | 2018-10-01 |  | Medium | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 150%, but was less than or equal to 160% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 160%, but was less than or equal to 170% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 170%, but was less than or equal to 180% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. | Following the conclusion of each month each Balancing Authority’s absolute value of PIIaccum for either the On-Peak period or Off-Peak period exceeded 180% of the previous calendar year’s Peak Demand or peak generation for generation-only Balancing Authorities. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-004-WECC-3 | R2. | Each Balancing Authority shall, upon discovery of an error in the calculation of PIIhourly, recalculate within 90 days, the value of PIIhourly and adjust the PIIaccum from the time of the error. | 2018-10-01 |  | Medium | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 90 days of the discovery of the error; but made the required recalculations and adjustments within 120 days. | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 120 days of the discovery of the error; but made the required recalculations and adjustments within 150 days. | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 150 days of the discovery of the error; but made the required recalculations and adjustments within 180 days. | The Balancing Authority did not recalculate PIIhourly and adjust the PIIaccum within 150 days of the discovery of the error. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-004-WECC-3 | R3. | Each Balancing Authority shall keep its Automatic Time Error Correction (ATEC) in service, with an allowable exception period of less than or equal to an accumulated 24 hours per calendar quarter for ATEC to be out of service. | 2018-10-01 |  | Medium | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 24 hours, but less than or equal to 72 hours. | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 72 hours, but less than or equal to 120 hours. | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 120 hours, but less than or equal to 168 hours | The Balancing Authority operated during a calendar quarter without ATEC in service for more than an accumulated 168 hours. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-004-WECC-3 | R4. | Each Balancing Authority shall compute each of the following using the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, no later than 50 minutes after each hour, | 2018-10-01 |  | Medium | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within 50 minutes, but made the required calculations in less than or equal to two hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within two hours, but made the required calculations in less than or equal to four hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within four hours, but made the required calculations in less than or equal to six hours. | The Balancing Authority did not compute PIIhourly, PIIaccum, and IATEC within six hours. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-004-WECC-3 | R5. | Each Balancing Authority shall be able to change its Automatic Generation Control operating mode between Flat Frequency (for blackout restoration); Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; and Tie Line Bias plus Time Error Control (used in ATEC mode), to correspond to current operating conditions. | 2018-10-01 |  | Medium | N/A | N/A | N/A | The Balancing Authority is not able to change its AGC operating mode between Flat Frequency (for blackout restoration; Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; or Tie Line Bias plus Time Error control (used in ATEC mode). |  | BA
Mandatory Subject to Enforcement | BAL | BAL-004-WECC-3 | R6. | Each Balancing Authority shall recalculate the PIIhourly and PIIaccum for the On-Peak and Off-Peak periods whenever adjustments are made to hourly Inadvertent Interchange or ?TE. | 2018-10-01 |  | Medium | N/A | N/A | N/A | When making adjustments to hourly Inadvertent Interchange or ?TE, the Balancing Authority did not recalculate the PIIhourly and the PIIaccum for the On-Peak and Off-Peak periods. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-004-WECC-3 | R7. | Each Balancing Authority shall make the same adjustment to the PIIaccum as it did for any month-end meter reading adjustments to Inadvertent Interchange. | 2018-10-01 |  | Medium | N/A | N/A | N/A | When making any month-end meter reading adjustments to Inadvertent Interchange, the Balancing Authority did not make the same adjustment to the PIIaccum. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-004-WECC-3 | R8. | Each Balancing Authority shall payback Inadvertent Interchange using ATEC rather than bilateral and unilateral payback. | 2018-10-01 |  | Medium | N/A | N/A | N/A | The Balancing Authority paid back Inadvertent Interchange using bilateral and unilateral payback rather than using ATEC. |  | BA
Inactive | BAL | BAL-005-0 | R1. | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. | 2007-06-18 | 2008-08-26 | Medium | N/A | N/A | N/A | N/A |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R2. | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. | 2007-06-18 | 2008-08-26 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R3. | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. | 2007-06-18 | 2008-08-26 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R4. | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. | 2007-06-18 | 2008-08-26 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R5. | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. | 2007-06-18 | 2008-08-26 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R6. | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. | 2007-06-18 | 2008-08-26 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R7. | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. | 2007-06-18 | 2008-08-26 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R8. | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. | 2007-06-18 | 2008-08-26 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R9. | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. | 2007-06-18 | 2008-08-26 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R10. | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. | 2007-06-18 | 2008-08-26 | High | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R11. | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. | 2007-06-18 | 2008-08-26 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R12. | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. | 2007-06-18 | 2008-08-26 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R13. | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. | 2007-06-18 | 2008-08-26 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R14. | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. | 2007-06-18 | 2008-08-26 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R15. | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. | 2007-06-18 | 2008-08-26 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R16. | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. | 2007-06-18 | 2008-08-26 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0 | R17. | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See standard for formula. | 2007-06-18 | 2008-08-26 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R1. | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. | 2009-05-13 | 2012-09-12 | [6 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R2. | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. | 2009-05-13 | 2012-09-12 | High | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R3. | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. | 2009-05-13 | 2012-09-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R4. | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. | 2009-05-13 | 2012-09-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R5. | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. | 2009-05-13 | 2012-09-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R6. | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. | 2009-05-13 | 2012-09-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R7. | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. | 2009-05-13 | 2012-09-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R8. | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. | 2009-05-13 | 2012-09-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R9. | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. | 2009-05-13 | 2012-09-12 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R10. | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. | 2009-05-13 | 2012-09-12 | High | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R11. | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. | 2009-05-13 | 2012-09-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R12. | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. | 2009-05-13 | 2012-09-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R13. | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. | 2009-05-13 | 2012-09-12 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R14. | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. | 2009-05-13 | 2012-09-12 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R15. | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. | 2009-05-13 | 2012-09-12 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R16. | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. | 2009-05-13 | 2012-09-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.1b | R17. | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values | 2009-05-13 | 2012-09-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R1. | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. | 2012-09-13 | 2018-12-31 | [6 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R2. | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. (Retirement approved by FERC effective January 21, 2014.) | 2012-09-13 | 2018-12-31 | High |  |  |  | The Balancing Authority failed to maintain Regulating Reserve that can be controlled by AGC to meet Control Performance Standard. |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R3. | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. | 2012-09-13 | 2018-12-31 | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to ensure adequate metering, communications, and control equipment was provided. |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R4. | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. | 2012-09-13 | 2018-12-31 | Medium |  |  |  | The Balancing Authority providing Regulation Service failed to notify the Host Balancing Authority for whom it is controlling if it was unable to provide the service, as well as any Intermediate Balancing Authorities. |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R5. | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. | 2012-09-13 | 2018-12-31 | Medium |  |  |  | The Balancing Authority receiving Regulation Service failed to ensure that back-up plans were in place to provide replacement Regulation Service. |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R6. | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. | 2012-09-13 | 2018-12-31 | Medium | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE. | The Balancing Authority failed to calculate ACE as specified in the requirement. |  | The Balancing Authority failed to notify the Reliability Coordinator within 30 minutes of its inability to calculate ACE and failed to use the ACE calculation specified in the requirement in its attempt to calculate ACE. |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R7. | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. | 2012-09-13 | 2018-12-31 | Medium |  |  |  | The Balancing Authority failed to operate AGC continuously when there were no adverse impacts OR if their AGC was inoperative the Balancing Authority failed to use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R8. | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. | 2012-09-13 | 2018-12-31 | Medium |  |  |  | The Balancing Authority failed to ensure that data acquisition for and calculation of ACE occurred at least every six seconds. |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R9. | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. | 2012-09-13 | 2018-12-31 | Low |  |  |  | The Balancing Authority failed to include all Interchanged Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R10. | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. | 2012-09-13 | 2018-12-31 | High |  |  |  | The Balancing Authority failed to include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R11. | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. | 2012-09-13 | 2018-12-31 | Medium |  |  |  | The Balancing Authority failed to include the effect of Ramp rates in the Scheduled Interchange values to calculate ACE. |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R12. | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. | 2012-09-13 | 2018-12-31 | Medium |  |  |  | The Balancing Authority failed to include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R13. | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. | 2012-09-13 | 2018-12-31 | Low |  |  |  | The Balancing Authority failed to perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment OR the Balancing Authority failed to adjust the component (e.g., Tie Line |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R14. | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. | 2012-09-13 | 2018-12-31 | Low | N/A | The responsible entity did not provide its operating personnel with real-time values for one of the following: ACE, Interconnection frequency or Net Actual Interchange. | The responsible entity did not provide its operating personnel with real-time values for two of the following: ACE, Interconnection frequency or Net Actual Interchange. | The responsible entity did not provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. OR The respo |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R15. | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. | 2012-09-13 | 2018-12-31 | Low |  |  | The Balancing Authority failed to periodically test backup power supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power sup | The Balancing Authority failed to provide adequate and reliable backup power supplies to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R16. | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. | 2012-09-13 | 2018-12-31 | Medium | The Balancing Authority failed to collect coincident data to the greatest practical extent. |  | The Balancing Authority failed to flag missing or bad data for operator display and archival purposes. | The Balancing Authority failed to sample data at least at the same periodicity with which ACE is calculated. |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0.2b | R17. | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values | 2012-09-13 | 2018-12-31 | Medium |  |  |  | The Balancing Authority failed to at least annually check and calibrate its time error and frequency devices against a common reference. |  | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R1. | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. |  | 2008-04-15 | [6 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R2. | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. |  | 2008-04-15 | High | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R3. | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. |  | 2008-04-15 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R4. | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. |  | 2008-04-15 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R5. | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. |  | 2008-04-15 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R6. | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. |  | 2008-04-15 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R7. | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. |  | 2008-04-15 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R8. | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. |  | 2008-04-15 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R9. | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2008-04-15 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R10. | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. |  | 2008-04-15 | High | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R11. | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. |  | 2008-04-15 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R12. | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. |  | 2008-04-15 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R13. | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. |  | 2008-04-15 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R14. | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. |  | 2008-04-15 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R15. | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. |  | 2008-04-15 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R16. | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. |  | 2008-04-15 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0a | R17. | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See standard for formula. |  | 2008-04-15 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R1. | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. | 2008-08-27 | 2009-05-12 | [6 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R2. | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. | 2008-08-27 | 2009-05-12 | High | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R3. | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. | 2008-08-27 | 2009-05-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R4. | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. | 2008-08-27 | 2009-05-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R5. | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. | 2008-08-27 | 2009-05-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R6. | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. | 2008-08-27 | 2009-05-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R7. | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. | 2008-08-27 | 2009-05-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R8. | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. | 2008-08-27 | 2009-05-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R9. | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. | 2008-08-27 | 2009-05-12 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R10. | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. | 2008-08-27 | 2009-05-12 | High | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R11. | Balancing Authorities shall include the effect of Ramp Rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. | 2008-08-27 | 2009-05-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R12. | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. | 2008-08-27 | 2009-05-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R13. | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. | 2008-08-27 | 2009-05-12 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R14. | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. | 2008-08-27 | 2009-05-12 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R15. | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. | 2008-08-27 | 2009-05-12 | Low | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R16. | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. | 2008-08-27 | 2009-05-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Inactive | BAL | BAL-005-0b | R17. | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values | 2008-08-27 | 2009-05-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP
Mandatory Subject to Enforcement | BAL | BAL-005-1 | R1. | The Balancing Authority shall use a design scan rate of no more than six seconds in acquiring data necessary to calculate Reporting ACE. | 2019-01-01 |  | Medium | N/A | N/A | N/A | Balancing Authority was using a design scan rate of greater than six seconds to acquire the data necessary to calculate Reporting ACE. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-005-1 | R2. | A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. | 2019-01-01 |  | Medium | The Balancing Authority failed to notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 50 minutes from the beginning of the inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 50 minutes of the beginning of an inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 55 minutes from the beginning of an inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 55 minutes of the beginning of an inability to calculate Reporting ACE but notified its Reliability Coordinator in less than or equal to 60 minutes from the beginning of an inability to calculate Reporting ACE. | The Balancing Authority failed to notify its Reliability Coordinator within 60 minutes of the beginning of an inability to calculate Reporting ACE. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-005-1 | R3. | Each Balancing Authority shall use frequency metering equipment for the calculation of Reporting ACE: | 2019-01-01 |  | Medium | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.95% of the calendar year but was available greater than or equal to 99.94 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.94% of the calendar year but was available greater than or equal to 99.93 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.93% of the calendar year but was available greater than or equal to 99.92 % of the calendar year. | The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE was available less than 99.92% of the calendar year OR The Balancing Authority’s frequency metering equipment used for the calculation of Reporting ACE failed to have a minimum accuracy of 0.001 Hz. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-005-1 | R4. | The Balancing Authority shall make available to the operator information associated with Reporting ACE including, but not limited to, quality flags indicating missing or invalid data. | 2019-01-01 |  | Medium | N/A | N/A | N/A | The Balancing Authority failed to make available information indicating missing or invalid data associated with Reporting ACE to its operators. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-005-1 | R5. | Each Balancing Authority’s system used to calculate Reporting ACE shall be available a minimum of 99.5% of each calendar year. | 2019-01-01 |  | Medium | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.5% of the calendar year but was available greater than or equal to 99.4 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.4% of the calendar year but was available greater than or equal to 99.3 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.3% of the calendar year but was available greater than or equal to 99.2 % of the calendar year. | The Balancing Authority’s system used for the calculation of Reporting ACE was available less than 99.2% of the calendar year. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-005-1 | R6. | Each Balancing Authority that is within a multiple Balancing Authority Interconnection shall implement an Operating Process to identify and mitigate errors affecting the accuracy of scan rate data used in the calculation of Reporting ACE for each Balancing Authority Area. | 2019-01-01 |  | Medium | N/A | N/A | N/A | The Balancing Authority failed to implement an Operating Process to identify and mitigate errors affecting the scan-rate accuracy of data used in the calculation of Reporting ACE. |  | BA
Mandatory Subject to Enforcement | BAL | BAL-005-1 | R7. | Each Balancing Authority shall ensure that each Tie-Line, Pseudo-Tie, and Dynamic Schedule with an Adjacent Balancing Authority is equipped with: | 2019-01-01 |  | Medium | N/A | N/A | N/A | The Balancing Authority failed to use a common source for Tie-Lines, Pseudo-ties and Dynamic Schedules with its Adjacent Balancing Authorities OR The Balancing Authority failed to use a time synchronized common source for hourly megawatt hour values that are agreed-upon to aid in the identification and mitigation of errors. |  | BA
Inactive | BAL | BAL-006-0 | R1. | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. |  | 2006-05-01 | [6 empty] | BA
Inactive | BAL | BAL-006-0 | R2. | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. |  | 2006-05-01 | [6 empty] | BA
Inactive | BAL | BAL-006-0 | R3. | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | 2006-05-01 | [6 empty] | BA
Inactive | BAL | BAL-006-0 | R4. | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: |  | 2006-05-01 | [6 empty] | BA
Inactive | BAL | BAL-006-0 | R5. | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. |  | 2006-05-01 | [6 empty] | BA
Inactive | BAL | BAL-006-1 | R1. | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. | 2007-06-18 | 2009-05-12 | Low | [5 empty] | BA
Inactive | BAL | BAL-006-1 | R2. | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. | 2007-06-18 | 2009-05-12 | Low |  |  | . |  |  | BA
Inactive | BAL | BAL-006-1 | R3. | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. | 2007-06-18 | 2009-05-12 | Low | [5 empty] | BA
Inactive | BAL | BAL-006-1 | R4. | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: | 2007-06-18 | 2009-05-12 | Low | [5 empty] | BA
Inactive | BAL | BAL-006-1 | R5. | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. | 2007-06-18 | 2009-05-12 | Low | [5 empty] | BA
Inactive | BAL | BAL-006-1.1 | R1. | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. | 2009-05-13 | 2011-03-31 | [6 empty] | BA
Inactive | BAL | BAL-006-1.1 | R2. | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. | 2009-05-13 | 2011-03-31 | [6 empty] | BA
Inactive | BAL | BAL-006-1.1 | R3. | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. | 2009-05-13 | 2011-03-31 | [6 empty] | BA
Inactive | BAL | BAL-006-1.1 | R4. | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: | 2009-05-13 | 2011-03-31 | [6 empty] | BA
Inactive | BAL | BAL-006-1.1 | R5. | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. | 2009-05-13 | 2011-03-31 | [6 empty] | BA
Inactive | BAL | BAL-006-2 | R1. | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. | 2011-04-01 | 2018-12-31 | Low | N/A | N/A | N/A | Each Balancing Authority failed to calculate and record hourly Inadvertent Interchange. |  | BA
Inactive | BAL | BAL-006-2 | R2. | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. | 2011-04-01 | 2018-12-31 | Low | N/A | N/A | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. OR Failed to take into account interchange served by jointly owned generators. | The Balancing Authority failed to include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. AND Failed to take into account interchange served by jointly owned generators. |  | BA
Inactive | BAL | BAL-006-2 | R3. | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. | 2011-04-01 | 2018-12-31 | Low | N/A | N/A | N/A | The Balancing Authority failed to ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. |  | BA
Inactive | BAL | BAL-006-2 | R4. | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: | 2011-04-01 | 2018-12-31 | Low | The Balancing Authority failed to record Actual Net Interchange values that are equal but opposite in sign to its Adjacent Balancing Authorities. | The Balancing Authority failed to compute Inadvertent Interchange. | The Balancing Authority failed to operate to a common Net Interchange Schedule that is equal but opposite to its Adjacent Balancing Authorities. | N/A |  | BA
Inactive | BAL | BAL-006-2 | R5. | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. | 2011-04-01 | 2018-12-31 | Low | Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities, submitted a report to their respective Regional Reliability Organizations Survey Contact describing the nature and the cause of the dispute but failed to provide a process for correcting the discrepancy. | Adjacent Balancing Authorities that could not mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month, failed to submit a report to their respective Regional Reliability Organizations Survey Contact describing the nature and the cause of the dispute as well as a process for correcting the discrepancy. | N/A | N/A |  | BA
Mandatory Subject to Enforcement | BAL | BAL-502-RF-03 | R1. | The Planning Coordinator shall perform and document a Resource Adequacy analysis annually. The Resource Adequacy analysis shall | 2018-01-01 |  | Medium | The Planning Coordinator Resource Adequacy analysis failed to consider 1 or 2 of the Resource availability characteristics subcomponents under Requirement R1, Part 1.4 and documentation of how and why they were included in the analysis or why they were not included OR The Planning Coordinator Resource Adequacy analysis failed to consider Transmission maintenance outage schedules and document how and why they were included in the analysis or why they were not included per Requirement R1, Part 1.5 | The Planning Coordinator Resource Adequacy analysis failed to express the planning reserve margin developed from Requirement R1, Part 1.1 as a percentage of the net Median forecast peak Load per Requirement R1, Part 1.1.2 OR The Planning Coordinator Resource Adequacy analysis failed to include 1 of the Load forecast Characteristics subcomponents under Requirement R1, Part 1.3.1 and documentation of its use OR The Planning Coordinator Resource Adequacy analysis failed to include 1 of the Resource Characteristics subcomponents under Requirement R1, Part 1.3.2 and documentation of its use OR The Planning Coordinator Resource Adequacy analysis failed to document that all Load in the Planning Coordinator area is accounted for in its Resource Adequacy analysis per Requirement R1, Part 1.7 | The Planning Coordinator Resource Adequacy analysis failed to be performed or verified separately for individual years of Year One through Year Ten per Requirement R1, Part 1.2 OR The Planning Coordinator failed to perform an analysis or verification for one year in the 2 through 5 year period or one year in the 6 though 10 year period or both per Requirement R1, Part 1.2.2 OR The Planning Coordinator Resource Adequacy analysis failed to include 2 or more of the Load forecast Characteristics subcomponents under Requirement R1, Part 1.3.1 and documentation of their use OR The Planning Coordinator Resource Adequacy analysis failed to include 2 or more of the Resource Characteristics subcomponents under Requirement R1, Part 1.3.2 and documentation of their use OR The Planning Coordinator Resource Adequacy analysis failed to include Transmission limitations and documentation of its use per Requirement R1, Part 1.3.3 OR The Planning Coordinator Resource Adequacy analysis failed to include assistance from other interconnected systems OR The Planning Coordinator Resource Adequacy analysis failed to consider 3 or more Resource availability characteristics subcomponents under Requirement R1, Part 1.4 and documentation of how and why they were included in the analysis or why they were not included OR The Planning Coordinator Resource Adequacy analysis failed to document that capacity resources are appropriately accounted for in its Resource Adequacy analysis per Requirement R1, Part 1.6 | The Planning Coordinator failed to perform and document a Resource Adequacy analysis annually per R1. OR The Planning Coordinator Resource Adequacy analysis failed to calculate a Planning reserve margin that will result in the sum of the probabilities for loss of Load for the integrated peak hour for all days of each planning year analyzed for each planning period being equal to 0.1 per Requirement R1, Part 1.1 OR The Planning Coordinator failed to perform an analysis for Year One per Requirement R1, Part 1.2.1 | [10 empty] | PCPA
Mandatory Subject to Enforcement | BAL | BAL-502-RF-03 | R2. | The Planning Coordinator shall annually document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis | 2018-01-01 |  | Low | The Planning Coordinator failed to publicly post the documents as specified per requirement Requirement R2, Part 2.1 and Requirement R2, Part 2.2 later than 30 calendar days prior to the beginning of Year One per Requirement R2, Part 2.3 | The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis for one of the years in the 2 through 10 year period per Requirement R2, Part 2.1. OR The Planning Coordinator failed to document the Planning Reserve margin calculated per requirement R1.1 for each of the three years in the analysis per Requirement R2, Part 2.2. | The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis for year 1 of the 10 year period per Requirement R2, Part 2.1. OR The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis for two or more of the years in the 2 through 10 year period per Requirement R2, Part 2.1. | The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis per Requirement R2, Part 2. | [10 empty] | PCPA
Mandatory Subject to Enforcement | BAL | BAL-502-RF-03 | R3. | The Planning Coordinator shall identify any gaps between the needed amount of planning reserves defined in Requirement R1, Part 1.1 and the projected planning reserves documented in Requirement R2 | 2018-01-01 |  | Low | None | None | None | The Planning Coordinator failed to identify any gaps between the needed amount of planning reserves and the projected planning reserves, per R3 | [10 empty] | PCPA
Inactive | BAL | BAL-502-RFC-02 | R1. | The Planning Coordinator shall perform and document a Resource Adequacy analysis annually. The Resource Adequacy analysis shall: [See Standard pdf for requirements of the Resource Adequacy analysis] | 2011-05-23 | 2017-12-31 | Medium | The Planning Coordinator Resource Adequacy analysis failed to consider 1 or 2 of the Resource availability characteristics subcomponents under R1.4 and documentation of how and why they were included in the analysis or why they were not included OR The Planning Coordinator Resource Adequacy analysis failed to consider Transmission maintenance outage schedules and document how and why they were included in the analysis or why they were not included per R1.5 | The Planning Coordinator Resource Adequacy analysis failed to express the planning reserve margin developed from R1.1 as a percentage of the net Median forecast peak Load per R1.1.2 OR The Planning Coordinator Resource Adequacy analysis failed to include 1 of the Load forecast Characteristics subcomponents under R1.3.1 and documentation of its use OR The Planning Coordinator Resource Adequacy analysis failed to document that all Load in the Planning Coordinator area is accounted for in its Resource Adequacy analysis per R1.7 | The Planning Coordinator Resource Adequacy analysis failed to be performed or verified separately for individual years of Year One through Year Ten per R1.2 OR The Planning Coordinator failed to perform an analysis or verification for one year in the 2 through 5 year period or one year in the 6 though 10 year period or both per R1.2.2 OR The Planning Coordinator Resource Adequacy analysis failed to include 2 or more of the Load forecast Characteristics subcomponents under R1.3.1 and documentation of their use OR The Planning Coordinator Resource Adequacy analysis failed to include 2 or more of the Resource Characteristics subcomponents under R1.3.2 and documentation of their use OR The Planning Coordinator Resource Adequacy analysis failed to include Transmission limitations and documentation of its use per R1.3.3 OR The Planning Coordinator Resource Adequacy analysis failed to include assistance from other interconnected systems and documentation of its use per R1.3.4 OR The Planning Coordinator Resource Adequacy analysis failed to consider 3 or more Resource availability characteristics subcomponents under R1.4 and documentation of how and why they were included in the analysis or why they were not included OR The Planning Coordinator Resource Adequacy analysis failed to document that capacity resources are appropriately accounted for in its Resource Adequacy analysis per R1.6 | The Planning Coordinator failed to perform and document a Resource Adequacy analysis annually per R1 OR The Planning Coordinator Resource Adequacy analysis failed to calculate a Planning reserve margin that will result in the sum of the probabilities for loss of Load for the integrated peak hour for all days of each planning year analyzed for each planning period being equal to 0.1 per OR The Planning Coordinator failed to perform an analysis for Year One per R1.2.1 R1.1 | [10 empty] | PCPA
Inactive | BAL | BAL-502-RFC-02 | R2. | The Planning Coordinator shall annually document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis. [See Standard pdf for the requirements of the documentation] | 2011-05-23 | 2017-12-31 | Low | The Planning Coordinator failed to publicly post the documents as specified per requirement R2.1 and R2.2 later than 30 calendar days prior to the beginning of Year One per R2.3 | The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis for one of the years in the 2 through 10 year period per R2.1 OR The Planning Coordinator failed to document the Planning Reserve margin calculated per requirement R1.1 for each of the three years in the analysis per R2.2. | The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis for year 1 of the 10 year period per R2.1 OR The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis for two or more of the years in the 2 through 10 year period per R2.1. | The Planning Coordinator failed to document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis per R2. | [10 empty] | PCPA
Inactive | BAL | BAL-STD-002-0 | WR1. | The reliable operation of the interconnected power system requires that adequate generating capacity be available at all times to maintain scheduled frequency and avoid loss of firm load following transmission or generation contingencies. This generating capacity is necessary to: -supply requirements for load variations. -replace generating capacity and energy lost due to forced outages of generation or transmission equipment. -meet on-demand obligations. -replace energy lost due to curtailment of interruptible imports. a. Minimum Operating Reserve. Each Balancing Authority shall maintain minimum Operating Reserve which is the sum of the following: (i) Regulating reserve. Sufficient Spinning Reserve, immediately responsive to Automatic Generation Control (AGC) to provide sufficient regulating margin to allow the Balancing Authority to meet NERC’s Control Performance Criteria (see BAL-001-0). (ii) Contingency reserve. An amount of Spinning Reserve and Nonspinning Reserve (at least half of which must be Spinning Reserve), sufficient to meet the NERC Disturbance Control Standard BAL-002-0, equal to the greater of: (a) The loss of generating capacity due to forced outages of generation or transmission equipment that would result from the most severe single contingency; or (b) The sum of five percent of the load responsibility served by hydro generation and seven percent of the load responsibility served by thermal generation. The combined unit ramp rate of each Balancing Authority’s on-line, unloaded generating capacity must be capable of responding to the Spinning Reserve requirement of that Balancing Authority within ten minutes (iii) Additional reserve for interruptible imports. An amount of reserve, which can be made effective within ten minutes, equal to interruptible imports. (iv) Additional reserve for on-demand obligations. An amount of reserve, which can be made effective within ten minutes, equal to on-demand obligations to other entities or Balancing Authorities b. Acceptable types of Nonspinning Reserve. The Nonspinning Reserve obligations identified in subsections a (ii), a (iii), and a (iv), if any, can be met by use of the following: (i) interruptible load; (ii) interruptible exports; (iii) on-demand rights from other entities or Balancing Authorities; (iv) Spinning Reserve in excess of requirements in subsections a (i) and a (ii); or (v) off-line generation which qualifies as Nonspinning Reserve. c. Knowledge of Operating Reserve. Operating Reserves shall be calculated such that the amount available which can be fully activated in the next ten minutes will be known at all times. d. Restoration of Operating Reserve. After the occurrence of any event necessitating the use of Operating Reserve, that reserve shall be restored as promptly as practicable. The time taken to restore reserves shall not exceed 60 minutes (Source: WECC Criterion) | 2007-06-18 | 2014-09-30 | [6 empty] | BA | [15 empty] | RSG
Inactive | CIP | CIP-001-0 | R1. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. |  | 2007-01-01 | [6 empty] | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001-0 | R2. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. |  | 2007-01-01 | [6 empty] | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001-0 | R3. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. |  | 2007-01-01 | [6 empty] | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001-0 | R4. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. |  | 2007-01-01 | [6 empty] | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001-1 | R1. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. | 2007-06-18 | 2011-02-01 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001-1 | R2. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. | 2007-06-18 | 2011-02-01 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001-1 | R3. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. | 2007-06-18 | 2011-02-01 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001-1 | R4. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. | 2007-06-18 | 2011-02-01 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001-1a | R1. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. | 2011-02-02 | 2011-09-30 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001-1a | R2. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. | 2011-02-02 | 2011-09-30 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001-1a | R3. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. | 2011-02-02 | 2011-09-30 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001-1a | R4. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. | 2011-02-02 | 2011-09-30 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | CIP | CIP-001-2a | R1. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi site sabotage affecting larger portions of the Interconnection. | 2011-10-01 | 2013-12-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-001-2a | R2. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. | 2011-10-01 | 2013-12-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-001-2a | R3. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. | 2011-10-01 | 2013-12-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-001-2a | R4. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. | 2011-10-01 | 2013-12-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-001-2a | EA.1. | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. | 2011-10-01 | 2013-12-31 | [6 empty] | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-001-2a | EA.2. | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. | 2011-10-01 | 2013-12-31 | [6 empty] | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-001-2a | EA.3. | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. | 2011-10-01 | 2013-12-31 | [6 empty] | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-001-2a | EA.4. | Each Reliability Coordinator, Balancing Authority, Transmission Owner, Transmission Operator, Generator Owner, Generator Operator, and Load Serving Entity shall establish communications contacts with local Federal Bureau of Investigation (FBI) officials and develop reporting procedures as appropriate to their circumstances. | 2011-10-01 | 2013-12-31 | [6 empty] | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002-1 | R1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-1 | R2. | Critical Asset Identification - The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-1 | R3. | Critical Cyber Asset Identification - Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: | 2008-07-01 | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-1 | R4. | Annual Approval - A senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-2 | R1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-2 | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-2 | R3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-2, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: | 2010-04-01 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-2 | R4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3 | R1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets.. | 2010-10-01 | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3 | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. | 2010-10-01 | 2016-06-30 | High | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3 | R3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: | 2010-10-01 | 2016-06-30 | High | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3 | R4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3a | R1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | 2013-03-21 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3a | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | 2013-03-21 | High | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3a | R3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | 2013-03-21 | High | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3a | R4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | 2013-03-21 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3b | R1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3b | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | 2016-06-30 | High | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3b | R3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: |  | 2016-06-30 | High | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3b | R4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3(i) | R1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. |  | 2014-11-13 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3(i) | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | 2014-11-13 | High | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3(i) | R3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3(i), Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: See Standard for Requirement Parts. |  | 2014-11-13 | High | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3(i) | R4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | 2014-11-13 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3(i)b | R1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. See Standard for Requirement Parts |  | 2014-11-13 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3(i)b | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. |  | 2014-11-13 | High | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3(i)b | R3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3(i)b, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: See Standard for Requirement Parts |  | 2014-11-13 | High | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-3(i)b | R4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | 2014-11-13 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-4 | R1. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the criteria contained in CIP-002-4 Attachment 1 – Critical Asset Criteria. The Responsible Entity shall update this list as necessary, and review it at least annually. | 2014-10-01 | 2014-02-03 | High | N/A | N/A | The Responsible Entity has developed a list of Critical Assets but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of its identified Critical Assets even if such list is null. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-4 | R2. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R1, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. The Responsible Entity shall update this list as necessary, and review it at least annually. For each group of generating units (including nuclear generation) at a single plant location identified in Attachment 1, criterion 1.1, the only Cyber Assets that must be considered are those shared Cyber Assets that could, within 15 minutes, adversely impact the reliable operation of any combination of units that in aggregate equal or exceed Attachment 1, criterion 1.1. For the purpose of Standard CIP-002-4, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: • The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, • The Cyber Asset uses a routable protocol within a control center; or, • The Cyber Asset is dial-up accessible. | 2014-10-01 | 2014-02-03 | High | N/A | N/A | The Responsible Entity has developed a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 even if such list is null. OR A Cyber Asset essential to the operation of the Critical Asset was identified that met at least one of the bulleted characteristics in this requirement but was not included in the Critical Cyber Asset List. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-4 | R3. | Annual Approval — The senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1 and R2 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | 2014-10-01 | 2014-02-03 | Low | N/A | N/A | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of the list of Critical Assets. OR The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of the list of Critical Cyber Assets (even if such lists are null.) | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of both the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-4a | R1. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the criteria contained in CIP-002-4 Attachment 1 – Critical Asset Criteria. The Responsible Entity shall update this list as necessary, and review it at least annually. |  | 2013-03-21 | High | N/A | N/A | The Responsible Entity has developed a list of Critical Assets but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of its identified Critical Assets even if such list is null. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-4a | R2. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R1, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. The Responsible Entity shall update this list as necessary, and review it at least annually. For each group of generating units (including nuclear generation) at a single plant location identified in Attachment 1, criterion 1.1, the only Cyber Assets that must be considered are those shared Cyber Assets that could, within 15 minutes, adversely impact the reliable operation of any combination of units that in aggregate equal or exceed Attachment 1, criterion 1.1. For the purpose of Standard CIP-002-4, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: • The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, • The Cyber Asset uses a routable protocol within a control center; or, • The Cyber Asset is dial-up accessible. |  | 2013-03-21 | High | N/A | N/A | The Responsible Entity has developed a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 but the list has not been reviewed and updated annually as required. | The Responsible Entity did not develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset list as per requirement R2 even if such list is null. OR A Cyber Asset essential to the operation of the Critical Asset was identified that met at least one of the bulleted characteristics in this requirement but was not included in the Critical Cyber Asset List. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-4a | R3. | Annual Approval — The senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1 and R2 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | 2013-03-21 | Low | N/A | N/A | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of the list of Critical Assets. OR The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of the list of Critical Cyber Assets (even if such lists are null.) | The Responsible Entity does not have a signed and dated record of the senior manager or delegate(s)’s annual approval of both the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-002-5 | R1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3:[See Standard for sub-req's] i.Control Centers and backup Control Centers; ii.Transmission stations and substations; iii.Generation resources; iv.Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v.Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi.For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  | 2014-02-03 | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002-5 | R2. | The Responsible Entity shall: [See Standard for sub-req's] |  | 2014-02-03 | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) or The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002-5.1 | R1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3:[See Standard for sub-req's] i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. | 2016-07-01 | 2016-12-26 | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. |  | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002-5.1 | R2. | The Responsible Entity shall: [See Standard for sub-req's] | 2016-07-01 | 2016-12-26 | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) or The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) or The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) |  | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-002-5.1a | R1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. | 2016-12-27 |  | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than five percent but less than or equal to 10 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than two, but fewer than or equal to four BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 10 percent but less than or equal to 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than four, but fewer than or equal to six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, more than 15 percent of BES assets have not been considered, according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, more than six BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. |  | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-002-5.1a | R2. | The Responsible Entity shall: | 2016-12-27 |  | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) OR The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) |  | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002-6 | R1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: i. Control Centers and backup Control Centers; ii. Transmission stations and substations; iii. Generation resources; iv. Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v. Remedial Action Schemes that support the reliable operation of the Bulk Electric System; and vi. For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. |  | 2021-02-04 | High | For Responsible Entities with more than a total of 40 BES assets in Requirement R1, five percent or fewer BES assets have not been considered according to Requirement R1; OR For Responsible Entities with a total of 40 or fewer BES assets, 2 or fewer BES assets in Requirement R1, have not been considered according to Requirement R1; OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, five percent or fewer high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, five or fewer high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact and BES Cyber Systems, more than five but less than or equal to 10 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than five percent but less than or equal to 10 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than five but less than or equal to 10 high or medium BES Cyber Systems have not been identified. | For Responsible Entities with more than a total of 100 high or medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high or medium impact and BES Cyber Assets, more than 10 but less than or equal to 15 identified BES Cyber Assets have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 10 percent but less than or equal to 15 percent high or medium BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 10 but less than or equal to 15 high or medium BES Cyber Systems have not been identified. | Systems, more than 15 percent of identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 identified BES Cyber Systems have not been categorized or have been incorrectly categorized at a lower category. OR For Responsible Entities with more than a total of 100 high and medium impact BES Cyber Systems, more than 15 percent of high or medium impact BES Cyber Systems have not been identified; OR For Responsible Entities with a total of 100 or fewer high and medium impact BES Cyber Systems, more than 15 high or medium impact BES Cyber Systems have not been identified. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-002-6 | R2. | Each Responsible Entity shall: |  | 2021-02-04 | Low | The Responsible Entity did not complete its review and update for the identification required for R1 within 15 calendar months but less than or equal to 16 calendar months of the previous review. (R2.1) OR The Responsible Entity did not complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 15 calendar months but less than or equal to 16 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 16 calendar months but less than or equal to 17 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 16 calendar months but less than or equal to 17 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 17 calendar months but less than or equal to 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 17 calendar months but less than or equal to 18 calendar months of the previous approval. (R2.2) | The Responsible Entity did not complete its review and update for the identification required for R1 within 18 calendar months of the previous review. (R2.1) OR The Responsible Entity failed to complete its approval of the identifications required by R1 by the CIP Senior Manager or delegate according to Requirement R2 within 18 calendar months of the previous approval. (R2.2) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003-1 | R1. | Cyber Security Policy - The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-1 | R2. | Leadership - The Responsible Entity shall assign a senior manager with overall responsibility for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009 | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-1 | R3. | Exceptions - Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-1 | R4. | Information Protection - The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. | 2008-07-01 | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-1 | R5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-1 | R6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendorrelated changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-2 | R1. | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-2 | R2. | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-2 through CIP-009-2. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-2 | R3. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-2 | R4. | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. | 2010-04-01 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-2 | R5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-2 | R6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-3 | R1. | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: | 2010-10-01 | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-3 | R2. | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. | 2010-10-01 | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-3 | R3. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-3 | R4. | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. | 2010-10-01 | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-3 | R5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-3 | R6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-3a | R1. | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-3a | R2. | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. |  | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-3a | R3. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-3a | R4. | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-3a | R5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-3a | R6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-4 | R1. | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: | 2014-10-01 | 2014-02-03 | Medium | N/A | N/A | The Responsible Entity has documented but not implemented a cyber security policy. | The Responsible Entity has not documented or implemented a cyber security policy. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-4 | R2. | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-4 through CIP-009-4. | 2014-10-01 | 2014-02-03 | Low | N/A | N/A | N/A | The Responsible Entity has not assigned a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009-4. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-4 | R3. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). | 2014-10-01 | 2014-01-21 | Low | N/A | N/A | In Instances where the Responsible Entity cannot conform to its cyber security policy, in R1, exceptions were documented, but were not authorized by the senior manager or delegate(s). | In Instances where the Responsible Entity cannot conform to its cyber security policy, in R1, exceptions were not documented, and were not authorized by the senior manager or delegate(s). |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-4 | R4. | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. | 2014-10-01 | 2014-02-03 | Medium | N/A | The Responsible Entity implemented but did not document a program to identify, classify, and protect information associated with Critical Cyber Assets. | The Responsible Entity documented but did not implement a program to identify, classify, and protect information associated with Critical Cyber Assets. | The Responsible Entity did not implement or did not document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-4 | R5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. | 2014-10-01 | 2014-02-03 | Low | N/A | The Responsible Entity implemented but did not document a program for managing access to protected Critical Cyber Asset information. | The Responsible Entity documented but did not implement a program for managing access to protected Critical Cyber Asset information. | The Responsible Entity did not implement or did not document a program for managing access to protected Critical Cyber Asset information. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-4 | R6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. | 2014-10-01 | 2014-02-03 | Low | The Responsible Entity has established but not documented a change control process OR The Responsible Entity has established but not documented a configuration management process. | The Responsible Entity has established but not documented both a change control process and configuration management process | The Responsible Entity has not established and documented a change control process OR The Responsible Entity has not established and documented a configuration management process. | The Responsible Entity has not established and documented a change control process AND The Responsible Entity has not established and documented a configuration management process. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-4a | R1. | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: |  | 2014-02-03 | Medium | N/A | N/A | The Responsible Entity has documented but not implemented a cyber security policy. | The Responsible Entity has not documented or implemented a cyber security policy. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-4a | R2. | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-4 through CIP-009-4. |  | 2014-02-03 | Low | N/A | N/A | N/A | The Responsible Entity has not assigned a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009-4. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-4a | R3. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). |  | 2014-02-03 | Low | N/A | N/A | In Instances where the Responsible Entity cannot conform to its cyber security policy, in R1, exceptions were documented, but were not authorized by the senior manager or delegate(s). | In Instances where the Responsible Entity cannot conform to its cyber security policy, in R1, exceptions were not documented, and were not authorized by the senior manager or delegate(s). |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-4a | R4. | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | 2014-02-03 | Medium | N/A | The Responsible Entity implemented but did not document a program to identify, classify, and protect information associated with Critical Cyber Assets. | The Responsible Entity documented but did not implement a program to identify, classify, and protect information associated with Critical Cyber Assets. | The Responsible Entity did not implement or did not document a program to identify, classify, and protect information associated with Critical Cyber Assets. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-4a | R5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. |  | 2014-02-03 | Low | N/A | The Responsible Entity implemented but did not document a program for managing access to protected Critical Cyber Asset information | The Responsible Entity documented but did not implement a program for managing access to protected Critical Cyber Asset information. | The Responsible Entity did not implement or did not document a program for managing access to protected Critical Cyber Asset information. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-4a | R6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. |  | 2014-02-03 | Low | The Responsible Entity has established but not documented a change control process OR The Responsible Entity has established but not documented a configuration management process. | The Responsible Entity has established but not documented both a change control process and configuration management process. | The Responsible Entity has not established and documented a change control process OR The Responsible Entity has not established and documented a configuration management process. | The Responsible Entity has not established and documented a change control process AND The Responsible Entity has not established and documented a configuration management process. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-003-5 | R1. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems, shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: |  | 2016-06-30 | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1) or The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1) or The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate according to Requirement R1 within 18 calendar months of the previous approval. (R1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003-5 | R2. | Each Responsible Entity for its assets identified in CIP-002-5, Requirement R1, Part R1.3, shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented cyber security policies that collectively address the following topics, and review and obtain CIP Senior Manager approval for those policies at least once every 15 calendar months: | 2017-04-01 | 2016-06-30 | Low | The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only three of the topics as required by R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) or The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only three of the topics as required by R2 but did not identify, assess, or correct the deficiencies. OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R2) | The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only two of the topics as required by R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) or The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only two of the topics as required by R2 but did not identify, assess, or correct the deficiencies. or The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R2) | The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only one of the topics as required by R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) or The Responsible Entity documented and implemented one or more cyber security policies for assets with a low impact rating that address only one of the topics as required by R2 but did not identify, assess, or correct the deficiencies. or The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R2) | The Responsible Entity did not document or implement any cyber security policies for assets with a low impact rating that address the topics as required by R2. (R2) or The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by R2 within 18 calendar months of the previous review. (R2) or The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by R2 by the CIP Senior Manager according to Requirement R2 within 18 calendar months of the previous approval. (R2) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003-5 | R3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. |  | 2016-06-30 | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. or The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003-5 | R4. | The Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. |  | 2016-06-30 | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, has a process to delegate actions from the CIP Senior Manager, and has Identified deficiencies but did not assess or correct the deficiencies.(R4) or The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, has a process to delegate actions from the CIP Senior Manager, but did not identify, assess, or correct the deficiencies.(R4) or The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003-6 | R1. | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: | 2016-07-01 | 2019-12-31 | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1) The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager or delegate within 18 calendar months of the previous approval. (R1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003-6 | R2. | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. Note: An inventory, list, or discrete identification of low impact BES Cyber Systems or their BES Cyber Assets is not required. Lists of authorized users are not required. | 2016-07-01 | 2019-12-31 | Low | The Responsible Entity had one or more documented cyber security policies for assets with a low impact rating but failed to address one of the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R2) | The Responsible Entity had one or more documented cyber security policies for assets with a low impact rating but failed to address two of the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R2) | The Responsible Entity had one or more documented cyber security policies for assets with a low impact rating but failed to address three of the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R2) | The Responsible Entity did not have any documented cyber security policies for assets with a low impact rating that address the topics as required by Requirement R2. (R2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 within 18 calendar months of the previous review. (R2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for assets with a low impact rating as required by Requirement R2 by the CIP Senior Manager within 18 calendar months of the previous approval. (R2) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003-6 | R3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. | 2016-07-01 | 2019-12-31 | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003-6 | R4. | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. | 2016-07-01 | 2019-12-31 | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003-7 | R1. | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: | 2020-01-01 | 2020-03-31 | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address one of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address two of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address three of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address four or more of the six topics required by R1. (R1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003-7 | R2. | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. | 2020-01-01 | 2020-03-31 | Low | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity implemented electronic access controls but failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets, but failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls but failed to implement authentication for all Dial-up Connectivity that provides access to low impact BES Cyber System(s), per Cyber Asset capability according to Requirement R2, Attachment 1, Section 3.2 (R2) OR The Responsible Entity documented one or more incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented the physical access controls for its assets containing low impact BES Cyber Systems, but failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls for its assets containing low impact BES Cyber Systems, but failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident, but failed to notify the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a low impact BES Cyber System according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) for its assets containing low impact BES Cyber Systems according to Requirement R2, Attachment 1. (R2) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003-7 | R3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. | 2020-01-01 | 2020-03-31 | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-003-7 | R4. | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. | 2020-01-01 | 2020-03-31 | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003-8 | R1. | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: | 2020-04-01 | 2026-03-31 | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1.) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address one of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address two of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address three of the six topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems, but did not address four or more of the six topics required by R1. (R1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP-002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003-8 | R2. | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. | 2020-04-01 | 2026-03-31 | Low | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity implemented electronic access controls but failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets, but failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls but failed to implement authentication for all Dial-up Connectivity that provides access to low impact BES Cyber System(s), per Cyber Asset capability according to Requirement R2, Attachment 1, Section 3.2 (R2) OR The Responsible Entity documented one or more incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity documented the physical access controls for its assets containing low impact BES Cyber Systems, but failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls for its assets containing low impact BES Cyber Systems, but failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident, but failed to notify the Electricity Information Sharing and Analysis Center (E-ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a low impact BES Cyber System according to Requirement R2, Attachment 1, Section 5.3. (R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) for its assets containing low impact BES Cyber Systems according to Requirement R2, Attachment 1. (R2) |  | BA | DP | DP-UFLS |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003-8 | R3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. | 2020-04-01 | 2026-03-31 | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-003-8 | R4. | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. | 2020-04-01 | 2026-03-31 | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003-9 | R1. | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: | 2026-04-01 |  | Medium | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address one of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems, but did not address one of the seven topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by Requirement R1 within 15 calendar months but did complete this review in less than or equal to 16 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 15 calendar months but did complete this approval in less than or equal to 16 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address two of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems, but did not address two of the seven topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by Requirement R1 within 16 calendar months but did complete this review in less than or equal to 17 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 16 calendar months but did complete this approval in less than or equal to 17 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address three of the nine topics required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems, but did not address three of the seven topics required by R1. (R1.2) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by R1 within 17 calendar months but did complete this review in less than or equal to 18 calendar months of the previous review. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 17 calendar months but did complete this approval in less than or equal to 18 calendar months of the previous approval. (R1.2) | The Responsible Entity documented and implemented one or more cyber security policies for its high impact and medium impact BES Cyber Systems, but did not address four or more of the nine topics required by R1. (R1.1) OR The Responsible Entity did not have any documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1. (R1.1) OR The Responsible Entity did not complete its review of the one or more documented cyber security policies as required by R1 within 18 calendar months of the previous review. (R1) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its high impact and medium impact BES Cyber Systems as required by R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.1) OR The Responsible Entity documented one or more cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems, but did not address four or more of the seven topics required by R1. (R1.2) OR The Responsible Entity did not have any documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by R1. (R1.2) OR The Responsible Entity did not complete its approval of the one or more documented cyber security policies for its assets identified in CIP‐002 containing low impact BES Cyber Systems as required by Requirement R1 by the CIP Senior Manager within 18 calendar months of the previous approval. (R1.2) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003-9 | R2. | Each Responsible Entity with at least one asset identified in CIP‐002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. Note: An inventory, list, or discrete identification of low impact BES Cyber Systems or their BES Cyber Assets is not required. Lists of authorized users are not required. | 2026-04-01 |  | Low | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document cyber security awareness according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity implemented electronic access controls but failed to document its cyber security plan(s) for electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document one or more Cyber Security Incident response plan(s) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to update each Cyber Security Incident response plan(s) within 180 days according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets, but failed to document the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) OR The Responsible Entity implemented vendor electronic remote access security controls but failed to document its cyber security process for vendor electronic remote access security controls according to Requirement R2, Attachment 1, Section 6. (R2) | The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to reinforce cyber security practices at least once every 15 calendar months according to Requirement R2, Attachment 1, Section 1. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document electronic access controls according to Requirement R2, Attachment 1, Section 3. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls but failed to implement authentication for all Dial‐up Connectivity that provides access to low impact BES Cyber System(s), per Cyber Asset capability according to Requirement R2, Attachment 1, Section 3.2 (R2) OR The Responsible Entity documented one or more incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to include the process for identification, classification, and response to Cyber Security Incidents according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to document the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E‐ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Sections 5.1 and 5.3. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media section(s) according to Requirement R2, Attachment 1, Section 5.3. (R2) OR The Responsible Entity documented its cyber security process for vendor electronic remote access security controls, but failed to implement vendor electronic remote access security controls according to Requirement R2, Attachment 1, Section 6. (R2) | The Responsible Entity documented the physical access controls for its assets containing low impact BES Cyber Systems, but failed to implement the physical security controls according to Requirement R2, Attachment 1, Section 2. (R2) OR The Responsible Entity documented its cyber security plan(s) for electronic access controls for its assets containing low impact BES Cyber Systems, but failed to permit only necessary inbound and outbound electronic access controls according to Requirement R2, Attachment 1, Section 3.1. (R2) OR The Responsible Entity documented one or more Cyber Security Incident response plan(s) within its cyber security plan(s) for its assets containing low impact BES Cyber Systems, but failed to test each Cyber Security Incident response plan(s) at least once every 36 calendar months according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented the determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident, but failed to notify the Electricity Information Sharing and Analysis Center (E‐ISAC) according to Requirement R2, Attachment 1, Section 4. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by the Responsible Entity according to Requirement R2, Attachment 1, Section 5.1. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to Requirement R2, Attachment 1, Section 5.2. (R2) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation for the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a low impact BES Cyber System according to Requirement R2, Attachment 1, Section 5.3. (R2) OR The Responsible Entity failed to document and implement its cyber security process for vendor electronic remote access security controls according to Requirement R2, Attachment 1, Section 6. (R2) | The Responsible Entity failed to document and implement one or more cyber security plan(s) for its assets containing low impact BES Cyber Systems according to Requirement R2, Attachment 1. (R2) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003-9 | R3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. | 2026-04-01 |  | Medium | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 30 calendar days but did document this change in less than 40 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 40 calendar days but did document this change in less than 50 calendar days of the change. (R3) | The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 50 calendar days but did document this change in less than 60 calendar days of the change. (R3) | The Responsible Entity has not identified, by name, a CIP Senior Manager. OR The Responsible Entity has identified by name a CIP Senior Manager, but did not document changes to the CIP Senior Manager within 60 calendar days of the change. (R3) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | CIP | CIP-003-9 | R4. | he Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. | 2026-04-01 |  | Low | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 30 calendar days but did document this change in less than 40 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 40 calendar days but did document this change in less than 50 calendar days of the change. (R4) | The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 50 calendar days but did document this change in less than 60 calendar days of the change. (R4) | The Responsible Entity has used delegated authority for actions where allowed by the CIP Standards, but does not have a process to delegate actions from the CIP Senior Manager. (R4) OR The Responsible Entity has identified a delegate by name, title, date of delegation, and specific actions delegated, but did not document changes to the delegate within 60 calendar days of the change. (R4) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004-1 | R1. | Awareness — The Responsible Entity shall establish, maintain, and document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: Direct communications (e.g., emails, memos, computer based training, etc.); Indirect communications (e.g., posters, intranet, brochures, etc.); Management support and reinforcement (e.g., presentations, meetings, etc.). | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-1 | R2. | Training — The Responsible Entity shall establish, maintain, and document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and review the program annually and update as necessary. | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-1 | R3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access. A personnel risk assessment shall be conducted pursuant to that program within thirty days of such personnel being granted such access. Such program shall at a minimum include: | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-1 | R4. | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-2 | R1. | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: Direct communications (e.g. emails, memos, computer based training, etc.); Indirect communications (e.g. posters, intranet, brochures, etc.); Management support and reinforcement (e.g., presentations, meetings, etc.). | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-2 | R2. | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-2 | R3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-2 | R4. | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-3 | R1. | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). | 2010-10-01 | 2012-12-11 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-3 | R2. | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. | 2010-10-01 | 2012-12-11 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-3 | R3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: | 2010-10-01 | 2012-12-11 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-3 | R4. | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. | 2010-10-01 | 2012-12-11 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-3a | R1. | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). | 2012-12-12 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-3a | R2. | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. | 2012-12-12 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-3a | R3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: | 2012-12-12 | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-3a | R4. | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. | 2012-12-12 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-4 | R1. | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). |  | 2012-12-11 | Low | The Responsible Entity established, implemented, and maintained but did not document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive ongoing reinforcement in sound security practices. | The Responsibility Entity did not provide security awareness reinforcement on at least a quarterly basis. | The Responsible Entity did document but did not establish, implement, nor maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. | The Responsible Entity did not establish, implement, maintain, nor document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-4 | R2. | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. |  | 2012-12-11 | Low | The Responsible Entity established, implemented, and maintained but did not document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. | The Responsibility Entity did not review the training program on an annual basis. | The Responsible Entity did document but did not establish, implement, nor maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. | The Responsible Entity did not establish, implement, maintain, or document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-4 | R3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: |  | 2012-12-11 | Medium | N/A | The Responsible Entity has a personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access, but the program is not documented. | The Responsible Entity has a personnel risk assessment program as stated in R3, but conducted the personnel risk assessment pursuant to that program after such personnel were granted such access except in specified circumstances such as an emergency. | The Responsible Entity does not have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access. OR The Responsible Entity did not conduct the personnel risk assessment pursuant to that program for personnel granted such access except in specified circumstances such as an emergency. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-4 | R4. | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. |  | 2012-12-11 | Low | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing at least one individual but less than 5% of the authorized personnel. | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing 5% or more but less than 10% of the authorized personnel. | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing 10% or more but less than 15%of the authorized personnel. | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing 15% or more of the authorized personnel. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-4a | R1. | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). | 2014-10-01 | 2014-02-03 | Low | The Responsible Entity established, implemented, and maintained but did not document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive ongoing reinforcement in sound security practices. | The Responsibility Entity did not provide security awareness reinforcement on at least a quarterly basis. | The Responsible Entity did document but did not establish, implement, nor maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. | The Responsible Entity did not establish, implement, maintain, nor document a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-4a | R2. | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. | 2014-10-01 | 2014-02-03 | Low | The Responsible Entity established, implemented, and maintained but did not document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. | The Responsibility Entity did not review the training program on an annual basis. | The Responsible Entity did document but did not establish, implement, nor maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. | The Responsible Entity did not establish, implement, maintain, or document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-4a | R3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: | 2014-10-01 | 2014-02-03 | Medium | N/A | The Responsible Entity has a personnel risk assessment program, as stated in R3, for personnel having authorized cyber or authorized unescorted physical access, but the program is not documented. | The Responsible Entity has a personnel risk assessment program as stated in R3, but conducted the personnel risk assessment pursuant to that program after such personnel were granted such access except in specified circumstances such as an emergency. | The Responsible Entity does not have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access. OR The Responsible Entity did not conduct the personnel risk assessment pursuant to that program for personnel granted such access except in specified circumstances such as an emergency |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-4a | R4. | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. | 2014-10-01 | 2014-02-03 | Low | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing at least one individual but less than 5% of the authorized personnel. | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing 5% or more but less than 10% of the authorized personnel. | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing 10% or more but less than 15%of the authorized personnel. | The Responsible Entity did not maintain complete list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets, missing 15% or more of the authorized personnel. |  | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-004-5 | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-5 Table R1 – Security Awareness Program. |  | 2013-09-30 | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) or The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004-5 | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-5 Table R2 – Cyber Security Training Program. |  | 2013-09-30 | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) or The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004-5 | R3. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented personnel risk assessment programs to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-5 Table R3 – Personnel Risk Assessment Program. |  | 2013-09-30 | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) or The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date and has identified deficiencies, and did not identify, assess, and correct the deficiencies. (3.5) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004-5 | R4. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access management programs that collectively include each of the applicable requirement parts in CIP-004-5 Table R4 – Access Management Program. |  | 2013-09-30 | Low | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter, and did not identify, assess and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies.(4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System Information storage location, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for two BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for two BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for three BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for three BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not implement any documented program(s) for access management. (R4) or The Responsible Entity has implemented one or more documented program(s) for access management that includes a process to authorize electronic access, unescorted physical access, or access to the designated storage locations where BES Cyber System Information is located, and did not identify, assess, and correct the deficiencies. (4.1) or The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004-5 | R5. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access revocation programs that collectively include each of the applicable requirement parts in CIP-004-5 Table R5 – Access Revocation. |  | 2013-09-30 | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for one individual, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances, and did not identify, assess, and correct the deficiencies. (5.5) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for two individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for three or more individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access, unescorted physical access, or BES Cyber System Information storage locations. (R5) or The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004-5.1 | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-5 Table R1 – Security Awareness Program. |  | 2016-06-30 | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) or The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004-5.1 | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-5 Table R2 – Cyber Security Training Program. |  | 2016-06-30 | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) or The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9, and did not identify, assess and correct the deficiencies. (2.1) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access, and did not identify, assess and correct the deficiencies. (2.2) or The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date, and did not identify, assess and correct the deficiencies. (2.3) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004-5.1 | R3. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented personnel risk assessment programs to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program. |  | 2016-06-30 | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date, and did not identify, assess, and correct the deficiencies. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) or The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals, and did not identify, assess, and correct the deficiencies. (R3) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.1 & 3.4) or The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.2 & 3.4) or The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals, and did not identify, assess, and correct the deficiencies. (3.3 & 3.4) or The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date and has identified deficiencies, and did not identify, assess, and correct the deficiencies. (3.5) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004-5.1 | R4. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access management programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program. |  | 2016-06-30 | Medium | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter, and did not identify, assess and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies.(4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System Information storage location, privileges were incorrect or unnecessary, and did not identify, assess and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for two BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for two BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for three BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for three BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) | The Responsible Entity did not implement any documented program(s) for access management. (R4) or The Responsible Entity has implemented one or more documented program(s) for access management that includes a process to authorize electronic access, unescorted physical access, or access to the designated storage locations where BES Cyber System Information is located, and did not identify, assess, and correct the deficiencies. (4.1) or The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters, and did not identify, assess, and correct the deficiencies. (4.2) or The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber Systems, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.3) or The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber System Information storage locations, privileges were incorrect or unnecessary, and did not identify, assess, and correct the deficiencies. (4.4) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004-5.1 | R5. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access revocation programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation. |  | 2016-06-30 | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for one individual, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals, and did not identify, assess, and correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances, and did not identify, assess, and correct the deficiencies. (5.5) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for two individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for three or more individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action, and did not identify, assess, and correct the deficiencies. (5.3) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access, unescorted physical access, or BES Cyber System Information storage locations. (R5) or The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals, and did not identify, assess, and correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date, and did not identify, assess, and correct the deficiencies. (5.2) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004-6 | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program. | 2016-07-01 | 2023-12-31 | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) OR The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004-6 | R2. | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program. | 2016-07-01 | 2023-12-31 | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) OR The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004-6 | R3. | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program. | 2016-07-01 | 2023-12-31 | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5 | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) OR The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004-6 | R4. | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program. | 2016-07-01 | 2023-12-31 | Medium | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for one BES Cyber System Information storage location, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for two BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for more than 5% but less than (or equal to) 10% of its BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for three BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for three BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) | The Responsible Entity did not implement any documented program(s) for access management. (R4) OR The Responsible Entity has implemented one or more documented program(s) for access management that includes a process to authorize electronic access, unescorted physical access, or access to the designated storage locations where BES Cyber System Information is located. (4.1) OR The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) OR The Responsible Entity has implemented processes to verify that access to the designated storage locations for BES Cyber System Information is correct and necessary within 15 calendar months of the previous verification but for four or more BES Cyber System Information storage locations, privileges were incorrect or unnecessary. (4.4) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-004-6 | R5. | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation. | 2016-07-01 | 2023-12-31 | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals. (5.4) OR The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals. (5.5) OR The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances. (5.5) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for two individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action. (5.3) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) OR The Responsible Entity has implemented one or more process(es) to revoke the individual’s access to the designated storage locations for BES Cyber System Information but, for three or more individuals, did not do so by the end of the next calendar day following the effective date and time of the termination action. (5.3) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access, unescorted physical access, or BES Cyber System Information storage locations. (R5) OR The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004-7 | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-7 Table R1 – Security Awareness Program. | 2024-01-01 |  | Low | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so between 10 and 30 calendar days after the start of a subsequent calendar quarter. (1.1) | The Responsible Entity did not reinforce cyber security practices during a calendar quarter but did so within the subsequent quarter but beyond 30 calendar days after the start of that calendar quarter. (1.1) | The Responsible Entity did not document or implement any security awareness process(es) to reinforce cyber security practices. (R1) OR The Responsible Entity did not reinforce cyber security practices and associated physical security practices for at least two consecutive calendar quarters. (1.1) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004-7 | R2. | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-7 Table R2 – Cyber Security Training Program. | 2024-01-01 |  | Low | The Responsible Entity implemented a cyber security training program but failed to include one of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train one individual (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train one individual with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include two of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train two individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity implemented a cyber security training program but failed to include three of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train three individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) | The Responsible Entity did not implement a cyber security training program appropriate to individual roles, functions, or responsibilities. (R2) OR The Responsible Entity implemented a cyber security training program but failed to include four or more of the training content topics in Requirement Parts 2.1.1 through 2.1.9. (2.1) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals (with the exception of CIP Exceptional Circumstances) prior to their being granted authorized electronic and authorized unescorted physical access. (2.2) OR The Responsible Entity implemented a cyber security training program but failed to train four or more individuals with authorized electronic or authorized unescorted physical access within 15 calendar months of the previous training completion date. (2.3) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004-7 | R3. | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-7 Table R3 – Personnel Risk Assessment Program. | 2024-01-01 |  | Medium | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for one individual. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for one individual. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for one individual. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for one individual. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for one individual with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for two individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for two individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for two individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for two individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for two individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for three individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for three individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for three individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for three individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for three individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) | The Responsible Entity did not have all of the required elements as described by 3.1 through 3.4 included within documented program(s) for implementing Personnel Risk Assessments (PRAs), for individuals, including contractors and service vendors, for obtaining and retaining authorized cyber or authorized unescorted physical access. (R3) OR The Responsible Entity has a program for conducting Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, but did not conduct the PRA as a condition of granting authorized electronic or authorized unescorted physical access for four or more individuals. (R3) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not confirm identity for four or more individuals. (3.1 & 3.4) OR The Responsible Entity has a process to perform seven-year criminal history record checks for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not include the required checks described in 3.2.1 and 3.2.2 for four or more individuals. (3.2 & 3.4) OR The Responsible Entity did conduct Personnel Risk Assessments (PRAs) for individuals, including contractors and service vendors, with authorized electronic or authorized unescorted physical access but did not evaluate criminal history records check for access authorization for four or more individuals. (3.3 & 3.4) OR The Responsible Entity did not conduct Personnel Risk Assessments (PRAs) for four or more individuals with authorized electronic or authorized unescorted physical access within 7 calendar years of the previous PRA completion date. (3.5) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004-7 | R4. | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-7 Table R4 – Access Management Program. | 2024-01-01 |  | Medium | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so less than 10 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for 5% or less of its BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 10 and 20 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for more than 5% but less than (or equal to) 10% of its BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) | The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records during a calendar quarter but did so between 20 and 30 calendar days after the start of a subsequent calendar quarter. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for more than 10% but less than (or equal to) 15% of its BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) | The Responsible Entity did not implement any documented program(s) for access management. (R4) OR The Responsible Entity did not implement one or more documented program(s) for access management that includes a process to authorize electronic access or unescorted physical access. (4.1) OR The Responsible Entity did not verify that individuals with active electronic or active unescorted physical access have authorization records for at least two consecutive calendar quarters. (4.2) OR The Responsible Entity has implemented processes to verify that user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and necessary within 15 calendar months of the previous verification but for more than 15% of its BES Cyber Systems, privileges were incorrect or unnecessary. (4.3) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004-7 | R5. | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-7 Table R5 – Access Revocation. | 2024-01-01 |  | Medium | The Responsible Entity has implemented one or more process(es) to revoke the individual’s user accounts upon termination action but did not do so for within 30 calendar days of the date of termination action for one or more individuals. (5.3) OR The Responsible Entity has implemented one or more process(es) to change passwords for shared accounts known to the user upon termination action, reassignment, or transfer, but did not do so for within 30 calendar days of the date of termination action, reassignment, or transfer for one or more individuals. (5.4) OR The Responsible Entity has implemented one or more process(es) to determine and document extenuating operating circumstances following a termination action, reassignment, or transfer, but did not change one or more passwords for shared accounts known to the user within 10 calendar days following the end of the extenuating operating circumstances. (5.4) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for one individual. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for one individual, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) | The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for two individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for two individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) | The Responsible Entity has not implemented any documented program(s) for access revocation for electronic access or unescorted physical access. (R5) OR The Responsible Entity has implemented one or more process(es) to remove the ability for unescorted physical access and Interactive Remote Access upon a termination action or complete the removal within 24 hours of the termination action but did not initiate those removals for three or more individuals. (5.1) OR The Responsible Entity has implemented one or more process(es) to determine that an individual no longer requires retention of access following reassignments or transfers but, for three or more individuals, did not revoke the authorized electronic access to individual accounts and authorized unescorted physical access by the end of the next calendar day following the predetermined date. (5.2) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-004-7 | R6. | Each Responsible Entity shall implement one or more documented access management program(s) to authorize, verify, and revoke provisioned access to BCSI pertaining to the “Applicable Systems” identified in CIP-004-7 Table R6 – Access Management for BES Cyber System Information that collectively include each of the applicable requirement parts in CIP‐004‐X Table R6 – Access Management for BES Cyber System Information. To be considered access to BCSI in the context of this requirement, an individual has both the ability to obtain and use BCSI. Provisioned access is to be considered the result of the specific actions taken to provide an individual(s) the means to access BCSI (e.g., may include physical keys or access cards, user accounts and associated rights and privileges, encryption keys). | 2024-01-01 |  | Medium | The Responsible Entity has implemented one or more program(s) as required by Requirement R6 Part 6.1 but, for one individual, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (6.1) OR The Responsible Entity performed the verification required by Requirement R6 Part 6.2 more than 15 calendar months but less than or equal to 16 calendar months of the previous verification. (6.2) OR The Responsible Entity has implemented one or more program(s) to remove the individual’s ability to use provisioned access to BCSI but, for one individual, did not do so by the timeframe required in Requirement R6, Part 6.3. | The Responsible Entity has implemented one or more program(s) as required by Requirement R6 Part 6.1 but, for two individuals, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (6.1) OR The Responsible Entity performed the verification required by Requirement R6 Part 6.2 more than 16 calendar months but less than or equal to 17 calendar months of the previous verification. (6.2) OR The Responsible Entity has implemented one or more program(s) to remove the individual’s ability to use provisioned access to BCSI but, for two individuals, did not do so by the timeframe required in Requirement R6, Part 6.3. | The Responsible Entity has implemented one or more program(s) as required by Requirement R6 Part 6.1 but, for three individuals, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (6.1) OR The Responsible Entity performed the verification required by Requirement R6 Part 6.2 more than 17 calendar months but less than or equal to 18 calendar months of the previous verification. (6.2) OR The Responsible Entity has implemented one or more program(s) to remove the individual’s ability to use provisioned access to BCSI but, for three individuals, did not do so by the timeframe required in Requirement R6, Part 6.3. | The Responsible Entity did not implement one or more documented access management program(s) for BCSI. (R6) OR The Responsible Entity has implemented one or more program(s) as required by Requirement R6 Part 6.1 but, for four or more individuals, did not authorize provisioned electronic access to electronic BCSI or provisioned physical access to physical BCSI. (6.1) OR The Responsible Entity performed the verification required by Requirement R6 Part 6.2 more than 18 calendar months of the previous verification. (6.2) OR The Responsible Entity has implemented one or more program(s) to remove the individual’s ability to use provisioned access to BCSI but, for four or more individuals, did not do so by the timeframe required in Requirement R6, Part 6.3. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005-1 | R1. | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | 2008-07-01 | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-1 | R2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | 2008-07-01 | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-1 | R3. | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. | 2008-07-01 | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-1 | R4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: | 2008-07-01 | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-1 | R5. | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005. | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-1a | R1. | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | 2011-02-01 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-1a | R2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | 2011-02-01 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-1a | R3. | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | 2011-02-01 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-1a | R4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | 2011-02-01 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-1a | R5. | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005. |  | 2011-02-01 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-2 | R1. | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | 2010-04-01 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-2 | R2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | 2010-04-01 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-2 | R3. | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. | 2010-04-01 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-2 | R4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: | 2010-04-01 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-2 | R5. | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-2. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-2a | R1. | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | 2011-02-01 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-2a | R2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | 2011-02-01 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-2a | R3. | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. |  | 2011-02-01 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-2a | R4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | 2011-02-01 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-2a | R5. | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-2. |  | 2011-02-01 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-3 | R1. | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | 2010-10-01 | 2011-02-01 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-3 | R2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | 2010-10-01 | 2011-02-01 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-3 | R3. | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. | 2010-10-01 | 2011-02-01 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-3 | R4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: | 2010-10-01 | 2011-02-01 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-3 | R5. | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. | 2010-10-01 | 2011-02-01 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-3a | R1. | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | 2011-02-02 | 2016-06-30 | Medium | N/A | N/A | N/A | The Responsible Entity did not ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. OR The Responsible Entity did not identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-3a | R2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | 2011-02-02 | 2016-06-30 | Medium | N/A | N/A | N/A | The Responsible Entity did not implement or did not document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-3a | R3. | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. | 2011-02-02 | 2016-06-30 | Medium | N/A | N/A | N/A | The Responsible Entity did not implement or did not document electronic or manual processes monitoring and logging access points. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-3a | R4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: | 2011-02-02 | 2016-06-30 | Medium | N/A | N/A | N/A | The Responsible Entity did not perform a Vulnerability Assessment at least annually for one or more of the access points to the Electronic Security Perimeter(s). ORThe vulnerability assessment did not include one (1) or more of the subrequirements R4.1, R4.2, R4.3, R4.4, R4.5. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-3a | R5. | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. | 2011-02-02 | 2016-06-30 | Low | The Responsible Entity did not review, update, and maintain greater than 5% but less than or equal to 10% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 5% but less than or equal to 10% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 10% but less than or equal to 15% of the documentation to support compliance with the requirements of Standard CIP-005. | The Responsible Entity did not review, update, and maintain greater than 15% of the documentation to support compliance with the requirements of Standard CIP-005. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-4a | R1. | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | 2014-10-01 | 2014-02-03 | Medium | The Responsible Entity did not document one or more access points to the Electronic Security Perimeter(s). | The Responsible Entity identified but did not document one or more Electronic Security Perimeter(s). | The Responsible Entity did not ensure that one or more of the Critical Cyber Assets resides within an Electronic Security Perimeter. OR The Responsible Entity did not identify nor document one or more Electronic Security Perimeter(s). | The Responsible Entity did not ensure that one or more Critical Cyber Assets resides within an Electronic Security Perimeter, and the Responsible Entity did not identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s) for all Critical Cyber Assets. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-4a | R2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | 2014-10-01 | 2014-02-03 | Medium | N/A | The Responsible Entity implemented but did not document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | The Responsible Entity documented but did not implement the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | The Responsible Entity did not implement nor document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-4a | R3. | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. | 2014-10-01 | 2014-02-03 | Medium | The Responsible Entity did not document the electronic or manual processes for monitoring and logging access to access points. OR The Responsible Entity did not implement electronic or manual processes monitoring and logging at less than 5% of the access points. | The Responsible Entity did not implement electronic or manual processes monitoring and logging at 5% or more but less than 10% of the access points. | The Responsible Entity did not implement electronic or manual processes monitoring and logging at 10% or more but less than 15 % of the access points. | The Responsible Entity did not implement electronic or manual processes monitoring and logging at 15% or more of the access points. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-4a | R4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: | 2014-10-01 | 2014-02-03 | Medium | The Responsible Entity did not perform a Vulnerability Assessment at least annually for less than 5% of access points to the Electronic Security Perimeter(s). | The Responsible Entity did not perform a Vulnerability Assessment at least annually for 5% or more but less than 10% of access points to the Electronic Security Perimeter(s). | The Responsible Entity did not perform a Vulnerability Assessment at least annually for 10% or more but less than 15% of access points to the Electronic Security Perimeter(s). | The Responsible Entity did not perform a Vulnerability Assessment at least annually for 15% or more of access points to the Electronic Security Perimeter(s). OR The vulnerability assessment did not include one (1) or more of the subrequirements R 4.1, R4.2, R4.3, R4.4, R4.5. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-4a | R5. | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-4. | 2014-10-01 | 2014-02-03 | Low | The Responsible Entity did not review, update, and maintain at least one but less than or equal to 5% of the documentation to support compliance with the requirements of Standard CIP-005-4. | The Responsible Entity did not review, update, and maintain greater than 5% but less than or equal to 10% of the documentation to support compliance with the requirements of Standard CIP-005-4. | The Responsible Entity did not review, update, and maintain greater than 10% but less than or equal to 15% of the documentation to support compliance with the requirements of Standard CIP-005-4. | The Responsible Entity did not review, update, and maintain greater than 15% of the documentation to support compliance with the requirements of Standard CIP-005-4. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-005-5 | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-5 Table R1 – Electronic Security Perimeter. | 2016-07-01 | 2020-06-30 | Medium | N/A | N/A | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-5 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1) OR External Routable Connectivity through the ESP was not through an identified EAP. (1.2) OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) OR The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005-5 | R2. | Each Responsible Entity allowing Interactive Remote Access to BES Cyber Systems shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-5 Table R2 – Interactive Remote Access Management. | 2016-07-01 | 2020-06-30 | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3. |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005-6 | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter. | 2020-07-01 | 2022-09-30 | Medium |  |  | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-6 Table R1 – Electronic Security Perimeter. (R1) OR The Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1) OR External Routable Connectivity through the ESP was not through an identified EAP. (1.2) OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) OR The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-005-6 | R2. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-6 Table R2 –Remote Access Management. | 2020-07-01 | 2022-09-30 | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have either: one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4); or one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4) and one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005-7 | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-7 Table R1 – Electronic Security Perimeter. | 2022-10-01 |  | Medium | NULL | NULL | The Responsible Entity did not have a method for detecting malicious communications for both inbound and outbound communications. (1.5) | The Responsible Entity did not document one or more processes for CIP-005-6 Table R1 – Electronic Security Perimeter. (R1) ORThe Responsible Entity did not have all applicable Cyber Assets connected to a network via a routable protocol within a defined Electronic Security Perimeter (ESP). (1.1)ORExternal Routable Connectivity through the ESP was not through an identified EAP. (1.2)OR The Responsible Entity did not require inbound and outbound access permissions and deny all other access by default. (1.3) The Responsible Entity did not perform authentication when establishing dial-up connectivity with the applicable Cyber Assets, where technically feasible. (1.4) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005-7 | R2. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-7 Table R2 –Remote Access Management. | 2022-10-01 |  | Medium | The Responsible Entity does not have documented processes for one or more of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for one of the applicable items for Requirement Parts 2.1 through 2.3. | The Responsible Entity did not implement processes for two of the applicable items for Requirement Parts 2.1 through 2.3;OR The Responsible Entity did not have either: one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4); or one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). | The Responsible Entity did not implement processes for three of the applicable items for Requirement Parts 2.1 through 2.3; OR The Responsible Entity did not have one or more method(s) for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access) (2.4) and one or more methods to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access) (2.5). |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-005-7 | R3. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts in CIP-005-7 Table R3 –Vendor Remote Access Management for EACMS and PACS. | 2022-10-01 |  | Medium | The Responsible Entity did not document one or more processes for CIP-005-7 Table R3 – Vendor Remote Access Management for EACMS and PACS. (R3) | The Responsible Entity had method(s) as required by Part 3.1 for EACMS but did not have a method to determine authenticated vendor-initiated remote connections for PACS (3.1).OR The Responsible Entity had method(s) as required by Part 3.2 for EACMS but did not have a method to terminate authenticated vendor-initiated remote connections for PACS (3.2). | The Responsible Entity did not implement processes for either Part 3.1 or Part 3.2. (R3) OR The Responsible Entity had method(s) as required by Part 3.1 for PACS but did not have a method to determine authenticated vendor-initiated remote connections for EACMS (3.1). OR The Responsible Entity had method(s) as required by Part 3.2 for PACS but did not have a method to terminate authenticated vendor-initiated remote connections or control the ability to reconnect for EACMS (3.2). | The Responsible Entity did not implement any processes for CIP-005-7 Table R3 – Vendor Remote Access Management for EACMS and PACS. (R3) OR The Responsible Entity did not have any methods as required by Parts 3.1 and 3.2 (R3). |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006-1 | R1. | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: | 2008-07-01 | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1 | R2. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: | 2008-07-01 | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1 | R3. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: | 2008-07-01 | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1 | R4. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1 | R5. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1 | R6. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: | 2008-07-01 | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1a | R1. | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  | 2009-12-22 | Medium | N/A | N/A | The Responsible Entity created a physical security plan but did not gain approval by a senior manager or delegate(s). OR The Responsible Entity created but did not maintain a physical security plan. | The Responsible Entity did not create and maintain a physical security plan. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1a | R2. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  | 2009-12-22 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1a | R3. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  | 2009-12-22 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1a | R4. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  | 2009-12-22 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1a | R5. | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | 2009-12-22 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1a | R6. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  | 2009-12-22 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1b | R1. | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  | 2009-12-22 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1b | R2. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  | 2009-12-22 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1b | R3. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  | 2009-12-22 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1b | R4. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  | 2009-12-22 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1b | R5. | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | 2009-12-22 | Low |  | . |  |  |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1b | R6. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  | 2009-12-22 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1c | R1. | Physical Security Plan — The Responsible Entity shall create and maintain a physical security plan, approved by a senior manager or delegate(s) that shall address, at a minimum, the following: |  | 2010-04-20 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1c | R2. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: |  | 2010-04-20 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1c | R3. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008. One or more of the following monitoring methods shall be used: |  | 2010-04-20 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1c | R4. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: |  | 2010-04-20 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1c | R5. | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | 2010-04-20 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-1c | R6. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly. The program must include, at a minimum, the following: |  | 2010-04-20 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2 | R1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: | 2010-04-01 | 2010-07-14 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2 | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: | 2010-04-01 | 2010-07-14 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2 | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. | 2010-04-01 | 2010-07-14 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2 | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | 2010-04-01 | 2010-07-14 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2 | R5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | 2010-04-01 | 2010-07-14 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2 | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | 2010-04-01 | 2010-07-14 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2 | R7. | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. | 2010-04-01 | 2010-07-14 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2 | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: | 2010-04-01 | 2010-07-14 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2a | R1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: | 2010-07-15 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2a | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: | 2010-07-15 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2a | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. | 2010-07-15 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2a | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | 2010-07-15 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2a | R5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | 2010-07-15 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2a | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | 2010-07-15 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2a | R7. | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. | 2010-07-15 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2a | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: | 2010-07-15 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2b | R1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | 2010-07-14 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2b | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | 2010-07-14 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2b | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | 2010-07-14 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2b | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | 2010-07-14 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2b | R5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | 2010-07-14 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2b | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | 2010-07-14 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2b | R7. | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | 2010-07-14 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2b | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | 2010-07-14 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2c | R1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2c | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2c | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2c | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: --Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. --Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. --Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. --Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2c | R5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-2. One or more of the following monitoring methods shall be used: --Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. --Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2c | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: --Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. --Video Recording: Electronic capture of video images of sufficient quality to determine identity. --Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2c | R7. | Access Log Retention — The responsible entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-2c | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3 | R1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | 2010-09-30 | [6 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3 | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | 2010-09-30 | [6 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3 | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | 2010-09-30 | [6 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3 | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | 2010-09-30 | [6 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3 | R5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | 2010-09-30 | [6 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3 | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | 2010-09-30 | [6 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3 | R7. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | 2010-09-30 | [6 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3 | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | 2010-09-30 | [6 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3a | R1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: | 2010-10-01 | 2011-05-18 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3a | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: | 2010-10-01 | 2011-05-18 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3a | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. | 2010-10-01 | 2011-05-18 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3a | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | 2010-10-01 | 2011-05-18 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3a | R5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | 2010-10-01 | 2011-05-18 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3a | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | 2010-10-01 | 2011-05-18 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3a | R7. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. | 2010-10-01 | 2011-05-18 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3a | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: | 2010-10-01 | 2011-05-18 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3c | R1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: | 2011-05-19 | 2016-06-30 | Medium | N/A | N/A | The Responsible Entity created a physical security plan but did not gain approval by a senior manager or delegate(s). OR The Responsible Entity created and implemented but did not maintain a physical security plan. | The Responsible Entity did not document, implement, and maintain a physical security plan. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3c | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: | 2011-05-19 | 2016-06-30 | Medium | N/A | N/A | N/A | A Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, was not protected from unauthorized physical access. Perimeter access point such as electronic lock control mechanisms and badge readers was not afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3a Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3c | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. | 2011-05-19 | 2016-06-30 | Medium | N/A | N/A | N/A | A Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) does not reside within an identified Physical Security Perimeter. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3c | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | 2011-05-19 | 2016-06-30 | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or has not implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3c | R5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | 2011-05-19 | 2016-06-30 | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or has not implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following monitoring methods: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. OR An unauthorized access attempt was not reviewed immediately and handled in accordance with CIP-008-3. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3c | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | 2011-05-19 | 2016-06-30 | Low | N/A | N/A | N/A | The Responsible Entity has not implemented or has not documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method, • Video Recording: Electronic capture of video images of sufficient quality to determine identity, or • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. OR The Responsible Entity has not recorded sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3c | R7. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. | 2011-05-19 | 2016-06-30 | Low | N/A | N/A |  | N/A |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3c | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: | 2011-05-19 | 2016-06-30 | Medium | N/A | N/A | N/A | The Responsible Entity has not implemented a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. OR The implemented program does not include one or more of the requirements; R8.1, R8.2, and R8.3. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3d | R1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | 2013-03-21 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3d | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | 2013-03-21 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3d | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | 2013-03-21 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3d | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | 2013-03-21 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3d | R5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | 2013-03-21 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3d | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | 2013-03-21 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3d | R7. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | 2013-03-21 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-3d | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | 2013-03-21 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4c | R1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: | 2014-10-01 | 2014-02-03 | Medium | N/A | N/A | The Responsible Entity created a physical security plan but did not gain approval by a senior manager or delegate(s). OR The Responsible Entity created and implemented but did not maintain a physical security plan. | The Responsible Entity did not document, implement, and maintain a physical security plan. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4c | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: | 2014-10-01 | 2014-02-03 | Medium | A Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers was provided with all but one (1) of the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP- 009-4. | A Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers was provided with all but two (2) of the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP009-4. | A Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers was provided with all but three (3) of the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP-009-4. | A Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, was not protected from unauthorized physical access. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4c | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. | 2014-10-01 | 2014-02-03 | Medium | N/A | N/A | N/A | A Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) does not reside within an identified Physical Security Perimeter. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4c | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | 2014-10-01 | 2014-02-03 | Medium | N/A | The Responsible Entity has implemented but not documented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “mantrap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | The Responsible Entity has documented but not implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | The Responsible Entity has not documented or has not implemented the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets.. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4c | R5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-4. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | 2014-10-01 | 2014-02-03 | Medium | N/A | The Responsible Entity has implemented but not documented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twentyfour hours a day, seven days a week using one or more of the following monitoring methods: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | The Responsible Entity has documented but not implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following monitoring methods: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | The Responsible Entity has not documented or has not implemented the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week using one or more of the following monitoring methods: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. OR An unauthorized access attempt was not reviewed immediately and handled in accordance with CIP-008-4. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4c | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | 2014-10-01 | 2014-02-03 | Low | The Responsible Entity has implemented but not documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method, • Video Recording: Electronic capture of video images of sufficient quality to determine identity, or • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4, and has provided logging that records sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. | The Responsible Entity has implemented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method, • Video Recording: Electronic capture of video images of sufficient quality to determine identity, or • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4, but has not provided logging that records sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week.. | The Responsible Entity has documented but not implemented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method, • Video Recording: Electronic capture of video images of sufficient quality to determine identity, or • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | The Responsible Entity has not implemented or has not documented the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method, • Video Recording: Electronic capture of video images of sufficient quality to determine identity, or • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4c | R7. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. | 2014-10-01 | 2014-02-03 | Low | The Responsible Entity retained physical access logs for 75 or more calendar days, but for less than 90 calendar days. | The Responsible Entity retained physical access logs for 60 or more calendar days, but for less than 75 calendar days | The Responsible Entity retained physical access logs for 45 or more calendar days, but for less than 60 calendar days. | The Responsible Entity retained physical access logs for less than 45 calendar days. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4c | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: | 2014-10-01 | 2014-02-03 | Medium | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly but the program does not include one of the Requirements R8.1, R8.2, and R8.3. | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly but the program does not include two of the Requirements R8.1, R8.2, and R8.3. | The Responsible Entity has implemented a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly but the program does not include any of the Requirements R8.1, R8.2, and R8.3. | The Responsible Entity has not implemented a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4d | R1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: |  | 2013-03-21 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4d | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: |  | 2013-03-21 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4d | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. |  | 2013-03-21 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4d | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | 2013-03-21 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4d | R5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-4. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. |  | 2013-03-21 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4d | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. |  | 2013-03-21 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4d | R7. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. |  | 2013-03-21 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-4d | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: |  | 2013-03-21 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-006-5 | R1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented physical security plans that collectively include all of the applicable requirement parts in CIP-006-5 Table R1 – Physical Security Plan. |  | 2016-06-30 | Medium | The Responsible Entity has a process to log authorized physical entry into any Physical Security Perimeter with sufficient information to identify the individual and date and time of entry and identified deficiencies but did not assess or correct the deficiencies. (1.8) OR The Responsible Entity has a process to log authorized physical entry into any Physical Security Perimeter with sufficient information to identify the individual and date and time of entry but did not identify, assess, or correct the deficiencies. (1.8) OR The Responsible Entity has a process to retain physical access logs for 90 calendar days and identified deficiencies but did not assess or correct the deficiencies. (1.9) OR The Responsible Entity has a process to retain physical access logs for 90 calendar days but did not identify, assess, or correct the deficiencies. (1.9) | The Responsible Entity has a process to alert for unauthorized physical access to Physical Access Control Systems and identified deficiencies but did not assess or correct the deficiencies. (1.7) OR The Responsible Entity has a process to alert for unauthorized physical access to Physical Access Control Systems but did not identify, assess, or correct the deficiencies. (1.7) OR The Responsible Entity has a process communicate alerts within 15 minutes to identified personnel and identified deficiencies but did not assess or correct the deficiencies. (1.7) OR The Responsible Entity has a process communicate alerts within 15 minutes to identified personnel but did not identify, assess, or correct the deficiencies. (1.7) | The Responsible Entity has a process to alert for detected unauthorized access through a physical access point into a Physical security Perimeter and identified deficiencies but did not assess or correct the deficiencies. (1.5) OR The Responsible Entity has a process to alert for detected unauthorized access through a physical access point into a Physical security Perimeter but did not identify, assess, or correct deficiencies. (1.5) OR The Responsible Entity has a process to communicate alerts within 15 minutes to identified personnel and identified deficiencies but did not assess or correct the deficiencies. (1.5) OR The Responsible Entity has a process to communicate alerts within 15 minutes to identified personnel but did not identify, assess, or correct the deficiencies. (1.5) OR The Responsible Entity has a process to monitor for unauthorized physical access to a Physical Access Control Systems and identified deficiencies but did not assess or correct the deficiencies. (1.6) OR The Responsible Entity has a process to monitor for unauthorized physical access to a Physical Access Control Systems but did not identify, assess, or correct the deficiencies. (1.6) | The Responsible Entity did not document or implement operational or procedural controls to restrict physical access. (1.1) OR The Responsible Entity documented and implemented operational or procedural controls to restrict physical access and identified deficiencies but did not assess or correct the deficiencies. (1.1) OR The Responsible Entity documented and implemented operational or procedural controls to restrict physical access but did not identify, assess, or correct the deficiencies. (1.1) OR The Responsible Entity has documented and implemented physical access controls, but at least one control does not exist to restrict access to Applicable Systems. (1.2) OR The Responsible Entity has documented and implemented physical access controls, restricts access to Applicable Systems using at least one control, and identified deficiencies, but did not assess or correct the deficiencies. (1.2) OR The Responsible Entity has documented and implemented physical access controls, restricts access to Applicable Systems using at least one control, but did not identify, assess, or correct the deficiencies. (1.2) OR The Responsible Entity has documented and implemented physical access controls, but at least two different controls do not exist to restrict access to Applicable Systems. (1.3) OR The Responsible Entity documented and implemented operational or procedural controls, restricts access to Applicable Systems using at least two different controls, and identified deficiencies, but did not assess or correct the deficiencies. (1.3) OR The Responsible Entity documented and implemented operational or procedural controls, restricts access to Applicable Systems using at least two different controls, but did not identify, assess, or correct the deficiencies. (1.3) OR The Responsible Entity does not have a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter. (1.4) OR The Responsible Entity has a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter and identified deficiencies, but did not assess or correct the deficiencies. (1.4) OR The Responsible Entity has a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter, but did not identify, assess, or correct the deficiencies. (1.4) OR The Responsible Entity does not have a process to alert for detected unauthorized access through a physical access point into a Physical security Perimeter or to communicate such alerts within 15 minutes to identified personnel. (1.5) OR The Responsible Entity does not have a process to monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control Systems. (1.6) OR The Responsible Entity does not have a process to alert for unauthorized physical access to Physical Access Control Systems or to communicate such alerts within 15 minutes to identified personnel (1.7) OR The Responsible Entity does not have a process to log authorized physical entry into each Physical Security Perimeter with sufficient information to identify the individual and date and time of entry. (1.8) OR The Responsible Entity does not have a process to retain physical access logs for 90 calendar days. (1.9) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006-5 | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented visitor control programs that include each of the applicable requirement parts in CIP-006-5 Table R2 – Visitor Control Program. |  | 2016-06-30 | Medium | N/A | The Responsible Entity included a visitor control program that requires logging of each of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact and identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity included a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact and but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity included a visitor control program to retain visitor logs for at least ninety days and identified deficiencies but did not assess or correct the deficiencies. (2.3) OR The Responsible Entity included a visitor control program to retain visitor logs for at least ninety days but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity included a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter, and identified deficiencies but did not assess or correct deficiencies. (2.1) OR The Responsible Entity included a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter but did not identify, assess, or correct deficiencies. (2.1) | The Responsible Entity has failed to include or implement a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter. (2.1) OR The Responsible Entity has failed to include or implement a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact. (2.2) OR The Responsible Entity failed to include or implement a visitor control program to retain visitor logs for at least ninety days. (2.3) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-006-5 | R3. | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP-006-5 Table R3 – Maintenance and Testing Program. |  | 2016-06-30 | Medium | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 24 calendar months but did complete required testing within 25 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 25 calendar months but did complete required testing within 26 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 26 calendar months but did complete required testing within 27 calendar months. (3.1) | The Responsible Entity has not documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter. (3.1) OR The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 27 calendar months. (3.1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006-6 | R1. | Each Responsible Entity shall implement one or more documented physical security plan(s) that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan. | 2016-07-01 |  | Medium | N/A | N/A | N/A | The Responsible Entity did not document or implement physical security plans. (R1) OR The Responsible Entity did not document or implement operational or procedural controls to restrict physical access. (1.1) OR The Responsible Entity has documented and implemented physical access controls, but at least one control does not exist to restrict access to Applicable Systems. (1.2) OR The Responsible Entity has documented and implemented physical access controls, but at least two different controls do not exist to restrict access to Applicable Systems. (1.3) OR The Responsible Entity does not have a process to monitor for unauthorized access through a physical access point into a Physical Security Perimeter. (1.4) OR The Responsible Entity does not have a process to alert for detected unauthorized access through a physical access point into a Physical Security Perimeter or to communicate such alerts within 15 minutes to identified personnel. (1.5) OR The Responsible Entity does not have a process to monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control Systems. (1.6) OR The Responsible Entity does not have a process to alert for unauthorized physical access to Physical Access Control Systems or to communicate such alerts within 15 minutes to identified personnel. (1.7) OR The Responsible Entity does not have a process to log authorized physical entry into each Physical Security Perimeter with sufficient information to identify the individual and date and time of entry. (1.8) OR The Responsible Entity does not have a process to retain physical access logs for 90 calendar days. (1.9) OR The Responsible Entity did not document or implement physical access restrictions, encryption, monitoring or equally effective logical protections for cabling and other nonprogrammable communication components used for connection between applicable Cyber Assets within the same Electronic Security Perimeter in those instances when such cabling and components are located outside of a Physical Security Perimeter. (1.10) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006-6 | R2. | Each Responsible Entity shall implement one or more documented visitor control program(s) that include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program. | 2016-07-01 |  | Medium | N/A | N/A | N/A | The Responsible Entity has failed to include or implement a visitor control program that requires continuous escorted access of visitors within any Physical Security Perimeter. (2.1) OR The Responsible Entity has failed to include or implement a visitor control program that requires logging of the initial entry and last exit dates and times of the visitor, the visitor’s name, and the point of contact. (2.2) OR The Responsible Entity failed to include or implement a visitor control program to retain visitor logs for at least ninety days. (2.3) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-006-6 | R3. | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing program(s) that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program. | 2016-07-01 |  | Medium | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 24 calendar months but did complete required testing within 25 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 25 calendar months but did complete required testing within 26 calendar months. (3.1) | The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 26 calendar months but did complete required testing within 27 calendar months. (3.1) | The Responsible Entity did not document or implement a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter. (3.1) OR The Responsible Entity has documented and implemented a maintenance and testing program for Physical Access Control Systems and locally mounted hardware or devices at the Physical Security Perimeter, but did not complete required testing within 27 calendar months. (3.1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007-1 | R1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | 2008-07-01 | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-1 | R2. | Ports and Services — The Responsible Entity shall establish and document a process to ensure that only those ports and services required for normal and emergency operations are enabled. | 2008-07-01 | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-1 | R3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003 Requirement R6, shall establish and document a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-1 | R4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | 2008-07-01 | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-1 | R5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-1 | R6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-1 | R7. | Disposal or Redeployment — The Responsible Entity shall establish formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005. | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-1 | R8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-1 | R9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007 at least annually. Changes resulting from modifications to the systems or controls shall be documented within ninety calendar days of the change. | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2 | R1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-2, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2 | R2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2 | R3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-2 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2 | R4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | 2010-03-31 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2 | R5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2 | R6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2 | R7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-2. |  | 2010-03-31 | [6 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2 | R8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2 | R9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-2 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2a | R1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-2, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | 2010-04-01 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2a | R2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. | 2010-04-01 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2a | R3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-2 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2a | R4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | 2010-04-01 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2a | R5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2a | R6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2a | R7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-2. | 2010-04-01 | 2010-09-30 | [6 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2a | R8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-2a | R9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-2 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Pending Regulatory Filing | CIP | CIP-007-3 | R1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | [8 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Pending Regulatory Filing | CIP | CIP-007-3 | R2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. | [8 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Pending Regulatory Filing | CIP | CIP-007-3 | R3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | [8 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Pending Regulatory Filing | CIP | CIP-007-3 | R4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | [8 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Pending Regulatory Filing | CIP | CIP-007-3 | R5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | [8 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Pending Regulatory Filing | CIP | CIP-007-3 | R6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | [8 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Pending Regulatory Filing | CIP | CIP-007-3 | R7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. | [8 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Pending Regulatory Filing | CIP | CIP-007-3 | R8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | [8 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Pending Regulatory Filing | CIP | CIP-007-3 | R9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. | [8 empty] | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3a | R1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | 2010-10-01 | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3a | R2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. | 2010-10-01 | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3a | R3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3a | R4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | 2010-10-01 | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3a | R5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3a | R6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3a | R7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3a | R8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3a | R9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3b | R1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3b | R2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3b | R3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3b | R4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3b | R5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3b | R6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3b | R7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. |  | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3b | R8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-3b | R9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4a | R1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-4, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | 2014-10-01 | 2014-02-03 | Medium | N/A | The Responsible Entity did create, implement and maintain the test procedures as required in R1.1, but did not document that testing is performed as required in R1.2. OR The Responsible Entity did not document the test results as required in R1.3. | The Responsible Entity did not create, implement and maintain the test procedures as required in R1.1. | The Responsible Entity did not create, implement and maintain the test procedures as required in R1.1, AND The Responsible Entity did not document that testing was performed as required in R1.2 AND The Responsible Entity did not document the test results as required in R1.3. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4a | R2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. | 2014-10-01 | 2014-02-03 | Medium | N/A | The Responsible Entity established (implemented) but did not document a process to ensure that only those ports and services required for normal and emergency operations are enabled. | The Responsible Entity documented but did not establish (implement) a process to ensure that only those ports and services required for normal and emergency operations are enabled. | The Responsible Entity did not establish (implement) or did not document a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4a | R3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | 2014-10-01 | 2014-02-03 | Low | The Responsible Entity established (implemented) and documented, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, a security patch management program but did not include one or more of the following: tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity established (implemented) but did not document, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity documented but did not establish (implement), either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity did not establish (implement) nor document, either separately or as a component of the documented configuration management process specified in CIP003-4 Requirement R6, a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4a | R4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | 2014-10-01 | 2014-02-03 | Medium | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on at least one but less than 5% of Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on at least 5% but less than 10% of Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on at least 10% but less than 15% of Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity, where technically feasible, did not use anti-virus software or other malicious software (“malware”) prevention tools, on one or more Cyber Assets within the Electronic Security Perimeter(s). |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4a | R5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | 2014-10-01 | 2014-02-03 | Low | N/A | The Responsible Entity implemented but did not document technical and procedural controls that enforce access authentication of, and accountability for, all user activity. | The Responsible Entity documented but did not implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity. | The Responsible Entity did not document or did not implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4a | R6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | 2014-10-01 | 2014-02-03 | Low | The Responsible Entity, as technically feasible, did not implement automated tools or organizational process controls to monitor system events that are related to cyber security for at least one but less than 5% of Cyber Assets inside the Electronic Security Perimeter(s). | The Responsible Entity, as technically feasible, did not implement automated tools or organizational process controls to monitor system events that are related to cyber security for 5% or more but less than 10% of Cyber Assets inside the Electronic Security Perimeter(s). | The Responsible Entity did not implement automated tools or organizational process controls, as technically feasible, to monitor system events that are related to cyber security for 10% or more but less than 15% of Cyber Assets inside the Electronic Security Perimeter(s). | The Responsible Entity as technically feasible, did not implement automated tools or organizational process controls, to monitor system events that are related to cyber security on one or more of Cyber Assets inside the Electronic Security Perimeter(s). |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4a | R7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. | 2014-10-01 | 2014-02-03 | Low | The Responsible Entity established and implemented formal methods, processes, and procedures for disposal and redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP- 005-4 but did not maintain records as specified in R7.3. | The Responsible Entity established and implemented formal methods, processes, and procedures for disposal of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4 but did not address redeployment as specified in R7.2. | The Responsible Entity established and implemented formal methods, processes, and procedures for redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4 but did not address disposal as specified in R7.1. | The Responsible Entity did not establish or implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4a | R8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | 2014-10-01 | 2014-02-03 | Low | The Responsible Entity performed at least annually a Vulnerability Assessment that included 95% or more but less than 100% of Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity performed at least annually a Vulnerability Assessment that included 90% or more but less than 95% of Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity performed at least annually a Vulnerability Assessment that included more than 85% but less than 90% of Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity did not perform a Vulnerability Assessment on one or more Cyber Assets within the Electronic Security Perimeter at least annually. OR The vulnerability assessment did not include one (1) or more of the subrequirements 8.1, 8.2, 8.3, 8.4. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4a | R9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-4 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. | 2014-10-01 | 2014-02-03 | Low | N/A | N/A | The Responsible Entity did not review and update the documentation specified in Standard CIP-007-4 at least annually. OR The Responsible Entity did not document changes resulting from modifications to the systems or controls within thirty calendar days of the change being completed. | The Responsible Entity did not review and update the documentation specified in Standard CIP-007-4 at least annually and changes resulting from modifications to the systems or controls were not documented within thirty calendar days of the change being completed. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4b | R1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-4, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. |  | 2014-02-03 | Medium | N/A | The Responsible Entity did create, implement and maintain the test procedures as required in R1.1, but did not document that testing is performed as required in R1.2. OR The Responsible Entity did not document the test results as required in R1.3. | The Responsible Entity did not create, implement and maintain the test procedures as required in R1.1 | The Responsible Entity did not create, implement and maintain the test procedures as required in R1.1, AND The Responsible Entity did not document that testing was performed as required in R1.2 AND The Responsible Entity did not document the test results as required in R1.3. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4b | R2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | 2014-02-03 | Medium | N/A | The Responsible Entity established (implemented) but did not document a process to ensure that only those ports and services required for normal and emergency operations are enabled. | The Responsible Entity documented but did not establish (implement) a process to ensure that only those ports and services required for normal and emergency operations are enabled. | The Responsible Entity did not establish (implement) or did not document a process to ensure that only those ports and services required for normal and emergency operations are enabled. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4b | R3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | 2014-02-03 | Low | The Responsible Entity established (implemented) and documented, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, a security patch management program but did not include one or more of the following: tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity established (implemented) but did not document, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity documented but did not establish (implement), either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity did not establish (implement) nor document, either separately or as a component of the documented configuration management process specified in CIP003-4 Requirement R6, a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4b | R4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). |  | 2014-02-03 | Medium | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on at least one but less than 5% of Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on at least 5% but less than 10% of Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity, as technically feasible, did not use anti-virus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on at least 10% but less than 15% of Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity, as technically feasible, did not use antivirus software and other malicious software (“malware”) prevention tools, nor implemented compensating measures, on 15% or more Cyber Assets within the Electronic Security Perimeter(s). |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4b | R5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. |  | 2014-02-03 | Low | N/A | The Responsible Entity implemented but did not document technical and procedural controls that enforce access authentication of, and accountability for, all user activity. | The Responsible Entity documented but did not implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity. | The Responsible Entity did not document nor implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4b | R6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. |  | 2014-02-03 | Low | The Responsible Entity, as technically feasible, did not implement automated tools or organizational process controls to monitor system events that are related to cyber security for at least one but less than 5% of Cyber Assets inside the Electronic Security Perimeter(s). | The Responsible Entity, as technically feasible, did not implement automated tools or organizational process controls to monitor system events that are related to cyber security for 5% or more but less than 10% of Cyber Assets inside the Electronic Security Perimeter(s). | The Responsible Entity did not implement automated tools or organizational process controls, as technically feasible, to monitor system events that are related to cyber security for 10% or more but less than 15% of Cyber Assets inside the Electronic Security Perimeter(s). | The Responsible Entity did not implement automated tools or organizational process controls, as technically feasible, to monitor system events that are related to cyber security for 15% or more of Cyber Assets inside the Electronic Security Perimeter(s). |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4b | R7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. |  | 2014-02-03 | Low | The Responsible Entity established and implemented formal methods, processes, and procedures for disposal and redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP- 005-4 but did not maintain records as specified in R7.3. | The Responsible Entity established and implemented formal methods, processes, and procedures for disposal of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4 but did not address redeployment as specified in R7.2. | The Responsible Entity established and implemented formal methods, processes, and procedures for redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4 but did not address disposal as specified in R7.1. | The Responsible Entity did not establish or implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4b | R8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: |  | 2014-02-03 | Low | The Responsible Entity performed at least annually a Vulnerability Assessment that included 95% or more but less than 100% of Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity performed at least annually a Vulnerability Assessment that included 90% or more but less than 95% of Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity performed at least annually a Vulnerability Assessment that included more than 85% but less than 90% of Cyber Assets within the Electronic Security Perimeter. | The Responsible Entity performed at least annually a Vulnerability Assessment for 85% or less of Cyber Assets within the Electronic Security Perimeter. OR The vulnerability assessment did not include one (1) or more of the subrequirements 8.1, 8.2, 8.3, 8.4. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-4b | R9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-4 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. |  | 2014-02-03 | Low | N/A | N/A | The Responsible Entity did not review and update the documentation specified in Standard CIP-007-4 at least annually. OR The Responsible Entity did not document changes resulting from modifications to the systems or controls within thirty calendar days of the change being completed. | The Responsible Entity did not review and update the documentation specified in Standard CIP-007-4 at least annually and changes resulting from modifications to the systems or controls were not documented within thirty calendar days of the change being completed. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-007-5 | R1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R1 – Ports and Services. |  | 2016-06-30 | Medium | N/A | The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media and has identified deficiencies but did not assess or correct the deficiencies. (1.2) OR The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media but did not identify, assess, or correct the deficiencies. (1.2) | The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled and has identified deficiencies but did not assess or correct the deficiencies. (1.1) OR The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled but did not identify, assess, or correct the deficiencies. (1.1) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R1 and has identified deficiencies but did not assess or correct the deficiencies. (R1) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R1 but did not identify, assess, or correct the deficiencies. (R1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007-5 | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R2 – Security Patch Management. |  | 2016-06-30 | Medium | The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified and has identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion and has identified deficiencies but did not assess or correct the deficiencies. (2.3) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking or evaluating cyber security patches for applicable Cyber Assets and has identified deficiencies but did not assess or correct the deficiencies. (2.1) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking, or evaluating cyber security patches for applicable Cyber Assets but did not identify, assess, or correct the deficiencies. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified and has identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion and has identified deficiencies but did not assess or correct the deficiencies. (2.3) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets and has identified deficiencies but did not assess or correct the deficiencies. (2.1) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets but did not identify, assess, or correct the deficiencies. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the source or sources identified and has identified deficiencies but did not assess or correct the deficiencies. (2.2) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the days source or sources identified but did not identify, assess, or correct the deficiencies. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion and has identified deficiencies but did not assess or correct the deficiencies. (2.3) OR Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion but did not identify, assess, or correct the deficiencies. (2.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R2 and has identified deficiencies but did not assess or correct the deficiencies. (R2) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R2 but did not identify, assess, or correct the deficiencies. (R2) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for tracking, evaluating, or installing cyber security patches for applicable Cyber Assets and has identified deficiencies but did not assess or correct the deficiencies. (2.1) OR The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for tracking, evaluating, or installing cyber security patches for applicable Cyber Assets but did not identify, assess, or correct the deficiencies. (2.1) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch and documented a revision or extension to the timeframe but did not obtain approval by the CIP Senior Manager or delegate and has identified deficiencies but did not assess or correct the deficiencies. (2.4) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch and documented a revision or extension to the timeframe but did not obtain approval by the CIP Senior Manager or delegate but did not identify, assess, or correct the deficiencies. (2.4) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan and has identified deficiencies but did not assess or correct the deficiencies. (2.4) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan but did not identify, assess, or correct the deficiencies. (2.4) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007-5 | R3. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R3 – Malicious Code Prevention. |  | 2016-06-30 | Medium | N/A | The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns and has identified deficiencies but did not assess or correct the deficiencies. (3.3) OR The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns and did not identify, assess, or correct the deficiencies. (3.3) | The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code and has identified deficiencies but did not assess or correct the deficiencies. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code and did not identify, assess, or correct the deficiencies. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections and has identified deficiencies but did not assess or correct the deficiencies. (3.3) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections and did not identify, assess, or correct the deficiencies. (3.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R3 and has identified deficiencies but did not assess or correct the deficiencies. (R3) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R3 and did not identify, assess, or correct the deficiencies. (R3) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code and has identified deficiencies but did not assess or correct the deficiencies. (3.1) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code and did not identify, assess, or correct the deficiencies. (3.1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007-5 | R4. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R4 – Security Event Monitoring. |  | 2016-06-30 | Medium | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review and has identified deficiencies but did not assess or correct the deficiencies. (4.4) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review but did not identify, assess, or correct the deficiencies. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review and has identified deficiencies but did not assess or correct the deficiencies. (4.4) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review but did not identify, assess, or correct the deficiencies. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2 and has identified deficiencies but did not assess or correct the deficiencies. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2 and did not identify, assess, or correct the deficiencies. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days and has identified deficiencies but did not assess or correct the deficiencies. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days and did not identify, assess, or correct the deficiencies. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals and has identified deficiencies but did not assess or correct the deficiencies. (4.4) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals and did not identify, assess, or correct the deficiencies. (4.4) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R4 and has identified deficiencies but did not assess or correct the deficiencies. (R4) OR The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R4 and did not identify, assess, or correct the deficiencies. (R4) OR The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3 and has identified deficiencies but did not assess or correct the deficiencies. (4.1) or The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3 and did not identify, assess, or correct the deficiencies. (4.1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-007-5 | R5. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-007-5 Table R5 – System Access Controls. |  | 2016-06-30 | Medium | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) | The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s) and has identified deficiencies but did not assess or correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s) and did not identify, assess, or correct the deficiencies. (5.2) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts and has identified deficiencies but did not assess or correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts and did not identify, assess, or correct the deficiencies. (5.3) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2 and has identified deficiencies but did not assess or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2 and did not identify, assess, or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R5 and has identified deficiencies but did not assess or correct the deficiencies. (R5) or The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-5 Table R5 and did not identify, assess, or correct the deficiencies. (R5) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access and has identified deficiencies but did not assess or correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access and did not identify, assess, or correct the deficiencies. (5.1) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords and has identified deficiencies but did not assess or correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords but did not identify, assess, or correct the deficiencies. (5.4) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2 and has identified deficiencies but did not assess or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2 and did not identify, assess, or correct the deficiencies. (5.5) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change and has identified deficiencies but did not assess or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change and did not identify, assess, or correct the deficiencies. (5.6) or The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts and has identified deficiencies but did not assess or correct the deficiencies. (5.7) or The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts and did not identify, assess, or correct the deficiencies. (5.7) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007-6 | R1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R1 – Ports and Services. | 2016-07-01 |  | Medium | N/A | The Responsible Entity has implemented and documented processes for Ports and Services but had no methods to protect against unnecessary physical input/output ports used for network connectivity, console commands, or removable media. (1.2) | The Responsible Entity has implemented and documented processes for determining necessary Ports and Services but, where technically feasible, had one or more unneeded logical network accessible ports enabled. (1.1) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R1. (R1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007-6 | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management. | 2016-07-01 |  | Medium | The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 35 calendar days but less than 50 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 35 calendar days but less than 50 calendar days of the evaluation completion. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes, including the identification of sources, for tracking or evaluating cyber security patches for applicable Cyber Assets. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 50 calendar days but less than 65 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 50 calendar days but less than 65 calendar days of the evaluation completion. (2.3) | The Responsible Entity has documented or implemented one or more process(es) for patch management but did not include any processes for installing cyber security patches for applicable Cyber Assets. (2.1) OR The Responsible Entity has documented and implemented one or more process(es) to evaluate uninstalled released security patches for applicability but did not evaluate the security patches for applicability within 65 calendar days of the last evaluation for the source or sources identified. (2.2) OR The Responsible Entity has one or more documented process(es) for evaluating cyber security patches but, in order to mitigate the vulnerabilities exposed by applicable security patches, did not apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan within 65 calendar days of the evaluation completion. (2.3) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R2. (R2) OR The Responsible Entity documented a mitigation plan for an applicable cyber security patch but did not implement the plan as created or revised within the timeframe specified in the plan. (2.4) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007-6 | R3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention. | 2016-07-01 |  | Medium | N/A | The Responsible Entity has implemented one or more documented process(es), but, where signatures or patterns are used, the Responsible Entity did not address testing the signatures or patterns. (3.3) | The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not mitigate the threat of detected malicious code. (3.2) OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention, but where signatures or patterns are used, the Responsible Entity did not update malicious code protections. (3.3). | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R3. (R3). OR The Responsible Entity has implemented one or more documented process(es) for malicious code prevention but did not deploy method(s) to deter, detect, or prevent malicious code. (3.1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007-6 | R4. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring. | 2016-07-01 |  | Medium | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 22 calendar days of the prior review. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed an interval and completed the review within 30 calendar days of the prior review. (4.4) | The Responsible Entity has documented and implemented one or more process(es) to generate alerts for necessary security events (as determined by the responsible entity) for the Applicable Systems (per device or system capability) but did not generate alerts for all of the required types of events described in 4.2.1 through 4.2.2. (4.2) OR The Responsible Entity has documented and implemented one or more process(es) to log applicable events identified in 4.1 (where technically feasible and except during CIP Exceptional Circumstances) but did not retain applicable event logs for at least the last 90 consecutive days. (4.3) OR The Responsible Entity has documented and implemented one or more process(es) to identify undetected Cyber Security Incidents by reviewing an entity-determined summarization or sampling of logged events at least every 15 calendar days but missed two or more intervals. (4.4) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R4. (R4) OR The Responsible Entity has documented and implemented one or more process(es) to log events for the Applicable Systems (per device or system capability) but did not detect and log all of the required types of events described in 4.1.1 through 4.1.3. (4.1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-007-6 | R5. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R5 – System Access Controls. | 2016-07-01 |  | Medium | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 15 calendar months but less than or equal to 16 calendar months of the last password change. (5.6) | The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 16 calendar months but less than or equal to 17 calendar months of the last password change. (5.6) | The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification or inventory of all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). (5.2) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, did not include the identification of the individuals with authorized access to shared accounts. (5.3) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access that did not technically or procedurally enforce one of the two password parameters as described in 5.5.1 and 5.5.2. (5.5) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 17 calendar months but less than or equal to 18 calendar months of the last password change. (5.6) | The Responsible Entity did not implement or document one or more process(es) that included the applicable items in CIP-007-6 Table R5. (R5) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access. (5.1) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but, where technically feasible, does not have a method(s) to enforce authentication of interactive user access. (5.1) OR The Responsible Entity has implemented one or more documented process(es) for System Access Controls but did not, per device capability, change known default passwords. (5.4) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but the Responsible Entity did not technically or procedurally enforce all of the password parameters described in 5.5.1 and 5.5.2. (5.5) OR The Responsible Entity has implemented one or more documented process(es) for password-only authentication for interactive user access but did not technically or procedurally enforce password changes or an obligation to change the password within 18 calendar months of the last password change. (5.6) OR The Responsible Entity has implemented one or more documented process(es) for System Access Control but, where technically feasible, did not either limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts. (5.7) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008-1 | R1. | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan. The Cyber Security Incident Response plan shall address, at a minimum, the following: | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008-1 | R2. | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. | 2008-07-01 | 2010-03-31 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008-2 | R1. | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008-2 | R2. | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008-3 | R1. | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008-3 | R2. | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008-4 | R1. | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: | 2014-10-01 | 2014-02-03 | Low | N/A | N/A | The Responsible Entity has developed a Cyber Security Incident response plan that addresses all of the components required by R1.1 through R1.6 but has not maintained the plan in accordance with those components. | The Responsible Entity has not developed a Cyber Security Incident response plan that addresses all of the components required by R1.1 through R1.6, or has not implemented the plan in response to a Cyber Security Incident. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008-4 | R2. | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. | 2014-10-01 | 2014-02-03 | Low | N/A | N/A | N/A | The Responsible Entity has not kept relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for at least three calendar years. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-008-5 | R1. | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-5 Table R1 – Cyber Security Incident Response Plan Specifications. | 2016-07-01 | 2020-12-31 | Low | N/A | N/A | The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include the roles and responsibilities of Cyber Security Incident response groups or individuals. (1.3) OR The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include incident handling procedures for Cyber Security Incidents. (1.4) | The Responsible Entity has not developed a Cyber Security Incident response plan with one or more processes to identify, classify, and respond to Cyber Security Incidents. (1.1) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to identify Reportable Cyber Security Incidents. (1.2) OR The Responsible Entity has developed a Cyber Security Incident response plan, but did not provide at least preliminary notification to ES-ISAC within one hour from identification of a Reportable Cyber Security Incident. (1.2) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008-5 | R2. | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | 2016-07-01 | 2020-12-31 | Low | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 15 calendar months, not exceeding 16 calendar months between tests of the plan. (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan. (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 17 calendar months, not exceeding 18 calendar months between tests of the plan. (2.1) OR The Responsible Entity did not document deviations, if any, from the plan during a test or when a Reportable Cyber Security Incident occurs. (2.2) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 19 calendar months between tests of the plan. (2.1) OR The Responsible Entity did not retain relevant records related to Reportable Cyber Security Incidents. (2.3) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-008-5 | R3. | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-5 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | 2016-07-01 | 2020-12-31 | Low | The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within greater than 90 but less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) | The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Cyber Security Incident response groups or individuals, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) or The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) or The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Cyber Security Incident response groups or individuals, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008-6 | R1. | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP-008-6 Table R1 – Cyber Security Incident Response Plan Specifications. | 2021-01-01 |  | Low | N/A | N/A | The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include the roles and responsibilities of Cyber Security Incident response groups or individuals. (1.3) OR The Responsible Entity has developed the Cyber Security Incident response plan(s), but the plan does not include incident handling procedures for Cyber Security Incidents. (1.4) The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to provide notification per Requirement R4. (1.2) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes that include criteria to evaluate and define attempts to compromise. (1.2) | The Responsible Entity has not developed a Cyber Security Incident response plan with one or more processes to identify, classify, and respond to Cyber Security Incidents. (1.1) OR The Responsible Entity has developed a Cyber Security Incident response plan, but the plan does not include one or more processes to identify Reportable Cyber Security Incidents or a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Part 1.2.1, a system identified in the “Applicable Systems” column for Part 1.2. (1.2) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008-6 | R2. | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP-008-6 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. | 2021-01-01 |  | Low | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 15 calendar months, not exceeding 16 calendar months between tests of the plan(s). (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan(s). (2.1) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 17 calendar months, not exceeding 18 calendar months between tests of the plan(s). (2.1) OR The Responsible Entity did not document deviations, if any, from the plan during a test or when a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 2.2 occurs. (2.2) | The Responsible Entity has not tested the Cyber Security Incident response plan(s) within 18 calendar months between tests of the plan(s). (2.1) OR The Responsible Entity did not retain relevant records related to Reportable Cyber Security Incidents or Cyber Security Incidents that were an attempt to compromise a system identified in the “Applicable Systems” column for Part 2.3. (2.3) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008-6 | R3. | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP-008-6 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. | 2021-01-01 |  | Low | The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within greater than 90 but less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) | The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not notified each person or group with a defined role in the Cyber Security Incident response plan of updates to the Cyber Security Incident response plan within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.3) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) OR The Responsible Entity has not updated the Cyber Security Incident response plan based on any documented lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.2) OR The Responsible Entity has not updated the Cyber Security Incident response plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of a test or actual incident response to a Reportable Cyber Security Incident. (3.1.1) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-008-6 | R4. | Each Responsible Entity shall notify the Electricity Information Sharing and Analysis Center (E-ISAC) and, if subject to the jurisdiction of the United States, the United States National Cybersecurity and Communications Integration Center (NCCIC), or their successors, of a Reportable Cyber Security Incident and a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column, unless prohibited by law, in accordance with each of the applicable requirement parts in CIP-008-6 Table R4 – Notifications and Reporting for Cyber Security Incidents. | 2021-01-01 |  | Low | The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.2 but failed to notify or update E-ISAC or NCCIC, or their successors, within the timelines pursuant to Part 4.2. (4.2) OR The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.3 but failed to report on one or more of the attributes within 7 days after determination of the attribute(s) not reported pursuant to Part 4.1. (4.3) OR The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident or a Cyber Security Incident that was an attempt to compromise a system identified in the “Applicable Systems” column for Part 4.1 but failed to report on one or more of the attributes after determination pursuant to Part 4.1. (4.1) | The Responsible Entity failed to notify E-ISAC or NCCIC, or their successors, of a Cyber Security Incident that was an attempt to compromise, as determined by applying the criteria from Requirement R1, Part 1.2.1, a system identified in the “Applicable Systems” column. (R4) | The Responsible Entity notified E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident but failed to notify or update E-ISAC or NCCIC, or their successors, within the timelines pursuant to Part 4.2. (4.2) OR The Responsible Entity failed to notify E-ISAC or NCCIC, or their successors, of a Reportable Cyber Security Incident. (R4) | The Responsible Entity failed to notify E-ISAC and NCCIC, or their successors, of a Reportable Cyber Security Incident. (R4) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009-1 | R1. | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: | 2008-07-01 | 2010-03-31 | Medium | N/A | The Responsible Entity has not annually reviewed recovery plan(s) for Critical Cyber Assets. | The Responsible Entity has created recovery plan(s) for Critical Cyber Assets but did not address one of the requirements CIP-009-1 R1.1 or R1.2. | The Responsible Entity has not created recovery plan(s) for Critical Cyber Assets that address at a minimum both requirements CIP-009-1 R1.1 and R1.2. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-1 | R2. | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. | 2008-07-01 | 2010-03-31 | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) have not been exercised at least annually. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-1 | R3. | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within ninety calendar days of the change. | 2008-07-01 | 2010-03-31 | Low | The Responsible Entity's recovery plan(s) have been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident but the updates were communicated to personnel responsible for the activation and impl | The Responsible Entity's recovery plan(s) have been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident but the updates were communicated to personnel responsible for the activation and impl | The Responsible Entity's recovery plan(s) have been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident but the updates were communicated to personnel responsible for the activation and impl | The Responsible Entity's recovery plan(s) have not been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. OR The Responsible Entity's recovery plan(s) have been updated to reflect any ch |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-1 | R4. | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. | 2008-07-01 | 2010-03-31 | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) do not include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-1 | R5. | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. | 2008-07-01 | 2010-03-31 | Low | N/A | N/A | N/A | The Responsible Entity's information essential to recovery that is stored on backup media has not been tested at least annually to ensure that the information is available. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-2 | R1. | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: | 2010-04-01 | 2010-09-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-2 | R2. | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-2 | R3. | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-2 | R4. | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-2 | R5. | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. | 2010-04-01 | 2010-09-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-3 | R1. | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: | 2010-10-01 | 2016-06-30 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-3 | R2. | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-3 | R3. | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-3 | R4. | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-3 | R5. | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. | 2010-10-01 | 2016-06-30 | Low | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-4 | R1. | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: | 2014-10-01 | 2014-02-03 | Medium | N/A | N/A | N/A | The Responsible Entity has not created or has not annually reviewed their recovery plan(s) for Critical Cyber Assets OR has created a plan but did not address one or more of the requirements CIP- 009-4 R1.1 and R1.2. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-4 | R2. | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. | 2014-10-01 | 2014-02-03 | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) have not been exercised at least annually. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-4 | R3. | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. | 2014-10-01 | 2014-02-03 | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) have not been updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. OR The Responsible Entity's recovery plan(s) have been updated to reflect any c |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-4 | R4. | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. | 2014-10-01 | 2014-02-03 | Low | N/A | N/A | N/A | The Responsible Entity's recovery plan(s) do not include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-4 | R5. | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. | 2014-10-01 | 2014-02-03 | Low | N/A | N/A | N/A | The Responsible Entity's information essential to recovery that is stored on backup media has not been tested at least annually to ensure that the information is available. |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP
Inactive | CIP | CIP-009-5 | R1. | Each Responsible Entity shall have one or more documented recovery plans that collectively include each of the applicable requirement parts in CIP-009-5 Table R1 – Recovery Plan Specifications. |  | 2016-06-30 | Medium | N/A | The Responsible Entity has developed recovery plan(s), but the plan(s) do not address one of the requirements included in Parts 1.2 through 1.5. | The Responsible Entity has developed recovery plan(s), but the plan(s) do not address two of the requirements included in Parts 1.2 through 1.5. | The Responsible Entity has not created recovery plan(s) for BES Cyber Systems. or The Responsible Entity has created recovery plan(s) for BES Cyber Systems, but the plan(s) does not address the conditions for activation in Part 1.1. or The Responsible Entity has created recovery plan(s) for BES Cyber Systems, but the plan(s) does not address three or more of the requirements in Parts 1.2 through 1.5. |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009-5 | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, its documented recovery plan(s) to collectively include each of the applicable requirement parts in CIP-009-5 Table R2 – Recovery Plan Implementation and Testing. |  | 2016-06-30 | Low | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 15 calendar months, not exceeding 16 calendar months between tests of the plan, and when tested, any deficiencies were identified, assessed, and corrected. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 15 calendar months, not exceeding 16 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.2) or The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 36 calendar months, not exceeding 37 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.3) | The Responsible Entity has not tested the recovery plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan, and when tested, any deficiencies were identified, assessed, and corrected. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 16 calendar months, not exceeding 17 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.2) or The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 37 calendar months, not exceeding 38 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.3) | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 17 calendar months, not exceeding 18 calendar months between tests of the plan, and when tested, any deficiencies were identified, assessed, and corrected. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 17 calendar months, not exceeding 18 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.2) or The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 38 calendar months, not exceeding 39 calendar months between tests, and when tested, any deficiencies were identified, assessed, and corrected. (2.3) | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 18 calendar months between tests of the plan. (2.1) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.1 and identified deficiencies, but did not assess or correct the deficiencies. (2.1) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.1 but did not identify, assess, or correct the deficiencies. (2.1) or The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 18 calendar months between tests. (2.2) or The Responsible Entity has tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 and identified deficiencies, but did not assess or correct the deficiencies. (2.2) or The Responsible Entity has tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 but did not identify, assess, or correct the deficiencies. (2.2) or The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.3 within 39 calendar months between tests of the plan. (2.3) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.3 and identified deficiencies, but did not assess or correct the deficiencies. (2.3) or The Responsible Entity has tested the recovery plan(s) according to R2 Part 2.3 but did not identify, assess, or correct the deficiencies. (2.3) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-009-5 | R3. | Each Responsible Entity shall maintain each of its recovery plans in accordance with each of the applicable requirement parts in CIP-009-5 Table R3 – Recovery Plan Review, Update and Communication. |  | 2016-06-30 | Low | The Responsible Entity has not notified each person or group with a defined role in the recovery plan(s) of updates within 90 and less than 210 calendar days of the update being completed. (3.1.3) | The Responsible Entity has not updated the recovery plan(s) based on any documented lessons learned within 90 and less than 210 calendar days of each recovery plan test or actual recovery. (3.1.2) or The Responsible Entity has not notified each person or group with a defined role in the recovery plan(s) of updates within 120 calendar days of the update being completed. (3.1.3) or The Responsible Entity has not updated the recovery plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Responders, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 210 calendar days of each recovery plan test or actual recovery. (3.1.1) or The Responsible Entity has not updated the recovery plan(s) based on any documented lessons learned within 120 calendar days of each recovery plan test or actual recovery. (3.1.2) or The Responsible Entity has not updated the recovery plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) Roles or responsibilities, or Responders, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 210 calendar days of each recovery plan test or actual recovery. (3.1.1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009-6 | R1. | Each Responsible Entity shall have one or more documented recovery plan(s) that collectively include each of the applicable requirement parts in CIP-009-6 Table R1 – Recovery Plan Specifications. | 2016-07-01 |  | Medium | N/A | The Responsible Entity has developed recovery plan(s), but the plan(s) do not address one of the requirements included in Parts 1.2 through 1.5. | The Responsible Entity has developed recovery plan(s), but the plan(s) do not address two of the requirements included in Parts 1.2 through 1.5. | The Responsible Entity has not created recovery plan(s) for BES Cyber Systems. OR The Responsible Entity has created recovery plan(s) for BES Cyber Systems, but the plan(s) does not address the conditions for activation in Part 1.1. OR The Responsible Entity has created recovery plan(s) for BES Cyber Systems, but the plan(s) does not address three or more of the requirements in Parts 1.2 through 1.5. |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009-6 | R2. | Each Responsible Entity shall implement its documented recovery plan(s) to collectively include each of the applicable requirement parts in CIP-009-6 Table R2 – Recovery Plan Implementation and Testing. | 2016-07-01 |  | Low | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 15 calendar months, not exceeding 16 calendar months between tests of the plan. (2.1) OR The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 15 calendar months, not exceeding 16 calendar months between tests. (2.2) OR The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 36 calendar months, not exceeding 37 calendar months between tests. (2.3) | The Responsible Entity has not tested the recovery plan(s) within 16 calendar months, not exceeding 17 calendar months between tests of the plan. (2.1) OR The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 16 calendar months, not exceeding 17 calendar months between tests. (2.2) OR The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 37 calendar months, not exceeding 38 calendar months between tests. (2.3) | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 17 calendar months, not exceeding 18 calendar months between tests of the plan. (2.1) OR The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 17 calendar months, not exceeding 18 calendar months between tests. (2.2) OR The Responsible Entity has not tested the recovery plan according to R2 Part 2.3 within 38 calendar months, not exceeding 39 calendar months between tests. (2.3) | The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.1 within 18 calendar months between tests of the plan. (2.1) OR The Responsible Entity has not tested a representative sample of the information used in the recovery of BES Cyber System functionality according to R2 Part 2.2 within 18 calendar months between tests. (2.2) OR The Responsible Entity has not tested the recovery plan(s) according to R2 Part 2.3 within 39 calendar months between tests of the plan. (2.3) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-009-6 | R3. | Each Responsible Entity shall maintain each of its recovery plan(s) in accordance with each of the applicable requirement parts in CIP-009-6 Table R3 – Recovery Plan Review, Update and Communication. | 2016-07-01 |  | Low | The Responsible Entity has not notified each person or group with a defined role in the recovery plan(s) of updates within 90 and less than 120 calendar days of the update being completed. (3.1.3) | The Responsible Entity has not updated the recovery plan(s) based on any documented lessons learned within 90 and less than 120 calendar days of each recovery plan test or actual recovery. (3.1.2) OR The Responsible Entity has not notified each person or group with a defined role in the recovery plan(s) of updates within 120 calendar days of the update being completed. (3.1.3) OR The Responsible Entity has not updated the recovery plan(s) or notified each person or group with a defined role within 60 and less than 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) • Roles or responsibilities, or • Responders, or • Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 90 and less than 120 calendar days of each recovery plan test or actual recovery. (3.1.1) OR The Responsible Entity has not updated the recovery plan(s) based on any documented lessons learned within 120 calendar days of each recovery plan test or actual recovery. (3.1.2) OR The Responsible Entity has not updated the recovery plan(s) or notified each person or group with a defined role within 90 calendar days of any of the following changes that the responsible entity determines would impact the ability to execute the plan: (3.2) • Roles or responsibilities, or • Responders, or Technology changes. | The Responsible Entity has neither documented lessons learned nor documented the absence of any lessons learned within 120 calendar days of each recovery plan test or actual recovery. (3.1.1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010-1 | R1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-010-1 Table R1 – Configuration Change Management. |  | 2016-06-30 | Medium | The Responsible Entity has documented and implemented a configuration change management process(es) that includes only four of the required baseline items listed in 1.1.1 through 1.1.5. (1.1) or The Responsible Entity has documented and implemented a configuration change management process(es) that includes all of the required baseline items listed in 1.1.1 through 1.1.5 and identified deficiencies but did not assess and correct the deficiencies. (1.1) or The Responsible Entity has documented and implemented a configuration change management process(es) that includes all of the required baseline items listed in 1.1.1 through 1.1.5 but did not identify, assess, and correct the deficiencies. (1.1) or The Responsible Entity has a process(es) to perform steps in 1.4.1 and 1.4.2 for a change(s) that deviates from the existing baseline configuration and identified deficiencies in the verification documentation but did not assess or correct the deficiencies. (1.4.3) or The Responsible Entity has a process(es) to perform steps in 1.4.1 and 1.4.2 for a change(s) that deviates from the existing baseline configuration but did not identify, assess, or correct the deficiencies in the verification documentation. (1.4.3) | The Responsible Entity has documented and implemented a configuration change management process(es) that includes only three of the required baseline items listed in 1.1.1 through 1.1.5. (1.1) or The Responsible Entity has documented and implemented a configuration change management process(es) that includes four of the required baseline items listed in 1.1.1 through 1.1.5 and identified deficiencies but did not assess and correct the deficiencies. (1.1) or The Responsible Entity has documented and implemented a configuration change management process(es) that includes four of the required baseline items listed in 1.1.1 through 1.1.5 but did not identify, assess, and correct the deficiencies. (1.1) or The Responsible Entity has a process(es) to determine required security controls in CIP-005 and CIP-007 that could be impacted by a change(s) that deviates from the existing baseline configuration and identified deficiencies in the determination of affected security controls, but did not assess, or correct the deficiencies. (1.4.1) or The Responsible Entity has a process(es) to determine required security controls in CIP-005 and CIP-007 that could be impacted by a change(s) that deviates from the existing baseline configuration but did not identify, assess, or correct the deficiencies in the determination of affected security controls. (1.4.1) | The Responsible Entity has documented and implemented a configuration change management process(es) that includes only two of the required baseline items listed in 1.1.1 through 1.1.5. (1.1) or The Responsible Entity has documented and implemented a configuration change management process(es) that includes three of the required baseline items listed in 1.1.1 through 1.1.5 and identified deficiencies but did not assess and correct the deficiencies. (1.1) or The Responsible Entity has documented and implemented a configuration change management process(es) that includes three of the required baseline items listed in 1.1.1 through 1.1.5 but did not identify, assess, and correct the deficiencies. (1.1) or The Responsible Entity has a process(es) that requires authorization and documentation for changes that deviate from the existing baseline configuration and identified deficiencies but did not assess or correct the deficiencies. (1.2) or The Responsible Entity has a process(es) that requires authorization and documentation for changes that deviate from the existing baseline configuration but did not identify, assess, or correct the deficiencies. (1.2) or The Responsible Entity has a process(es) to update baseline configurations within 30 calendar days of completing a change(s) that deviates from the existing baseline configuration and identified deficiencies but did not assess or correct the deficiencies. (1.3) or The Responsible Entity has a process(es) to update baseline configurations within 30 calendar days of completing a change(s) that deviates from the existing baseline configuration but did not identify, assess, or correct the deficiencies. (1.3) or The Responsible Entity has a process(es) to verify that required security controls in CIP-005 and CIP-007 are not adversely affected by a change(s) that deviates from the existing baseline configuration and identified deficiencies in required controls, but did not assess, or correct the deficiencies. (1.4.2) or The Responsible Entity has a process(es) to verify that required security controls in CIP-005 and CIP-007 are not adversely affected by a change(s) that deviates from the existing baseline configuration but did not identify, assess, or correct the deficiencies in the required controls. (1.4.2) or The Responsible Entity has a process for testing changes in an environment that models the baseline configuration prior to implementing a change that deviates from baseline configuration, and identified deficiencies but did not assess or correct the deficiencies. (1.5.1) or The Responsible Entity has a process for testing changes in an environment that models the baseline configuration prior to implementing a change that deviates from baseline configuration but did not identify, assess, or correct the deficiencies. (1.5.1) or The Responsible Entity has a process to document the test results and, if using a test environment, document the differences between the test and production environments and identified deficiencies but did not assess or correct the deficiencies. (1.5.2) or The Responsible Entity has a process to document the test results and, if using a test environment, document the differences between the test and production environments, but did not identify, assess, or correct the deficiencies. (1.5.2) | The Responsible Entity has not documented or implemented any configuration change management process(es). (R1) or The Responsible Entity has documented and implemented a configuration change management process(es) that includes only one of the required baseline items listed in 1.1.1 through 1.1.5. (1.1) or The Responsible Entity has documented and implemented a configuration change management process(es) that includes two or fewer of the required baseline items listed in 1.1.1 through 1.1.5 and identified deficiencies but did not assess and correct the deficiencies. (1.1) or The Responsible Entity has documented and implemented a configuration change management process(es) that includes two or fewer of the required baseline items listed in 1.1.1 through 1.1.5 but did not identify, assess, and correct the deficiencies. (1.1) or The Responsible Entity does not have a process(es) that requires authorization and documentation of changes that deviate from the existing baseline configuration. (1.2) or The Responsible Entity does not have a process(es) to update baseline configurations within 30 calendar days of completing a change(s) that deviates from the existing baseline configuration.(1.3) or The Responsible Entity does not have a process(es) to determine required security controls in CIP-005 and CIP-007 that could be impacted by a change(s) that deviates from the existing baseline configuration. (1.4.1) or The Responsible Entity has a process(es) to determine required security controls in CIP-005 and CIP-007 that could be impacted by a change(s) that deviates from the existing baseline configuration but did not verify and document that the required controls were not adversely affected following the change. (1.4.2 & 1.4.3) or The Responsible Entity does not have a process for testing changes in an environment that models the baseline configuration prior to implementing a change that deviates from baseline configuration. (1.5.1) or The Responsible Entity does not have a process to document the test results and, if using a test environment, document the differences between the test and production environments. (1.5.2) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010-1 | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP-010-1 Table R2 – Configuration Monitoring. |  | 2016-06-30 | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or implemented a process(es) to monitor for, investigate, and document detected unauthorized changes to the baseline at least once every 35 calendar days. (2.1) or The Responsible Entity has documented and implemented a process(es) to monitor for, investigate, and document detected unauthorized changes to the baseline at least once every 35 calendar days and identified deficiencies but did not assess or correct the deficiencies. (2.1) or The Responsible Entity has documented and implemented a process(es) to monitor for, investigate, and document detected unauthorized changes to the baseline at least once every 35 calendar days but did not identify, assess, or correct the deficiencies. (2.1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010-1 | R3. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-010-1 Table R3– Vulnerability Assessments. |  | 2016-06-30 | Medium | The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 15 months, but less than 18 months, since the last assessment on one of its applicable BES Cyber Systems. (3.1) or The Responsible Entity has implemented one or more documented active vulnerability assessment processes for Applicable Systems, but has performed an active vulnerability assessment more than 36 months, but less than 39 months, since the last active assessment on one of its applicable BES Cyber Systems. (3.2) | The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 18 months, but less than 21, months since the last assessment on one of its applicable BES Cyber Systems. (3.1) or The Responsible Entity has implemented one or more documented active vulnerability assessment processes for Applicable Systems, but has performed an active vulnerability assessment more than 39 months, but less than 42 months, since the last active assessment on one of its applicable BES Cyber Systems. (3.2) | The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 21 months, but less than 24 months, since the last assessment on one of its applicable BES Cyber Systems. (3.1) or The Responsible Entity has implemented one or more documented active vulnerability assessment processes for Applicable Systems, but has performed an active vulnerability assessment more than 42 months, but less than 45 months, since the last active assessment on one of its applicable BES Cyber Systems. (3.2) | The Responsible Entity has not implemented any vulnerability assessment processes for one of its applicable BES Cyber Systems. (R3) or The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 24 months since the last assessment on one of its applicable BES Cyber Systems. (3.1) or The Responsible Entity has implemented one or more documented active vulnerability assessment processes for Applicable Systems, but has performed an active vulnerability assessment more than 45 months since the last active assessment on one of its applicable BES Cyber Systems.(3.2) or The Responsible Entity has implemented and documented one or more vulnerability assessment processes for each of its applicable BES Cyber Systems, but did not perform the active vulnerability assessment in a manner that models an existing baseline configuration of its applicable BES Cyber Systems. (3.3) or The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has not documented the results of the vulnerability assessments, the action plans to remediate or mitigate vulnerabilities identified in the assessments, the planned date of completion of the action plan, and the execution status of the mitigation plans. (3.4) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010-2 | R1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management. | 2016-07-01 | 2020-06-30 | Medium | The Responsible Entity has documented and implemented a configuration change management process(es) that includes only four of the required baseline items listed in 1.1.1 through 1.1.5. (1.1) | The Responsible Entity has documented and implemented a configuration change management process(es) that includes only three of the required baseline items listed in 1.1.1 through 1.1.5. (1.1) | The Responsible Entity has documented and implemented a configuration change management process(es) that includes only two of the required baseline items listed in 1.1.1 through 1.1.5. (1.1) | The Responsible Entity has not documented or implemented any configuration change management process(es). (R1) OR The Responsible Entity has documented and implemented a configuration change management process(es) that includes only one of the required baseline items listed in 1.1.1 through 1.1.5. (1.1) OR The Responsible Entity does not have a process(es) that requires authorization and documentation of changes that deviate from the existing baseline configuration. (1.2) OR The Responsible Entity does not have a process(es) to update baseline configurations within 30 calendar days of completing a change(s) that deviates from the existing baseline configuration.(1.3) OR The Responsible Entity does not have a process(es) to determine required security controls in CIP-005 and CIP-007 that could be impacted by a change(s) that deviates from the existing baseline configuration. (1.4.1) OR The Responsible Entity has a process(es) to determine required security controls in CIP-005 and CIP-007 that could be impacted by a change(s) that deviates from the existing baseline configuration but did not verify and document that the required controls were not adversely affected following the change. (1.4.2 & 1.4.3) OR The Responsible Entity does not have a process for testing changes in an environment that models the baseline configuration prior to implementing a change that deviates from baseline configuration. (1.5.1) OR The Responsible Entity does not have a process to document the test results and, if using a test environment, document the differences between the test and production environments. (1.5.2) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010-2 | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-2 Table R2 – Configuration Monitoring. | 2016-07-01 | 2020-06-30 | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or implemented a process(es) to monitor for, investigate, and document detected unauthorized changes to the baseline at least once every 35 calendar days. (2.1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010-2 | R3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-2 Table R3– Vulnerability Assessments. | 2016-07-01 | 2020-06-30 | Medium | The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 15 months, but less than 18 months, since the last assessment on one of its applicable BES Cyber Systems. (3.1) OR The Responsible Entity has implemented one or more documented active vulnerability assessment processes for Applicable Systems, but has performed an active vulnerability assessment more than 36 months, but less than 39 months, since the last active assessment on one of its applicable BES Cyber Systems. (3.2) | The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 18 months, but less than 21, months since the last assessment on one of its applicable BES Cyber Systems. (3.1) OR The Responsible Entity has implemented one or more documented active vulnerability assessment processes for Applicable Systems, but has performed an active vulnerability assessment more than 39 months, but less than 42 months, since the last active assessment on one of its applicable BES Cyber Systems. (3.2) | The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 21 months, but less than 24 months, since the last assessment on one of its applicable BES Cyber Systems. (3.1) OR The Responsible Entity has implemented one or more documented active vulnerability assessment processes for Applicable Systems, but has performed an active vulnerability assessment more than 42 months, but less than 45 months, since the last active assessment on one of its applicable BES Cyber Systems. (3.2) | The Responsible Entity has not implemented any vulnerability assessment processes for one of its applicable BES Cyber Systems. (R3) OR The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 24 months since the last assessment on one of its applicable BES Cyber Systems. (3.1) OR The Responsible Entity has implemented one or more documented active vulnerability assessment processes for Applicable Systems, but has performed an active vulnerability assessment more than 45 months since the last active assessment on one of its applicable BES Cyber Systems.(3.2) OR The Responsible Entity has implemented and documented one or more vulnerability assessment processes for each of its applicable BES Cyber Systems, but did not perform the active vulnerability assessment in a manner that models an existing baseline configuration of its applicable BES Cyber Systems. (3.3) OR The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has not documented the results of the vulnerability assessments, the action plans to remediate or mitigate vulnerabilities identified in the assessments, the planned date of completion of the action plan, and the execution status of the mitigation plans. (3.4) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010-2 | R4. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems and associated Protected Cyber Assets, shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) for Transient Cyber Assets and Removable Media that include the sections in Attachment 1. | 2017-04-01 | 2020-06-30 | Medium | The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to CIP-010-2, Requirement R4, Attachment 1, Section 1.1. (R4) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document the Removable Media sections according to CIP-010-2, Requirement R4, Attachment 1, Section 3. (R4) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document authorization for Transient Cyber Assets managed by the Responsible Entity according to CIP-010-2, Requirement R4, Attachment 1, Section 1.2. (R4) | The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media sections according to CIP-010-2, Requirement R4, Attachment 1, Section 3. (R4) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media plan, but failed to document mitigation of software vulnerabilities, mitigation for the introduction of malicious code, or mitigation of the risk of unauthorized use for Transient Cyber Assets managed by the Responsible Entity according to CIP-010-2, Requirement R4, Attachment 1, Sections 1.3, 1.4, and 1.5. (R4) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation of software vulnerabilities or mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to CIP-010-2, Requirement R4, Attachment 1, Sections 2.1, 2.2, and 2.3. (R4) | The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to authorize its Transient Cyber Asset(s) according to CIP-010-2, Requirement R4, Attachment 1, Section 1.2. (R4) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation of software vulnerabilities, mitigation for the introduction of malicious code, or mitigation of the risk of unauthorized use for Transient Cyber Assets managed by the Responsible Entity according to CIP-010-2, Requirement R4, Attachment 1, Sections 1.3, 1.4, and 1.5. (R4) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation of software vulnerabilities or mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to CIP-010-2, Requirement R4, Attachment 1, Sections 2.1, 2.2, and 2.3. (R4) | The Responsible Entity failed to document or implement one or more plan(s) for Transient Cyber Assets and Removable Media according to CIP-010-2, Requirement R4. (R4) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010-3 | R1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management. | 2020-07-01 | 2022-09-30 | Medium | The Responsible Entity has documented and implemented a configuration change management process(es) that includes only four of the required baseline items listed in 1.1.1 through 1.1.5. (1.1) | The Responsible Entity has documented and implemented a configuration change management process(es) that includes only three of the required baseline items listed in 1.1.1 through 1.1.5. (1.1) | The Responsible Entity has documented and implemented a configuration change management process(es) that includes only two of the required baseline items listed in 1.1.1 through 1.1.5. (1.1) OR The Responsible Entity has a process as specified in Part 1.6 to verify the identity of the software source (1.6.1) but does not have a process as specified in Part 1.6 to verify the integrity of the software provided by the software source when the method to do so is available to the Responsible Entity from the software source. (1.6.2) | The Responsible Entity has not documented or implemented any configuration change management process(es). (R1) OR The Responsible Entity has documented and implemented a configuration change management process(es) that includes only one of the required baseline items listed in 1.1.1 through 1.1.5. (1.1) OR The Responsible Entity does not have a process(es) that requires authorization and documentation of changes that deviate from the existing baseline configuration. (1.2) OR The Responsible Entity does not have a process(es) to update baseline configurations within 30 calendar days of completing a change(s) that deviates from the existing baseline configuration.(1.3) OR The Responsible Entity does not have a process(es) to determine required security controls in CIP-005 and CIP-007 that could be impacted by a change(s) that deviates from the existing baseline configuration. (1.4.1) OR The Responsible Entity has a process(es) to determine required security controls in CIP-005 and CIP-007 that could be impacted by a change(s) that deviates from the existing baseline configuration but did not verify and document that the required controls were not adversely affected following the change. (1.4.2 & 1.4.3) OR The Responsible Entity does not have a process for testing changes in an environment that models the baseline configuration prior to implementing a change that deviates from baseline configuration. (1.5.1) OR The Responsible Entity does not have a process to document the test results and, if using a test environment, document the differences between the test and production environments. (1.5.2) OR The Responsible Entity does not have a process as specified in Part 1.6 to verify the identity of the software source and the integrity of the software provided by the software source when the method to do so is available to the Responsible Entity from the software source. (1.6) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010-3 | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R2 – Configuration Monitoring. | 2020-07-01 | 2022-09-30 | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or implemented a process(es) to monitor for, investigate, and document detected unauthorized changes to the baseline at least once every 35 calendar days. (2.1) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010-3 | R3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R3– Vulnerability Assessments. | 2020-07-01 | 2022-09-30 | Medium | The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 15 months, but less than 18 months, since the last assessment on one of its applicable BES Cyber Systems. (3.1) OR The Responsible Entity has implemented one or more documented active vulnerability assessment processes for Applicable Systems, but has performed an active vulnerability assessment more than 36 months, but less than 39 months, since the last active assessment on one of its applicable BES Cyber Systems. (3.2) | The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 18 months, but since the last assessment on one of its applicable BES Cyber Systems. (3.1) OR The Responsible Entity has implemented one or more documented active vulnerability assessment processes for Applicable Systems, but has performed an active vulnerability assessment more than 39 months, but less than 42 months, since the last active assessment on one of its applicable BES Cyber Systems. (3.2) | The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 21 months, but less than 24 months, since the last assessment on one of its applicable BES Cyber Systems. (3.1) OR The Responsible Entity has implemented one or more documented active vulnerability assessment processes for Applicable Systems, but has performed an active vulnerability assessment more than 42 months, but less than 45 months, since the last active assessment on one of its applicable BES Cyber Systems. (3.2) | The Responsible Entity has not implemented any vulnerability assessment processes for one of its applicable BES Cyber Systems. (R3) OR The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 24 months since the last assessment on one of its applicable BES Cyber Systems. (3.1) OR The Responsible Entity has implemented one or more documented active vulnerability assessment processes for Applicable Systems, but has performed an active vulnerability assessment more than 45 months since the last active assessment on one of its applicable BES Cyber Systems.(3.2) OR The Responsible Entity has implemented and documented one or more vulnerability assessment processes for each of its applicable BES Cyber Systems, but did not perform the active vulnerability assessment in a manner that models an existing baseline configuration of its applicable BES Cyber Systems. (3.3) OR The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has not documented the results of the vulnerability assessments, the action plans to remediate or mitigate vulnerabilities identified in the assessments, the planned date of completion of the action plan, and the execution status of the mitigation plans. (3.4) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-010-3 | R4. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems and associated Protected Cyber Assets, shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) for Transient Cyber Assets and Removable Media that include the sections in Attachment 1. | 2020-07-01 | 2022-09-30 | Medium | The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to CIP-010-3, Requirement R4, Attachment 1, Section 1.1. (R4) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document the Removable Media sections according to CIP-010-3, Requirement R4, Attachment 1, Section 3. (R4) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document authorization for Transient Cyber Assets managed by the Responsible Entity according to CIP-010-3, Requirement R4, Attachment 1, Section 1.2. (R4) | The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media sections according to CIP-010-3, Requirement R4, Attachment 1, Section 3. (R4) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media plan, but failed to document mitigation of software vulnerabilities, mitigation for the introduction of malicious code, or mitigation of the risk of unauthorized use for Transient Cyber Assets managed by the Responsible Entity according to CIP-010-3, Requirement R4, Attachment 1, Sections 1.3, 1.4, and 1.5. (R4) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation of software vulnerabilities or mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to CIP-010-3, Requirement R4, Attachment 1, Sections 2.1, 2.2, and 2.3. (R4) | The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to authorize its Transient Cyber Asset(s) according to CIP-010-3, Requirement R4, Attachment 1, Section 1.2. (R4) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation of software vulnerabilities, mitigation for the introduction of malicious code, or mitigation of the risk of unauthorized use for Transient Cyber Assets managed by the Responsible Entity according to CIP-010-3, Requirement R4, Attachment 1, Sections 1.3, 1.4, and 1.5. (R4) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation of software vulnerabilities or mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to CIP-010-3, Requirement R4, Attachment 1, Sections 2.1, 2.2, and 2.3. (R4) | The Responsible Entity failed to document or implement one or more plan(s) for Transient Cyber Assets and Removable Media according to CIP-010-3, Requirement R4. (R4) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010-4 | R1. | R1. Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-4 Table R1 – Configuration Change Management. | 2022-10-01 |  | Medium | The Responsible Entity has documented and implemented a configuration change management process(es) that includes only four of the required baseline items listed in 1.1.1 through 1.1.5. (1.1) | The Responsible Entity has documented and implemented a configuration change management process(es) that includes only three of the required baseline items listed in 1.1.1 through 1.1.5. (1.1) | The Responsible Entity has documented and implemented a configuration change management process(es) that includes only two of the required baseline items listed in 1.1.1 through 1.1.5. (1.1)OR The Responsible Entity has a process as specified in Part 1.6 to verify the identity of the software source (1.6.1) but does not have a process as specified in Part 1.6 to verify the integrity of the software provided by the software source when the method to do so is available to the Responsible Entity from the software source. (1.6.2) | The Responsible Entity has not documented or implemented any configuration change management process(es). (R1)ORThe Responsible Entity has documented and implemented a configuration change management process(es) that includes only one of the required baseline items listed in 1.1.1 through 1.1.5. (1.1)ORThe Responsible Entity does not have a process(es) that requires authorization and documentation of changes that deviate from the existing baseline configuration. (1.2)ORThe Responsible Entity does not have a process(es) to update baseline configurations within 30 calendar days of completing a change(s) that deviates from the existing baseline configuration.(1.3)ORThe Responsible Entity does not have a process(es) to determine required security controls in CIP-005 and CIP-007 that could be impacted by a change(s) that deviates from the existing baseline configuration. (1.4.1)ORThe Responsible Entity has a process(es) to determine required security controls in CIP-005 and CIP-007 that could be impacted by a change(s) that deviates from the existing baseline configuration but did not verify and document that the required controls were not adversely affected following the change. (1.4.2 & 1.4.3) ORThe Responsible Entity does not have a process for testing changes in an environment that models the baseline configuration prior to implementing a change that deviates from baseline configuration. (1.5.1)ORThe Responsible Entity does not have a process to document the test results and, if using a test environment, document the differences between the test and production environments. (1.5.2)ORThe Responsible Entity does not have a process as specified in Part 1.6 to verify the identity of the software source and the integrity of the software provided by the software source when the method to do so is available to the Responsible Entity from the software source. (1.6) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010-4 | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-4 Table R2 – Configuration Monitoring | 2022-10-01 |  | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or implemented a process(es) to monitor for, investigate, and document detected unauthorized changes to the baseline at least once every 35 calendar days. (2.1) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010-4 | R3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R3– Vulnerability Assessments. | 2022-10-01 |  | Medium | The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 15 months, but less than 18 months, since the last assessment on one of its applicable BES Cyber Systems. (3.1)OR The Responsible Entity has implemented one or more documented active vulnerability assessment processes for Applicable Systems, but has performed an active vulnerability assessment more than 36 months, but less than 39 months, since the last active assessment on one of its applicable BES Cyber Systems. (3.2) | The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 18 months, but less than 21 months, since the last assessment on one of its applicable BES Cyber Systems. (3.1)OR The Responsible Entity has implemented one or more documented active vulnerability assessment processes for Applicable Systems, but has performed an active vulnerability assessment more than 39 months, but less than 42 months, since the last active assessment on one of its applicable BES Cyber Systems. (3.2) | The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 21 months, but less than 24 months, since the last assessment on one of its applicable BES Cyber Systems. (3.1)OR The Responsible Entity has implemented one or more documented active vulnerability assessment processes for Applicable Systems, but has performed an active vulnerability assessment more than 42 months, but less than 45 months, since the last active assessment on one of its applicable BES Cyber Systems. (3.2) | The Responsible Entity has not implemented any vulnerability assessment processes for one of its applicable BES Cyber Systems. (R3) OR The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has performed a vulnerability assessment more than 24 months since the last assessment on one of its applicable BES Cyber Systems. (3.1)OR The Responsible Entity has implemented and documented one or more vulnerability assessment processes for each of its applicable BES Cyber Systems, but did not perform the active vulnerability assessment in a manner that models an existing baseline configuration of its applicable BES Cyber Systems. (3.3) OR The Responsible Entity has implemented one or more documented vulnerability assessment processes for each of its applicable BES Cyber Systems, but has not documented the results of the vulnerability assessments, the action plans to remediate or mitigate vulnerabilities identified in the assessments, the planned date of completion of the action plan, and the execution status of the |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-010-4 | R4. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems and associated Protected Cyber Assets, shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) for Transient Cyber Assets and Removable Media that include the sections in Attachment 1. | 2022-10-01 |  | Medium | The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to manage its Transient Cyber Asset(s) according to CIP-010-3, Requirement R4, Attachment 1, Section 1.1. (R4) ORThe Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document the Removable Media sections according to CIP-010-3, Requirement R4, Attachment 1, Section 3. (R4)OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document authorization for Transient Cyber Assets managed by the Responsible Entity according to CIP-010-3, Requirement R4, Attachment 1, Section 1.2. (R4) | The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement the Removable Media sections according to CIP-010-3, Requirement R4, Attachment 1, Section 3. (R4) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media plan, but failed to document mitigation of software vulnerabilities, mitigation for the introduction of malicious code, or mitigation of the risk of unauthorized use for Transient Cyber Assets managed by the Responsible Entity according to CIP-010-3, Requirement R4, Attachment 1, Sections 1.3, 1.4, and 1.5. (R4)OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to document mitigation of software vulnerabilities or mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to CIP-010-3, Requirement R4, Attachment 1, Sections 2.1, 2.2, and 2.3. (R4) | The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to authorize its Transient Cyber Asset(s) according to CIP-010-3, Requirement R4, Attachment 1, Section 1.2. (R4) OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation of software vulnerabilities, mitigation for the introduction of malicious code, or mitigation of the risk of unauthorized use for Transient Cyber Assets managed by the Responsible Entity according to CIP-010-3, Requirement R4, Attachment 1, Sections 1.3, 1.4, and 1.5. (R4)OR The Responsible Entity documented its plan(s) for Transient Cyber Assets and Removable Media, but failed to implement mitigation of software vulnerabilities or mitigation for the introduction of malicious code for Transient Cyber Assets managed by a party other than the Responsible Entity according to CIP-010-3, Requirement R4, Attachment 1, Sections 2.1, 2.2, and 2.3. (R4) | The Responsible Entity failed to document or implement one or more plan(s) for Transient Cyber Assets and Removable Media according to CIP-010-3, Requirement R4. (R4) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011-1 | R1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented information protection program(s) that collectively includes each of the applicable requirement parts in CIP-011-1 Table R1 – Information Protection. |  | 2016-06-30 | Medium | N/A | N/A | The Responsible Entity has implemented a BES Cyber System Information protection program which includes one or more methods to identify BES Cyber System Information and has identified deficiencies but did not assess or correct the deficiencies. (1.1) or The Responsible Entity has implemented a BES Cyber System Information protection program which includes one or more methods to identify BES Cyber System Information but did not identify, assess, or correct the deficiencies. (1.1) or The Responsible Entity has implemented a BES Cyber System Information protection program which includes one or more procedures for protection and secure handling BES Cyber System Information and has identified deficiencies but did not assess or correct the deficiencies. (1.2) or The Responsible Entity has implemented a BES Cyber System Information protection program which includes one or more procedures for protection and secure handling BES Cyber System Information but did not identify, assess, or correct the deficiencies. (1.2) | The Responsible Entity has not documented or implemented a BES Cyber System Information protection program (R1). |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011-1 | R2. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts in CIP-011-1 Table R2 – BES Cyber Asset Reuse and Disposal. |  | 2016-06-30 | Low | N/A | The Responsible Entity implemented one or more documented processes but did not include processes for reuse as to prevent the unauthorized retrieval of BES Cyber System Information from the BES Cyber Asset. (2.1) | The Responsible Entity implemented one or more documented processes but did not include disposal or media destruction processes to prevent the unauthorized retrieval of BES Cyber System Information from the BES Cyber Asset. (2.2) | The Responsible Entity has not documented or implemented any processes for applicable requirement parts in CIP-011-1 Table R2 – BES Cyber Asset Reuse and Disposal. (R2) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011-2 | R1. | Each Responsible Entity shall implement one or more documented information protection program(s) that collectively includes each of the applicable requirement parts in CIP-011-2 Table R1 – Information Protection. | 2016-07-01 | 2023-12-31 | Medium | N/A | N/A | N/A | The Responsible Entity has not documented or implemented a BES Cyber System Information protection program (R1). |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-011-2 | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include the applicable requirement parts in CIP-011-2 Table R2 – BES Cyber Asset Reuse and Disposal. | 2016-07-01 | 2023-12-31 | Low | N/A | The Responsible Entity implemented one or more documented processes but did not include processes for reuse as to prevent the unauthorized retrieval of BES Cyber System Information from the BES Cyber Asset. (2.1) | The Responsible Entity implemented one or more documented processes but did not include disposal or media destruction processes to prevent the unauthorized retrieval of BES Cyber System Information from the BES Cyber Asset. (2.2) | The Responsible Entity has not documented or implemented any processes for applicable requirement parts in CIP-011-2 Table R2 – BES Cyber Asset Reuse and Disposal. (R2) |  | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-011-3 | R1. | Each Responsible Entity shall implement one or more documented information protection program(s) for BES Cyber System Information (BCSI) pertaining to “Applicable Systems” identified in CIP-011-3 Table R1 – Information Protection Program that collectively includes each of the applicable requirement parts in CIP-011-3 Table R1 – Information Protection Program. | 2024-01-01 |  | Medium | N/A | N/A | The Responsible Entity documented, but did not, implement one or more BCSI protection program(s). (R1) OR The Responsible Entity documented but did not implement at least one method to identify BCSI. (1.1) OR The Responsible Entity documented but did not implement at least one method to protect and securely handle BCSI. (1.2) | The Responsible Entity neither documented nor implemented one or more BCSI protection program(s). (R1) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-011-3 | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include the applicable requirement parts in CIP-011-3 Table R2 – BES Cyber Asset Reuse and Disposal. | 2024-01-01 |  | Low | N/A | The Responsible Entity implemented one or more documented processes but did not include processes for reuse as to prevent the unauthorized retrieval of BCSI from the BES Cyber Asset. (2.1) | The Responsible Entity implemented one or more documented processes but did not include disposal or media destruction processes to prevent the unauthorized retrieval of BCSI from the BES Cyber Asset. (2.2) | The Responsible Entity has not documented or implemented any processes for applicable requirement parts in CIP-011-3 Table R3 – BES Cyber Asset Reuse and Disposal. (R2) |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-012-1 | R1. | The Responsible Entity shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) to mitigate the risks posed by unauthorized disclosure and unauthorized modification of Real-time Assessment and Real-time monitoring data while being transmitted between any applicable Control Centers. The Responsible Entity is not required to include oral communications in its plan. The plan shall include: | 2022-07-01 |  | Medium | N/A | The Responsible Entity documented its plan(s) but failed to include one of the applicable Parts of the plan as specified in Requirement R1. | The Responsible Entity documented its plan(s) but failed to include two of the applicable Parts of the plan as specified in Requirement R1. | The Responsible Entity failed to document plan(s) for Requirement R1; Or • The Responsible Entity failed to implement any Part of its plan(s) for Requirement R1, except under CIP Exceptional Circumstances. |  | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Filed and Pending Regulatory Approval | CIP | CIP-012-2 | R1. | The Responsible Entity shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) to mitigate the risks posed by unauthorized disclosure, unauthorized modification, and loss of availability, of data used in Real-time Assessment and Real-time monitoring while such data is being transmitted between any applicable Control Centers. The Responsible Entity is not required to include oral communications in its plan. The plan shall include: |  |  | Medium | N/A | The Responsible Entity documented its plan(s), but failed to include one of the applicable Parts of the plan as specified in Requirement R1. | The Responsible Entity documented its plan(s), but failed to include two of the applicable Parts of the plan as specified in Requirement R1. | The Responsible Entity failed to document its plan(s) for Requirement R1; Or The Responsible Entity failed to implement three or more Parts of its plan(s) for Requirement R1, except under CIP Exceptional Circumstances. |  | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013-1 | R1. | Each Responsible Entity shall develop one or more documented supply chain cyber security risk management plan(s) for high and medium impact BES Cyber Systems. The plan(s) shall include: | 2020-07-01 | 2022-09-30 | Medium | The Responsible Entity developed one or more documented supply chain cyber security risk management plan(s) which include the use of process(es) in planning for procurement of BES Cyber Systems to identify and assess cyber security risk(s) to the BES as specified in Part 1.1, and include the use of process(es) for procuring BES Cyber systems as specified in Part 1.2, but the plans do not include one of the parts in Part 1.2.1 through Part 1.2.6. | The Responsible Entity developed one or more documented supply chain cyber security risk management plan(s) which include the use of process(es) in planning for procurement of BES Cyber Systems to identify and assess cyber security risk(s) to the BES as specified in Part 1.1, and include the use of process(es) for procuring BES Cyber systems as specified in Part 1.2, but the plans do not include two or more of the parts in Part 1.2.1 through Part 1.2.6. | The Responsible Entity developed one or more documented supply chain cyber security risk management plan(s), but the plan(s) did not include the use of process(es) in planning for procurement of BES Cyber Systems to identify and assess cyber security risk(s) to the BES as specified in Part 1.1, or the plan(s) did not include the use of process(es) for procuring BES Cyber systems as specified in Part 1.2. | The Responsible Entity developed one or more documented supply chain cyber security risk management plan(s), but the plan(s) did not include the use of process(es) in planning for procurement of BES Cyber Systems to identify and assess cyber security risk(s) to the BES as specified in Part 1.1, and the plan(s) did not include the use of process(es) for procuring BES Cyber systems as specified in Part 1.2. OR The Responsible Entity did not develop one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013-1 | R2. | Each Responsible Entity shall implement its supply chain cyber security risk management plan(s) specified in Requirement R1. Note: Implementation of the plan does not require the Responsible Entity to renegotiate or abrogate existing contracts (including amendments to master agreements and purchase orders). Additionally, the following issues are beyond the scope of Requirement R2: (1) the actual terms and conditions of a procurement contract; and (2) vendor performance and adherence to a contract. | 2020-07-01 | 2022-09-30 | Medium | The Responsible Entity implemented its supply chain cyber security risk management plan(s) including the use of process(es) in planning for procurement of BES Cyber Systems to identify and assess cyber security risk(s) to the BES as specified in Requirement R1 Part 1.1, and including the use of process(es) for procuring BES Cyber systems as specified in Requirement R1 Part 1.2, but did not implement one of the parts in Requirement R1 Part 1.2.1 through Part 1.2.6. | The Responsible Entity implemented its supply chain cyber security risk management plan(s) including the use of process(es) in planning for procurement of BES Cyber Systems to identify and assess cyber security risk(s) to the BES as specified in Requirement R1 Part 1.1, and including the use of process(es) for procuring BES Cyber systems as specified in Requirement R1 Part 1.2, but did not implement two or more of the parts in Requirement R1 Part 1.2.1 through Part 1.2.6. | The Responsible Entity implemented its supply chain cyber security risk management plan(s), but did not implement the use of process(es) in planning for procurement of BES Cyber Systems to identify and assess cyber security risk(s) to the BES as specified in Requirement R1 Part 1.1, or did not implement the use of process(es) for procuring BES Cyber systems as specified in Requirement R1 Part 1.2. | The Responsible Entity implemented its supply chain cyber security risk management plan(s), but did not implement the use of process(es) in planning for procurement of BES Cyber Systems to identify and assess cyber security risk(s) to the BES as specified in Requirement R1 Part 1.1, and did not implement the use of process(es) for procuring BES Cyber systems as specified in Requirement R1 Part 1.2; OR The Responsible Entity did not implement its supply chain cyber security risk management plan(s) specified in the requirement. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-013-1 | R3. | Each Responsible Entity shall review and obtain CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) specified in Requirement R1 at least once every 15 calendar months. | 2020-07-01 | 2022-09-30 | Medium | The Responsible Entity reviewed and obtained CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) but did so more than 15 calendar months but less than or equal to 16 calendar months since the previous review as specified in the Requirement. | The Responsible Entity reviewed and obtained CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) but did so more than 16 calendar months but less than or equal to 17 calendar months since the previous review as specified in the Requirement. | The Responsible Entity reviewed and obtained CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) but did so more than 17 calendar months but less than or equal to 18 calendar months since the previous review as specified in the Requirement. | The Responsible Entity did not review and obtain CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) within 18 calendar months of the previous review as specified in the Requirement. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-013-2 | R1. | Each Responsible Entity shall develop one or more documented supply chain cyber security risk management plan(s) for high and medium impact BES Cyber Systems and their associated Electronic Access Control or Monitoring Systems (EACMS) and Physical Access Control Systems (PACS). The plan(s) shall include: | 2022-10-01 |  | Medium | The Responsible Entity developed one or more documented supply chain cyber security risk management plan(s) which include the use of process(es) in planning for procurement of BES Cyber Systems, and their associated EACMS and PACS, to identify and assess cyber security risk(s) to the BES as specified in Part 1.1, and include the use of process(es) for procuring BES Cyber Systems and their associated EACMS and PACS, as specified in Part 1.2, but the plans do not include one of the parts in Part 1.2.1 through Part 1.2.6. | The Responsible Entity developed one or more documented supply chain cyber security risk management plan(s) which include the use of process(es) in planning for procurement of BES Cyber Systems, and their associated EACMS and PACS, to identify and assess cyber security risk(s) to the BES as specified in Part 1.1, and include the use of process(es) for procuring BES Cyber Systems and their associated EACMS and PACS, as specified in Part 1.2, but the plans do not include two or more of the parts in Part 1.2.1 through Part 1.2.6. | The Responsible Entity developed one or more documented supply chain cyber security risk management plan(s), but the plan(s) did not include the use of process(es) in planning for procurement of BES Cyber Systems, and their associated EACMS and PACS, to identify and assess cyber security risk(s) to the BES as specified in Part 1.1, or the plan(s) did not include the use of process(es) for procuring BES Cyber Systems and their associated EACMS and PACS, as specified in Part 1.2. | The Responsible Entity developed one or more documented supply chain cyber security risk management plan(s), but the plan(s) did not include the use of process(es) in planning for procurement of BES Cyber Systems, and their associated EACMS and PACS, to identify and assess cyber security risk(s) to the BES as specified in Part 1.1, and the plan(s) did not include the use of process(es) for procuring BES Cyber Systems and their associated EACMS and PACS, as specified in Part 1.2. OR The Responsible Entity did not develop one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-013-2 | R2. | Each Responsible Entity shall implement its supply chain cyber security risk management plan(s) specified in Requirement R1. | 2022-10-01 |  | Medium | The Responsible Entity implemented its supply chain cyber security risk management plan(s) including the use of process(es) in planning for procurement of BES Cyber Systems, and their associated EACMS and PACS, to identify and assess cyber security risk(s) to the BES as specified in Requirement R1 Part 1.1, and including the use of process(es) for procuring BES Cyber Systems and their associated EACMS and PACS, as specified in Requirement R1 Part 1.2, but did not implement one of the parts in Requirement R1 Part 1.2.1 through Part 1.2.6. | The Responsible Entity implemented its supply chain cyber security risk management plan(s) including the use of process(es) in planning for procurement of BES Cyber Systems, and their associated EACMS and PACS, to identify and assess cyber security risk(s) to the BES as specified in Requirement R1 Part 1.1, and including the use of process(es) for procuring BES Cyber Systems and their associated EACMS and PACS, as specified in Requirement R1 Part 1.2, but did not implement two or more of the parts in Requirement R1 Part 1.2.1 through Part 1.2.6. | The Responsible Entity implemented its supply chain cyber security risk management plan(s), but did not implement the use of process(es) in planning for procurement of BES Cyber Systems, and their associated EACMS and PACS, to identify and assess cyber security risk(s) to the BES as specified in Requirement R1 Part 1.1, or did not implement the use of process(es) for procuring BES Cyber Systems and their associated EACMS and PACS, as specified in Requirement R1 Part 1.2. | The Responsible Entity implemented its supply chain cyber security risk management plan(s), but did not implement the use of process(es) in planning for procurement of BES Cyber Systems, and their associated EACMS and PACS, to identify and assess cyber security risk(s) to the BES as specified in Requirement R1 Part 1.1, and did not implement the use of process(es) for procuring BES Cyber Systems and their associated EACMS and PACS, as specified in Requirement R1 Part 1.2; OR The Responsible Entity did not implement its supply chain cyber security risk management plan(s) specified in the requirement. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-013-2 | R3. | Each Responsible Entity shall review and obtain CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) specified in Requirement R1 at least once every 15 calendar months. | 2022-10-01 |  | Medium | The Responsible Entity reviewed and obtained CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) but did so more than 15 calendar months but less than or equal to 16 calendar months since the previous review as specified in the Requirement. | The Responsible Entity reviewed and obtained CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) but did so more than 16 calendar months but less than or equal to 17 calendar months since the previous review as specified in the Requirement. | The Responsible Entity reviewed and obtained CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) but did so more than 17 calendar months but less than or equal to 18 calendar months since the previous review as specified in the Requirement. | The Responsible Entity did not review and obtain CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) within 18 calendar months of the previous review as specified in the Requirement. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | CIP | CIP-014-1 | R1. | Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection. [Please see the standard for more information] | 2015-10-01 | 2015-10-01 | High | The Transmission Owner performed an initial risk assessment but did so after the date specified in the implementation plan for performing the initial risk assessment but less than or equal to two calendar months after that date; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 30 calendar months but less than or equal to 32 calendar months; OR The Transmission Owner that has not identified in its previous risk assessment any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 60 calendar months but less than or equal to 62 calendar months. | The Transmission Owner performed an initial risk assessment but did so more than two calendar months after the date specified in the implementation plan for performing the initial risk assessment but less than or equal to four calendar months after that date; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 32 calendar months but less than or equal to 34 calendar months; OR The Transmission Owner that has not identified in its previous risk assessment any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 62 calendar months but less than or equal to 64 calendar months. | The Transmission Owner performed an initial risk assessment but did so more than four calendar months after the date specified in the implementation plan for performing the initial risk assessment but less than or equal to six calendar months after that date; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 34 calendar months but less than or equal to 36 calendar months; OR The Transmission Owner that has not identified in its previous risk assessment any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 64 calendar months but less than or equal to 66 calendar months; OR The Transmission Owner performed a risk assessment but failed to include Part 1.2. | The Transmission Owner performed an initial risk assessment but did so more than six calendar months after the date specified in the implementation plan for performing the initial risk assessment; OR The Transmission Owner failed to perform an initial risk assessment; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after more than 36 calendar months; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection failed to perform a risk assessment; OR The Transmission Owner that has not identified in its previous risk assessment any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after more than 66 calendar months; OR The Transmission Owner that has not identified in its previous risk assessment any Transmission station and Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection failed to perform a subsequent risk assessment. | [18 empty] | TO
Inactive | CIP | CIP-014-1 | R2. | Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1.[Please see the standard for more information] | 2015-10-01 | 2015-10-01 | Medium | The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but did so in more than 90 calendar days but less than or equal to 100 calendar days following completion of Requirement R1; OR The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 and modified or documented the technical basis for not modifying its identification under Requirement R1 as required by Part 2.3 but did so more than 60 calendar days and less than or equal to 70 calendar days from completion of the third party verification. | The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but did so more than 100 calendar days but less than or equal to 110 calendar days following completion of Requirement R1; OR The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 and modified or documented the technical basis for not modifying its identification under Requirement R1 as required by Part 2.3 but did so more than 70 calendar days and less than or equal to 80 calendar days from completion of the third party verification. | The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but did so more than 110 calendar days but less than or equal to 120 calendar days following completion of Requirement R1; OR The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 and modified or documented the technical basis for not modifying its identification under Requirement R1 as required by Part 2.3 but did so more than 80 calendar days from completion of the third party verification; OR The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but failed to modify or document the technical basis for not modifying its identification under R1 as required by Part 2.3. | The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but did so more than 120 calendar days following completion of Requirement R1; OR The Transmission Owner failed to have an unaffiliated third party verify the risk assessment performed under Requirement R1; OR The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but failed to implement procedures for protecting information per Part 2.4. | [18 empty] | TO
Inactive | CIP | CIP-014-1 | R3. | For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2. [Please see the standard for more information] | 2015-10-01 | 2015-10-01 | Low | The Transmission Owner notified the Transmission Operator that operates the primary control center as specified in Requirement R3 but did so more than seven calendar days and less than or equal to nine calendar days following the completion of Requirement R2; OR The Transmission Owner notified the Transmission Operator that operates the primary control center of the removal from the identification in Requirement R1 but did so more than seven calendar days and less than or equal to nine calendar days following the verification or the subsequent risk assessment. | The Transmission Owner notified the Transmission Operator that operates the primary control center as specified in Requirement R3 but did so more than nine calendar days and less than or equal to 11 calendar days following the completion of Requirement R2; OR The Transmission Owner notified the Transmission Operator that operates the primary control center of the removal from the identification in Requirement R1 but did so more than nine calendar days and less than or equal to 11 calendar days following the verification or the subsequent risk assessment. | The Transmission Owner notified the Transmission Operator that operates the primary control center as specified in Requirement R3 but did so more than 11 calendar days and less than or equal to 13 calendar days following the completion of Requirement R2; OR The Transmission Owner notified the Transmission Operator that operates the primary control center of the removal from the identification in Requirement R1 but did so more than 11 calendar days and less than or equal to 13 calendar days following the verification or the subsequent risk assessment. | The Transmission Owner notified the Transmission Operator that operates the primary control center as specified in Requirement R3 but did so more than 13 calendar days following the completion of Requirement R2; OR The Transmission Owner failed to notify the Transmission Operator that it operates a control center identified in Requirement R1; OR The Transmission Owner notified the Transmission Operator that operates the primary control center of the removal from the identification in Requirement R1 but did so more than 13 calendar days following the verification or the subsequent risk assessment. OR The Transmission Owner failed to notify the Transmission Operator that operates the primary control center of the removal from the identification in Requirement R1. | [18 empty] | TO
Inactive | CIP | CIP-014-1 | R4. | Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: [Please see the standard for more information] | 2015-10-01 | 2015-10-01 | Medium | N/A | The Responsible Entity conducted an evaluation of the potential physical threats and vulnerabilities to each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but failed to consider one of Parts 4.1 through 4.3 in the evaluation. | The Responsible Entity conducted an evaluation of the potential physical threats and vulnerabilities to each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but failed to consider two of Parts 4.1 through 4.3 in the evaluation. | The Responsible Entity failed to conduct an evaluation of the potential physical threats and vulnerabilities to each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1; OR The Responsible Entity conducted an evaluation of the potential physical threats and vulnerabilities to each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but failed to consider Parts 4.1 through 4.3. | [18 empty] | TO | TOP
Inactive | CIP | CIP-014-1 | R5. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: [Please see the standard for more information] | 2015-10-01 | 2015-10-01 | High | The Responsible Entity developed and implemented a documented physical security plan(s) that covers each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but did so more than 120 calendar days but less than or equal to 130 calendar days after completing Requirement R2; OR The Responsible Entity developed and implemented a documented physical security plan(s) that covers its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2 but failed to include one of Parts 5.1 through 5.4 in the plan. | The Responsible Entity developed and implemented a documented physical security plan(s) that covers each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but did so more than 130 calendar days but less than or equal to 140 calendar days after completing Requirement R2; OR The Responsible Entity developed and implemented a documented physical security plan(s) that covers its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2 but failed to include two of Parts 5.1 through 5.4 in the plan. | The Responsible Entity developed and implemented a documented physical security plan(s) that covers each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but did so more than 140 calendar days but less than or equal to 150 calendar days after completing Requirement R2; OR The Responsible Entity developed and implemented a documented physical security plan(s) that covers its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2 but failed to include three of Parts 5.1 through 5.4 in the plan. | The Responsible Entity developed and implemented a documented physical security plan(s) that covers each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but did so more than 150 calendar days after completing the verification in Requirement R2; OR The Responsible Entity failed to develop and implement a documented physical security plan(s) that covers its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. OR The Responsible Entity developed and implemented a documented physical security plan(s) that covers its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement 2 but failed to include Parts 5.1 through 5.4 in the plan. | [18 empty] | TO | TOP
Inactive | CIP | CIP-014-1 | R6. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. [Please see the standard for more information] | 2015-10-01 | 2015-10-01 | Medium | The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 but did so in more than 90 calendar days but less than or equal to 100 calendar days; OR The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 and modified or documented the reason for not modifying the security plan(s) as specified in Part 6.3 but did so more than 60 calendar days and less than or equal to 70 calendar days following completion of the third party review. | The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 but did so in more than 100 calendar days but less than or equal to 110 calendar days; OR The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 and modified or documented the reason for not modifying the security plan(s) as specified in Part 6.3 but did so more than 70 calendar days and less than or equal to 80 calendar days following completion of the third party review. | The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 but did so more than 110 calendar days but less than or equal to 120 calendar days; OR The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 and modified or documented the reason for not modifying the security plan(s) as specified in Part 6.3 but did so more than 80 calendar days following completion of the third party review; OR The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 but did not document the reason for not modifying the security plan(s) as specified in Part 6.3. | The Responsible Entity failed to have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 in more than 120 calendar days; OR The Responsible Entity failed to have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5; OR The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 but failed to implement procedures for protecting information per Part 6.3. | [18 empty] | TO | TOP
Inactive | CIP | CIP-014-2 | R1. | Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. | 2015-10-02 | 2022-06-16 | High | The Transmission Owner performed an initial risk assessment but did so after the date specified in the implementation plan for performing the initial risk assessment but less than or equal to two calendar months after that date; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 30 calendar months but less than or equal to 32 calendar months; OR The Transmission Owner that has not identified in its previous risk assessment any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 60 calendar months but less than or equal to 62 calendar months. | The Transmission Owner performed an initial risk assessment but did so more than two calendar months after the date specified in the implementation plan for performing the initial risk assessment but less than or equal to four calendar months after that date; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 32 calendar months but less than or equal to 34 calendar months; OR The Transmission Owner that has not identified in its previous risk assessment any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 62 calendar months but less than or equal to 64 calendar months. | The Transmission Owner performed an initial risk assessment but did so more than four calendar months after the date specified in the implementation plan for performing the initial risk assessment but less than or equal to six calendar months after that date; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 34 calendar months but less than or equal to 36 calendar months; The Transmission Owner that has not identified in its previous risk assessment any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 64 calendar months but less than or equal to 66 calendar months; OR The Transmission Owner performed a risk assessment but failed to include Part 1.2. | The Transmission Owner performed an initial risk assessment but did so more than six calendar months after the date specified in the implementation plan for performing the initial risk assessment; OR The Transmission Owner failed to perform an initial risk assessment; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after more than 36 calendar months; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection failed to perform a risk assessment; OR The Transmission Owner that has not identified in its previous risk assessment any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after more than 66 calendar months; OR The Transmission Owner that has not identified in its previous risk assessment any Transmission station and Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection failed to perform a subsequent risk assessment. | [18 empty] | TO
Inactive | CIP | CIP-014-2 | R2. | Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1. | 2015-10-02 | 2022-06-16 | Medium | The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but did so in more than 90 calendar days but less than or equal to 100 calendar days following completion of Requirement R1; OR The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 and modified or documented the technical basis for not modifying its identification under Requirement R1 as required by Part 2.3 but did so more than 60 calendar days and less than or equal to 70 calendar days from completion of the third party verification. | The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but did so more than 100 calendar days but less than or equal to 110 calendar days following completion of Requirement R1; OR The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 and modified or documented the technical basis for not modifying its identification under Requirement R1 as required by Part 2.3 but did so more than 70 calendar days and less than or equal to 80 calendar days from completion of the third party verification. | The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but did so more than 110 calendar days but less than or equal to 120 calendar days following completion of Requirement R1; OR The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 and modified or documented the technical basis for not modifying its identification under Requirement R1 as required by Part 2.3 but did so more than 80 calendar days from completion of the third party verification; OR The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but failed to modify or document the technical basis for not modifying its identification under R1 as required by Part 2.3. | The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but did so more than 120 calendar days following completion of Requirement R1; OR The Transmission Owner failed to have an unaffiliated third party verify the risk assessment performed under Requirement R1; The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but failed to implement procedures for protecting information per Part 2.4. | [18 empty] | TO
Inactive | CIP | CIP-014-2 | R3. | For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2 | 2015-10-02 | 2022-06-16 | Low | The Transmission Owner notified the Transmission Operator that operates the primary control center as specified in Requirement R3 but did so more than seven calendar days and less than or equal to nine calendar days following the completion of Requirement R2; OR The Transmission Owner notified the Transmission Operator that operates the primary control center of the removal from the identification in Requirement R1 but did so more than seven calendar days and less than or equal to nine calendar days following the verification or the subsequent risk assessment. | The Transmission Owner notified the Transmission Operator that operates the primary control center as specified in Requirement R3 but did so more than nine calendar days and less than or equal to 11 calendar days following the completion of Requirement R2; OR The Transmission Owner notified the Transmission Operator that operates the primary control center of the removal from the identification in Requirement R1 but did so more than nine calendar days and less than or equal to 11 calendar days following the verification or the subsequent risk assessment. | The Transmission Owner notified the Transmission Operator that operates the primary control center as specified in Requirement R3 but did so more than 11 calendar days and less than or equal to 13 calendar days following the completion of Requirement R2; OR The Transmission Owner notified the Transmission Operator that operates the primary control center of the removal from the identification in Requirement R1 but did so more than 11 calendar days and less than or equal to 13 calendar days following the verification or the subsequent risk assessment. | The Transmission Owner notified the Transmission Operator that operates the primary control center as specified in Requirement R3 but did so more than 13 calendar days following the completion of Requirement R2; OR The Transmission Owner failed to notify the Transmission Operator that it operates a control center identified in Requirement R1; OR The Transmission Owner notified the Transmission Operator that operates the primary control center of the removal from the identification in Requirement R1 but did so more than 13 calendar days following the verification or the subsequent risk assessment. OR The Transmission Owner failed to notify the Transmission Operator that operates the primary control center of the removal from the identification in Requirement R1. | [18 empty] | TO
Inactive | CIP | CIP-014-2 | R4. | Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: | 2015-10-02 | 2022-06-16 | Medium | N/A | The Responsible Entity conducted an evaluation of the potential physical threats and vulnerabilities to each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but failed to consider one of Parts 4.1 through 4.3 in the evaluation. | The Responsible Entity conducted an evaluation of the potential physical threats and vulnerabilities to each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but failed to consider two of Parts 4.1 through 4.3 in the evaluation. | The Responsible Entity failed to conduct an evaluation of the potential physical threats and vulnerabilities to each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1; OR The Responsible Entity conducted an evaluation of the potential physical threats and vulnerabilities to each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but failed to consider Parts 4.1 through 4.3. | [18 empty] | TO | TOP
Inactive | CIP | CIP-014-2 | R5. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: | 2015-10-02 | 2022-06-16 | High | The Responsible Entity developed and implemented a documented physical security plan(s) that covers each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but did so more than 120 calendar days but less than or equal to 130 calendar days after completing Requirement R2; OR The Responsible Entity developed and implemented a documented physical security plan(s) that covers its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2 but failed to include one of Parts 5.1 through 5.4 in the plan. | The Responsible Entity developed and implemented a documented physical security plan(s) that covers each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but did so more than 130 calendar days but less than or equal to 140 calendar days after completing Requirement R2; OR The Responsible Entity developed and implemented a documented physical security plan(s) that covers its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2 but failed to include two of Parts 5.1 through 5.4 in the plan. | The Responsible Entity developed and implemented a documented physical security plan(s) that covers each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but did so more than 140 calendar days but less than or equal to 150 calendar days after completing Requirement R2; OR The Responsible Entity developed and implemented a documented physical security plan(s) that covers its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2 but failed to include three of Parts 5.1 through 5.4 in the plan. | The Responsible Entity developed and implemented a documented physical security plan(s) that covers each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but did so more than 150 calendar days after completing the verification in Requirement R2; OR The Responsible Entity failed to develop and implement a documented physical security plan(s) that covers its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. OR The Responsible Entity developed and implemented a documented physical security plan(s) that covers its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement 2 but failed to include Parts 5.1 through 5.4 in the plan. | [18 empty] | TO | TOP
Inactive | CIP | CIP-014-2 | R6. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. | 2015-10-02 | 2022-06-16 | Medium | The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 but did so in more than 90 calendar days but less than or equal to 100 calendar days; OR The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 and modified or documented the reason for not modifying the security plan(s) as specified in Part 6.3 but did so more than 60 calendar days and less than or equal to 70 calendar days following completion of the third party review. | The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 but did so in more than 100 calendar days but less than or equal to 110 calendar days; OR The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 and modified or documented the reason for not modifying the security plan(s) as specified in Part 6.3 but did so more than 70 calendar days and less than or equal to 80 calendar days following completion of the third party review. | The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 but did so more than 110 calendar days but less than or equal to 120 calendar days; OR The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 and modified or documented the reason for not modifying the security plan(s) as specified in Part 6.3 but did so more than 80 calendar days following completion of the third party review; OR The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 but did not document the reason for not modifying the security plan(s) as specified in Part 6.3. | The Responsible Entity failed to have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 in more than 120 calendar days; OR The Responsible Entity failed to have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5; OR The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 but failed to implement procedures for protecting information per Part 6.4. | [18 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014-3 | R1. | Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. | 2022-06-16 |  | High | The Transmission Owner performed an initial risk assessment but did so after the date specified in the implementation plan for performing the initial risk assessment but less than or equal to two calendar months after that date; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 30 calendar months but less than or equal to 32 calendar months; OR The Transmission Owner that has not identified in its previous risk assessment any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 60 calendar months but less than or equal to 62 calendar months. | The Transmission Owner performed an initial risk assessment but did so more than two calendar months after the date specified in the implementation plan for performing the initial risk assessment but less than or equal to four calendar months after that date; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 32 calendar months but less than or equal to 34 calendar months; OR The Transmission Owner that has not identified in its previous risk assessment any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 62 calendar months but less than or equal to 64 calendar months. | The Transmission Owner performed an initial risk assessment but did so more than four calendar months after the date specified in the implementation plan for performing the initial risk assessment but less than or equal to six calendar months after that date; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 34 calendar months but less than or equal to 36 calendar months; OR The Transmission Owner that has not identified in its previous risk assessment any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after 64 calendar months but less than or equal to 66 calendar months; OR The Transmission Owner performed a risk assessment but failed to include Part 1.2. | The Transmission Owner performed an initial risk assessment but did so more than six calendar months after the date specified in the implementation plan for performing the initial risk assessment; OR The Transmission Owner failed to perform an initial risk assessment; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after more than 36 calendar months; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection failed to perform a risk assessment; OR The Transmission Owner that has not identified in its previous risk assessment any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after more than 66 calendar months; OR The Transmission Owner performed an initial risk assessment but did so more than six calendar months after the date specified in the implementation plan for performing the initial risk assessment; OR The Transmission Owner failed to perform an initial risk assessment; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after more than 36 calendar months; OR The Transmission Owner that has identified in its previous risk assessment one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection failed to perform a risk assessment; OR The Transmission Owner that has not identified in its previous risk assessment any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection performed a subsequent risk assessment but did so after more than 66 calendar months; OR The Transmission Owner that has not identified in its previous risk assessment any Transmission station and Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection failed to perform a subsequent risk assessment. | [18 empty] | TO
Mandatory Subject to Enforcement | CIP | CIP-014-3 | R2. | Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1. | 2022-06-16 |  | Medium | The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but did so in more than 90 calendar days but less than or equal to 100 calendar days following completion of Requirement R1; OR The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 and modified or documented the technical basis for not modifying its identification under Requirement R1 as required by Part 2.3 but did so more than 60 calendar days and less than or equal to 70 calendar days from completion of the third party verification. | The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but did so more than 100 calendar days but less than or equal to 110 calendar days following completion of Requirement R1; Or The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 and modified or documented the technical basis for not modifying its identification under Requirement R1 as required by Part 2.3 but did so more than 70 calendar days and less than or equal to 80 calendar days from completion of the third party verification. | The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but did so more than 110 calendar days but less than or equal to 120 calendar days following completion of Requirement R1; OR The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 and modified or documented the technical basis for not modifying its identification under Requirement R1 as required by Part 2.3 but did so more than 80 calendar days from completion of the third party verification; OR The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but failed to modify or document the technical basis for not modifying its identification under R1 as required by Part 2.3. | The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but did so more than 120 calendar days following completion of Requirement R1; OR The Transmission Owner failed to have an unaffiliated third party verify the risk assessment performed under Requirement R1; OR The Transmission Owner had an unaffiliated third party verify the risk assessment performed under Requirement R1 but failed to implement procedures for protecting information per Part 2.4. | [18 empty] | TO
Mandatory Subject to Enforcement | CIP | CIP-014-3 | R3. | For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2. | 2022-06-16 |  | Low | The Transmission Owner notified the Transmission Operator that operates the primary control center as specified in Requirement R3 but did so more than seven calendar days and less than or equal to nine calendar days following the completion of Requirement R2; OR The Transmission Owner notified the Transmission Operator that operates the primary control center of the removal from the identification in Requirement R1 but did so more than seven calendar days and less than or equal to nine calendar days following the verification or the subsequent risk assessment. | The Transmission Owner notified the Transmission Operator that operates the primary control center as specified in Requirement R3 but did so more than nine calendar days and less than or equal to 11 calendar days following the completion of Requirement R2; OR The Transmission Owner notified the Transmission Operator that operates the primary control center of the removal from the identification in Requirement R1 but did so more than nine calendar days and less than or equal to 11 calendar days following the verification or the subsequent risk assessment. | The Transmission Owner notified the Transmission Operator that operates the primary control center as specified in Requirement R3 but did so more than 11 calendar days and less than or equal to 13 calendar days following the completion of Requirement R2; OR The Transmission Owner notified the Transmission Operator that operates the primary control center of the removal from the identification in Requirement R1 but did so more than 11 calendar days and less than or equal to 13 calendar days following the verification or the subsequent risk assessment. | The Transmission Owner notified the Transmission Operator that operates the primary control center as specified in Requirement R3 but did so more than 13 calendar days following the completion of Requirement R2; OR The Transmission Owner failed to notify the Transmission Operator that it operates a control center identified in Requirement R1; OR The Transmission Owner notified the Transmission Operator that operates the primary control center of the removal from the identification in Requirement R1 but did so more than 13 calendar days following the verification or the subsequent risk assessment. OR The Transmission Owner failed to notify the Transmission Operator that operates the primary control center of the removal from the identification in Requirement R1. | [18 empty] | TO
Mandatory Subject to Enforcement | CIP | CIP-014-3 | R4. | Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: | 2022-06-16 |  | Medium | N/A | The Responsible Entity conducted an evaluation of the potential physical threats and vulnerabilities to each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but failed to consider one of Parts 4.1 through 4.3 in the evaluation. | The Responsible Entity conducted an evaluation of the potential physical threats and vulnerabilities to each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but failed to consider two of Parts 4.1 through 4.3 in the evaluation. | The Responsible Entity failed to conduct an evaluation of the potential physical threats and vulnerabilities to each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1; OR The Responsible Entity conducted an evaluation of the potential physical threats and vulnerabilities to each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but failed to consider Parts 4.1 through 4.3. | [18 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014-3 | R5. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: | 2022-06-16 |  | High | The Responsible Entity developed and implemented a documented physical security plan(s) that covers each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but did so more than 120 calendar days but less than or equal to 130 calendar days after completing Requirement R2; OR The Responsible Entity developed and implemented a documented physical security plan(s) that covers its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2 but failed to include one of Parts 5.1 through 5.4 in the plan. | The Responsible Entity developed and implemented a documented physical security plan(s) that covers each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but did so more than 130 calendar days but less than or equal to 140 calendar days after completing Requirement R2; OR The Responsible Entity developed and implemented a documented physical security plan(s) that covers its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2 but failed to include two of Parts 5.1 through 5.4 in the plan. | The Responsible Entity developed and implemented a documented physical security plan(s) that covers each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but did so more than 140 calendar days but less than or equal to 150 calendar days after completing Requirement R2; OR The Responsible Entity developed and implemented a documented physical security plan(s) that covers its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2 but failed to include three of Parts 5.1 through 5.4 in the plan. | The Responsible Entity developed and implemented a documented physical security plan(s) that covers each of its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 but did so more than 150 calendar days after completing the verification in Requirement R2; OR The Responsible Entity failed to develop and implement a documented physical security plan(s) that covers its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. OR The Responsible Entity developed and implemented a documented physical security plan(s) that covers its Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement 2 but failed to include Parts 5.1 through 5.4 in the plan. | [18 empty] | TO | TOP
Mandatory Subject to Enforcement | CIP | CIP-014-3 | R6. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. | 2022-06-16 |  | Medium | The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 but did so in more than 90 calendar days but less than or equal to 100 calendar days; OR The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 and modified or documented the reason for not modifying the security plan(s) as specified in Part 6.3 but did so more than 60 calendar days and less than or equal to 70 calendar days following completion of the third party review. | The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 but did so in more than 100 calendar days but less than or equal to 110 calendar days; OR The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 and modified or documented the reason for not modifying the security plan(s) as specified in Part 6.3 but did so more than 70 calendar days and less than or equal to 80 calendar days following completion of the third party review. | The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 but did so more than 110 calendar days but less than or equal to 120 calendar days; OR The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 and modified or documented the reason for not modifying the security plan(s) as specified in Part 6.3 but did so more than 80 calendar days following completion of the third party review; OR The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 but did not document the reason for not modifying the security plan(s) as specified in Part 6.3. | The Responsible Entity failed to have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 in more than 120 calendar days; OR The Responsible Entity failed to have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5; OR The Responsible Entity had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 but failed to implement procedures for protecting information per Part 6.4. | [18 empty] | TO | TOP
Inactive | COM | COM-001-0 | R1. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall provide adequate and reliable telecommunications facilities for the exchange of Interconnection and operating information: |  | 2007-01-01 | [6 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-0 | R2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall manage, alarm, test and/or actively monitor vital telecommunications facilities. Special attention shall be given to emergency telecommunications facilities and equipment not used for routine communications. |  | 2007-01-01 | [6 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-0 | R3. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall provide a means to coordinate telecommunications among their respective areas. This coordination shall include the ability to investigate and recommend solutions to telecommunications problems within the area and with other areas. |  | 2007-01-01 | [6 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-0 | R4. | Unless agreed to otherwise, each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use English as the language for all communications between and among operating personnel responsible for the real-time generation control and operation of the interconnected Bulk Electric System. Transmission Operators and Balancing Authorities may use an alternate language for internal operations. |  | 2007-01-01 | [6 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-0 | R5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have written operating instructions and procedures to enable continued operation of the system during the loss of telecommunications facilities. |  | 2007-01-01 | [6 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-0 | R6. | Each NERCNet User Organization shall adhere to the requirements in Attachment 1-COM001-0, “NERCNet Security Policy.” |  | 2007-01-01 | [6 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-1 | R1. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide adequate and reliable telecommunications facilities for the exchange of Interconnection and operating information: | 2007-06-18 | 2009-05-12 | High | [5 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-1 | R2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall manage, alarm, test and/or actively monitor vital telecommunications facilities. Special attention shall be given to emergency telecommunications facilities and equipment not used for routine communications. | 2007-06-18 | 2009-05-12 | Medium | [5 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-1 | R3. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall provide a means to coordinate telecommunications among their respective areas. This coordination shall include the ability to investigate and recommend solutions to telecommunications problems within the area and with other areas. | 2007-06-18 | 2009-05-12 | Low | [5 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-1 | R4. | Unless agreed to otherwise, each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use English as the language for all communications between and among operating personnel responsible for the real-time generation control and operation of the interconnected Bulk Electric System. Transmission Operators and Balancing Authorities may use an alternate language for internal operations. | 2007-06-18 | 2009-05-12 | Medium | [5 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-1 | R5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have written operating instructions and procedures to enable continued operation of the system during the loss of telecommunications facilities. | 2007-06-18 | 2009-05-12 | Low | [5 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-1 | R6. | Each NERCNet User Organization shall adhere to the requirements in Attachment 1-COM-001-0, “NERCNet Security Policy.” | 2007-06-18 | 2009-05-12 | Low | [17 empty] | RE
Inactive | COM | COM-001-1.1 | R1. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall provide adequate and reliable telecommunications facilities for the exchange of Interconnection and operating information: | 2009-05-13 | 2015-09-30 | High | The responsible entity's telecommunications is not redundant or diversely routed as applicable by other operating entities for the exchange of interconnection or operating data. | The responsible entity's telecommunications is not redundant or diversely routed as applicable and has failed to establish telecommunications internally for the exchange of interconnection or operating data needed to maintain BES reliability. | The responsible entity's telecommunications is not redundant or diversely routed as applicable and has failed to establish telecommunications internally and with other Reliability Coordinators, Transmission Operators, or Balancing Authorities for the exch | The responsible entity's telecommunications is not redundant or diversely routed as applicable and has failed to establish telecommunications internally and with both other and its Reliability Coordinators, Transmission Operators, or Balancing Authorities |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-1.1 | R2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall manage, alarm, test and/or actively monitor vital telecommunications facilities. Special attention shall be given to emergency telecommunications facilities and equipment not used for routine communications. | 2009-05-13 | 2015-09-30 | Medium |  | The responsible entity has failed to manage, alarm, and test or actively monitor its emergency telecommunications facilities. | The responsible entity has failed to manage, alarm, and test or actively monitor its primary telecommunications facilities. | The responsible entity has failed to manage, alarm, and test or actively monitor its primary and emergency telecommunications facilities. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-1.1 | R3. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall provide a means to coordinate telecommunications among their respective areas. This coordination shall include the ability to investigate and recommend solutions to telecommunications problems within the area and with other areas. | 2009-05-13 | 2015-09-30 | Low |  |  | The responsible entity failed to assist in the investigation and recommending of solutions to telecommunications problems within the area and with other areas. | The responsible entity failed to provide a means to coordinate telecommunications among their respective areas including assisting in the investigation and recommending of solutions to telecommunications problems within the area and with other areas. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-1.1 | R4. | Unless agreed to otherwise, each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use English as the language for all communications between and among operating personnel responsible for the real-time generation control and operation of the interconnected Bulk Electric System. Transmission Operators and Balancing Authorities may use an alternate language for internal operations. | 2009-05-13 | 2016-06-30 | Medium |  |  |  | If using a language other than English, the responsible entity failed to provide documentation of agreement to use a language other than English for all communications between and among operating personnel responsible for the real-time generation control |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-1.1 | R5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have written operating instructions and procedures to enable continued operation of the system during the loss of telecommunications facilities. | 2009-05-13 | 2015-09-30 | Low |  |  |  | The responsible entity did not have written operating instructions and procedures to enable continued operation of the system during the loss of telecommunications facilities. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-1.1 | R6. | Each NERCNet User Organization shall adhere to the requirements in Attachment 1-COM-001, “NERCNet Security Policy.” | 2009-05-13 | 2015-09-30 | Low | The NERCNet User Organization failed to adhere to less than 25% of the requirements listed in COM-001-0, Attachment 1, "NERCNet Security Policy". | The NERCNet User Organization failed to adhere to 25% or more but less than 50% of the requirements listed in COM-001-0, Attachment 1, "NERCNet Security Policy". | The NERCNet User Organization failed to adhere to 50% or more but less than 75% of the requirements listed in COM-001-0, Attachment 1, "NERCNet Security Policy". | The NERCNet User Organization failed to adhere to 75% or more of the requirements listed in COM-001-0, Attachment 1, "NERCNet Security Policy". |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-2 | R1. | Each Reliability Coordinator shall have Interpersonal Communication capability with the following entities (unless the Reliability Coordinator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | 2015-10-01 | 2015-11-12 | High | N/A | N/A | The Reliability Coordinator failed to have Interpersonal Communication capability with one of the entities listed in Requirement R1, Parts 1.1 or 1.2, except when the Reliability Coordinator detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. | The Reliability Coordinator failed to have Interpersonal Communication capability with two or more of the entities listed in Requirement R1, Parts 1.1 or 1.2, except when the Reliability Coordinator detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. | [12 empty] | RC
Inactive | COM | COM-001-2 | R2. | R2. Each Reliability Coordinator shall designate an Alternative Interpersonal Communication capability with the following entities: | 2015-10-01 | 2015-11-12 | High | N/A | N/A | The Reliability Coordinator failed to designate Alternative Interpersonal Communication capability with one of the entities listed in Requirement R2, Parts 2.1 or 2.2. | The Reliability Coordinator failed to designate Alternative Interpersonal Communication capability with two or more of the entities listed in Requirement R2, Parts 2.1 or 2.2. | [12 empty] | RC
Inactive | COM | COM-001-2 | R3. | R3. Each Transmission Operator shall have Interpersonal Communication capability with the following entities (unless the Transmission Operator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | 2015-10-01 | 2015-11-12 | High | N/A | N/A | The Transmission Operator failed to have Interpersonal Communication capability with one of the entities listed in Requirement R3, Parts 3.1, 3.2, 3.3, 3.4, 3.5, or 3.6, except when the Transmission Operator detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. | The Transmission Operator failed to have Interpersonal Communication capability with two or more of the entities listed in Requirement R3, Parts 3.1, 3.2, 3.3, 3.4, 3.5, or 3.6, except when the Transmission Operator detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. | [19 empty] | TOP
Inactive | COM | COM-001-2 | R4. | Each Transmission Operator shall designate an Alternative Interpersonal Communication capability with the following entities: | 2015-10-01 | 2015-11-12 | High | N/A | N/A | The Transmission Operator failed to designate Alternative Interpersonal Communication capability with one of the entities listed in Requirement R4, Parts 4.1, 4.2, 4.3, or 4.4. | The Transmission Operator failed to designate Alternative Interpersonal Communication capability with two or more of the entities listed in Requirement R4, Parts 4.1, 4.2, 4.3, or 4.4. | [19 empty] | TOP
Inactive | COM | COM-001-2 | R5. | R5. Each Balancing Authority shall have Interpersonal Communication capability with the following entities (unless the Balancing Authority detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | 2015-10-01 | 2015-11-12 | High | N/A | N/A | The Balancing Authority failed to have Interpersonal Communication capability with one of the entities listed in Requirement R5, Parts 5.1, 5.2, 5.3, 5.4, or 5.5, except when the Balancing Authority detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. | The Balancing Authority failed to have Interpersonal Communication capability with two or more of the entities listed in Requirement R5, Parts 5.1, 5.2, 5.3, 5.4, or 5.5, except when the Balancing Authority detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. |  | BA
Inactive | COM | COM-001-2 | R6. | Each Balancing Authority shall designate an Alternative Interpersonal Communication capability with the following entities: | 2015-10-01 | 2015-11-12 | High | N/A | N/A | The Balancing Authority failed to designate Alternative Interpersonal Communication capability with one of the entities listed in Requirement R6, Parts 6.1, 6.2, or 6.3. | The Balancing Authority failed to designate Alternative Interpersonal Communication capability with two or more of the entities listed in Requirement R6, Parts 6.1, 6.2, or 6.3. |  | BA
Inactive | COM | COM-001-2 | R7. | Each Distribution Provider shall have Interpersonal Communication capability with the following entities (unless the Distribution Provider detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | 2015-10-01 | 2015-11-12 | Medium | N/A | N/A | The Distribution Provider failed to have Interpersonal Communication capability with one of the entities listed in Requirement R7, Parts 7.1 or 7.2, except when the Distribution Provider detected a failure of its Interpersonal Communication capability in accordance with Requirement R11. | The Distribution Provider failed to have Interpersonal Communication capability with two or more of the entities listed in Requirement R7, Parts 7.1 or 7.2, except when the Distribution Provider detected a failure of its Interpersonal Communication capability in accordance with Requirement R11. |  |  | DP
Inactive | COM | COM-001-2 | R8. | R8. Each Generator Operator shall have Interpersonal Communication capability with the following entities (unless the Generator Operator detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | 2015-10-01 | 2015-11-12 | High | N/A | N/A | The Generator Operator failed to have Interpersonal Communication capability with one of the entities listed in Requirement R8, Parts 8.1 or 8.2, except when a Generator Operator detected a failure of its Interpersonal Communication capability in accordance with Requirement R11. | The Generator Operator failed to have Interpersonal Communication capability with two or more of the entities listed in Requirement R8, Parts 8.1 or 8.2, except when a Generator Operator detected a failure of its Interpersonal Communication capability in accordance with Requirement R11. | [6 empty] | GOP
Inactive | COM | COM-001-2 | R9. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall test its Alternative Interpersonal Communication capability at least once each calendar month. If the test is unsuccessful, the responsible entity shall initiate action to repair or designate a replacement Alternative Interpersonal Communication capability within 2 hours. | 2015-10-01 | 2015-11-12 | Medium | The Reliability Coordinator, Transmission Operator, or Balancing Authority tested the Alternative Interpersonal Communication capability but failed to initiate action to repair or designate a replacement Alternative Interpersonal Communication in more than 2 hours and less than or equal to 4 hours upon an unsuccessful test. | The Reliability Coordinator, Transmission Operator, or Balancing Authority tested the Alternative Interpersonal Communication capability but failed to initiate action to repair or designate a replacement Alternative Interpersonal Communication in more than 4 hours and less than or equal to 6 hours upon an unsuccessful test. | The Reliability Coordinator, Transmission Operator, or Balancing Authority tested the Alternative Interpersonal Communication capability but failed to initiate action to repair or designate a replacement Alternative Interpersonal Communication in more than 6 hours and less than or equal to 8 hours upon an unsuccessful test. | The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to test the Alternative Interpersonal Communication capability once each calendar month. OR The Reliability Coordinator, Transmission Operator, or Balancing Authority tested the Alternative Interpersonal Communication capability but failed to initiate action to repair or designate a replacement Alternative Interpersonal Communication in more than 8 hours upon an unsuccessful test. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-2 | R10. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall notify entities as identified in Requirements R1, R3, and R5, respectively within 60 minutes of the detection of a failure of its Interpersonal Communication capability that lasts 30 minutes or longer. | 2015-06-22 | 2015-11-12 | Medium | The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to notify the entities identified in Requirements R1, R3, and R5, respectively upon the detection of a failure of its Interpersonal Communication capability in more than 60 minutes but less than or equal to 70 minutes. | The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to notify the entities identified in Requirements R1, R3, and R5, respectively upon the detection of a failure of its Interpersonal Communication capability in more than 70 minutes but less than or equal to 80 minutes. | The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to notify the entities identified in Requirements R1, R3, and R5, respectively upon the detection of a failure of its Interpersonal Communication capability in more than 80 minutes but less than or equal to 90 minutes. | The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to notify the entities identified in Requirements R1, R3, and R5, respectively upon the detection of a failure of its Interpersonal Communication capability in more than 90 minutes. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-2 | R11. | Each Distribution Provider and Generator Operator that detects a failure of its Interpersonal Communication capability shall consult each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of its Interpersonal Communication capability. | 2015-10-01 | 2015-11-12 | Medium | N/A | N/A | N/A | The Distribution Provider or Generator Operator that detected a failure of its Interpersonal Communication capability failed to consult with each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of the Interpersonal Communication capability. |  |  | DP |  |  |  | GOP
Inactive | COM | COM-001-2.1 | R1. | Each Reliability Coordinator shall have Interpersonal Communication capability with the following entities (unless the Reliability Coordinator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | 2015-11-13 | 2017-09-30 | High | N/A | N/A | The Reliability Coordinator failed to have Interpersonal Communication capability with one of the entities listed in Requirement R1, Parts 1.1 or 1.2, except when the Reliability Coordinator detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. | The Reliability Coordinator failed to have Interpersonal Communication capability with two or more of the entities listed in Requirement R1, Parts 1.1 or 1.2, except when the Reliability Coordinator detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. | [12 empty] | RC
Inactive | COM | COM-001-2.1 | R2. | Each Reliability Coordinator shall designate an Alternative Interpersonal Communication capability with the following entities: | 2015-11-13 | 2017-09-30 | High | N/A | N/A | The Reliability Coordinator failed to designate Alternative Interpersonal Communication capability with one of the entities listed in Requirement R2, Parts 2.1 or 2.2. | The Reliability Coordinator failed to designate Alternative Interpersonal Communication capability with two or more of the entities listed in Requirement R2, Parts 2.1 or 2.2. | [12 empty] | RC
Inactive | COM | COM-001-2.1 | R3. | Each Transmission Operator shall have Interpersonal Communication capability with the following entities (unless the Transmission Operator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | 2015-11-13 | 2017-09-30 | High | N/A | N/A | The Transmission Operator failed to have Interpersonal Communication capability with one of the entities listed in Requirement R3, Parts 3.1, 3.2, 3.3, 3.4, 3.5, or 3.6, except when the Transmission Operator detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. | The Transmission Operator failed to have Interpersonal Communication capability with two or more of the entities listed in Requirement R3, Parts 3.1, 3.2, 3.3, 3.4, 3.5, or 3.6, except when the Transmission Operator detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. | [19 empty] | TOP
Inactive | COM | COM-001-2.1 | R4. | Each Transmission Operator shall designate an Alternative Interpersonal Communication capability with the following entities: | 2015-11-13 | 2017-09-30 | High | N/A | N/A | The Transmission Operator failed to designate Alternative Interpersonal Communication capability with one of the entities listed in Requirement R4, Parts 4.1, 4.2, 4.3, or 4.4. | The Transmission Operator failed to designate Alternative Interpersonal Communication capability with two or more of the entities listed in Requirement R4, Parts 4.1, 4.2, 4.3, or 4.4. | [19 empty] | TOP
Inactive | COM | COM-001-2.1 | R5. | Each Balancing Authority shall have Interpersonal Communication capability with the following entities (unless the Balancing Authority detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | 2015-11-13 | 2017-09-30 | High | N/A | N/A | The Balancing Authority failed to have Interpersonal Communication capability with one of the entities listed in Requirement R5, Parts 5.1, 5.2, 5.3, 5.4, or 5.5, except when the Balancing Authority detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. | The Balancing Authority failed to have Interpersonal Communication capability with two or more of the entities listed in Requirement R5, Parts 5.1, 5.2, 5.3, 5.4, or 5.5, except when the Balancing Authority detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. |  | BA
Inactive | COM | COM-001-2.1 | R6. | Each Balancing Authority shall designate an Alternative Interpersonal Communication capability with the following entities: | 2015-11-13 | 2017-09-30 | High | N/A | N/A | The Balancing Authority failed to designate Alternative Interpersonal Communication capability with one of the entities listed in Requirement R6, Parts 6.1, 6.2, or 6.3. | The Balancing Authority failed to designate Alternative Interpersonal Communication capability with two or more of the entities listed in Requirement R6, Parts 6.1, 6.2, or 6.3. |  | BA
Inactive | COM | COM-001-2.1 | R7. | Each Distribution Provider shall have Interpersonal Communication capability with the following entities (unless the Distribution Provider detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | 2015-11-13 | 2017-09-30 | Medium | N/A | N/A | The Distribution Provider failed to have Interpersonal Communication capability with one of the entities listed in Requirement R7, Parts 7.1 or 7.2, except when the Distribution Provider detected a failure of its Interpersonal Communication capability in accordance with Requirement R11. | The Distribution Provider failed to have Interpersonal Communication capability with two or more of the entities listed in Requirement R7, Parts 7.1 or 7.2, except when the Distribution Provider detected a failure of its Interpersonal Communication capability in accordance with Requirement R11. |  |  | DP
Inactive | COM | COM-001-2.1 | R8. | Each Generator Operator shall have Interpersonal Communication capability with the following entities (unless the Generator Operator detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | 2015-11-13 | 2017-09-30 | High | N/A | N/A | The Generator Operator failed to have Interpersonal Communication capability with one of the entities listed in Requirement R8, Parts 8.1 or 8.2, except when a Generator Operator detected a failure of its Interpersonal Communication capability in accordance with Requirement R11. | The Generator Operator failed to have Interpersonal Communication capability with two or more of the entities listed in Requirement R8, Parts 8.1 or 8.2, except when a Generator Operator detected a failure of its Interpersonal Communication capability in accordance with Requirement R11. | [6 empty] | GOP
Inactive | COM | COM-001-2.1 | R9. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall test its Alternative Interpersonal Communication capability at least once each calendar month. If the test is unsuccessful, the responsible entity shall initiate action to repair or designate a replacement Alternative Interpersonal Communication capability within 2 hours. | 2015-11-13 | 2017-09-30 | Medium | The Reliability Coordinator, Transmission Operator, or Balancing Authority tested the Alternative Interpersonal Communication capability but failed to initiate action to repair or designate a replacement Alternative Interpersonal Communication in more than 2 hours and less than or equal to 4 hours upon an unsuccessful test. | The Reliability Coordinator, Transmission Operator, or Balancing Authority tested the Alternative Interpersonal Communication capability but failed to initiate action to repair or designate a replacement Alternative Interpersonal Communication in more than 4 hours and less than or equal to 6 hours upon an unsuccessful test. | The Reliability Coordinator, Transmission Operator, or Balancing Authority tested the Alternative Interpersonal Communication capability but failed to initiate action to repair or designate a replacement Alternative Interpersonal Communication in more than 6 hours and less than or equal to 8 hours upon an unsuccessful test. | The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to test the Alternative Interpersonal Communication capability once each calendar month. OR The Reliability Coordinator, Transmission Operator, or Balancing Authority tested the Alternative Interpersonal Communication capability but failed to initiate action to repair or designate a replacement Alternative Interpersonal Communication in more than 8 hours upon an unsuccessful test. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-2.1 | R10. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall notify entities as identified in Requirements R1, R3, and R5, respectively within 60 minutes of the detection of a failure of its Interpersonal Communication capability that lasts 30 minutes or longer. | 2015-11-13 | 2017-09-30 | Medium | The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to notify the entities identified in Requirements R1, R3, and R5, respectively upon the detection of a failure of its Interpersonal Communication capability in more than 60 minutes but less than or equal to 70 minutes. | The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to notify the entities identified in Requirements R1, R3, and R5, respectively upon the detection of a failure of its Interpersonal Communication capability in more than 70 minutes but less than or equal to 80 minutes. | The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to notify the entities identified in Requirements R1, R3, and R5, respectively upon the detection of a failure of its Interpersonal Communication capability in more than 80 minutes but less than or equal to 90 minutes. | The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to notify the entities identified in Requirements R1, R3, and R5, respectively upon the detection of a failure of its Interpersonal Communication capability in more than 90 minutes. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-001-2.1 | R11. | Each Distribution Provider and Generator Operator that detects a failure of its Interpersonal Communication capability shall consult each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of its Interpersonal Communication capability. | 2015-11-13 | 2017-09-30 | Medium | N/A | N/A | N/A | The Distribution Provider or Generator Operator that detected a failure of its Interpersonal Communication capability failed to consult with each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of the Interpersonal Communication capability. |  |  | DP |  |  |  | GOP
Mandatory Subject to Enforcement | COM | COM-001-3 | R1. | Each Reliability Coordinator shall have Interpersonal Communication capability with the following entities (unless the Reliability Coordinator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | 2017-10-01 |  | High | N/A | N/A | The Reliability Coordinator failed to have Interpersonal Communication capability with one of the entities listed in Requirement R1, Parts 1.1 or 1.2, except when the Reliability Coordinator detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. | The Reliability Coordinator failed to have Interpersonal Communication capability with two or more of the entities listed in Requirement R1, Parts 1.1 or 1.2, except when the Reliability Coordinator detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. | [12 empty] | RC
Mandatory Subject to Enforcement | COM | COM-001-3 | R2. | Each Reliability Coordinator shall designate an Alternative Interpersonal Communication capability with the following entities: | 2017-10-01 |  | High | N/A | N/A | The Reliability Coordinator failed to designate Alternative Interpersonal Communication capability with one of the entities listed in Requirement R2, Parts 2.1 or 2.2. | The Reliability Coordinator failed to designate Alternative Interpersonal Communication capability with two or more of the entities listed in Requirement R2, Parts 2.1 or 2.2. | [12 empty] | RC
Mandatory Subject to Enforcement | COM | COM-001-3 | R3. | Each Transmission Operator shall have Interpersonal Communication capability with the following entities (unless the Transmission Operator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | 2017-10-01 |  | High | N/A | N/A | The Transmission Operator failed to have Interpersonal Communication capability with one of the entities listed in Requirement R3, Parts 3.1, 3.2, 3.3, 3.4, 3.5, or 3.6, except when the Transmission Operator detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. | The Transmission Operator failed to have Interpersonal Communication capability with two or more of the entities listed in Requirement R3, Parts 3.1, 3.2, 3.3, 3.4, 3.5, or 3.6, except when the Transmission Operator detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. | [19 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001-3 | R4. | Each Transmission Operator shall designate an Alternative Interpersonal Communication capability with the following entities: | 2017-10-01 |  | High | N/A | N/A | The Transmission Operator failed to designate Alternative Interpersonal Communication capability with one of the entities listed in Requirement R4, Parts 4.1, 4.2, 4.3, or 4.4. | The Transmission Operator failed to designate Alternative Interpersonal Communication capability with two or more of the entities listed in Requirement R4, Parts 4.1, 4.2, 4.3, or 4.4. | [19 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001-3 | R5. | Each Balancing Authority shall have Interpersonal Communication capability with the following entities (unless the Balancing Authority detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | 2017-10-01 |  | High | N/A | N/A | The Balancing Authority failed to have Interpersonal Communication capability with one of the entities listed in Requirement R5, Parts 5.1, 5.2, 5.3, 5.4, or 5.5, except when the Balancing Authority detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. | The Balancing Authority failed to have Interpersonal Communication capability with two or more of the entities listed in Requirement R5, Parts 5.1, 5.2, 5.3, 5.4, or 5.5, except when the Balancing Authority detected a failure of its Interpersonal Communication capability in accordance with Requirement R10. |  | BA
Mandatory Subject to Enforcement | COM | COM-001-3 | R6. | Each Balancing Authority shall designate an Alternative Interpersonal Communication capability with the following entities: | 2017-10-01 |  | High | N/A | N/A | The Balancing Authority failed to designate Alternative Interpersonal Communication capability with one of the entities listed in Requirement R6, Parts 6.1, 6.2, or 6.3. | The Balancing Authority failed to designate Alternative Interpersonal Communication capability with two or more of the entities listed in Requirement R6, Parts 6.1, 6.2, or 6.3. |  | BA
Mandatory Subject to Enforcement | COM | COM-001-3 | R7. | Each Distribution Provider shall have Interpersonal Communication capability with the following entities (unless the Distribution Provider detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | 2017-10-01 |  | Medium | N/A | N/A | The Distribution Provider failed to have Interpersonal Communication capability with one of the entities listed in Requirement R7, Parts 7.1 or 7.2, except when the Distribution Provider detected a failure of its Interpersonal Communication capability in accordance with Requirement R11. | The Distribution Provider failed to have Interpersonal Communication capability with two or more of the entities listed in Requirement R7, Parts 7.1 or 7.2, except when the Distribution Provider detected a failure of its Interpersonal Communication capability in accordance with Requirement R11. |  |  | DP
Mandatory Subject to Enforcement | COM | COM-001-3 | R8. | Each Generator Operator shall have Interpersonal Communication capability with the following entities (unless the Generator Operator detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | 2017-10-01 |  | High | N/A | N/A | The Generator Operator failed to have Interpersonal Communication capability with one of the entities listed in Requirement R8, Parts 8.1 or 8.2, except when a Generator Operator detected a failure of its Interpersonal Communication capability in accordance with Requirement R11. | The Generator Operator failed to have Interpersonal Communication capability with two or more of the entities listed in Requirement R8, Parts 8.1 or 8.2, except when a Generator Operator detected a failure of its Interpersonal Communication capability in accordance with Requirement R11. | [6 empty] | GOP
Mandatory Subject to Enforcement | COM | COM-001-3 | R9. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall test its Alternative Interpersonal Communication capability at least once each calendar month. If the test is unsuccessful, the responsible entity shall initiate action to repair or designate a replacement Alternative Interpersonal Communication capability within 2 hours. | 2017-10-01 |  | Medium | The Reliability Coordinator, Transmission Operator, or Balancing Authority tested the Alternative Interpersonal Communication capability but failed to initiate action to repair or designate a replacement Alternative Interpersonal Communication in more than 2 hours and less than or equal to 4 hours upon an unsuccessful test. | The Reliability Coordinator, Transmission Operator, or Balancing Authority tested the Alternative Interpersonal Communication capability but failed to initiate action to repair or designate a replacement Alternative Interpersonal Communication in more than 4 hours and less than or equal to 6 hours upon an unsuccessful test. | The Reliability Coordinator, Transmission Operator, or Balancing Authority tested the Alternative Interpersonal Communication capability but failed to initiate action to repair or designate a replacement Alternative Interpersonal Communication in more than 6 hours and less than or equal to 8 hours upon an unsuccessful test. | The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to test the Alternative Interpersonal Communication capability once each calendar month. OR The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to test the Alternative Interpersonal Communication capability once each calendar month. OR The Reliability Coordinator, Transmission Operator, or Balancing Authority tested the Alternative Interpersonal Communication capability but failed to initiate action to repair or designate a replacement Alternative Interpersonal Communication in more than 8 hours upon an unsuccessful test. |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001-3 | R10. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall notify entities as identified in Requirements R1, R3, and R5, respectively within 60 minutes of the detection of a failure of its Interpersonal Communication capability that lasts 30 minutes or longer. | 2017-10-01 |  | Medium | The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to notify the entities identified in Requirements R1, R3, and R5, respectively upon the detection of a failure of its Interpersonal Communication capability in more than 60 minutes but less than or equal to 70 minutes. | The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to notify the entities identified in Requirements R1, R3, and R5, respectively upon the detection of a failure of its Interpersonal Communication capability in more than 70 minutes but less than or equal to 80 minutes. | The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to notify the entities identified in Requirements R1, R3, and R5, respectively upon the detection of a failure of its Interpersonal Communication capability in more than 80 minutes but less than or equal to 90 minutes. | The Reliability Coordinator, Transmission Operator, or Balancing Authority failed to notify the entities identified in Requirements R1, R3, and R5, respectively upon the detection of a failure of its Interpersonal Communication capability in more than 90 minutes. |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001-3 | R11. | Each Distribution Provider and Generator Operator that detects a failure of its Interpersonal Communication capability shall consult each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of its Interpersonal Communication capability. | 2017-10-01 |  | Medium | N/A | N/A | N/A | The Distribution Provider or Generator Operator that detected a failure of its Interpersonal Communication capability failed to consult with each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of the Interpersonal Communication capability. |  |  | DP |  |  |  | GOP
Mandatory Subject to Enforcement | COM | COM-001-3 | R12. | Each Reliability Coordinator, Transmission Operator, Generator Operator, and Balancing Authority shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between Control Centers within the same functional entity, and/or between a Control Center and field personnel. | 2017-10-01 |  | High | N/A | N/A | N/A | The Reliability Coordinator, Transmission Operator, Generator Operator, or Balancing Authority failed to have internal Interpersonal Communication capability for the exchange of operating information. |  | BA |  |  |  |  | GOP | [5 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-001-3 | R13. | Each Distribution Provider shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between control centers within the same functional entity, and/or between a control center and field personnel. | 2017-10-01 |  | Medium | N/A | N/A | N/A | The Distribution Provider failed to have internal Interpersonal Communication capability for the exchange of operating information. |  |  | DP
Inactive | COM | COM-002-0 | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall have communications (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators. Such communications shall be staffed and available for addressing a real-time emergency condition. |  | 2006-11-01 | [6 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | COM | COM-002-0 | R2. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators through predetermined communication paths of any condition that could threaten the reliability of its area or when firm load shedding is anticipated. The following information shall be conveyed to others in the Interconnection via an Interconnection-wide telecommunications system: |  | 2006-11-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | COM | COM-002-0 | R3. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner; shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |  | 2006-11-01 | [6 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-002-1 | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall have communications (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators. Such communications shall be staffed and available for addressing a real-time emergency condition. |  | 2007-01-01 | [6 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | COM | COM-002-1 | R2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner; shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |  | 2007-01-01 | [6 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-002-2 | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall have communications (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators. Such communications shall be staffed and available for addressing a real-time emergency condition. | 2007-06-18 | 2016-06-30 | High | [5 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | COM | COM-002-2 | R2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner; shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. | 2007-06-18 | 2016-06-30 | Medium | [5 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-002-2a | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall have communications (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators. Such communications shall be staffed and available for addressing a real-time emergency condition. |  | 2016-06-30 | High |  | The responsible entity did not have data links with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators. | The responsible entity did not staff the communications (voice and data links) on a 24 hour basis. | The responsible entity failed to have communications (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators. |  | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | COM | COM-002-2a | R2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner; shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |  | 2016-06-30 | Medium |  | The responsible entity provided a clear directive in a clear, concise and definitive manner and required the recipient to repeat the directive, but did not acknowledge the recipient was correct in the repeated directive. | The responsible entity provided a clear directive in a clear, concise and definitive manner, but did not require the recipient to repeat the directive. | The responsible entity failed to provide a clear directive in a clear, concise and difinitive manner when required. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-002-3 | R1. | When a Reliability Coordinator, Transmission Operator, or Balancing Authority requires actions to be executed as a Reliability Directive, the Reliability Coordinator, Transmission Operator, or Balancing Authority shall identify the action as a Reliability Directive to the recipient. |  | 2016-06-30 | High | N/A | N/A | N/A | The Reliability Coordinator, Transmission Operator, or Balancing Authority that required actions to be executed as a Reliability Directive failed to identify the action as a Reliability Directive to the recipient. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | COM | COM-002-3 | R2. | Each Balancing Authority, Transmission Operator, Generator Operator, and Distribution Provider that is the recipient of a Reliability Directive shall repeat, restate, rephrase, or recapitulate the Reliability Directive. |  | 2016-06-30 | High | N/A | N/A | N/A | The Transmission Operator, Generator Operator, or Distribution Provider that was the recipient of a Reliability Directive failed to repeat, restate, rephrase, or recapitulate the Reliability Directive. |  | BA | DP |  |  |  | GOP | [12 empty] | TOP
Inactive | COM | COM-002-3 | R3. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority that issues a Reliability Directive shall either: • Confirm that the response from the recipient of the Reliability Directive (in accordance with Requirement R2) was accurate, or • Reissue the Reliability Directive to resolve a misunderstanding. |  | 2016-06-30 | High | N/A | N/A | The Reliability Coordinator, Transmission Operator, or Balancing Authority issued a Reliability Directive, but did not confirm that the response from the recipient of the Reliability Directive (in accordance with Requirement R2) was accurate. | The Reliability Coordinator, Transmission Operator, or Balancing Authority issued a Reliability Directive and failed to reissue the Reliability Directive to resolve a misunderstanding when the recipient did not repeat the Reliability Directive accurately. |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002-4 | R1. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall develop documented communications protocols for its operating personnel that issue and receive Operating Instructions. The protocols shall, at a minimum:[Please see the standard for more information] | 2016-07-01 |  | Low | The responsible entity did not specify the instances that require time identification when issuing an oral or written Operating Instruction and the format for that time identification, as required in Requirement R1, Part 1.5 OR The responsible entity did not specify the nomenclature for Transmission interface Elements and Transmission interface Facilities when issuing an oral or written Operating Instruction, as required in Requirement R1, Part 1.6. | The responsible entity did not require the issuer and receiver of an oral or written Operating Instruction to use the English language, unless agreed to otherwise, as required in Requirement R1, Part 1.1. An alternate language may be used for internal operations. | The responsible entity did not include Requirement R1, Part 1.4 in its documented communication protocols. | The responsible entity did not include Requirement R1, Part 1.2 in its documented communications protocols OR The responsible entity did not include Requirement R1, Part 1.3 in its documented communications protocols OR The responsible entity did not develop any documented communications protocols as required in Requirement R1. |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002-4 | R2. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall conduct initial training for each of its operating personnel responsible for the Real-time operation of the interconnected Bulk Electric System on the documented communications protocols developed in Requirement R1 prior to that individual operator issuing an Operating Instruction. | 2016-07-01 |  | Low | N/A | N/A | An individual operator responsible for the Real-time operation of the interconnected Bulk Electric System at the responsible entity issued an Operating Instruction, prior to being trained on the documented communications protocols developed in Requirement R1. | An individual operator responsible for the Real-time operation of the interconnected Bulk Electric System at the responsible entity issued an Operating Instruction during an Emergency prior to being trained on the documented communications protocols developed in Requirement R1. |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002-4 | R3. | Each Distribution Provider and Generator Operator shall conduct initial training for each of its operating personnel who can receive an oral two-party, person-to-person Operating Instruction prior to that individual operator receiving an oral two-party, person-to-person Operating Instruction to either: -Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or -Request that the issuer reissue the Operating Instruction. | 2016-07-01 |  | Low | N/A | N/A | An individual operator at the responsible entity received an Operating Instruction prior to being trained. | An individual operator at the responsible entity received an Operating Instruction during an Emergency prior to being trained. |  |  | DP |  |  |  | GOP
Mandatory Subject to Enforcement | COM | COM-002-4 | R4. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall at least once every twelve (12) calendar months:[Please see the standard for more information] | 2016-07-01 |  | Medium | The responsible entity assessed adherence to the documented communications protocols in Requirements R1 by its operating personnel that issue and receive Operating Instructions and provided feedback to those operating personnel and took corrective action, as appropriate AND The responsible entity assessed the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions and modified its documented communication protocols, as necessary AND The responsible entity exceeded twelve (12) calendar months between assessments. | The responsible entity assessed adherence to the documented communications protocols in Requirement R1 by its operating personnel that issue and receive Operating Instructions, but did not provide feedback to those operating personnel OR The responsible entity assessed adherence to the documented communications protocols in Requirements R1 by its operating personnel that issue and receive Operating Instructions and provided feedback to those operating personnel but did not take corrective action, as appropriate OR The responsible entity assessed the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions, but did not modify its documented communication protocols, as necessary. | The responsible entity did not assess adherence to the documented communications protocols in Requirements R1 by its operating personnel that issue and receive Operating Instructions OR The responsible entity did not assess the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions. | The responsible entity did not assess adherence to the documented communications protocols in Requirements R1 by its operating personnel that issue and receive Operating Instructions AND The responsible entity did not assess the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions. |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002-4 | R5. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: -Confirm the receiver’s response if the repeated information is correct (in accordance with Requirement R6). - Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver, or -Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. | 2016-07-01 |  | High | N/A | The responsible entity that issued an Operating Instruction during an Emergency did not take one of the following actions: Confirmed the receiver’s response if the repeated information was correct (in accordance with Requirement R6). Reissued the Operating Instruction if the repeated information was incorrect or if requested by the receiver. Took an alternative action if a response was not received or if the Operating Instruction was not understood by the receiver. | N/A | The responsible entity that issued an Operating Instruction during an Emergency did not take one of the following actions: Confirmed the receiver’s response if the repeated information was correct (in accordance with Requirement R6). Reissued the Operating Instruction if the repeated information was incorrect or if requested by the receiver. Took an alternative action if a response was not received or if the Operating Instruction was not understood by the receiver. AND Instability, uncontrolled separation, or cascading failures occurred as a result. |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002-4 | R6. | Each Balancing Authority, Distribution Provider, Generator Operator, and Transmission Operator that receives an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: -Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or -Request that the issuer reissue the Operating Instruction. | 2016-07-01 |  | High | N/A | The responsible entity did not repeat, not necessarily verbatim, the Operating Instruction during an Emergency and receive confirmation from the issuer that the response was correct, or request that the issuer reissue the Operating Instruction when receiving an Operating Instruction. | N/A | The responsible entity did not repeat, not necessarily verbatim, the Operating Instruction during an Emergency and receive confirmation from the issuer that the response was correct, or request that the issuer reissue the Operating Instruction when receiving an Operating Instruction AND Instability, uncontrolled separation, or cascading failures occurred as a result. |  | BA | DP |  |  |  | GOP | [12 empty] | TOP
Mandatory Subject to Enforcement | COM | COM-002-4 | R7. | Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues a written or oral single-party to multiple-party burst Operating Instruction during an Emergency shall confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. | 2016-07-01 |  | High | N/A | The responsible entity that that issued a written or oral single-party to multiple-party burst Operating Instruction during an Emergency did not confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. | N/A | The responsible entity that that issued a written or oral single-party to multiple-party burst Operating Instruction during an Emergency did not confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction AND Instability, uncontrolled separation, or cascading failures occurred as a result. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-001-0 | R1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. | 2007-06-18 | 2011-12-14 | High | [5 empty] | BA
Inactive | EOP | EOP-001-0 | R2. | The Transmission Operator shall have an emergency load reduction plan for all identified IROLs. The plan shall include the details on how the Transmission Operator will implement load reduction in sufficient amount and time to mitigate the IROL violation before system separation or collapse would occur. The load reduction plan must be capable of being implemented within 30 minutes. | 2007-06-18 | 2011-09-30 | Medium | [23 empty] | TOP
Inactive | EOP | EOP-001-0 | R3. | Each Transmission Operator and Balancing Authority shall: | 2007-06-18 | 2011-12-14 | Medium | The Transmission Operator or Balancing Authority failed to comply with one (1) of the sub-components. | The Transmission Operator or Balancing Authority failed to comply with two (2) of the sub-components. | The Transmission Operator or Balancing Authority has failed to comply with three (3) of the sub-components. | The Transmission Operator or Balancing Authority has failed to comply with four (4) of the sub-components. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-0 | R4. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: | 2007-06-18 | 2011-12-14 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-0 | R5. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan. | 2007-06-18 | 2011-12-14 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-0 | R6. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. | 2007-06-18 | 2011-12-14 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-0 | R7. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: | 2007-06-18 | 2011-12-14 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-0.1b | R1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. | 2012-09-13 | 2013-06-30 | High | [5 empty] | BA
Inactive | EOP | EOP-001-0.1b | R2. | The Transmission Operator shall have an emergency load reduction plan for all identified IROLs. The plan shall include the details on how the Transmission Operator will implement load reduction in sufficient amount and time to mitigate the IROL violation before system separation or collapse would occur. The load reduction plan must be capable of being implemented within 30 minutes. | 2012-09-13 | 2011-09-30 | Medium | The Transmission Operator has demonstrated the existence of the emergency load reduction plan but the plan will take longer than 30 minutes. |  | The Transmission Operator fails to include details on how load reduction is to be implemented in sufficient amount and time to mitigate IROL violation. | The Transmission Operator failed to demonstrate the existence of emergency load reduction plans for all identified IROLs. | [19 empty] | TOP
Inactive | EOP | EOP-001-0.1b | R3. | Each Transmission Operator and Balancing Authority shall: | 2012-09-13 | 2013-06-30 | Medium | The Transmission Operator or Balancing Authority failed to comply with one (1) of the sub-components. | The Transmission Operator or Balancing Authority failed to comply with two (2) of the sub-components. | The Transmission Operator or Balancing Authority has failed to comply with three (3) of the sub-components. | The Transmission Operator or Balancing Authority has failed to comply with four (4) of the sub-components. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-0.1b | R4. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: | 2012-09-13 | 2013-06-30 | Medium | The Transmission Operator or Balancing Authority failed to comply with one (1) of the sub-components. | The Transmission Operator or Balancing Authority failed to comply with two (2) of the sub-components. | The Transmission Operator or Balancing Authority has failed to comply with three (3) of the sub-components. | The Transmission Operator or Balancing Authority has failed to comply with all four (4) of the sub-components. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-0.1b | R5. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001 when developing an emergency plan. | 2012-09-13 | 2013-06-30 | Medium | The Transmission Operator and Balancing Authority emergency plan has complied with 90% or more of the number of sub-components. | The Transmission Operator and Balancing Authority emergency plan has complied with 70% to 90% of the number of sub-components. | The Transmission Operator and Balancing Authority emergency plan has complied with between 50% to 70% of the number of sub-components. | The Transmission Operator and Balancing Authority emergency plan has complied with 50% or less of the number of sub-components |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-0.1b | R6. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. | 2012-09-13 | 2013-06-30 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-0.1b | R7. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: | 2012-09-13 | 2013-06-30 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-0b | R1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. | 2011-12-15 | 2012-09-12 | High | [5 empty] | BA
Inactive | EOP | EOP-001-0b | R2. | The Transmission Operator shall have an emergency load reduction plan for all identified IROLs. The plan shall include the details on how the Transmission Operator will implement load reduction in sufficient amount and time to mitigate the IROL violation before system separation or collapse would occur. The load reduction plan must be capable of being implemented within 30 minutes. | 2011-12-15 | 2011-09-30 | Medium | [23 empty] | TOP
Inactive | EOP | EOP-001-0b | R3. | Each Transmission Operator and Balancing Authority shall: | 2011-12-15 | 2012-09-12 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-0b | R4. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: | 2011-12-15 | 2012-09-12 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-0b | R5. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan. | 2011-12-15 | 2012-09-12 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-0b | R6. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. | 2011-12-15 | 2012-09-12 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-0b | R7. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: | 2011-12-15 | 2012-09-12 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-1 | R1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. |  | 2011-05-23 |  | The Balancing Authority failed to demonstrate the existence of the necessary operating agreements for less than 25% of the adjacent BAs. Or less than 25% of those agreements do not contain provisions for emergency assistance. | The Balancing Authority failed to demonstrate the existence of the necessary operating agreements for 25% to 50% of the adjacent BAs. Or 25 to 50% of those agreements do not contain provisions for emergency assistance. | The Balancing Authority failed to demonstrate the existence of the necessary operating agreements for 50% to 75% of the adjacent BAs. Or 50% to 75% of those agreements do not contain provisions for emergency assistance. | The Balancing Authority failed to demonstrate the existence of the necessary operating agreements for 75% or more of the adjacent BAs. Or more than 75% of those agreements do not contain provisions for emergency assistance. |  | BA
Inactive | EOP | EOP-001-1 | R2. | Each Transmission Operator and Balancing Authority shall: |  | 2011-05-23 |  | The Transmission Operator or Balancing Authority failed to comply with one (1) of the sub-components. | The Transmission Operator or Balancing Authority failed to comply with two (2) of the sub-components. | The Transmission Operator or Balancing Authority has failed to comply with three (3) of the sub-components. | The Transmission Operator or Balancing Authority has failed to comply with four (4) of the sub-components. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-1 | R3. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: |  | 2011-05-23 |  | The Transmission Operator or Balancing Authority failed to comply with one (1) of the sub-components. | The Transmission Operator or Balancing Authority failed to comply with two (2) of the sub-components. | The Transmission Operator or Balancing Authority has failed to comply with three (3) of the sub-components. | The Transmission Operator or Balancing Authority has failed to comply with all four (4) of the sub-components. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-1 | R4. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan. |  | 2011-05-23 |  | The Transmission Operator and Balancing Authority’s emergency plan has complied with 90% or more of the number of sub-components. | The Transmission Operator and Balancing Authority’s emergency plan has complied with 70% to 90% of the number of sub-components. | The Transmission Operator and Balancing Authority’s emergency plan has complied with between 50% to 70% of the number of subcomponents. | The Transmission Operator and Balancing Authority’s emergency plan has complied with 50% or less of the number of sub-components |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-1 | R5. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. |  | 2011-05-23 |  | The Transmission Operator and Balancing Authority is missing minor program/procedural elements. | The Transmission Operator and Balancing Authority has failed to annually review one of it's emergency plans | The Transmission Operator and Balancing Authority has failed to annually review two of its emergency plans or communicate with one of it's neighboring Balancing Authorities. | The Transmission Operator and Balancing Authority has failed to annually review and/or communicate any emergency plans with its Reliability Coordinator, neighboring Transmission Operators or Balancing Authorities. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-1 | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: |  | 2011-05-23 |  | The Transmission Operator and/or the Balancing Authority failed to comply with one (1) of the subcomponents. | The Transmission Operator and/or the Balancing Authority failed to comply with two (2) of the subcomponents. | The Transmission Operator and/or the Balancing Authority has failed to comply with three (3) of the sub-components. | The Transmission Operator and/or the Balancing Authority has failed to comply with four (4) or more of the sub-components. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-2 | R1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. |  | 2011-12-14 |  | The Balancing Authority failed to demonstrate the existence of the necessary operating agreements for less than 25% of the adjacent BAs. Or less than 25% of those agreements do not contain provisions for emergency assistance | The Balancing Authority failed to demonstrate the existence of the necessary operating agreements for 25% to 50% of the adjacent BAs. Or 25 to 50% of those agreements do not contain provisions for emergency assistance | The Balancing Authority failed to demonstrate the existence of the necessary operating agreements for 50% to 75% of the adjacent BAs. Or 50% to 75% of those agreements do not contain provisions for emergency assistance. | The Balancing Authority failed to demonstrate the existence of the necessary operating agreements for 75% or more of the adjacent BAs. Or more than 75% of those agreements do not contain provisions for emergency assistance. |  | BA
Inactive | EOP | EOP-001-2 | R2. | Each Transmission Operator and Balancing Authority shall: |  | 2011-12-14 |  | The Transmission Operator or Balancing Authority failed to comply with one (1) of the sub-components. | The Transmission Operator or Balancing Authority failed to comply with two (2) of the sub-components. |  | The Transmission Operator or Balancing Authority has failed to comply with three (3) of the sub-components. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-2 | R3. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: |  | 2011-12-14 |  | The Transmission Operator or Balancing Authority failed to comply with one (1) of the sub-components. | The Transmission Operator or Balancing Authority failed to comply with two (2) of the sub-components. | The Transmission Operator or Balancing Authority has failed to comply with three (3) of the sub-components. | The Transmission Operator or Balancing Authority has failed to comply with all four (4) of the sub-components. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-2 | R4. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan. |  | 2011-12-14 |  | The Transmission Operator and Balancing Authority’s emergency plan has complied with 90% or more of the number of sub-components. | The Transmission Operator and Balancing Authority’s emergency plan has complied with 70% to 90% of the number of sub-components. | The Transmission Operator and Balancing Authority’s emergency plan has complied with between 50% to 70% of the number of subcomponents. | The Transmission Operator and Balancing Authority’s emergency plan has complied with 50% or less of the number of sub-components. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-2 | R5. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. |  | 2011-12-14 |  | The Transmission Operator and Balancing Authority is missing minor program/procedural elements. | The Transmission Operator and Balancing Authority has failed to annually review one of it's emergency plans | The Transmission Operator and Balancing Authority has failed to annually review two of its emergency plans or communicate with one of it's neighboring Balancing Authorities. | The Transmission Operator and Balancing Authority has failed to annually review and/or communicate any emergency plans with its Reliability Coordinator, neighboring Transmission Operators or Balancing Authorities. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-2 | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: |  | 2011-12-14 |  | The Transmission Operator and/or the Balancing Authority failed to comply with one (1) of the subcomponents. | The Transmission Operator and/or the Balancing Authority failed to comply with two (2) of the subcomponents. | The Transmission Operator and/or the Balancing Authority has failed to comply with three (3) of the sub-components. | The Transmission Operator and/or the Balancing Authority has failed to comply with four (4) or more of the sub-components. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-2.1b | R1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. | 2013-07-01 | 2017-03-31 | High | The Balancing Authority failed to demonstrate the existence of the necessary operating agreements for less than 25% of the adjacent BAs. Or less than 25% of those agreements do not contain provisions for emergency assistance. | The Balancing Authority failed to demonstrate the existence of the necessary operating agreements for 25% to 50% of the adjacent BAs. Or 25 to 50% of those agreements do not contain provisions for emergency assistance. | The Balancing Authority failed to demonstrate the existence of the necessary operating agreements for 50% to 75% of the adjacent BAs. Or 50% to 75% of those agreements do not contain provisions for emergency assistance. | The Balancing Authority failed to demonstrate the existence of the necessary operating agreements for 75% or more of the adjacent BAs. Or more than 75% of those agreements do not contain provisions for emergency assistance |  | BA
Inactive | EOP | EOP-001-2.1b | R2. | Each Transmission Operator and Balancing Authority shall: | 2013-07-01 | 2017-03-31 | Medium | The Transmission Operator or Balancing Authority failed to comply with one (1) of the sub-components. | The Transmission Operator or Balancing Authority failed to comply with two (2) of the sub-components. |  | The Transmission Operator or Balancing Authority has failed to comply with three (3) of the sub-components. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-2.1b | R3. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: | 2013-07-01 | 2017-03-31 | Medium | The Transmission Operator or Balancing Authority failed to comply with one (1) of the sub-components. | The Transmission Operator or Balancing Authority failed to comply with two (2) of the sub-components. | The Transmission Operator or Balancing Authority has failed to comply with three (3) of the sub-components. | The Transmission Operator or Balancing Authority has failed to comply with all four (4) of the sub-components. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-2.1b | R4. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001 when developing an emergency plan. | 2013-07-01 | 2017-03-31 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-2.1b | R5. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. | 2013-07-01 | 2017-03-31 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-2.1b | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: | 2013-07-01 | 2017-03-31 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-2b | R1. | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. |  | 2012-09-12 | High | [5 empty] | BA
Inactive | EOP | EOP-001-2b | R2. | Each Transmission Operator and Balancing Authority shall: |  | 2012-09-12 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-2b | R3. | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: |  | 2012-09-12 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-2b | R4. | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan. |  | 2012-09-12 | Medium | The Transmission Operator and Balancing Authority’s emergency plan has complied with 90% or more of the number of sub-components. | The Transmission Operator and Balancing Authority’s emergency plan has complied with 70% to 90% of the number of sub-components. | The Transmission Operator and Balancing Authority’s emergency plan has complied with between 50% to 70% of the number of subcomponents. | The Transmission Operator and Balancing Authority’s emergency plan has complied with 50% or less of the number of sub-components |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-2b | R5. | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. |  | 2012-09-12 | Medium | The Transmission Operator and Balancing Authority is missing minor program/procedural elements. | The Transmission Operator and Balancing Authority has failed to annually review one of it's emergency plans | The Transmission Operator and Balancing Authority has failed to annually review two of its emergency plans or communicate with one of it's neighboring Balancing Authorities. | The Transmission Operator and Balancing Authority has failed to annually review and/or communicate any emergency plans with its Reliability Coordinator, neighboring Transmission Operators or Balancing Authorities. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-001-2b | R6. | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: |  | 2012-09-12 | Medium | The Transmission Operator and/or the Balancing Authority failed to comply with one (1) of the subcomponents. | The Transmission Operator and/or the Balancing Authority failed to comply with two (2) of the subcomponents. | The Transmission Operator and/or the Balancing Authority has failed to comply with three (3) of the sub-components. | The Transmission Operator and/or the Balancing Authority has failed to comply with four (4) or more of the sub-components. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-002-0 | R1. | Each Balancing Authority and Reliability Coordinator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area and shall exercise specific authority to alleviate capacity and energy emergencies. |  | 2006-11-01 | [6 empty] | BA | [10 empty] | RC
Inactive | EOP | EOP-002-0 | R2. | Each Balancing Authority and Reliability Coordinator shall implement its capacity and energy emergency plan, when required and as appropriate, to reduce risks to the interconnected system. |  | 2006-11-01 | [6 empty] | BA | [10 empty] | RC
Inactive | EOP | EOP-002-0 | R3. | A Balancing Authority that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. |  | 2006-11-01 | [6 empty] | BA
Inactive | EOP | EOP-002-0 | R4. | A Reliability Coordinator that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to neighboring areas. |  | 2006-11-01 | [17 empty] | RC
Inactive | EOP | EOP-002-0 | R5. | A Balancing Authority anticipating an operating capacity or energy emergency shall perform all actions necessary including bringing on all available generation, postponing equipment maintenance, scheduling interchange purchases in advance, and being prepared to reduce firm load |  | 2006-11-01 | [6 empty] | BA
Inactive | EOP | EOP-002-0 | R6. | A deficient Balancing Authority shall only use the assistance provided by the Interconnection’s frequency bias for the time needed to implement corrective actions. The Balancing Authority shall not unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond that supplied through frequency bias action and Interchange Schedule changes. Such unilateral adjustment may overload transmission facilities. |  | 2006-11-01 | [6 empty] | BA
Inactive | EOP | EOP-002-0 | R7. | If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to: |  | 2006-11-01 | [6 empty] | BA
Inactive | EOP | EOP-002-0 | R8. | Once the Balancing Authority has exhausted the steps listed in Requirement 7, or if these steps cannot be completed in sufficient time to resolve the emergency condition, the Balancing Authority shall: |  | 2006-11-01 | [6 empty] | BA
Inactive | EOP | EOP-002-0 | R9. | A Reliability Coordinator that has any Balancing Authority within its Reliability Coordinator area experiencing a potential or actual Energy Emergency shall initiate an Energy Emergency Alert as detailed in Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” The Reliability Coordinator shall act to mitigate the emergency condition, including a request for emergency assistance if required. |  | 2006-11-01 | [6 empty] | BA | [10 empty] | RC
Inactive | EOP | EOP-002-0 | R10. | When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff (See Attachment 1-IRO006-0 “Transmission Loading Relief Procedure” for explanation of Transmission Service Priorities): |  | 2006-11-01
Inactive | EOP | EOP-002-1 | R1. | Each Balancing Authority and Reliability Coordinator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area and shall exercise specific authority to alleviate capacity and energy emergencies. |  | 2007-01-01 | [6 empty] | BA | [10 empty] | RC
Inactive | EOP | EOP-002-1 | R2. | Each Balancing Authority shall implement its capacity and energy emergency plan, when required and as appropriate, to reduce risks to the interconnected system. |  | 2007-01-01 | [6 empty] | BA
Inactive | EOP | EOP-002-1 | R3. | A Balancing Authority that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. |  | 2007-01-01 | [6 empty] | BA
Inactive | EOP | EOP-002-1 | R4. | A Balancing Authority anticipating an operating capacity or energy emergency shall perform all actions necessary including bringing on all available generation, postponing equipment maintenance, scheduling interchange purchases in advance, and being prepared to reduce firm load. |  | 2007-01-01 | [6 empty] | BA
Inactive | EOP | EOP-002-1 | R5. | A deficient Balancing Authority shall only use the assistance provided by the Interconnection’s frequency bias for the time needed to implement corrective actions. The Balancing Authority shall not unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond that supplied through frequency bias action and Interchange Schedule changes. Such unilateral adjustment may overload transmission facilities. |  | 2007-01-01 | [6 empty] | BA
Inactive | EOP | EOP-002-1 | R6. | If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to: |  | 2007-01-01 | [6 empty] | BA
Inactive | EOP | EOP-002-1 | R7. | Once the Balancing Authority has exhausted the steps listed in Requirement 6, or if these steps cannot be completed in sufficient time to resolve the emergency condition, the Balancing Authority shall: |  | 2007-01-01 | [6 empty] | BA
Inactive | EOP | EOP-002-1 | R8. | A Reliability Coordinator that has any Balancing Authority within its Reliability Coordinator area experiencing a potential or actual Energy Emergency shall initiate an Energy Emergency Alert as detailed in Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” The Reliability Coordinator shall act to mitigate the emergency condition, including a request for emergency assistance if required. |  | 2007-01-01 | [6 empty] | BA | [10 empty] | RC
Inactive | EOP | EOP-002-1 | R9. | When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff (See Attachment 1-IRO006-0 “Transmission Loading Relief Procedure” for explanation of Transmission Service Priorities): |  | 2007-01-01 | [13 empty] | LSE |  |  |  | RC
Inactive | EOP | EOP-002-2 | R1. | Each Balancing Authority and Reliability Coordinator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area and shall exercise specific authority to alleviate capacity and energy emergencies. | 2007-06-18 | 2009-05-12 | High |  |  |  | The Balancing Authority or Reliability Coordinator does not have responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area OR The Balancing Authority or Reliability Coordinator |  | BA | [10 empty] | RC
Inactive | EOP | EOP-002-2 | R2. | Each Balancing Authority shall implement its capacity and energy emergency plan, when required and as appropriate, to reduce risks to the interconnected system. | 2007-06-18 | 2009-05-12 | High |  |  |  | The Balancing Authority did not implement its capacity and energy emergency plan, when required and as appropriate, to reduce risks to the interconnected system. |  | BA
Inactive | EOP | EOP-002-2 | R3. | A Balancing Authority that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. | 2007-06-18 | 2009-05-12 | High |  |  | The Balancing Authority communicated its current and future system conditions to its Reliability Coordinator but did not communicate to one or more of its neighboring Balancing Authorities. | The Balancing Authority has failed to communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. |  | BA
Inactive | EOP | EOP-002-2 | R4. | A Balancing Authority anticipating an operating capacity or energy emergency shall perform all actions necessary including bringing on all available generation, postponing equipment maintenance, scheduling interchange purchases in advance, and being prepared to reduce firm load. | 2007-06-18 | 2009-05-12 | High |  |  |  | The Balancing Authority has failed to perform the necessary actions as required and stated in the requirement. |  | BA
Inactive | EOP | EOP-002-2 | R5. | A deficient Balancing Authority shall only use the assistance provided by the Interconnection’s frequency bias for the time needed to implement corrective actions. The Balancing Authority shall not unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond that supplied through frequency bias action and Interchange Schedule changes. Such unilateral adjustment may overload transmission facilities. | 2007-06-18 | 2009-05-12 | High |  |  | The Balancing Authority used the assistance provided by the Interconnection’s frequency bias for more time than needed to implement corrective actions. | The Balancing Authority used the assistance provided by the Interconnection’s frequency bias for more time than needed to implement corrective actions and unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond th |  | BA
Inactive | EOP | EOP-002-2 | R6. | If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to: | 2007-06-18 | 2009-05-12 | High | The Balancing Authority failed to comply with one of the sub-components. | The Balancing Authority failed to comply with 2 of the sub-components. | The Balancing Authority failed to comply with 3 of the sub-components. | The Balancing Authority failed to comply with more than 3 of the sub-components. |  | BA
Inactive | EOP | EOP-002-2 | R7. | Once the Balancing Authority has exhausted the steps listed in Requirement 6, or if these steps cannot be completed in sufficient time to resolve the emergency condition, the Balancing Authority shall: | 2007-06-18 | 2009-05-12 | High |  |  | The Balancing Authority has met only one of the two requirements | The Balancing Authority has not met either of the two requirements |  | BA
Inactive | EOP | EOP-002-2 | R8. | A Reliability Coordinator that has any Balancing Authority within its Reliability Coordinator area experiencing a potential or actual Energy Emergency shall initiate an Energy Emergency Alert as detailed in Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” The Reliability Coordinator shall act to mitigate the emergency condition, including a request for emergency assistance if required. | 2007-06-18 | 2009-05-12 | High | The Reliability Coordinator’s implementation of an Energy Emergency Alert has missed minor program/procedural elements in Attachment 1-EOP-002-0. |  |  | The Reliability Coordinator has failed to meet one or more of the requirements of Attachment 1-EOP-002-0. | [12 empty] | RC
Inactive | EOP | EOP-002-2 | R9. | When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff (See Attachment 1-IRO-006-0 “Transmission Loading Relief Procedure” for explanation of Transmission Service Priorities): | 2007-06-18 | 2009-05-12 | High | The Reliability Coordinator failed to comply with one (1) of the sub-components. | The Reliability Coordinator failed to comply with two (2) of the sub-components. | The Reliability Coordinator has failed to comply with three (3) of the sub-components. | The Reliability Coordinator has failed to comply with all four (4) of the sub-components. | [8 empty] | LSE |  |  |  | RC
Inactive | EOP | EOP-002-2.1 | R1. | Each Balancing Authority and Reliability Coordinator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area and shall exercise specific authority to alleviate capacity and energy emergencies. | 2009-05-13 | 2011-09-30 |  |  |  |  | The Balancing Authority or Reliability Coordinator does not have responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area OR The Balancing Authority or Reliability Coordinator |  | BA | [10 empty] | RC
Inactive | EOP | EOP-002-2.1 | R2. | Each Balancing Authority shall implement its capacity and energy emergency plan, when required and as appropriate, to reduce risks to the interconnected system. | 2009-05-13 | 2011-09-30 |  |  |  |  | The Balancing Authority did not implement its capacity and energy emergency plan, when required and as appropriate, to reduce risks to the interconnected system. |  | BA
Inactive | EOP | EOP-002-2.1 | R3. | A Balancing Authority that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. | 2009-05-13 | 2011-09-30 |  |  |  | The Balancing Authority communicated its current and future system conditions to its Reliability Coordinator but did not communicate to one or more of its neighboring Balancing Authorities. | The Balancing Authority has failed to communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. |  | BA
Inactive | EOP | EOP-002-2.1 | R4. | A Balancing Authority anticipating an operating capacity or energy emergency shall perform all actions necessary including bringing on all available generation, postponing equipment maintenance, scheduling interchange purchases in advance, and being prepared to reduce firm load. | 2009-05-13 | 2011-09-30 |  |  |  |  | The Balancing Authority has failed to perform the necessary actions as required and stated in the requirement. |  | BA
Inactive | EOP | EOP-002-2.1 | R5. | A deficient Balancing Authority shall only use the assistance provided by the Interconnection’s frequency bias for the time needed to implement corrective actions. The Balancing Authority shall not unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond that supplied through frequency bias action and Interchange Schedule changes. Such unilateral adjustment may overload transmission facilities. | 2009-05-13 | 2011-09-30 |  |  |  | The Balancing Authority used the assistance provided by the Interconnection’s frequency bias for more time than needed to implement corrective actions. | The Balancing Authority used the assistance provided by the Interconnection’s frequency bias for more time than needed to implement corrective actions and unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond th |  | BA
Inactive | EOP | EOP-002-2.1 | R6. | If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to: | 2009-05-13 | 2011-09-30 |  | The Balancing Authority failed to comply with one of the sub-components. | The Balancing Authority failed to comply with 2 of the sub-components. | The Balancing Authority failed to comply with 3 of the sub-components. | The Balancing Authority failed to comply with more than 3 of the sub-components. |  | BA
Inactive | EOP | EOP-002-2.1 | R7. | Once the Balancing Authority has exhausted the steps listed in Requirement 6, or if these steps cannot be completed in sufficient time to resolve the emergency condition, the Balancing Authority shall: | 2009-05-13 | 2011-09-30 |  |  |  | The Balancing Authority has met only one of the two requirements | The Balancing Authority has not met either of the two requirements |  | BA
Inactive | EOP | EOP-002-2.1 | R8. | A Reliability Coordinator that has any Balancing Authority within its Reliability Coordinator area experiencing a potential or actual Energy Emergency shall initiate an Energy Emergency Alert as detailed in Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” The Reliability Coordinator shall act to mitigate the emergency condition, including a request for emergency assistance if required. | 2009-05-13 | 2011-09-30 |  | The Reliability Coordinator’s implementation of an Energy Emergency Alert has missed minor program/procedural elements in Attachment 1-EOP-002-0. |  |  | The Reliability Coordinator has failed to meet one or more of the requirements of Attachment 1-EOP-002-0. | [12 empty] | RC
Inactive | EOP | EOP-002-2.1 | R9. | When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff (See Attachment 1-IRO-006-0 “Transmission Loading Relief Procedure” for explanation of Transmission Service Priorities): | 2009-05-13 | 2011-09-30 |  | The Reliability Coordinator failed to comply with one (1) of the sub-components. | The Reliability Coordinator failed to comply with two (2) of the sub-components. | The Reliability Coordinator has failed to comply with three (3) of the sub-components. | The Reliability Coordinator has failed to comply with all four (4) of the sub-components. | [8 empty] | LSE |  |  |  | RC
Inactive | EOP | EOP-002-3 | R1. | Each Balancing Authority and Reliability Coordinator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area and shall exercise specific authority to alleviate capacity and energy emergencies. | 2011-01-10 | 2012-09-12 | High | N/A | N/A | N/A | The Balancing Authority or Reliability Coordinator does not have responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area OR The Balancing Authority or Reliability Coordinator |  | BA | [10 empty] | RC
Inactive | EOP | EOP-002-3 | R2. | Each Balancing Authority shall, when required and as appropriate, take one or more actions as described in its capacity and energy emergency plan, , to reduce risks to the interconnected system. | 2011-01-10 | 2012-09-12 | High | N/A | N/A | N/A | The Balancing Authority did not implement its capacity and energy emergency plan, when required and as appropriate, to reduce risks to the interconnected system. |  | BA
Inactive | EOP | EOP-002-3 | R3. | A Balancing Authority that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. | 2011-01-10 | 2012-09-12 | High | N/A | N/A | The Balancing Authority communicated its current and future system conditions to its Reliability Coordinator but did not communicate to one or more of its neighboring Balancing Authorities. | The Balancing Authority has failed to communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. |  | BA
Inactive | EOP | EOP-002-3 | R4. | A Balancing Authority anticipating an operating capacity or energy emergency shall perform all actions necessary including bringing on all available generation, postponing equipment maintenance, scheduling interchange purchases in advance, and being prepared to reduce firm load. | 2011-01-10 | 2012-09-12 | High | N/A | N/A | N/A | The Balancing Authority has failed to perform the necessary actions as required and stated in the requirement. |  | BA
Inactive | EOP | EOP-002-3 | R5. | A deficient Balancing Authority shall only use the assistance provided by the Interconnection’s frequency bias for the time needed to implement corrective actions. The Balancing Authority shall not unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond that supplied through frequency bias action and Interchange Schedule changes. Such unilateral adjustment may overload transmission facilities. | 2011-01-10 | 2012-09-12 | High | N/A | N/A | The Balancing Authority used the assistance provided by the Interconnection’s frequency bias for more time than needed to implement corrective actions. | The Balancing Authority used the assistance provided by the Interconnection’s frequency bias for more time than needed to implement corrective actions and unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond th |  | BA
Inactive | EOP | EOP-002-3 | R6. | If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to: | 2011-01-10 | 2012-09-12 | High | The Balancing Authority failed to comply with one of the sub-components. | The Balancing Authority failed to comply with 2 of the sub-components. | The Balancing Authority failed to comply with 3 of the sub-components. | The Balancing Authority failed to comply with more than 3 of the sub-components. |  | BA
Inactive | EOP | EOP-002-3 | R7. | Once the Balancing Authority has exhausted the steps listed in Requirement 6, or if these steps cannot be completed in sufficient time to resolve the emergency condition, the Balancing Authority shall: | 2011-01-10 | 2012-09-12 | High | N/A | N/A | The Balancing Authority has met only one of the two requirements | The Balancing Authority has not met either of the two requirements |  | BA
Inactive | EOP | EOP-002-3 | R8. | A Reliability Coordinator that has any Balancing Authority within its Reliability Coordinator area experiencing a potential or actual Energy Emergency shall initiate an Energy Emergency Alert as detailed in Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” The Reliability Coordinator shall act to mitigate the emergency condition, including a request for emergency assistance if required. | 2011-01-10 | 2012-09-12 | High | The Reliability Coordinator’s implementation of an Energy Emergency Alert has missed minor program/procedural elements in Attachment 1-EOP-002-0. | N/A | N/A | The Reliability Coordinator has failed to meet one or more of the requirements of Attachment 1-EOP-002-0. | [12 empty] | RC
Inactive | EOP | EOP-002-3 | R9. | When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff (See Attachment 1-IRO-006-0 “Transmission Loading Relief Procedure” for explanation of Transmission Service Priorities): | 2011-01-10 | 2012-09-12 | High | The Reliability Coordinator failed to comply with one (1) of the sub-components. | The Reliability Coordinator failed to comply with two (2) of the sub-components. | The Reliability Coordinator has failed to comply with three (3) of the sub-components. | The Reliability Coordinator has failed to comply with all four (4) of the sub-components. | [8 empty] | LSE |  |  |  | RC
Inactive | EOP | EOP-002-3.1 | R1. | Each Balancing Authority and Reliability Coordinator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area and shall exercise specific authority to alleviate capacity and energy emergencies. | 2012-09-13 | 2017-03-31 | High | [5 empty] | BA | [10 empty] | RC
Inactive | EOP | EOP-002-3.1 | R2. | Each Balancing Authority shall, when required and as appropriate, take one or more actions as described in its capacity and energy emergency plan to reduce risks to the interconnected system. | 2012-09-13 | 2017-03-31 | High | [5 empty] | BA
Inactive | EOP | EOP-002-3.1 | R3. | A Balancing Authority that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. | 2012-09-13 | 2017-03-31 | High | [5 empty] | BA
Inactive | EOP | EOP-002-3.1 | R4. | A Balancing Authority anticipating an operating capacity or energy emergency shall perform all actions necessary including bringing on all available generation, postponing equipment maintenance, scheduling interchange purchases in advance, and being prepared to reduce firm load. | 2012-09-13 | 2017-03-31 | High | [5 empty] | BA
Inactive | EOP | EOP-002-3.1 | R5. | A deficient Balancing Authority shall only use the assistance provided by the Interconnection’s frequency bias for the time needed to implement corrective actions. The Balancing Authority shall not unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond that supplied through frequency bias action and Interchange Schedule changes. Such unilateral adjustment may overload transmission facilities. | 2012-09-13 | 2017-03-31 | High | [5 empty] | BA
Inactive | EOP | EOP-002-3.1 | R6. | If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to: | 2012-09-13 | 2017-03-31 | High | [5 empty] | BA
Inactive | EOP | EOP-002-3.1 | R7. | Once the Balancing Authority has exhausted the steps listed in Requirement 6, or if these steps cannot be completed in sufficient time to resolve the emergency condition, the Balancing Authority shall: | 2012-09-13 | 2017-03-31 | High | [5 empty] | BA
Inactive | EOP | EOP-002-3.1 | R8. | A Reliability Coordinator that has any Balancing Authority within its Reliability Coordinator area experiencing a potential or actual Energy Emergency shall initiate an Energy Emergency Alert as detailed in Attachment 1-EOP-002 “Energy Emergency Alerts.” The Reliability Coordinator shall act to mitigate the emergency condition, including a request for emergency assistance if required. | 2012-09-13 | 2017-03-31 | High | [16 empty] | RC
Inactive | EOP | EOP-002-3.1 | R9. | When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff: | 2012-09-13 | 2017-03-31 | High | [12 empty] | LSE |  |  |  | RC
Inactive | EOP | EOP-003-0 | R1. | After taking all other remedial steps, a Transmission Operator or Balancing Authority operating with insufficient generation or transmission capacity shall shed customer load rather than risk an uncontrolled failure of components or cascading outages of the Interconnection. |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-0 | R2. | Each Transmission Operator and Balancing Authority shall establish plans for automatic load shedding for underfrequency or undervoltage conditions. |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-0 | R3. | Each Transmission Operator and Balancing Authority shall coordinate load shedding plans among other interconnected Transmission Operators and Balancing Authorities. |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-0 | R4. | A Transmission Operator or Balancing Authority shall consider one or more of these factors in designing an automatic load shedding scheme: frequency, rate of frequency decay, voltage level, rate of voltage decay, or power flow levels. |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-0 | R5. | A Transmission Operator or Balancing Authority shall implement load shedding in steps established to minimize the risk of further uncontrolled separation, loss of generation, or system shutdown. |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-0 | R6. | After a Transmission Operator or Balancing Authority Area separates from the Interconnection, if there is insufficient generating capacity to restore system frequency following automatic underfrequency load shedding, the Transmission Operator or Balancing Authority shall shed additional load. |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-0 | R7. | The Transmission Operator and Balancing Authority shall coordinate automatic load shedding throughout their areas with underfrequency isolation of generating units, tripping of shunt capacitors, and other automatic actions that will occur under abnormal frequency, voltage, or power flow conditions. |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-0 | R8. | Each Transmission Operator or Balancing Authority shall have plans for operator-controlled manual load shedding to respond to real-time emergencies. The Transmission Operator or Balancing Authority shall be capable of implementing the load shedding in a timeframe adequate for responding to the emergency. |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-1 | R1. | After taking all other remedial steps, a Transmission Operator or Balancing Authority operating with insufficient generation or transmission capacity shall shed customer load rather than risk an uncontrolled failure of components or cascading outages of the Interconnection. | 2007-06-18 | 2013-09-30 | High |  |  |  | The Transmission Operator or Balancing Authority has failed shed customer load. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-1 | R2. | Each Transmission Operator and Balancing Authority shall establish plans for automatic load shedding for underfrequency or undervoltage conditions. | 2007-06-18 | 2013-09-30 | High |  |  |  | The applicable entity did not establish plans for automatic load-shedding, as directed by the requirement. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-1 | R3. | Each Transmission Operator and Balancing Authority shall coordinate load shedding plans among other interconnected Transmission Operators and Balancing Authorities. | 2007-06-18 | 2013-09-30 | High | The applicable entity did not coordinate load shedding plans, as directed by the requirement, affecting 5% or less of its required entities. | The applicable entity did not coordinate load shedding plans, as directed by the requirement, affecting between 5-10% of its required entities. | The applicable entity did not coordinate load shedding plans, as directed by the requirement, affecting 10-15%, inclusive, of its required entities. | The applicable entity did not coordinate load shedding plans, as directed by the requirement, affecting greater than 15% of its required entities. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-1 | R4. | A Transmission Operator or Balancing Authority shall consider one or more of these factors in designing an automatic load shedding scheme: frequency, rate of frequency decay, voltage level, rate of voltage decay, or power flow levels. | 2007-06-18 | 2013-09-30 | High |  |  |  | The Transmission Operator or Balancing Authority did not consider at least one of the five elements (frequency, rate of frequency decay, voltage level, rate of voltage decay, or power flow levels) listed in the requirement. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-1 | R5. | A Transmission Operator or Balancing Authority shall implement load shedding in steps established to minimize the risk of further uncontrolled separation, loss of generation, or system shutdown. | 2007-06-18 | 2013-09-30 | High |  |  |  | The Transmission Operator or Balancing Authority has failed to implement load shedding as directed in the requirement. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-1 | R6. | After a Transmission Operator or Balancing Authority Area separates from the Interconnection, if there is insufficient generating capacity to restore system frequency following automatic underfrequency load shedding, the Transmission Operator or Balancing Authority shall shed additional load. | 2007-06-18 | 2013-09-30 | High |  |  |  | The Transmission Operator or Balancing Authority did not shed load. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-1 | R7. | The Transmission Operator and Balancing Authority shall coordinate automatic load shedding throughout their areas with underfrequency isolation of generating units, tripping of shunt capacitors, and other automatic actions that will occur under abnormal frequency, voltage, or power flow conditions. | 2007-06-18 | 2013-09-30 | High | The applicable entity did not coordinate automatic load shedding, as directed by the requirement, affecting 5% or less of its automatic actions. (Coordination with individual generating units is considered as one automatic action for purposes of determin | The applicable entity did not coordinate automatic load shedding, as directed by the requirement, affecting between 5 -10% of its automatic actions. (Coordination with individual generating units is considered as one automatic action for purposes of deter | The applicable entity did not coordinate automatic load shedding, as directed by the requirement, affecting 10-15%, inclusive, of its automatic actions. (Coordination with individual generating units is considered as one automatic action for purposes of d | The applicable entity did not coordinate automatic load shedding, as directed by the requirement, affecting greater than 15% of its automatic actions. (Coordination with individual generating units is considered as one automatic action for purposes of det |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-1 | R8. | Each Transmission Operator or Balancing Authority shall have plans for operator-controlled manual load shedding to respond to real-time emergencies. The Transmission Operator or Balancing Authority shall be capable of implementing the load shedding in a timeframe adequate for responding to the emergency. | 2007-06-18 | 2013-09-30 | High |  | The applicable entity did not have plans for operator controlled manual load shedding, as directed by the requirement. | The applicable entity did not have the capability to implement the load shedding, as directed by the requirement. | The applicable entity did not have plans for operator controlled manual load shedding, as directed by the requirement nor had the capability to implement the load shedding, as directed by the requirement. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-2 | R1. | After taking all other remedial steps, a Transmission Operator or Balancing Authority operating with insufficient generation or transmission capacity shall shed customer load rather than risk an uncontrolled failure of components or cascading outages of the Interconnection. | 2012-07-10 | 2017-03-31 | High | N/A | N/A | N/A | The Transmission Operator or Balancing Authority failed to shed customer load. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-2 | R2. | Each Transmission Operator shall establish plans for automatic load shedding for undervoltage conditions if the Transmission Operator or its associated Transmission Planner(s) or Planning Coordinator(s) determine that an under-voltage load shedding scheme is required. | 2012-07-10 | 2017-03-31 | High | N/A | N/A | N/A | The Transmission Operator did not establish plans for automatic load shedding for undervoltage conditions as directed by the requirement. | [19 empty] | TOP
Inactive | EOP | EOP-003-2 | R3. | Each Transmission Operator and Balancing Authority shall coordinate load shedding plans, excluding automatic under-frequency load shedding plans, among other interconnected Transmission Operators and Balancing Authorities. | 2012-07-10 | 2017-03-31 | High | The responsible entity did not coordinate load shedding plans, as directed by the requirement, affecting 5% or less of its required entities. | The responsible entity did not coordinate load shedding plans, as directed by the requirement, affecting more than 5% up to (and including) 10% of its required entities. | The responsible entity did not coordinate load shedding plans, as directed by the requirement, affecting more than 10%, up to (and including) 15% or less, of its required entities. | The responsible entity did not coordinate load shedding plans, as directed by the requirement, affecting more than 15% of its required entities. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-2 | R4. | A Transmission Operator shall consider one or more of these factors in designing an automatic under voltage load shedding scheme: voltage level, rate of voltage decay, or power flow levels. | 2012-07-10 | 2017-03-31 | High | N/A | N/A | N/A | The Transmission Operator failed to consider at least one of the three elements voltage level, rate of voltage decay, or power flow levels) listed in the requirement. | [19 empty] | TOP
Inactive | EOP | EOP-003-2 | R5. | A Transmission Operator or Balancing Authority shall implement load shedding, excluding automatic under-frequency load shedding, in steps established to minimize the risk of further uncontrolled separation, loss of generation, or system shutdown. | 2012-07-10 | 2017-03-31 | High | N/A | N/A | N/A | The Transmission Operator or Balancing Authority failed to implement load shedding in steps established to minimize the risk of further uncontrolled separation, loss of generation, or system shutdown. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-2 | R6. | After a Transmission Operator or Balancing Authority Area separates from the Interconnection, if there is insufficient generating capacity to restore system frequency following automatic underfrequency load shedding, the Transmission Operator or Balancing Authority shall shed additional load. | 2012-07-10 | 2017-03-31 | High | N/A | N/A | N/A | The Transmission Operator or Balancing Authority failed to shed additional load after it had separated from the Interconnection when there was insufficient generating capacity to restore system frequency following automatic underfrequency load shedding. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-003-2 | R7. | The Transmission Operator shall coordinate automatic undervoltage load shedding throughout their areas with tripping of shunt capacitors, and other automatic actions that will occur under abnormal voltage, or power flow conditions | 2012-07-10 | 2017-03-31 | High | The Transmission Operator did not coordinate automatic undervoltage load shedding with 5% or less of the types of automatic actions described in the Requirement. | The Transmission Operator did not coordinate automatic undervoltage load shedding with more than 5% up to (and including) 10% of the types of automatic actions described in the Requirement. | The Transmission Operator did not coordinate automatic undervoltage load shedding with more than 10% up to (and including) 15% of the types of automatic actions described in the Requirement. | The Transmission Operator did not coordinate automatic undervoltage load shedding with more than 15% of the types of automatic actions described in the Requirement. | [19 empty] | TOP
Inactive | EOP | EOP-003-2 | R8. | Each Transmission Operator or Balancing Authority shall have plans for operator controlled manual load shedding to respond to real-time emergencies. The Transmission Operator or Balancing Authority shall be capable of implementing the load shedding in a timeframe adequate for responding to the emergency. | 2012-07-10 | 2017-03-31 | High | N/A | The responsible entity did not have plans for operator controlled manual load shedding, as directed by the requirement. | The responsible entity has plans for manual load shedding but did not have the capability to implement the load shedding, as directed by the requirement. | The responsible entity did not have plans for operator controlled manual load shedding, as directed by the requirement nor had the capability to implement the load shedding, as directed by the requirement. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-004-1 | R1. | Each Regional Reliability Organization shall establish and maintain a Regional reporting procedure to facilitate preparation of preliminary and final disturbance reports. | 2007-06-18 | 2013-12-31 | Low | The Regional Reliability Organization has demonstrated the existence of a regional reporting procedure, but the procedure is missing minor details or minor program/procedural elements. | The Regional Reliability Organization Regional reporting procedure have been is missing one element that would make the procedure meet the requirement. | The Regional Reliability Organization Regional has a regional reporting procedure but the procedure is not current. | The Regional Reliability Organization does not have a regional reporting procedure. | [15 empty] | RRO
Inactive | EOP | EOP-004-1 | R2. | A Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load-Serving Entity shall promptly analyze Bulk Electric System disturbances on its system or facilities. | 2007-06-18 | 2013-12-31 | Medium |  | The responsible entities has failed to analyze 1% to 25% of its disturbances on the BES or was negligent in the timeliness of analyzing the disturbances 1% to 25% of the time. | The responsible entities has failed to analyze 26% to 50% of its disturbances on the BES or was negligent in the timeliness of analyzing the disturbances 26% to 50% of the time. | The responsible entities has failed to analyze more than 50% of its disturbances on the BES or negligent in the timeliness of analyzing the disturbances more than 50% of the time |  | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | EOP | EOP-004-1 | R3. | A Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load-Serving Entity experiencing a reportable incident shall provide a preliminary written report to its Regional Reliability Organization and NERC. | 2007-06-18 | 2013-12-31 | Low |  |  |  | The responsible entities failed to provide a preliminary written report as directed by the requirement. |  | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP
Inactive | EOP | EOP-004-1 | R4. | When a Bulk Electric System disturbance occurs, the Regional Reliability Organization shall make its representatives on the NERC Operating Committee and Disturbance Analysis Working Group available to the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity immediately affected by the disturbance for the purpose of providing any needed assistance in the investigation and to assist in the preparation of a final report. | 2007-06-18 | 2013-12-31 | Low |  |  |  | The RRO did not make its representatives on the NERC Operating Committee and Disturbance Analysis Working Group available for the purpose of providing any needed assistance in the investigation and to assist in the preparation of a final report. | [15 empty] | RRO
Inactive | EOP | EOP-004-1 | R5. | The Regional Reliability Organization shall track and review the status of all final report recommendations at least twice each year to ensure they are being acted upon in a timely manner. If any recommendation has not been acted on within two years, or if Regional Reliability Organization tracking and review indicates at any time that any recommendation is not being acted on with sufficient diligence, the Regional Reliability Organization shall notify the NERC Planning Committee and Operating Committee of the status of the recommendation(s) and the steps the Regional Reliability Organization has taken to accelerate implementation. | 2007-06-18 | 2013-12-31 | Low | The Regional Reliability Organization reviewed all final report recommendations less than twice a year. | The Regional Reliability Organization reviewed 75% or more final report recommendations twice a year. | The Regional Reliability Organization has not reported on any recommendation has not been acted on within two years to the NERC Planning and Operating Committees. | The Regional Reliability Organization has not reviewed the final report recommendations or did not notify the NERC Planning and Operating Committees. | [15 empty] | RRO
Inactive | EOP | EOP-004-2 | R1. | Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-2 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | 2014-01-01 | 2017-03-31 | Low | The Responsible Entity had an Operating Plan, but failed to include one applicable event type. | The Responsible Entity had an Operating Plan, but failed to include two applicable event types. | The Responsible Entity had an Operating Plan, but failed to include three applicable event types. | The Responsible Entity had an Operating Plan, but failed to include four or more applicable event types. OR The Responsible Entity failed to have an event reporting Operating Plan. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | EOP | EOP-004-2 | R2. | Each Responsible Entity shall report events per their Operating Plan within 24 hours of recognition of meeting an event type threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). | 2014-01-01 | 2017-03-31 | Medium | The Responsible Entity submitted an event report (e.g., written or verbal) to all required recipients more than 24 hours but less than or equal to 36 hours after meeting an event threshold for reporting. OR The Responsible Entity failed to submit an event report (e.g., written or verbal) to one entity identified in its event reporting Operating Plan within 24 hours. | The Responsible Entity submitted an event report (e.g., written or verbal) to all required recipients more than 36 hours but less than or equal to 48 hours after meeting an event threshold for reporting. OR The Responsible Entity failed to submit an event report (e.g., written or verbal) to two entities identified in its event reporting Operating Plan within 24 hours. | The Responsible Entity submitted an event report (e.g., written or verbal) to all required recipients more than 48 hours but less than or equal to 60 hours after meeting an event threshold for reporting. OR The Responsible Entity failed to submit an event report (e.g., written or verbal) to three entities identified in its event reporting Operating Plan within 24 hours. | The Responsible Entity submitted an event report (e.g., written or verbal) to all required recipients more than 60 hours after meeting an event threshold for reporting. OR The Responsible Entity failed to submit an event report (e.g., written or verbal) to four or more entities identified in its event reporting Operating Plan within 24 hours. OR The Responsible Entity failed to submit a report for an event in EOP-004 Attachment 1. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | EOP | EOP-004-2 | R3. | Each Responsible Entity shall validate all contact information contained in the Operating Plan pursuant to Requirement R1 each calendar year. | 2014-01-01 | 2017-03-31 | Medium | The Responsible Entity validated all contact information contained in the Operating Plan but was late by less than one calendar month. OR The Responsible Entity validated 75% but less than 100% of the contact information contained in the Operating Plan. | The Responsible Entity validated all contact information contained in the Operating Plan but was late by one calendar month or more but less than two calendar months. OR The Responsible Entity validated 50% and less than 75% of the contact information contained in the Operating Plan. | The Responsible Entity validated all contact information contained in the Operating Plan but was late by two calendar months or more but less than three calendar months. OR The Responsible Entity validated 25% and less than 50% of the contact information contained in the Operating Plan. | The Responsible Entity validated all contact information contained in the Operating Plan but was late by three calendar months or more. OR The Responsible Entity validated less than 25% of contact information contained in the Operating Plan. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | EOP | EOP-004-3 | R1. | Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-2-3 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | 2017-04-01 | 2019-03-31 | Low | The Responsible Entity had an Operating Plan, but failed to include one applicable event type. | The Responsible Entity had an Operating Plan, but failed to include two applicable event types. | The Responsible Entity had an Operating Plan, but failed to include three applicable event types. | The Responsible Entity had an Operating Plan, but failed to include four or more applicable event types. OR The Responsible Entity failed to have an event reporting Operating Plan. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | EOP | EOP-004-3 | R2. | Each Responsible Entity shall report events per their Operating Plan within 24 hours of recognition of meeting an event type threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). | 2017-04-01 | 2019-03-31 | Medium | The Responsible Entity submitted an event report (e.g., written or verbal) to all required recipients more than 24 hours but less than or equal to 36 hours after meeting an event threshold for reporting. OR The Responsible Entity failed to submit an event report (e.g., written or verbal) to one entity identified in its event reporting Operating Plan within 24 hours. | The Responsible Entity submitted an event report (e.g., written or verbal) to all required recipients more than 36 hours but less than or equal to 48 hours after meeting an event threshold for reporting. OR The Responsible Entity failed to submit an event report (e.g., written or verbal) to two entities identified in its event reporting Operating Plan within 24 hours. | The Responsible Entity submitted an event report (e.g., written or verbal) to all required recipients more than 48 hours but less than or equal to 60 hours after meeting an event threshold for reporting. OR The Responsible Entity failed to submit an event report (e.g., written or verbal) to three entities identified in its event reporting Operating Plan within 24 hours | The Responsible Entity submitted an event report (e.g., written or verbal) to all required recipients more than 60 hours after meeting an event threshold for reporting. OR The Responsible Entity failed to submit an event report (e.g., written or verbal) to four or more entities identified in its event reporting Operating Plan within 24 hours. OR The Responsible Entity failed to submit a report for an event in EOP-004 Attachment 1. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | EOP | EOP-004-3 | R3. | Each Responsible Entity shall validate all contact information contained in the Operating Plan pursuant to Requirement R1 each calendar year. | 2017-04-01 | 2019-03-31 | Medium | The Responsible Entity validated all contact information contained in the Operating Plan but was late by less than one calendar month. OR The Responsible Entity validated 75% but less than 100% of the contact information contained in the Operating Plan | The Responsible Entity validated all contact information contained in the Operating Plan but was late by one calendar month or more but less than two calendar months. OR The Responsible Entity validated 50% and less than 75% of the contact information contained in the Operating Plan. | The Responsible Entity validated all contact information contained in the Operating Plan but was late by two calendar months or more but less than three calendar months. OR The Responsible Entity validated 25% and less than 50% of the contact information contained in the Operating Plan. | The Responsible Entity validated all contact information contained in the Operating Plan but was late by three calendar months or more. OR The Responsible Entity validated less than 25% of contact information contained in the Operating Plan. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | EOP | EOP-004-4 | R1. | R1. Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-4 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | 2019-04-01 |  | Low | The Responsible Entity had an event reporting Operating Plan, but failed to include one applicable event type. | The Responsible Entity had an event reporting Operating Plan, but failed to include two applicable event types. | The Responsible Entity had an event reporting Operating Plan, but failed to include three applicable event types. | The Responsible Entity had an event reporting Operating Plan, but failed to include four or more applicable event types. OR The Responsible Entity failed to have an event reporting Operating Plan. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | EOP | EOP-004-4 | R2. | R2. Each Responsible Entity shall report events specified in EOP-004-4 Attachment 1 to the entities specified per their event reporting Operating Plan by the later of 24 hours of recognition of meeting an event type threshold for reporting or by the end of the Responsible Entity’s next business day (4 p.m. local time will be considered the end of the business day). | 2019-04-01 |  | Medium | The Responsible Entity submitted an event report (e.g., written or verbal) to all required recipients up to 24 hours after the timing requirement for submittal. OR The Responsible Entity failed to submit an event report (e.g., written or verbal) to one entity identified in its event reporting Operating Plan within 24 hours or by the end of the next business day, as applicable. | The Responsible Entity submitted an event report (e.g., written or verbal) to all required recipients more than 24 hours but less than or equal to 48 hours after the timing requirement for submittal. OR The Responsible Entity failed to submit an event report (e.g., written or verbal) to two entities identified in its event reporting Operating Plan within 24 hours or by the end of the next business day, as applicable. | The Responsible Entity submitted an event report (e.g., written or verbal) to all required recipients more than 48 hours but less than or equal to 72 hours after the timing requirement for submittal. OR The Responsible Entity failed to submit an event report (e.g., written or verbal) to three entities identified in its event reporting Operating Plan within 24 hours or by the end of the next business day, as applicable. | The Responsible Entity submitted an event report (e.g., written or verbal) to all required recipients more than 72 hours after the timing requirement for submittal. OR The Responsible Entity failed to submit an event report (e.g., written or verbal) to four or more entities identified in its event reporting Operating Plan within 24 hours or by the end of the next business day, as applicable. OR The Responsible Entity failed to submit a report for an event in EOP-004-4 Attachment 1. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | EOP | EOP-005-0 | R1. | Each Transmission Operator shall have a restoration plan to reestablish its electric system in a stable and orderly manner in the event of a partial or total shutdown of its system, including necessary operating instructions and procedures to cover emergency conditions, and the loss of vital telecommunications channels. Each Transmission Operator shall include the applicable elements listed in Attachment 1-EOP-005-0 in developing a restoration plan. |  | 2007-05-02 | [24 empty] | TOP
Inactive | EOP | EOP-005-0 | R2. | Each Transmission Operator shall review and update its restoration plan at least annually and whenever it makes changes in the power system network, and shall correct deficiencies found during the simulated restoration exercises. |  | 2007-05-02 | [24 empty] | TOP
Inactive | EOP | EOP-005-0 | R3. | Each Transmission Operator shall develop restoration plans with a priority of restoring the integrity of the Interconnection. |  | 2007-05-02 | [24 empty] | TOP
Inactive | EOP | EOP-005-0 | R4. | Each Transmission Operator shall coordinate its restoration plans with Balancing Authorities within its area, its Reliability Coordinator, and neighboring Transmission Operators and Balancing Authorities. |  | 2007-05-02 | [24 empty] | TOP
Inactive | EOP | EOP-005-0 | R5. | Each Transmission Operator and Balancing Authority shall periodically test its telecommunication facilities needed to implement the restoration plan. |  | 2007-05-02 | [6 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-005-0 | R6. | Each Transmission Operator and Balancing Authority shall train its operating personnel in the implementation of the restoration plan. Such training shall include simulated exercises, if practicable. |  | 2007-05-02 | [6 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-005-0 | R7. | Each Transmission Operator and Balancing Authority shall verify the restoration procedure by actual testing or by simulation. |  | 2007-05-02 | [6 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-005-0 | R8. | Each Transmission Operator shall ensure the availability and location of black start capability within its area to meet the needs of the restoration plan. |  | 2007-05-02 | [24 empty] | TOP
Inactive | EOP | EOP-005-0 | R9. | Following a disturbance in which one or more areas of the Bulk Electric System become isolated or blacked out, the affected Transmission Operators and Balancing Authorities shall begin immediately to return the Bulk Electric System to normal. |  | 2007-05-02 | [6 empty] | BA | [17 empty] | TOP
Inactive | EOP | EOP-005-1 | R1. | Each Transmission Operator shall have a restoration plan to reestablish its electric system in a stable and orderly manner in the event of a partial or total shutdown of its system, including necessary operating instructions and procedures to cover emergency conditions, and the loss of vital telecommunications channels. Each Transmission Operator shall include the applicable elements listed in Attachment 1-EOP-005 in developing a restoration plan. | 2007-06-18 | 2013-06-30 | Medium | The responsible entity has a restoration plan that includes 75 % or more but less than 100% of the applicable elements listed in Attachment 1. | The responsible entity has a restoration plan that includes 50% to 75% of the applicable elements listed in Attachment 1. | The responsible entity has a restoration plan that includes 25% - 50% of the applicable elements listed in Attachment 1. | The responsible entity has a restoration plan that includes less than 25% of the applicable elements listed in Attachment 1 OR the responsible entity has no restoration plan. | [19 empty] | TOP
Inactive | EOP | EOP-005-1 | R2. | Each Transmission Operator shall review and update its restoration plan at least annually and whenever it makes changes in the power system network, and shall correct deficiencies found during the simulated restoration exercises. | 2007-06-18 | 2013-06-30 | Medium | The Transmission Operator failed to review or update its restoration plan when it made changes in the power system network. | The Transmission Operator failed to review and update its restoration plan at least annually. | The Transmission Operator failed to review and update its restoration plan at least annually or whenever it made changes in the power system network, and failed to correct deficiencies found during the simulated restoration exercises. | The Transmission Operator failed to review and update its restoration plan at least annually and whenever it made changes in the power system network, and failed to correct deficiencies found during the simulated restoration exercises. | [19 empty] | TOP
Inactive | EOP | EOP-005-1 | R3. | Each Transmission Operator shall develop restoration plans with a priority of restoring the integrity of the Interconnection. | 2007-06-18 | 2013-06-30 | Medium |  |  |  | The Transmission Operator's restoration plans failed to make restoration of the integrity of the Interconnection a top priority. | [19 empty] | TOP
Inactive | EOP | EOP-005-1 | R4. | Each Transmission Operator shall coordinate its restoration plans with the Generator Owners and Balancing Authorities within its area, its Reliability Coordinator, and neighboring Transmission Operators and Balancing Authorities. | 2007-06-18 | 2013-06-30 | Medium | The Transmission Operator failed to coordinate its restoration plans with one of the entities listed in the requirement. | The Transmission Operator failed to coordinate its restoration plans with two of the entities listed in the requirement. | The Transmission Operator failed to coordinate its restoration plans with three of the entities listed in the requirement. | The Transmission Operator failed to coordinate its restoration plans with four or more of the entities listed in the requirement. | [19 empty] | TOP
Inactive | EOP | EOP-005-1 | R5. | Each Transmission Operator and Balancing Authority shall periodically test its telecommunication facilities needed to implement the restoration plan. | 2007-06-18 | 2013-06-30 | Medium |  |  |  | The responsible entity failed to periodically test its telecommunication facilities needed to implement the restoration plan. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-005-1 | R6. | Each Transmission Operator and Balancing Authority shall train its operating personnel in the implementation of the restoration plan. Such training shall include simulated exercises, if practicable. | 2007-06-18 | 2013-06-30 | High | The responsible entity only trained less than 100% but greater than or equal to 67 % of its operating personnel in the implementation of the restoration plan. | The responsible entity only trained less than 67 % but greater than or equal to 33 % of its operating personnel in the implementation of the restoration plan. | The responsible entity only trained less than 33 % of its operating personnel in the implementation of the restoration plan. | The responsible entity did not trained any of its operating personnel in the implementation of the restoration plan. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-005-1 | R7. | Each Transmission Operator and Balancing Authority shall verify the restoration procedure by actual testing or by simulation. | 2007-06-18 | 2013-06-30 | High | The responsible entity verified 76% to 99% of the restoration procedure by actual testing or by simulation. | The responsible entity verified 51% to 75% of the restoration procedure by actual testing or by simulation. | The responsible entity verified 26% to 50% of the restoration procedure by actual testing or by simulation. | The responsible entity verified less than 26% of the restoration procedure by actual testing or by simulation. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-005-1 | R8. | Each Transmission Operator shall verify that the number, size, availability, and location of system blackstart generating units are sufficient to meet Regional Reliability Organization restoration plan requirements for the Transmission Operator’s area. | 2007-06-18 | 2013-06-30 | High |  |  |  | The Transmission Operator failed to verify that the number, size, availability, and location of system blackstart generating units are sufficient to meet Regional Reliability Organization restoration plan requirements for the Transmission Operator’s area. | [19 empty] | TOP
Inactive | EOP | EOP-005-1 | R9. | The Transmission Operator shall document the Cranking Paths, including initial switching requirements, between each blackstart generating unit and the unit(s) to be started and shall provide this documentation for review by the Regional Reliability Organization upon request. Such documentation may include Cranking Path diagrams. | 2007-06-18 | 2013-06-30 | Medium |  |  |  | The Transmission Operator shall document the Cranking Paths, including initial switching requirements, between each blackstart generating unit and the unit(s) to be started and shall provide this documentation for review by the Regional Reliability Organi | [19 empty] | TOP
Inactive | EOP | EOP-005-1 | R10. | The Transmission Operator shall demonstrate, through simulation or testing, that the blackstart generating units in its restoration plan can perform their intended functions as required in the regional restoration plan. | 2007-06-18 | 2013-06-30 | Medium | The Transmission Operator only demonstrated, through simulation or testing, that between 67 and 99% of the blackstart generating units in its restoration plan can perform their intended functions as required in the regional restoration plan. | The Transmission Operator only demonstrated, through simulation or testing, that between 33 and 66% of the blackstart generating units in its restoration plan can perform their intended functions as required in the regional restoration plan. | The Transmission Operator only demonstrated, through simulation or testing, that less than 33% of the blackstart generating units in its restoration plan can perform their intended functions as required in the regional restoration plan. | The Transmission Operator did not demonstrate, through simulation or testing, that any of the blackstart generating units in its restoration plan can perform their intended functions as required in the regional restoration plan. | [19 empty] | TOP
Inactive | EOP | EOP-005-1 | R11. | Following a disturbance in which one or more areas of the Bulk Electric System become isolated or blacked out, the affected Transmission Operators and Balancing Authorities shall begin immediately to return the Bulk Electric System to normal. | 2007-06-18 | 2013-06-30 | High | The responsible entity failed to comply with less than 25% of the number of sub-components. | The responsible entity failed to comply with 25% or more and less than 50% of the number of sub-components. | The responsible entity failed to comply with 50% or more and less than 75% of the number of sub-components. | The responsible entity failed to comply with more than 75% of the number of sub-components. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-005-2 | R1. | Each Transmission Operator shall have a restoration plan approved by its Reliability Coordinator. The restoration plan shall allow for restoring the Transmission Operator’s System following a Disturbance in which one or more areas of the Bulk Electric System (BES) shuts down and the use of Blackstart Resources is required to restore the shut down area to service, to a state whereby the choice of the next Load to be restored is not driven by the need to control frequency or voltage regardless of whether the Blackstart Resource is located within the Transmission Operator’s System. The restoration plan shall include: | 2013-07-01 | 2019-03-31 | High | The Transmission Operator has an approved plan but failed to comply with one of the sub-requirements within the requirement. | The Transmission Operator has an approved plan but failed to comply with two of the sub-requirements within the requirement. | The Transmission Operator has an approved plan but failed to comply with three of the sub-requirements within the requirement. | The Transmission Operator does not have an approved restoration plan. | [19 empty] | TOP
Inactive | EOP | EOP-005-2 | R2. | Each Transmission Operator shall provide the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the implementation date of the plan. | 2013-07-01 | 2019-03-31 | Medium | The Transmission Operator failed to provide one of the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the implementation date of the plan. OR The Transmission Operator provided the information to all entities but was up to 10 calendar days late in doing so. | The Transmission Operator failed to provide two of the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the implementation date of the plan. OR The Transmission Operator provided the information to all entities but was more than 10 and less than or equal to 20 calendar days late in doing so. | The Transmission Operator failed to provide three of the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the implementation date of the plan. OR The Transmission Operator provided the information to all entities but was more than 20 and less than or equal to 30 calendar days late in doing so. | The Transmission Operator failed to provide four or more of the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the implementation date of the plan. OR The Transmission Operator provided the information to all entities but was more than 30 calendar days late in doing so. | [19 empty] | TOP
Inactive | EOP | EOP-005-2 | R3. | Each Transmission Operator shall review its restoration plan and submit it to its Reliability Coordinator annually on a mutually agreed predetermined schedule. | 2013-07-01 | 2019-03-31 | Medium | The Transmission Operator submitted the reviewed restoration plan or confirmation of no change within 30 calendar days after the pre-determined schedule. | The Transmission Operator submitted the reviewed restoration plan or confirmation of no change more than 30 and less than or equal to 60 calendar days after the pre-determined schedule. | The Transmission Operator submitted the reviewed restoration plan or confirmation of no change more than 60 and less than or equal to 90 calendar days after the pre-determined schedule. | The Transmission Operator submitted the reviewed restoration plan or confirmation of no change more than 90 calendar days after the predetermined schedule. | [19 empty] | TOP
Inactive | EOP | EOP-005-2 | R4. | Each Transmission Operator shall update its restoration plan within 90 calendar days after identifying any unplanned permanent System modifications, or prior to implementing a planned BES modification, that would change the implementation of its restoration plan. | 2013-07-01 | 2019-03-31 | Medium | The Transmission Operator failed to update and submit its restoration plan to the Reliability Coordinator within 90 calendar days of an unplanned change. | The Transmission Operator failed to update and submit its restoration plan to the Reliability Coordinator within more than 90 calendar days but less than120 calendar days of an unplanned change. | The Transmission Operator has failed to update and submit its restoration plan to the Reliability Coordinator within more than 120 calendar days but less than 150 calendar days of unplanned change. | The Transmission Operator has failed to update and submit its restoration plan to the Reliability Coordinator within more than 150 calendar days of an unplanned change. OR The Transmission Operator failed to update and submit its restoration plan to the Reliability Coordinator prior to a planned BES modification. | [19 empty] | TOP
Inactive | EOP | EOP-005-2 | R5. | Each Transmission Operator shall have a copy of its latest Reliability Coordinator approved restoration plan within its primary and backup control rooms so that it is available to all of its System Operators prior to its implementation date. | 2013-07-01 | 2019-03-31 | Low | N/A | N/A | N/A | The Transmission Operator did not make the latest Reliability Coordinator approved restoration plan available in its primary and backup control rooms prior to its implementation date. | [19 empty] | TOP
Inactive | EOP | EOP-005-2 | R6. | Each Transmission Operator shall verify through analysis of actual events, steady state and dynamic simulations, or testing that its restoration plan accomplishes its intended function. This shall be completed every five years at a minimum. Such analysis, simulations or testing shall verify: | 2013-07-01 | 2019-03-31 | Medium | The Transmission Operator performed the verification within the required timeframe but did not comply with one of the sub-requirements. | The Transmission Operator performed the verification within the required timeframe but did not comply with two of the sub-requirements. | The Transmission Operator performed the verification but did not complete it within the five calendar year period. | The Transmission Operator did not perform the verification or it took more than six calendar years to complete the verification. OR The Transmission Operator performed the verification within the required timeframe but did not comply with any of the sub-requirements. | [19 empty] | TOP
Inactive | EOP | EOP-005-2 | R7. | Following a Disturbance in which one or more areas of the BES shuts down and the use of Blackstart Resources is required to restore the shut down area to service, each affected Transmission Operator shall implement its restoration plan. If the restoration plan cannot be executed as expected the Transmission Operator shall utilize its restoration strategies to facilitate restoration. | 2013-07-01 | 2019-03-31 | High | N/A | N/A | N/A | The Transmission Operator did not implement its restoration plan following a Disturbance in which Blackstart Resources have been utilized in restoring the shut down area of the BES. Or, if the restoration plan cannot be executed as expected, the Transmission Operator did not utilize its restoration plan strategies to facilitate restoration. | [19 empty] | TOP
Inactive | EOP | EOP-005-2 | R8. | Following a Disturbance in which one or more areas of the BES shuts down and the use of Blackstart Resources is required to restore the shut down area to service, the Transmission Operator shall resynchronize area(s) with neighboring Transmission Operator area(s) only with the authorization of the Reliability Coordinator or in accordance with the established procedures of the Reliability Coordinator. | 2013-07-01 | 2019-03-31 | High | N/A | N/A | N/A | The Transmission Operator resynchronized without approval of the Reliability Coordinator or not in accordance with the established procedures of the Reliability Coordinator following a Disturbance in which Blackstart Resources have been utilized in restoring the shut down area of the BES to service. | [19 empty] | TOP
Inactive | EOP | EOP-005-2 | R9. | Each Transmission Operator shall have Blackstart Resource testing requirements to verify that each Blackstart Resource is capable of meeting the requirements of its restoration plan. These Blackstart Resource testing requirements shall include: | 2013-07-01 | 2019-03-31 | Medium | N/A | N/A | N/A | The Transmission Operator’s Blackstart Resource testing requirements do not address one or more of the sub-requirements of Requirement R9. | [19 empty] | TOP
Inactive | EOP | EOP-005-2 | R10. | Each Transmission Operator shall include within its operations training program, annual System restoration training for its System Operators to assure the proper execution of its restoration plan. This training program shall include training on the following: | 2013-07-01 | 2019-03-31 | Medium | The Transmission Operator’s training does not address one of the sub-requirements of Requirement R10. | The Transmission Operator’s training does not address two of the sub-requirements of Requirement R10. | The Transmission Operator’s training does not address three or more of the sub-requirements of Requirement R10. | The Transmission Operator has not included System restoration training in its operations training program. | [19 empty] | TOP
Inactive | EOP | EOP-005-2 | R11. | Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall provide a minimum of two hours of System restoration training every two calendar years to their field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks. | 2013-07-01 | 2019-03-31 | Medium | The Transmission Operator, applicable Transmission Owner, or applicable Distribution Provider failed to train 5% or less of the personnel required by Requirement R11 within a two calendar year period. | The Transmission Operator, applicable Transmission Owner, or applicable Distribution Provider failed to train more than 5% and up to 10% of the personnel required by Requirement R11 within a two calendar year period. | The Transmission Operator, applicable Transmission Owner, or applicable Distribution Provider failed to train more than 10% and up to 15% of the personnel required by Requirement R11 within a two calendar year period. | The Transmission Operator, applicable Transmission Owner, or applicable Distribution Provider failed to train more than 15% the personnel required by Requirement R11 within a two calendar year period. |  |  | DP | [15 empty] | TO | TOP
Inactive | EOP | EOP-005-2 | R12. | Each Transmission Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | 2013-07-01 | 2019-03-31 | Medium | N/A | N/A | N/A | The Transmission Operator has failed to comply with a request for their participation from the Reliability Coordinator. | [19 empty] | TOP
Inactive | EOP | EOP-005-2 | R13. | Each Transmission Operator and each Generator Operator with a Blackstart Resource shall have written Blackstart Resource Agreements or mutually agreed upon procedures or protocols, specifying the terms and conditions of their arrangement. Such Agreements shall include references to the Blackstart Resource testing requirements. | 2013-07-01 | 2019-03-31 | Medium | N/A | The Transmission Operator and Generator Operator with a Blackstart Resource do not reference Blackstart Resource Testing requirements in their written Blackstart Resource Agreements or mutually agreed upon procedures or protocols. | N/A | The Transmission Operator and Generator Operator with a Blackstart resource do not have a written Blackstart Resource Agreement or mutually agreed upon procedure or protocol. | [6 empty] | GOP | [12 empty] | TOP
Inactive | EOP | EOP-005-2 | R14. | Each Generator Operator with a Blackstart Resource shall have documented procedures for starting each Blackstart Resource and energizing a bus. | 2013-07-01 | 2019-03-31 | Medium | N/A | N/A | N/A | The Generator Operator does not have documented starting and bus energizing procedures for each Blackstart Resource. | [6 empty] | GOP
Inactive | EOP | EOP-005-2 | R15. | Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following such change. | 2013-07-01 | 2019-03-31 | Medium | The Generator Operator with a Blackstart Resource did not notify the Transmission Operator of a known change in Blackstart Resource capability affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours but did make the notification within 48 hours. | The Generator Operator with a Blackstart Resource did not notify the Transmission Operator of a known change in Blackstart Resource capability affecting the ability to meet the Transmission Operator’s restoration plan within 48 hours but did make the notification within 72 hours. | The Generator Operator with a Blackstart Resource did not notify the Transmission Operator of a known change in Blackstart Resource capability affecting the ability to meet the Transmission Operator’s restoration plan within 72 hours but did make the notification within 96 hours. | The Generator Operator with a Blackstart Resource did not notify the Transmission Operator of a known change in Blackstart Resource capability affecting the ability to meet the Transmission Operator’s restoration plan for more than 96 hours. | [6 empty] | GOP
Inactive | EOP | EOP-005-2 | R16. | Each Generator Operator with a Blackstart Resource shall perform Blackstart Resource tests, and maintain records of such testing, in accordance with the testing requirements set by the Transmission Operator to verify that the Blackstart Resource can perform as specified in the restoration plan. | 2013-07-01 | 2019-03-31 | Medium | The GOP with a Blackstart Resource performed tests and maintained records but the records did not include all of the items in R16.1. OR The Generator Operator did not supply the Blackstart Resource testing records as requested for 31 to 60 calendar days of the request. | The GOP with a Blackstart Resource performed tests and maintained records but did not supply the Blackstart Resource testing records as requested for 61 days to 90 calendar days after the request. | The GOP with a Blackstart Resource performed tests but either did not maintain records or did not supply the Blackstart Resource testing records as requested within 91 or more calendar days after the request. | The Generator Operator with a Blackstart Resource did not perform Blackstart Resource tests. | [6 empty] | GOP
Inactive | EOP | EOP-005-2 | R17. | Each Generator Operator with a Blackstart Resource shall provide a minimum of two hours of training every two calendar years to each of its operating personnel responsible for the startup of its Blackstart Resource generation units and energizing a bus. The training program shall include training on the following: | 2013-07-01 | 2019-03-31 | Medium | The Generator Operator with a Blackstart Resource did not train less than or equal to 10% of the personnel required by Requirement R17 within a two calendar year period. | The Generator Operator with a Blackstart Resource did not train more than 10% and less than or equal to 25% of the personnel required by Requirement R17 within a two calendar year period. | The Generator Operator with a Blackstart Resource did not train more than 25% and less than or equal to 50% of the personnel required by Requirement R17 within a two calendar year period. | The Generator Operator with a Blackstart Resource did not train more than 50% of the personnel required by Requirement R17 within a two calendar year period. | [6 empty] | GOP
Inactive | EOP | EOP-005-2 | R18. | Each Generator Operator shall participate in the Reliability Coordinator’s restoration drills, exercises, or simulations as requested by the Reliability Coordinator. | 2013-07-01 | 2019-03-31 | Medium | N/A | N/A | N/A | The Generator Operator failed to participate in the Reliability Coordinator’s restoration drills, exercises, or simulations as requested by the Reliability Coordinator. | [6 empty] | GOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R1. | Each Transmission Operator shall develop and implement a restoration plan approved by its Reliability Coordinator. The restoration plan shall be implemented to restore the Transmission Operator’s System following a Disturbance in which one or more areas of the Bulk Electric System (BES) shuts down and the use of Blackstart Resources is required to restore the shutdown area to a state whereby the choice of the next Load to be restored is not driven by the need to control frequency or voltage regardless of whether the Blackstart Resource is located within the Transmission Operator’s System. The restoration plan shall include: | 2019-04-01 |  | High | The Transmission Operator has an approved plan but failed to comply with one of the requirement parts within Requirement R1. | The Transmission Operator has an approved plan but failed to comply with two of the requirement parts within Requirement R1. | The Transmission Operator has an approved plan but failed to comply with three or more of the requirement parts within Requirement R1. | The Transmission Operator does not have an approved restoration plan. OR The Transmission Operator has an approved restoration plan, but failed to implement the applicable requirement parts within Requirement R1. | [19 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R2. | Each Transmission Operator shall provide the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date of the plan. | 2019-04-01 |  | Medium | The Transmission Operator failed to provide one of the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date of the plan. | The Transmission Operator failed to provide two of the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date of the plan. | The Transmission Operator failed to provide three of the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date of the plan. | The Transmission Operator failed to provide four or more of the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date of the plan. OR Transmission Operator failed to provide at least half of the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date. | [19 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R3. | Each Transmission Operator shall review its restoration plan and submit it to its Reliability Coordinator annually on a mutually-agreed, predetermined schedule. | 2019-04-01 |  | Medium | The Transmission Operator submitted the reviewed restoration plan within 30 calendar days after the mutually-agreed, predetermined schedule. | The Transmission Operator submitted the reviewed restoration plan more than 30 and less than or equal to 60 calendar days after the mutually-agreed, predetermined schedule. | The Transmission Operator submitted the reviewed restoration plan more than 60 and less than or equal to 90 calendar days after the mutually-agreed, predetermined schedule. | The Transmission Operator submitted the reviewed restoration plan more than 90 calendar days after the mutually-agreed, predetermined schedule. | [19 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R4. | Each Transmission Operator shall submit its revised restoration plan to its Reliability Coordinator for approval, when the revision would change its ability to implement its restoration plan, as follows: | 2019-04-01 |  | Medium | The Transmission Operator failed to submit its revised restoration plan to its Reliability Coordinator within 90 calendar days of an unplanned permanent System BES modification. | The Transmission Operator submitted its revised restoration plan to its Reliability Coordinator between 91 calendar days and 120 calendar days of an unplanned permanent System BES modification. | The Transmission Operator submitted its revised restoration plan to its Reliability Coordinator between 121 calendar days and 150 calendar days of an unplanned permanent System BES modification. | The Transmission Operator has failed to submit its revised restoration plan to its Reliability Coordinator within 150 calendar days of an unplanned permanent System BES modification. OR The Transmission Operator failed to submit its revised restoration plan to its Reliability Coordinator prior to a planned permanent BES modification. | [19 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R5. | Each Transmission Operator shall have a copy of its latest Reliability Coordinator approved restoration plan within its primary and backup control rooms so that it is available to all of its System Operators prior to its effective date. | 2019-04-01 |  | Low | N/A | N/A | N/A | The Transmission Operator did not make the latest Reliability Coordinator approved restoration plan available in its primary and backup control rooms prior to its effective date. | [19 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R6. | Each Transmission Operator shall verify through analysis of actual events, a combination of steady state and dynamic simulations, or testing that its restoration plan accomplishes its intended function. This shall be completed at least once every five years. Such analysis, simulations or testing shall verify: | 2019-04-01 |  | Medium | The Transmission Operator performed the verification within the required timeframe but did not comply with one of the requirement parts. | The Transmission Operator performed the verification within the required timeframe but did not comply with two of the requirement parts. | The Transmission Operator performed the verification but did not complete it within the required time frame. | The Transmission Operator did not perform the verification or it took more than six calendar years to complete the verification. OR The Transmission Operator performed the verification within the required timeframe but did not comply with any of the requirement parts. | [19 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R7. | Each Transmission Operator shall have Blackstart Resource testing requirements to verify that each Blackstart Resource is capable of meeting the requirements of its restoration plan. These Blackstart Resource testing requirements shall include: | 2019-04-01 |  | Medium | N/A | N/A | N/A | The Transmission Operator’s Blackstart Resource testing requirements do not address one or more of the requirement parts of Requirement R7. | [19 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R8. | Each Transmission Operator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall include training on the following: | 2019-04-01 |  | Medium | The Transmission Operator’s training does not address one of the requirement parts of Requirement R8. | The Transmission Operator’s training does not address two of the requirement parts of Requirement R8. | The Transmission Operator’s training does not address three or more of the requirement parts of Requirement R8. | The Transmission Operator has not included System restoration training in its operations training program. | [19 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R9. | Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall provide a minimum of two hours of System restoration training every two calendar years to their field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks. | 2019-04-01 |  | Medium | The Transmission Operator, applicable Transmission Owner, or applicable Distribution Provider failed to train 5% or less of the personnel required by Requirement R9 within a two-calendar-year period. | The Transmission Operator, applicable Transmission Owner, or applicable Distribution Provider failed to train more than 5% and up to 10% of the personnel required by Requirement R9 within a two-calendar-year period. | The Transmission Operator, applicable Transmission Owner, or applicable Distribution Provider failed to train more than 10% and up to 15% of the personnel required by Requirement R9 two-calendar-year period. | The Transmission Operator, applicable Transmission Owner, or applicable Distribution Provider failed to train more than 15% of the personnel required by Requirement R9 within a two-calendar-year period. |  |  | DP | [15 empty] | TO | TOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R10. | Each Transmission Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | 2019-04-01 |  | Medium | N/A | N/A | N/A | The Transmission Operator has failed to comply with a request for its participation from its Reliability Coordinator. | [19 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R11. | Each Transmission Operator and each Generator Operator with a Blackstart Resource shall have written Blackstart Resource Agreements or mutually agreed upon procedures or protocols, specifying the terms and conditions of their arrangement. Such Agreements shall include references to the Blackstart Resource testing requirements. | 2019-04-01 |  | Medium | N/A | The Transmission Operator and Generator Operator with a Blackstart Resource do not reference Blackstart Resource Testing requirements in their written Blackstart Resource Agreements or mutually-agreed upon procedures or protocols. | N/A | The Transmission Operator and Generator Operator with a Blackstart resource do not have a written Blackstart Resource Agreement or mutually-agreed upon procedure or protocol. | [6 empty] | GOP | [12 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R12. | Each Generator Operator with a Blackstart Resource shall have documented procedures for starting each Blackstart Resource and energizing a bus. | 2019-04-01 |  | Medium | N/A | N/A | N/A | The Generator Operator does not have documented starting and bus energizing procedures for each Blackstart Resource. | [6 empty] | GOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R13. | Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following such change. | 2019-04-01 |  | Medium | The Generator Operator with a Blackstart Resource did not notify the Transmission Operator of a known change in Blackstart Resource capability affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours but did make the notification within 48 hours. | The Generator Operator with a Blackstart Resource did not notify the Transmission Operator of a known change in Blackstart Resource capability affecting the ability to meet the Transmission Operator’s restoration plan within 48 hours but did make the notification within 72 hours. | The Generator Operator with a Blackstart Resource did not notify the Transmission Operator of a known change in Blackstart Resource capability affecting the ability to meet the Transmission Operator’s restoration plan within 72 hours but did make the notification within 96 hours. | The Generator Operator with a Blackstart Resource did not notify the Transmission Operator of a known change in Blackstart Resource capability affecting the ability to meet the Transmission Operator’s restoration plan for more than 96 hours. | [6 empty] | GOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R14. | Each Generator Operator with a Blackstart Resource shall perform Blackstart Resource tests, and maintain records of such testing, in accordance with the testing requirements set by the Transmission Operator to verify that the Blackstart Resource can perform as specified in the restoration plan. | 2019-04-01 |  | Medium | The Generator Operator with a Blackstart Resource performed tests and maintained records but the records did not include all of the items in Requirement R14, Part 14.1. OR The Generator Operator did not supply the Blackstart Resource testing records as requested for 31 to 60 calendar days after the request. | The Generator Operator with a Blackstart Resource performed tests and maintained records but did not supply the Blackstart Resource testing records as requested for 61 to 90 calendar days after the request. | The Generator Operator with a Blackstart Resource performed tests but either did not maintain records or did not supply the Blackstart Resource testing records as requested within 91 or more calendar days after the request. | The Generator Operator with a Blackstart Resource did not perform Blackstart Resource tests. | [6 empty] | GOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R15. | Each Generator Operator with a Blackstart Resource shall provide a minimum of two hours of training every two calendar years to each of its operating personnel responsible for the startup of its Blackstart Resource generation units and energizing a bus. The training program shall include training on the following: | 2019-04-01 |  | Medium | The Generator Operator with a Blackstart Resource did not train less than or equal to 10% of the personnel required by Requirement R15 within a two-calendar-year period. | The Generator Operator with a Blackstart Resource did not train more than 10% and less than or equal to 25% of the personnel required by Requirement R15 within a two-calendar-year period. | The Generator Operator with a Blackstart Resource did not train more than 25% and less than or equal to 50% of the personnel required by Requirement R15 within a two-calendar-year period. | The Generator Operator with a Blackstart Resource did not train more than 50% of the personnel required by Requirement R15 within a two-calendar-year period. | [6 empty] | GOP
Mandatory Subject to Enforcement | EOP | EOP-005-3 | R16. | Each Generator Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | 2019-04-01 |  | Medium | N/A | N/A | N/A | The Generator Operator failed to participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | [6 empty] | GOP
Inactive | EOP | EOP-006-0 | R1. | Each Reliability Coordinator shall be aware of the restoration plan of each Transmission Operator in its Reliability Coordinator Area in accordance with NERC and regional requirements. |  | 2007-01-01 | [17 empty] | RC
Inactive | EOP | EOP-006-0 | R2. | The Reliability Coordinator shall monitor restoration progress and coordinate any needed assistance. |  | 2007-01-01 | [17 empty] | RC
Inactive | EOP | EOP-006-0 | R3. | The Reliability Coordinator shall have a Reliability Coordinator Area restoration plan that provides coordination between individual Transmission Operator restoration plans and that ensures reliability is maintained during system restoration events. |  | 2007-01-01 | [17 empty] | RC
Inactive | EOP | EOP-006-0 | R4. | The Reliability Coordinator shall serve as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators and Transmission Operators or Balancing Authorities not immediately involved in restoration. |  | 2007-01-01 | [17 empty] | RC
Inactive | EOP | EOP-006-0 | R5. | Reliability Coordinators shall approve, communicate, and coordinate the re-synchronizing of major system islands or synchronizing points so as not to cause a Burden on adjacent Transmission Operator, Balancing Authority, or Reliability Coordinator Areas. |  | 2007-01-01 | [17 empty] | RC
Inactive | EOP | EOP-006-0 | R6. | The Reliability Coordinator shall take actions to restore normal operations once an operating emergency has been mitigated in accordance with its restoration plan. |  | 2007-01-01 | [17 empty] | RC
Inactive | EOP | EOP-006-1 | R1. | Each Reliability Coordinator shall be aware of the restoration plan of each Transmission Operator in its Reliability Coordinator Area in accordance with NERC and regional requirements. | 2007-06-18 | 2013-06-30 | Medium | The Reliability Coordinator is aware of more than 75% of its Transmission Operators restoration plans. | The Reliability Coordinator is aware of more than 50% but less than 75%of its Transmission Operators restoration plans. | The Reliability Coordinator is aware of more than 25% but less than 50% of its Transmission Operators restoration plans. | The Reliability Coordinator is not aware of any of its Transmission Operators restoration plans. | [12 empty] | RC
Inactive | EOP | EOP-006-1 | R2. | The Reliability Coordinator shall monitor restoration progress and coordinate any needed assistance. | 2007-06-18 | 2013-06-30 | High |  |  | The Reliability Coordinator failed to monitor restoration progress or failed to coordinate assistance. | The Reliability Coordinator failed to monitor restoration progress and failed to coordinate assistance. | [12 empty] | RC
Inactive | EOP | EOP-006-1 | R3. | The Reliability Coordinator shall have a Reliability Coordinator Area restoration plan that provides coordination between individual Transmission Operator restoration plans and that ensures reliability is maintained during system restoration events. | 2007-06-18 | 2013-06-30 | Medium |  | The Reliability Coordinator's Reliability Coordinator Area restoration plan did not coordinate with one individual Transmission Operator restoration plans. | The Reliability Coordinator's Reliability Coordinator Area restoration plan did not coordinate with more than one individual Transmission Operator restoration plans. | The Reliability Coordinator does not have a Reliability Coordinator Area restoration plan. | [12 empty] | RC
Inactive | EOP | EOP-006-1 | R4. | The Reliability Coordinator shall serve as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators and Transmission Operators or Balancing Authorities not immediately involved in restoration. | 2007-06-18 | 2013-06-30 | Medium | The Reliability Coordinator failed to disseminate information regarding restoration to one neighboring Reliability Coordinator or Transmission Operator or Balancing Authority not immediately involved in restoration. | The Reliability Coordinator failed to disseminate information regarding restoration to two neighboring Reliability Coordinators or Transmission Operators or Balancing Authorities not immediately involved in restoration. | The Reliability Coordinator failed to disseminate information regarding restoration to three neighboring Reliability Coordinators or Transmission Operators or Balancing Authorities not immediately involved in restoration. | The Reliability Coordinator failed to disseminate information regarding restoration to four or more neighboring Reliability Coordinators or Transmission Operators or Balancing Authorities not immediately involved in restoration. | [12 empty] | RC
Inactive | EOP | EOP-006-1 | R5. | Reliability Coordinators shall approve, communicate, and coordinate the re-synchronizing of major system islands or synchronizing points so as not to cause a Burden on adjacent Transmission Operator, Balancing Authority, or Reliability Coordinator Areas. | 2007-06-18 | 2013-06-30 | High |  |  |  | The Reliability Coordinators failed to approve, communicate, and coordinate the re-synchronizing of major system islands or synchronizing points and caused a Burden on adjacent Transmission Operator, Balancing Authority, or Reliability Coordinator Areas. | [12 empty] | RC
Inactive | EOP | EOP-006-1 | R6. | The Reliability Coordinator shall take actions to restore normal operations once an operating emergency has been mitigated in accordance with its restoration plan. | 2007-06-18 | 2013-06-30 | Medium |  |  |  | The Reliability Coordinator failed to take actions to restore normal operations once an operating emergency has been mitigated in accordance with its restoration plan. | [12 empty] | RC
Inactive | EOP | EOP-006-2 | R1. | Each Reliability Coordinator shall have a Reliability Coordinator Area restoration plan. The scope of the Reliability Coordinator’s restoration plan starts when Blackstart Resources are utilized to re-energize a shut down area of the Bulk Electric System (BES), or separation has occurred between neighboring Reliability Coordinators, or an energized island has been formed on the BES within the Reliability Coordinator Area. The scope of the Reliability Coordinator’s restoration plan ends when all of its Transmission Operators are interconnected and it its Reliability Coordinator Area is connected to all of its neighboring Reliability Coordinator Areas. The restoration plan shall include: | 2013-07-01 | 2019-03-31 | High | The Reliability Coordinator failed to include one subrequirement of Requirement R1 within its restoration plan. | The Reliability Coordinator failed to include two subrequirements of Requirement R1 within its restoration plan. | The Reliability Coordinator failed to include three of the sub-requirements of Requirement R1 within its restoration plan. | The Reliability Coordinator failed to include four or more of the sub-requirements within its restoration plan. | [12 empty] | RC
Inactive | EOP | EOP-006-2 | R2. | The Reliability Coordinator shall distribute its most recent Reliability Coordinator Area restoration plan to each of its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of creation or revision. | 2013-07-01 | 2019-03-31 | Low | The Reliability Coordinator distributed the most recent Reliability Coordinator Area restoration plan to the entities identified in Requirement R2 but was more than 30 calendar days late but less than 60 calendar days late. | The Reliability Coordinator distributed the most recent Reliability Coordinator Area restoration plan to the entities identified in Requirement R2 but was 60 calendar days or more late, but less than 90 calendar days late | The Reliability Coordinator distributed the most recent Reliability Coordinator Area restoration plan to the entities identified in Requirement R2 but was 90 or more calendar days late but less than 120 calendar days late. | The Reliability Coordinator distributed the most recent Reliability Coordinator Area restoration plan to entities identified in Requirement R2 but was 120 calendar days or more late. | [12 empty] | RC
Inactive | EOP | EOP-006-2 | R3. | Each Reliability Coordinator shall review its restoration plan within 13 calendar months of the last review. | 2013-07-01 | 2019-03-31 | Medium | N/A | N/A | N/A | The Reliability Coordinator did not review its restoration plan within 13 calendar months of the last review. | [12 empty] | RC
Inactive | EOP | EOP-006-2 | R4. | Each Reliability Coordinator shall review their neighboring Reliability Coordinator’s restoration plans. | 2013-07-01 | 2019-03-31 | Medium | The Reliability Coordinator did not review and resolve conflicts with the submitted restoration plans from its neighboring Reliability Coordinators within 30 calendar days but did resolve conflicts within 60 calendar days. | The Reliability Coordinator did not review and resolve conflicts with the submitted restoration plans from its neighboring Reliability Coordinators within 30 calendar days but did resolve conflicts within 90 calendar days. | The Reliability Coordinator did not review and resolve conflicts with the submitted restoration plans from its neighboring Reliability Coordinators within 30 calendar days but did resolve conflicts within 120 calendar days. | The Reliability Coordinator did not review and resolve conflicts with the submitted restoration plans from its neighboring Reliability Coordinators within 120 calendar days. | [12 empty] | RC
Inactive | EOP | EOP-006-2 | R5. | Each Reliability Coordinator shall review the restoration plans required by EOP-005 of the Transmission Operators within its Reliability Coordinator Area. | 2013-07-01 | 2019-03-31 | Medium | The Reliability Coordinator did not review and approve/disapprove the submitted restoration plans from its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of receipt but did review and approve/disapprove the plans within 45 calendar days of receipt. OR The Reliability Coordinator failed to notify the Transmission Operator of its approval or disapproval with stated reasons for disapproval within 30 calendar days of receipt but did notify the Transmission Operator of its approval or disapproval with reasons within 45 calendar days of receipt. | The Reliability Coordinator did not review and approve/disapprove the submitted restoration plans from its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of receipt but did review and approve/disapprove the plans within 60 calendar days of receipt. OR The Reliability Coordinator failed to notify the Transmission Operator of its approval or disapproval with stated reasons for disapproval within 30 calendar days of receipt, but did notify the Transmission Operator of its approval or disapproval with reasons within 60 calendar days of receipt | The Reliability Coordinator did not review and approve/disapprove the submitted restoration plans from its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of receipt but did review and approve/disapprove the plans within 90 calendar days of receipt. OR The Reliability Coordinator failed to notify the Transmission Operator of its approval or disapproval with stated reasons for disapproval within 30 calendar days of receipt but did notify the Transmission Operator of its approval or disapproval with reasons within 90 calendar days of receipt. | The Reliability Coordinator did not review and approve/disapprove the submitted restoration plans from its Transmission Operators and neighboring Reliability Coordinators for more than 90 calendar days of receipt. OR The Reliability Coordinator failed to notify the Transmission Operator of its approval or disapproval with stated reasons for disapproval for more than 90 calendar days of receipt. | [12 empty] | RC
Inactive | EOP | EOP-006-2 | R6. | Each Reliability Coordinator shall have a copy of its latest restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area within its primary and backup control rooms so that it is available to all of its System Operators prior to the implementation date. | 2013-07-01 | 2019-03-31 | Low | N/A | N/A | The Reliability Coordinator did not have a copy of the latest approved restoration plan of all Transmission Operators in its Reliability Coordinator Area within its primary and backup control rooms prior to the implementation date. | The Reliability Coordinator did not have a copy of its latest restoration plan within its primary and backup control rooms prior to the implementation date. | [12 empty] | RC
Inactive | EOP | EOP-006-2 | R7. | Each Reliability Coordinator shall work with its affected Generator Operators, and Transmission Operators as well as neighboring Reliability Coordinators to monitor restoration progress, coordinate restoration, and take actions to restore the BES frequency within acceptable operating limits. If the restoration plan cannot be completed as expected the Reliability Coordinator shall utilize its restoration plan strategies to facilitate System restoration. | 2013-07-01 | 2019-03-31 | High | N/A | N/A | N/A | The Reliability Coordinator did not work with its affected Generator Operators and Transmission Operators as well as neighboring Reliability Coordinators to monitor restoration progress, coordinate restoration, and take actions to restore the BES frequency within acceptable operating limits. OR When the restoration plan cannot be completed as expected, the Reliability Coordinator did not utilize its restoration plan strategies to facilitate System restoration. | [12 empty] | RC
Inactive | EOP | EOP-006-2 | R8. | The Reliability Coordinator shall coordinate or authorize resynchronizing islanded areas that bridge boundaries between Transmission Operators or Reliability Coordinators. If the resynchronization cannot be completed as expected the Reliability Coordinator shall utilize its restoration plan strategies to facilitate resynchronization. | 2013-07-01 | 2019-03-31 | High | N/A | N/A | N/A | The Reliability Coordinator did not coordinate or authorize resynchronizing islanded areas that bridge boundaries between Transmission Operators or Reliability Coordinators. OR If the resynchronization could not be completed as expected, the Reliability Coordinator did not utilize its restoration plan strategies to facilitate resynchronization. | [12 empty] | RC
Inactive | EOP | EOP-006-2 | R9. | Each Reliability Coordinator shall include within its operations training program, annual System restoration training for its System Operators to assure the proper execution of its restoration plan. This training program shall address the following: | 2013-07-01 | 2019-03-31 | Medium | N/A | N/A | The Reliability Coordinator included the annual System restoration training within its operations training program, but did not address both of the sub-requirements. | The Reliability Coordinator did not include the annual System restoration training within its operations training program. | [12 empty] | RC
Inactive | EOP | EOP-006-2 | R10. | Each Reliability Coordinator shall conduct two System restoration drills, exercises, or simulations per calendar year, which shall include the Transmission Operators and Generator Operators as dictated by the particular scope of the drill, exercise, or simulation that is being conducted. | 2013-07-01 | 2019-03-31 | Medium | The Reliability Coordinator only held one restoration drill, exercise, or simulation during the calendar year. | The Reliability Coordinator did not invite a Transmission Operator or Generator Operator identified in its restoration plan to participate in a drill, exercise, or simulation within two calendar years. | N/A | The Reliability Coordinator did not hold a restoration drill, exercise, or simulation during the calendar year. | [12 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006-3 | R1. | Each Reliability Coordinator shall develop and implement a Reliability Coordinator Area restoration plan. The scope of the Reliability Coordinator’s restoration plan starts when Blackstart Resources are utilized to re-energize a shutdown area of the Bulk Electric System (BES), or separation has occurred between neighboring Reliability Coordinators, or an energized island has been formed on the BES within the Reliability Coordinator Area. The scope of the Reliability Coordinator’s restoration plan ends when all of its Transmission Operators are interconnected and its Reliability Coordinator Area is connected to all of its neighboring Reliability Coordinator Areas. The restoration plan shall include: | 2019-04-01 |  | High | The Reliability Coordinator failed to include one requirement part of Requirement R1 within its restoration plan. | The Reliability Coordinator failed to include two requirement parts of Requirement R1 within its restoration plan. | The Reliability Coordinator failed to include three of the requirements parts of Requirement R1 within its restoration plan. | The Reliability Coordinator failed to include four or more of the requirement parts within its restoration plan. OR The Reliability Coordinator had a restoration plan, but failed to implement it. | [12 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006-3 | R2. | The Reliability Coordinator shall distribute its most recent Reliability Coordinator Area restoration plan to each of its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of creation or revision | 2019-04-01 |  | Low | The Reliability Coordinator distributed the most recent Reliability Coordinator Area restoration plan to the entities identified in Requirement R2 but was more than 30 calendar days late but less than 60 calendar days late. | The Reliability Coordinator distributed the most recent Reliability Coordinator Area restoration plan to the entities identified in Requirement R2 but was 60 calendar days or more late, but less than 90 calendar days late. | The Reliability Coordinator distributed the most recent Reliability Coordinator Area restoration plan to the entities identified in Requirement R2 but was 90 or more calendar days late but less than 120 calendar days late. | The Reliability Coordinator distributed the most recent Reliability Coordinator Area restoration plan to entities identified in Requirement R2 but was 120 calendar days or more late. | [12 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006-3 | R3. | Each Reliability Coordinator shall review its restoration plan within 13 calendar months of the last review. | 2019-04-01 |  | Medium | N/A | N/A | N/A | The Reliability Coordinator did not review its restoration plan within 13 calendar months of the last review. | [12 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006-3 | R4. | Each Reliability Coordinator shall review its neighboring Reliability Coordinator’s restoration plans and provide written notification of any conflicts discovered during that review within 60 calendar days of receipt. | 2019-04-01 |  | Medium | The Reliability Coordinator reviewed the submitted restoration plans from its neighboring Reliability Coordinators within 60 calendar days of receipt, and resolved conflicts between 31 and 60 calendar days following written notification. | The Reliability Coordinator reviewed the submitted restoration plans from its neighboring Reliability Coordinators within 60 calendar days of receipt and resolved conflicts between 61 and 90 calendar days following written notification. | The Reliability Coordinator reviewed the submitted restoration plans from its neighboring Reliability Coordinators within 60 calendar days of receipt and resolved conflicts 91 or more calendar days following written notification. | The Reliability Coordinator did not review the submitted restoration plans from its neighboring Reliability Coordinators within 60 calendar days of receipt. | [12 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006-3 | R5. | Each Reliability Coordinator shall review the restoration plans required by EOP-005 of the Transmission Operators within its Reliability Coordinator Area. | 2019-04-01 |  | Medium | The Reliability Coordinator did not review and approve/disapprove the submitted restoration plans, with stated reasons for disapproval, from its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of receipt but did review and approve/disapprove the plans within 45 calendar days of receipt. OR The Reliability Coordinator failed to notify the Transmission Operator of its approval or disapproval with stated reasons for disapproval within 30 calendar days of receipt but did notify the Transmission Operator of its approval or disapproval with reasons within 45 calendar days of receipt. | The Reliability Coordinator did not review and approve/disapprove the submitted restoration plans, with stated reasons for disapproval, from its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of receipt but did review and approve/disapprove the plans within 60 calendar days of receipt. OR The Reliability Coordinator failed to notify the Transmission Operator of its approval or disapproval with stated reasons for disapproval within 30 calendar days of receipt, but did notify the Transmission Operator of its approval or disapproval with reasons within 60 calendar days of receipt | The Reliability Coordinator did not review and approve/disapprove the submitted restoration plans, with stated reasons for disapproval, from its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of receipt but did review and approve/disapprove the plans within 90 calendar days of receipt. OR The Reliability Coordinator failed to notify the Transmission Operator of its approval or disapproval with stated reasons for disapproval within 30 calendar days of receipt but did notify the Transmission Operator of its approval or disapproval with reasons within 90 calendar days of receipt. | The Reliability Coordinator did not review and approve/disapprove the submitted restoration plans, with stated reasons for disapproval, from its Transmission Operators and neighboring Reliability Coordinators for more than 90 calendar days of receipt. OR The Reliability Coordinator failed to notify the Transmission Operator of its approval or disapproval with stated reasons for disapproval for more than 90 calendar days of receipt. | [12 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006-3 | R6. | Each Reliability Coordinator shall have a copy of its latest restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area within its primary and backup control rooms so that it is available to all of its System Operators prior to the effective date. | 2019-04-01 |  | Low | N/A | N/A | The Reliability Coordinator did not have a copy of the latest approved restoration plan of all Transmission Operators in its Reliability Coordinator Area within its primary and backup control rooms prior to the effective date. | The Reliability Coordinator did not have a copy of its latest restoration plan within its primary and backup control rooms prior to the effective date. | [12 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006-3 | R7. | Each Reliability Coordinator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall address the following: | 2019-04-01 |  | Medium | N/A | N/A | The Reliability Coordinator included the annual System restoration training within its operations training program, but did not address both of the requirement parts. | The Reliability Coordinator did not include the annual System restoration training within its operations training program. | [12 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-006-3 | R8. | Each Reliability Coordinator shall conduct two System restoration drills, exercises, or simulations per calendar year, which shall include the Transmission Operators and Generator Operators as dictated by the particular scope of the drill, exercise, or simulation that is being conducted. | 2019-04-01 |  | Medium | N/A | The Reliability Coordinator only held one restoration drill, exercise, or simulation during the calendar year. OR The Reliability Coordinator did not request each applicable Transmission Operator or Generator Operator identified in its restoration plan to participate in a drill, exercise, or simulation at least once every two calendar years. | N/A | The Reliability Coordinator did not hold a restoration drill, exercise, or simulation during the calendar year. | [12 empty] | RC
Inactive | EOP | EOP-007-0 | R1. | Each Regional Reliability Organization shall establish and maintain a system BCP, as part of an overall coordinated Regional SRP. The Regional SRP shall include requirements for verification through analysis how system blackstart generating units shall perform their intended functions and shall be sufficient to meet SRP expectations. The Regional Reliability Organization shall coordinate with and among other Regional Reliability Organizations as appropriate in the development of its BCP. The BCP shall include: |  | 2011-05-23 | Medium | [19 empty] | RRO
Inactive | EOP | EOP-007-0 | R2. | The Regional Reliability Organization shall provide documentation of its system BCPs to NERC within 30 calendar days of a request. |  | 2011-05-23 | Low | [19 empty] | RRO
Inactive | EOP | EOP-008-0 | R1. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have a plan to continue reliability operations in the event its control center becomes inoperable. The contingency plan must meet the following requirements: | 2007-06-18 | 2013-06-30 | Medium | The Reliability Coordinator, Transmission Operator and Balancing Authority failed to comply with one of the sub-requirements. | The Reliability Coordinator, Transmission Operator and Balancing Authority failed to comply with two of the sub-requirements. | The Reliability Coordinator, Transmission Operator and Balancing Authority failed to comply with three or four of the sub-requirements. | The Reliability Coordinator, Transmission Operator and Balancing Authority failed to comply with more than four of the sub-requirements. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008-1 | R1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. This Operating Plan for backup functionality shall include the following, at a minimum: [See Standard pdf for what the Operating Plan for backup functionality shall include] | 2011-06-27 | 2019-03-31 | Medium | The responsible entity had a current Operating Plan for backup functionality but the plan was missing one of the requirement’s six Parts (1.1 through 1.6). | The responsible entity had a current Operating Plan for backup functionality but the plan was missing two of the requirement’s six Parts (1.1 through 1.6). | The responsible entity had a current Operating Plan for backup functionality but the plan was missing three of the requirement’s six Parts (1.1 through 1.6). | The responsible entity had a current Operating Plan for backup functionality, but the plan was missing four or more of the requirement’s six Parts (1.1 through 1.6) OR The responsible entity did not have a current Operating Plan for backup functionality. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008-1 | R2. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a copy of its current Operating Plan for backup functionality available at its primary control center and at the location providing backup functionality. | 2011-06-27 | 2019-03-31 | Low | N/A | The responsible entity did not have a copy of its current Operating Plan for backup functionality available in at least one of its control locations. | N/A | The responsible entity did not have a copy of its current Operating Plan for backup functionality at any of its locations. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008-1 | R3. | Each Reliability Coordinator shall have a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards that depend on primary control center functionality. To avoid requiring a tertiary facility, a backup facility is not required during: · Planned outages of the primary or backup facilities of two weeks or less · Unplanned outages of the primary or backup facilities | 2011-06-27 | 2019-03-31 | High | N/A | N/A | N/A | The Reliability Coordinator does not have a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards that depend on primary control center functionality. | [12 empty] | RC
Inactive | EOP | EOP-008-1 | R4. | Each Balancing Authority and Transmission Operator shall have backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) that includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that depend on a Balancing Authority and Transmission Operator’s primary control center functionality respectively. To avoid requiring tertiary functionality, backup functionality is not required during: - Planned outages of the primary or backup functionality of two weeks or less - Unplanned outages of the primary or backup functionality | 2011-06-27 | 2019-03-31 | High | N/A | N/A | N/A | The responsible entity does not have backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) that includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that depend on a Balancing Authority and Transmission Operator’s primary control center functionality respectively. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-008-1 | R5. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall annually review and approve its Operating Plan for backup functionality. | 2011-06-27 | 2019-03-31 | Medium | The responsible entity did not update and approve its Operating Plan for backup functionality for more than 60 calendar days and less than or equal to 70 calendar days after a change to any part of the Operating Plan described in Requirement R1. | The responsible entity did not update and approve its Operating Plan for backup functionality for more than 70 calendar days and less than or equal to 80 calendar days after a change to any part of the Operating Plan described in Requirement R1. | The responsible entity did not update and approve its Operating Plan for backup functionality for more than 80 calendar days and less than or equal to 90 calendar days after a change to any part of the Operating Plan described in Requirement R1. | The responsible entity did not have evidence that its Operating Plan for backup functionality was annually reviewed and approved. OR, The responsible entity did not update and approve its Operating Plan for backup functionality for more than 90 calendar days after a change to any part of the Operating Plan described in Requirement R1. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008-1 | R6. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have primary and backup functionality that do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. | 2011-06-27 | 2019-03-31 | Medium | N/A | N/A | N/A | The responsible entity has primary and backup functionality that do depend on each other for the control center functionality required to maintain compliance with Reliability Standards. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008-1 | R7. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct and document results of an annual test of its Operating Plan that demonstrates: | 2011-06-27 | 2019-03-31 | Medium | The responsible entity conducted an annual test of its Operating Plan for backup functionality but it did not document the results. OR, The responsible entity conducted an annual test of its Operating Plan for backup functionality but the test was for less than two continuous hours but more than or equal to 1.5 continuous hours. | The responsible entity conducted an annual test of its Operating Plan for backup functionality but the test was for less than 1.5 continuous hours but more than or equal to 1 continuous hour. | The responsible entity conducted an annual test of its Operating Plan for backup functionality but the test did not assess the transition time between the simulated loss of its primary control center and the time to fully implement the backup functionality OR, The responsible entity conducted an annual test of its Operating Plan for backup functionality but the test was for less than 1 continuous hour but more than or equal to 0.5 continuous hours. | The responsible entity did not conduct an annual test of its Operating Plan for backup functionality. OR, The responsible entity conducted an annual test of its Operating Plan for backup functionality but the test was for less than 0.5 continuous hours. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-008-1 | R8. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of its primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide a plan to its Regional Entity within six calendar months of the date when the functionality is lost, showing how it will re-establish primary or backup functionality. | 2011-06-27 | 2019-03-31 | Medium | The responsible entity experienced a loss of its primary or backup functionality and anticipated that the loss of primary or backup functionality would last for more than six calendar months and provided a plan to its Regional Entity showing how it will re-establish primary or backup functionality but the plan was submitted more than six calendar months but less than or equal to seven calendar months after the date when the functionality was lost. | The responsible entity experienced a loss of its primary or backup functionality and anticipated that the loss of primary or backup functionality would last for more than six calendar months provided a plan to its Regional Entity showing how it will re-establish primary or backup functionality but the plan was submitted in more than seven calendar months but less than or equal to eight calendar months after the date when the functionality was lost. | The responsible entity experienced a loss of its primary or backup functionality and anticipated that the loss of primary or backup functionality would last for more than six calendar months provided a plan to its Regional Entity showing how it will re-establish primary or backup functionality but the plan was submitted in more than eight calendar months but less than or equal to nine calendar months after the date when the functionality was lost. | The responsible entity experienced a loss of its primary or backup functionality and anticipated that the loss of primary or backup functionality would last for more than six calendar months, but did not submit a plan to its Regional Entity showing how it will re-establish primary or backup functionality for more than nine calendar months after the date when the functionality was lost. |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008-2 | R1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. This Operating Plan for backup functionality shall include: | 2019-04-01 |  | Medium | The responsible entity had a current Operating Plan for backup functionality, but the plan was missing one of the requirement’s six parts (Requirement R1, Parts 1.1 through 1.6). | The responsible entity had a current Operating Plan for backup functionality, but the plan was missing two of the requirement’s six parts (Requirement R1, Parts 1.1 through 1.6). | The responsible entity had a current Operating Plan for backup functionality, but the plan was missing three of the requirement’s six parts (Requirement R1, Parts 1.1 through 1.6). | The responsible entity had a current Operating Plan for backup functionality, but the plan was missing four or more of the requirement’s six parts (Requirement R1, Parts 1.1 through 1.6) OR The responsible entity did not have a current Operating Plan for backup functionality. |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008-2 | R2. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a copy of its current Operating Plan for backup functionality available at its primary control center and at the location providing backup functionality. | 2019-04-01 |  | Low | N/A | The responsible entity did not have a copy of its current Operating Plan for backup functionality available in at least one of its control locations. | N/A | The responsible entity did not have a copy of its current Operating Plan for backup functionality at any of its locations. |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008-2 | R3. | Each Reliability Coordinator shall have a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards are applicable to the primary control center functionality. To avoid requiring a tertiary facility, a backup facility is not required during: • Planned outages of the primary or backup facilities of two weeks or less • Unplanned outages of the primary or backup facilities | 2019-04-01 |  | High | N/A | N/A | N/A | The Reliability Coordinator does not have a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards that are applicable to the primary control center functionality. | [12 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-008-2 | R4. | Each Balancing Authority and Transmission Operator shall have backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) that includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that are applicable to a Balancing Authority’s and Transmission Operator’s primary control center functionality. To avoid requiring tertiary functionality, backup functionality is not required during: • Planned outages of the primary or backup functionality of two weeks or less • Unplanned outages of the primary or backup functionality | 2019-04-01 |  | High | N/A | N/A | N/A | The responsible entity does not have backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) that includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that are applicable to a Balancing Authority’s and Transmission Operator’s primary control center functionality. |  | BA | [17 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008-2 | R5. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall annually review and approve its Operating Plan for backup functionality. | 2019-04-01 |  | Medium | The responsible entity did not update and approve its Operating Plan for backup functionality for more than 60 calendar days and less than or equal to 70 calendar days after a change to any part of the Operating Plan described in Requirement R1. | The responsible entity did not update and approve its Operating Plan for backup functionality for more than 70 calendar days and less than or equal to 80 calendar days after a change to any part of the Operating Plan described in Requirement R1. | The responsible entity did not update and approve its Operating Plan for backup functionality for more than 80 calendar days and less than or equal to 90 calendar days after a change to any part of the Operating Plan described in Requirement R1. | The responsible entity did not have evidence that its Operating Plan for backup functionality was annually reviewed and approved. OR The responsible entity did not update and approve its Operating Plan for backup functionality for more than 90 calendar days after a change to any part of the Operating Plan described in Requirement R1. |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008-2 | R6. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have primary and backup functionality that do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. | 2019-04-01 |  | Medium | N/A | N/A | N/A | The responsible entity has primary and backup functionality that do depend on each other for the control center functionality required to maintain compliance with Reliability Standards. |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008-2 | R7. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct and document results of an annual test of its Operating Plan that demonstrates: | 2019-04-01 |  | Medium | The responsible entity conducted an annual test of its Operating Plan for backup functionality, but it did not document the results OR The responsible entity conducted an annual test of its Operating Plan for backup functionality, but the test was for less than two continuous hours but more than or equal to 1.5 continuous hours. | The responsible entity conducted an annual test of its Operating Plan for backup functionality, but the test was for less than 1.5 continuous hours but more than or equal to 1 continuous hour. | The responsible entity conducted an annual test of its Operating Plan for backup functionality, but the test did not assess the transition time between the simulated loss of its primary control center and the time to fully implement the backup functionality OR The responsible entity conducted an annual test of its Operating Plan for backup functionality, but the test was for less than 1 continuous hour but more than or equal to 0.5 continuous hours. | The responsible entity did not conduct an annual test of its Operating Plan for backup functionality. OR The responsible entity conducted an annual test of its Operating Plan for backup functionality, but the test was for less than 0.5 continuous hours. |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-008-2 | R8. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of its primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide a plan to its Regional Entity within six calendar months of the date when the functionality is lost, showing how it will re-establish primary or backup functionality. | 2019-04-01 |  | Medium | The responsible entity experienced a loss of its primary or backup functionality and anticipated that the loss of primary or backup functionality would last for more than six calendar months and provided a plan to its Regional Entity showing how it will re-establish primary or backup functionality but the plan was submitted more than six calendar months but less than or equal to seven calendar months after the date when the functionality was lost. | The responsible entity experienced a loss of its primary or backup functionality and anticipated that the loss of primary or backup functionality would last for more than six calendar months provided a plan to its Regional Entity showing how it will re-establish primary or backup functionality but the plan was submitted in more than seven calendar months but less than or equal to eight calendar months after the date when the functionality was lost. | The responsible entity experienced a loss of its primary or backup functionality and anticipated that the loss of primary or backup functionality would last for more than six calendar months provided a plan to its Regional Entity showing how it will re-establish primary or backup functionality but the plan was submitted in more than eight calendar months but less than or equal to nine calendar months after the date when the functionality was lost. | The responsible entity experienced a loss of its primary or backup functionality and anticipated that the loss of primary or backup functionality would last for more than six calendar months, but did not submit a plan to its Regional Entity showing how it will re-establish primary or backup functionality for more than nine calendar months after the date when the functionality was lost. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | EOP | EOP-009-0 | R1. | The Generator Operator of each blackstart generating unit shall test the startup and operation of each system blackstart generating unit identified in the BCP as required in the Regional BCP (Reliability Standard EOP-007-0_R1). Testing records shall include the dates of the tests, the duration of the tests, and an indication of whether the tests met Regional BCP requirements. | 2007-06-18 | 2013-06-30 | Medium | The Generator Operator Blackstart unit testing and recording is missing minor program/procedural elements. | Startup and testing of each Blackstart unit was performed, but the testing records are incomplete. The testing records are missing 25% or less of data requested in the requirement'. | The Generator Operator's failed to test 25% or less of the Blackstart units or testing records are incomplete. The testing records are missing between 25% and 50% of data requested in the requirement. | The Generator Operator failed to test more than 25% of its Blackstart units or does not have Blackstart testing records or is missing more than 50% of the required data. | [6 empty] | GOP
Inactive | EOP | EOP-009-0 | R2. | The Generator Owner or Generator Operator shall provide documentation of the test results of the startup and operation of each blackstart generating unit to the Regional Reliability Organizations and upon request to NERC. | 2007-06-18 | 2013-06-30 | Low | The Generator Operator has provided the Blackstart testing documentation to its Regional Reliability Organization. However the documentation provided had missing minor program/procedural elements or failed to provide the documentation requested to NERC i |  |  | The Generator Operator did not provide the required Blackstart documentation to its Regional Reliability Organization. | [5 empty] | GO | GOP
Mandatory Subject to Enforcement | EOP | EOP-010-1 | R1. | Each Reliability Coordinator shall develop, maintain, and implement a GMD Operating Plan that coordinates GMD Operating Procedures or Operating Processes within its Reliability Coordinator Area. At a minimum, the GMD Operating Plan shall include: [Please see the standard for more information] | 2015-04-01 |  | Medium | The Reliability Coordinator had a GMD Operating Plan, but failed to maintain it. | N/A | The Reliability Coordinator's GMD Operating Plan failed to include one of the required elements as listed in Requirement R1, parts 1.1 or 1.2. | The Reliability Coordinator did not have a GMD Operating Plan OR The Reliability Coordinator failed to implement a GMD Operating Plan within its Reliability Coordinator Area. | [12 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-010-1 | R2. | Each Reliability Coordinator shall disseminate forecasted and current space weather information to functional entities identified as recipients in the Reliability Coordinator's GMD Operating Plan. | 2015-04-01 |  | Medium | N/A | N/A | N/A | The Reliability Coordinator failed to disseminate forecasted and current space weather information to all functional entities identified as recipients in the Reliability Coordinator's GMD Operating Plan. | [12 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-010-1 | R3. | Each Transmission Operator shall develop, maintain, and implement a GMD Operating Procedure or Operating Process to mitigate the effects of GMD events on the reliable operation of its respective system. At a minimum, the Operating Procedure or Operating Process shall include: [Please see the standard for more information] | 2015-04-01 |  | Medium | The Transmission Operator had a GMD Operating Procedure or Operating Process, but failed to maintain it. | The Transmission Operator's GMD Operating Procedure or Operating Process failed to include one of the required elements as listed in Requirement R3, parts 3.1 through 3.3. | The Transmission Operator's GMD Operating Procedure or Operating Process failed to include two or more of the required elements as listed in Requirement R3, parts 3.1 through 3.3. | The Transmission Operator did not have a GMD Operating Procedure or Operating Process OR The Transmission Operator failed to implement its GMD Operating Procedure or Operating Process. | [19 empty] | TOP
Inactive | EOP | EOP-011-1 | R1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable:[See Standard for additional information.] | 2017-04-01 | 2023-03-31 | High | N/A | The Transmission Operator developed a Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area but failed to maintain it. | The Transmission Operator developed an Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area but failed to have it reviewed by its Reliability Coordinator. | The Transmission Operator failed to develop an Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. OR The Transmission Operator developed a Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission s Operator Area but failed to implement it. | [19 empty] | TOP
Inactive | EOP | EOP-011-1 | R2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: [See Standard for additional information.] | 2017-04-01 | 2023-03-31 | High | N/A | The Balancing Authority developed a Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area but failed to maintain it. | The Balancing Authority developed an Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area but failed to have it reviewed by its Reliability Coordinator. | The Balancing Authority failed to develop an Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area. OR The Balancing Authority developed a Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area but failed to implement it. |  | BA
Inactive | EOP | EOP-011-1 | R3. | The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. | 2017-04-01 | 2023-03-31 | High | N/A | N/A | The Reliability Coordinator identified a reliability risk but failed to notify the Balancing Authority or Transmission Operator within 30 calendar days. | The Reliability Coordinator identified a reliability risk but failed to notify the Balancing Authority or Transmission Operator. | [12 empty] | RC
Inactive | EOP | EOP-011-1 | R4. | Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. | 2017-04-01 | 2023-03-31 | High | N/A | N/A | The Transmission Operator or Balancing Authority failed to update and resubmit tis Operating Plan(s) to its Reliability Coordinator within the timeframe specified by its Reliability Coordinator. | The Transmission Operator or Balancing Authority failed to update and resubmit its Operating Plan(s) to its Reliability Coordinator. |  | BA | [17 empty] | TOP
Inactive | EOP | EOP-011-1 | R5. | Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. | 2017-04-01 | 2023-03-31 | High | N/A | N/A | The Reliability Coordinator that received an Emergency notification from a Transmission Operator or Balancing Authority did notify neighboring Reliability Coordinators, Balancing Authorities and Transmission Operators but failed to notify within 30 minutes from the time of receiving notification. | The Reliability Coordinator that received an Emergency notification from a Transmission Operator or Balancing Authority failed to notify neighboring Reliability Coordinators, Balancing Authorities and Transmission Operators. | [12 empty] | RC
Inactive | EOP | EOP-011-1 | R6. | Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. | 2017-04-01 | 2023-03-31 | High | N/A | N/A | N/A | The Reliability Coordinator that had a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area failed to declare an Energy Emergency Alert. | [12 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-011-2 | R1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: | 2023-04-01 |  | High | N/A | The Transmission Operator developed a Reliability Coordinator- reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area but failed to maintain it. | The Transmission Operator developed an Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area but failed to have it reviewed by its Reliability Coordinator. | The Transmission Operator failed to develop an Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. OR The Transmission Operator developed a Reliability Coordinator- reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission s Operator Area but failed to implement it. | [19 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011-2 | R2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: | 2023-04-01 |  | High | N/A | The Balancing Authority developed a Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area but failed to maintain it. | The Balancing Authority developed an Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area but failed to have it reviewed by its Reliability Coordinator. | The Balancing Authority failed to develop an Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area. OR The Balancing Authority developed a Reliability Coordinator- reviewed Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area but failed to implement it. |  | BA
Mandatory Subject to Enforcement | EOP | EOP-011-2 | R3. | The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. | 2023-04-01 |  | High | N/A | N/A | The Reliability Coordinator identified a reliability risk but failed to notify the Balancing Authority or Transmission Operator within 30 calendar days. | The Reliability Coordinator identified a reliability risk but failed to notify the Balancing Authority or Transmission Operator. | [12 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-011-2 | R4. | Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. | 2023-04-01 |  | High | N/A | N/A | The Transmission Operator or Balancing Authority failed to update and resubmit tis Operating Plan(s) to its Reliability Coordinator within the timeframe specified by its Reliability Coordinator. | The Transmission Operator or Balancing Authority failed to update and resubmit its Operating Plan(s) to its Reliability Coordinator. |  | BA | [17 empty] | TOP
Mandatory Subject to Enforcement | EOP | EOP-011-2 | R5. | Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. | 2023-04-01 |  | High | N/A | N/A | The Reliability Coordinator that received an Emergency notification from a Transmission Operator or Balancing Authority did notify neighboring Reliability Coordinators, Balancing Authorities and Transmission Operators but failed to notify within 30 minutes from the time of receiving notification. | The Reliability Coordinator that received an Emergency notification from a Transmission Operator or Balancing Authority failed to notify neighboring Reliability Coordinators, Balancing Authorities and Transmission Operators. | [12 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-011-2 | R6. | Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. | 2023-04-01 |  | High | N/A | N/A | N/A | The Reliability Coordinator that had a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area failed to declare an Energy Emergency Alert. | [12 empty] | RC
Mandatory Subject to Enforcement | EOP | EOP-011-2 | R7. | Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: | 2023-04-01 |  | High | The Generator Owner implemented a cold weather preparedness plan(s) but failed to maintain it. | The Generator Owner’s cold weather preparedness plan failed to include one of the applicable requirement Parts within Requirement R7. | The Generator Owner had and maintained a cold weather preparedness plan(s) but failed to fully implement it. OR The Generator Owner’s cold weather preparedness plan failed to include two of the applicable requirement Parts within Requirement R7. | The Generator Owner does not have a cold weather preparedness plan. OR The Generator Owner has a cold weather preparedness plan, but failed to include any of the applicable requirement Parts within Requirement R7. | [5 empty] | GO
Mandatory Subject to Enforcement | EOP | EOP-011-2 | R8. | Each Generator Owner in conjunction with its Generator Operator shall identify the entity responsible for providing the generating unit-specific training, and that identified entity shall provide the training to its maintenance or operations personnel responsible for implementing cold weather preparedness plan(s) developed pursuant to Requirement R7. | 2023-04-01 |  | Medium | The Generator Owner or Generator Operator failed to provide generating unit-specific training as described in Requirement R8 to the greater of: one applicable personnel at a single generating unit; or 5% or less of its total applicable personnel. | The Generator Owner or Generator Operator failed to provide generating unit-specific training as described in Requirement R8 to the greater of: two applicable personnel at a single generating unit; or more than 5% or less than or equal to 10% of its total applicable personnel. | The Generator Owner or Generator Operator failed to provide generating unit-specific training as described in Requirement R8 to the greater of: three applicable personnel at a single generating unit; or more than 10% or less than or equal to 15% of its total applicable personnel. | The Generator Owner or Generator Operator failed to provide generating unit-specific training as described in Requirement R8 to the greater of: four applicable personnel at a single generating unit; or more than 15% of its total applicable personnel. | [5 empty] | GO | GOP
Filed and Pending Regulatory Approval | EOP | EOP-011-3 | R1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: |  |  | High | N/A | The Transmission Operator developed a Reliability Coordinator- reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area, but failed to maintain it. | The Transmission Operator developed an Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area, but failed to have it reviewed by its Reliability Coordinator. | The Transmission Operator failed to develop an Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. OR The Transmission Operator developed a Reliability Coordinator- reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area, but failed to implement it. | [19 empty] | TOP
Filed and Pending Regulatory Approval | EOP | EOP-011-3 | R2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: |  |  | High | N/A | The Balancing Authority developed a Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area, but failed to maintain it. | The Balancing Authority developed an Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area, but failed to have it reviewed by its Reliability Coordinator. | The Balancing Authority failed to develop an Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area. OR The Balancing Authority developed a Reliability Coordinator- reviewed Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area, but failed to implement it. |  | BA | [10 empty] | RC | [6 empty] | TOP
Filed and Pending Regulatory Approval | EOP | EOP-011-3 | R3. | The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. |  |  | High | N/A | N/A | The Reliability Coordinator identified a reliability risk, but failed to notify the Balancing Authority or Transmission Operator within 30 calendar days. | The Reliability Coordinator identified a reliability risk, but failed to notify the Balancing Authority or Transmission Operator. |  | BA | [10 empty] | RC | [6 empty] | TOP
Filed and Pending Regulatory Approval | EOP | EOP-011-3 | R4. | Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. |  |  | High | N/A | N/A | The Transmission Operator or Balancing Authority failed to update and resubmit its Operating Plan(s) to its Reliability Coordinator within the timeframe specified by its Reliability Coordinator. | The Transmission Operator or Balancing Authority failed to update and resubmit its Operating Plan(s) to its Reliability Coordinator. |  | BA | [17 empty] | TOP
Filed and Pending Regulatory Approval | EOP | EOP-011-3 | R5. | Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. |  |  | High | N/A | N/A | The Reliability Coordinator that received an Emergency notification from a Transmission Operator or Balancing Authority did notify neighboring Reliability Coordinators, Balancing Authorities and Transmission Operators, but failed to notify within 30 minutes from the time of receiving notification. | The Reliability Coordinator that received an Emergency notification from a Transmission Operator or Balancing Authority failed to notify neighboring Reliability Coordinators,Balancing Authorities and Transmission Operators. | [12 empty] | RC
Filed and Pending Regulatory Approval | EOP | EOP-011-3 | R6. | Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1 |  |  | High | N/A | N/A | N/A | The Reliability Coordinator that had a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area failed to declare an Energy Emergency Alert. | [12 empty] | RC
Filed and Pending Regulatory Approval | EOP | EOP-011-4 | R1. | Each Transmission Operator shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. The Operating Plan(s) shall include the following, as applicable: |  |  | High | N/A | The Transmission Operator developed a Reliability Coordinator- reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area, but failed to maintain it. | The Transmission Operator developed an Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area, but failed to have it reviewed by its Reliability Coordinator. | The Transmission Operator failed to develop an Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area. OR The Transmission Operator developed a Reliability Coordinator- reviewed Operating Plan(s) to mitigate operating Emergencies in its Transmission Operator Area, but failed to implement it. |  | BA | [10 empty] | RC
Filed and Pending Regulatory Approval | EOP | EOP-011-4 | R2. | Each Balancing Authority shall develop, maintain, and implement one or more Reliability Coordinator-reviewed Operating Plan(s) to mitigate Capacity Emergencies and Energy Emergencies within its Balancing Authority Area. The Operating Plan(s) shall include the following, as applicable: |  |  | High | N/A | The Balancing Authority developed a Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area, but failed to maintain it. | The Balancing Authority developed an Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area, but failed to have it reviewed by its Reliability Coordinator. | The Balancing Authority failed to develop an Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area. OR The Balancing Authority developed a Reliability Coordinator-reviewed Operating Plan(s) to mitigate operating Emergencies within its Balancing Authority Area, but failed to implement it. |  | BA
Filed and Pending Regulatory Approval | EOP | EOP-011-4 | R3. | The Reliability Coordinator shall review the Operating Plan(s) to mitigate operating Emergencies submitted by a Transmission Operator or a Balancing Authority regarding any reliability risks that are identified between Operating Plans. |  |  | High | N/A | N/A | The Reliability Coordinator identified a reliability risk, but failed to notify the Balancing Authority or Transmission Operator within 30 calendar days. | The Reliability Coordinator identified a reliability risk, but failed to notify the Balancing Authority or Transmission Operator. |  | BA | [10 empty] | RC | [6 empty] | TOP
Filed and Pending Regulatory Approval | EOP | EOP-011-4 | R4. | Each Transmission Operator and Balancing Authority shall address any reliability risks identified by its Reliability Coordinator pursuant to Requirement R3 and resubmit its Operating Plan(s) to its Reliability Coordinator within a time period specified by its Reliability Coordinator. |  |  | High | N/A | N/A | The Transmission Operator or Balancing Authority failed to update and resubmit its Operating Plan(s) to its Reliability Coordinator within the timeframe specified by its Reliability Coordinator. | The Transmission Operator or Balancing Authority failed to update and resubmit its Operating Plan(s) to its Reliability Coordinator. |  | BA | [10 empty] | RC | [6 empty] | TOP
Filed and Pending Regulatory Approval | EOP | EOP-011-4 | R5. | Each Reliability Coordinator that receives an Emergency notification from a Transmission Operator or Balancing Authority within its Reliability Coordinator Area shall notify, within 30 minutes from the time of receiving notification, other Balancing Authorities and Transmission Operators in its Reliability Coordinator Area, and neighboring Reliability Coordinators. |  |  | High | N/A | N/A | The Reliability Coordinator that received an Emergency notification from a Transmission Operator or Balancing Authority did notify neighboring Reliability Coordinators, Balancing Authorities and Transmission Operators, but failed to notify within 30 minutes from the time of receiving notification. | The Reliability Coordinator that received an Emergency notification from a Transmission Operator or Balancing Authority failed to notify neighboring Reliability Coordinators, Balancing Authorities and Transmission Operators. |  | BA | [10 empty] | RC | [6 empty] | TOP
Filed and Pending Regulatory Approval | EOP | EOP-011-4 | R6. | Each Reliability Coordinator that has a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area shall declare an Energy Emergency Alert, as detailed in Attachment 1. |  |  | High | N/A | N/A | N/A | The Reliability Coordinator that had a Balancing Authority experiencing a potential or actual Energy Emergency within its Reliability Coordinator Area failed to declare an Energy Emergency Alert. | [12 empty] | RC
Filed and Pending Regulatory Approval | EOP | EOP-011-4 | R7. | Each Transmission Operator shall annually identify and notify Distribution Providers, UFLS-Only Distribution Providers and Transmission Owners that are required to assist with the mitigation of operating Emergencies in its Transmission Operator Area through operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding |  |  | Low | N/A | The Transmission Operator identified on an annual basis the Distribution Providers, UFLS-Only Distribution Providers and Transmission Owners that are required to assist with the mitigation of operating Emergencies in its Transmission Operator Area through Operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding, but notified one or more of those entities more than one, but fewer than 30 days late. | The Transmission Operator identified on an annual basis the Distribution Providers, UFLS-Only Distribution Providers and Transmission Owners, that are required to assist with the mitigation of operating Emergencies in its Transmission Operator Area through Operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding, but notified one or more of those entities 30 days or more, but fewer than 60 days late. | The Transmission Operator did not identify or notify Distribution Providers, UFLS- Only Distribution Providers and Transmission Owners, that are required to assist with the mitigation of operating Emergencies in its Transmission Operator Area through Operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding. OR The Transmission Operator identified on an annual basis the Distribution Providers, UFLS-Only Distribution Providers and Transmission Owners, that are required to assist with the mitigation of operating Emergencies in its Transmission Operator Area through Operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding, but notified one or more of those entities 60 days or more late. |  |  | DP | DP-UFLS | [14 empty] | TO | TOP
Filed and Pending Regulatory Approval | EOP | EOP-011-4 | R8. | Each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner notified by a Transmission Operator per R7 to assist with the mitigation of operating Emergencies in its Transmission Operator Area shall develop, maintain, and implement a Load shedding plan. The Load shedding plan shall include the following, as applicable: |  |  | High | N/A | The applicable Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner developed a Load shedding plan(s), but failed to maintain it in accordance with Requirement R8. | The applicable Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner developed a Load shedding plan(s), but failed to provide it to its Transmission Operator in accordance with Requirement R8. | The applicable Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner failed to develop a Load shedding plan(s) in accordance with Requirement R8. OR The Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner developed a Load shedding plan(s), but failed to implement it in accordance with Requirement R8. |  |  | DP | DP-UFLS | [14 empty] | TO | TOP
Subject to Future Enforcement | EOP | EOP-012-1 | R1. | For each generating unit(s) with a commercial operation date subsequent to [Effective Date of this requirement], the Generator Owner shall: - Implement freeze protection measures that provide capability to operate for a period of not less than twelve (12) continuous hours at the Extreme Cold Weather Temperature for the unit(s), assuming a concurrent twenty (20) mph wind speed on any exposed Generator Cold Weather Critical Components; or - Explain in a declaration any technical, commercial, or operational constraints, as defined by the Generator Owner, that preclude the ability to implement appropriate freeze protection measures to provide capability of operating for twelve (12) hours at the documented Extreme Cold Weather Temperature. | 2028-04-01 |  | Medium | The Generator Owner did not have freeze protection measure(s) meeting the criteria in Requirement R1 for 5% or less of its units. OR The Generator Owner did not explain in a declaration any technical, commercial, or operational constraints that preclude the ability to implement appropriate freeze protection measures for 5% or less of its units. | The Generator Owner did not have freeze protection measure(s) meeting the criteria in Requirement R1 for more than 5%, but less than or equal to 10% of its units. OR The Generator Owner did not explain in a declaration any technical, commercial, or operational constraints that preclude the ability to implement appropriate freeze protection measures for more than 5%, but less than or equal to 10% of its units. | The Generator Owner did not have freeze protection measure(s) meeting the criteria in Requirement R1 for more than 10%, but less than or equal to 20% of its units. OR The Generator Owner did not explain in a declaration any technical, commercial, or operational constraints that preclude the ability to implement appropriate freeze protection measures for more than 10%, but less than or equal to 20% of its units. | The Generator Owner did not have freeze protection measure(s) meeting the criteria in Requirement R1 for more than 20% of its units. OR The Generator Owner did not explain in a declaration any technical, commercial, or operational constraints that preclude the ability to implement appropriate freeze protection measures for more than 20% of its units. | [5 empty] | GO
Subject to Future Enforcement | EOP | EOP-012-1 | R2. | For each generating unit(s) in commercial operation prior to [Effective Date of this requirement], the Generator Owner shall ensure its generating unit(s) add new or modify existing freeze protection measures as needed to provide the capability to operate for a period of not less than one (1) hour at the unit(s) Extreme Cold Weather Temperature. Generating unit(s) that are not capable of operating for one (1) hour at its Extreme Cold Weather Temperature shall develop a Corrective Action Plan (CAP) for the identified issues, including identification of any needed modifications to the cold weather preparedness plan required under Requirement R3. | 2028-04-01 |  | Medium | The Generator Owner did not have freeze protection measure(s) meeting the criteria in Requirement R2 for 5% or less of its units. OR The Generator Owner did not develop a CAP as required by Requirement R2 for 5% or less of its units. | The Generator Owner did not have freeze protection measure(s) meeting the criteria in Requirement R2 for more than 5%, but less than or equal to 10% of its units. OR The Generator Owner did not develop a CAP as required by Requirement R2 for more than 5%, but less than or equal to 10% of its units. | The Generator Owner did not have freeze protection measure(s) meeting the criteria in Requirement R2 for more than 10%, but less than or equal to 20% of its units. OR The Generator Owner did not develop a CAP as required by Requirement R2 for more than 10%, but less than or equal to 20% of its units. | The Generator Owner did not have freeze protection measure(s) meeting the criteria in Requirement R2 for more than 20% of its units. OR The Generator Owner did not develop a CAP as required by Requirement R2 for more than 20% of its units. | [5 empty] | GO
Subject to Future Enforcement | EOP | EOP-012-1 | R3. | Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: | 2024-10-01 |  | High | The Generator Owner implemented a cold weather preparedness plan(s), but failed to maintain it. | The Generator Owner’s cold weather preparedness plan failed to include one of the applicable Parts within Requirement R3. | The Generator Owner had and maintained a cold weather preparedness plan(s), but failed to implement it. OR The Generator Owner’s cold weather preparedness plan failed to include two of the applicable requirement parts within Requirement R3. | The Generator Owner does not have cold weather preparedness plan(s). OR The Generator Owner’scold weather preparedness plan failed to include three or more of the applicable requirement parts within Requirement R3. | [5 empty] | GO
Subject to Future Enforcement | EOP | EOP-012-1 | R4. | Once every five calendar years, each Generator Owner shall for each generating unit: | 2029-10-01 |  | Low | The Generator Owner completed the actions required in Requirement R4, but was late by 30 calendar days or less. | The Generator Owner completed the actions required in Requirement R4, but was late by greater than 30 calendar days, but less than or equal to 60 calendar days. | The Generator Owner failed to complete one of the applicable requirement parts in Requirement R4 Parts 4.1 through 4.3; OR The Generator Owner completed the actions required in Requirement R4, but was late by greater than 60 calendar days. | The Generator Owner failed to complete two or more of the applicable requirement parts in Requirement R4 Parts 4.1 through 4.3. | [5 empty] | GO
Subject to Future Enforcement | EOP | EOP-012-1 | R5. | Each Generator Owner in conjunction with its Generator Operator shall identify the entity responsible for providing the generating unit-specific training, and that identified entity shall provide annual training to its maintenance or operations personnel responsible for implementing the cold weather preparedness plan(s) developed pursuant to Requirement R3. | 2024-10-01 |  | Medium | The Generator Owner or Generator Operator failed to provide annual generating unit-specific training as described in Requirement R5 to the greater of: - one applicable personnel at a single generating unit; or - 5% or less of its total applicable personnel. | The Generator Owner or Generator Operator failed to provide annual generating unit-specific training as described in Requirement R5 to the greater of: - two applicable personnel at a single generating unit; or - more than 5%, but less than or equal to 10% of its total applicable personnel. | The Generator Owner or Generator Operator failed to provide annual generating unit-specific training as described in Requirement R5 to the greater of: - three applicable personnel at a single generating unit; or - more than 10%, but less than or equal to 15% of its total applicable personnel. | The Generator Owner or Generator Operator failed to provide annual generating unit-specific training as described in Requirement R5 to the greater of: - four applicable personnel at a single generating unit; or - more than 15% of its total applicable personnel. | [5 empty] | GO | GOP
Subject to Future Enforcement | EOP | EOP-012-1 | R6. | Each Generator Owner that owns a generating unit that experiences a Generator Cold Weather Reliability Event shall develop a CAP, within 150 days or by July 1, whichever is earlier, that contains at a minimum: | 2024-10-01 |  | High | The Generator Owner developed a CAP, but not within 150 days or by July 1 as required in Requirement R6. | The Generator Owner's CAP failed to comply with one of the elements in Requirement R6, Parts 6.1 through 6.3. | The Generator Owner's CAP failed to comply with two of the elements in Requirement R6, Parts 6.1 through 6.3. | The Generator Owner's CAP failed to comply with three of the elements in Requirement R6, Parts 6.1 through 6.3. OR The Generator Owner did not develop a CAP as required by Requirement R6. | [5 empty] | GO
Subject to Future Enforcement | EOP | EOP-012-1 | R7. | Each Generator Owner shall: | 2024-10-01 |  | Medium | The Generator Owner implemented a CAP or explained in a declaration why corrective actions are not being implemented, but failed to update the CAP when actions or timetables changed, in accordance with Requirement R7. | N/A | N/A | The Generator Owner failed to implement a CAP or explain in a declaration why corrective actions are not being implemented in accordance with Requirement R7. | [5 empty] | GO
Filed and Pending Regulatory Approval | EOP | EOP-012-2 | R1. | At least once every five calendar years, each Generator Owner shall, for each of its applicable generating unit(s): |  |  | Low | The Generator Owner did not calculate the Extreme Cold Weather Temperature and identify generating unit(s) cold weather data in accordance with Requirement R1 for 5% or less of its applicable units. | The Generator Owner did not calculate the Extreme Cold Weather Temperature and identify generating unit(s) cold weather data in accordance with Requirement R1 for more than 5%, but less than or equal to 10% of its applicable units. | The Generator Owner did not calculate the Extreme Cold Weather Temperature and identify generating unit(s) cold weather data in accordance with Requirement R1 for more than 10%, but less than or equal to 20% of its applicable units. | The Generator Owner did not calculate the Extreme Cold Weather Temperature and identify generating unit(s) cold weather data in accordance with Requirement R1 for more than 20% of its applicable units. | [5 empty] | GO
Filed and Pending Regulatory Approval | EOP | EOP-012-2 | R2. | Applicable to generating units with a commercial operation date on or after October 1, 2027: Each Generator Owner, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1, and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius),1 shall: - Implement freeze protection measures to protect Generator Cold Weather Critical Components that provide the capability to operate at the unit(s)’ Extreme Cold Weather Temperature with sustained concurrent twenty (20) mph wind speed for (i) a period of not less than twelve (12) continuous hours, or (ii) the maximum operational duration for intermittent energy resources if less than twelve (12) continuous hours; or - Develop a Corrective Action Plan(s) to add new or modify existing or previously planned freeze protection measures to provide the capability to operate at the unit(s)’ Extreme Cold Weather Temperature with a sustained concurrent twenty (20) mph wind speed for (i) a period of not less than twelve (12) continuous hours, or (ii) the maximum operational duration for intermittent energy resources if less than twelve (12) continuous hours. |  |  | Medium | The Generator Owner did not have freeze protection measure(s) for its applicable unit(s) meeting the criteria in Requirement R2 for 5% or less of its applicable units. OR The Generator Owner did not develop a Corrective Action Plan to implement appropriate freeze protection measures for 5% or less of its applicable units. | The Generator Owner did not have freeze protection measure(s) for its applicable unit(s) meeting the criteria in Requirement R2 for more than 5%, but less than or equal to 10% of its applicable units. OR The Generator Owner did not develop a Corrective Action Plan for more than 5%, but less than or equal to 10% of its applicable units. | The Generator Owner did not have freeze protection measure(s) meeting the criteria in Requirement R2 for more than 10%, but less than or equal to 20% of its applicable units. OR The Generator Owner did not develop a Corrective Action Plan for more than 10%, but less than or equal to 20% of its applicable units. | The Generator Owner did not have freeze protection measure(s) meeting the criteria in Requirement R2 for more than 20% of its applicable units. OR The Generator Owner did not develop a Corrective Action Plan for more than 20% of its applicable units. | [5 empty] | GO
Filed and Pending Regulatory Approval | EOP | EOP-012-2 | R4. | Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: |  |  | High | The Generator Owner implemented a cold weather preparedness plan(s) but failed to maintain it. | The Generator Owner’s cold weather preparedness plan failed to include one of the applicable Parts within Requirement R4. | The Generator Owner had and maintained a cold weather preparedness plan(s) but failed to implement it. OR The Generator Owner’s cold weather preparedness plan failed to include two of the applicable requirement parts within Requirement R4. | The Generator Owner does not have a cold weather preparedness plan(s). OR The Generator Owner’s cold weather preparedness plan failed to include three or more of the applicable requirement parts within Requirement R4. | [5 empty] | GO
Filed and Pending Regulatory Approval | EOP | EOP-012-2 | R5. | Each Generator Owner in conjunction with its Generator Operator shall identify the entity responsible for providing the generating unit-specific training, and that identified entity shall provide annual training to its maintenance or operations personnel responsible for implementing the cold weather preparedness plan(s) developed pursuant to Requirement R4. |  |  | Medium | The Generator Owner or Generator Operator failed to provide annual generating unit-specific training as described in Requirement R5 to the greater of: - one applicable personnel at a single generating unit; or - 5% or less of its total applicable personnel. | The Generator Owner or Generator Operator failed to provide annual generating unit-specific training as described in Requirement R5 to the greater of: - two applicable personnel at a single generating unit; or - more than 5%, but less than or equal to 10% of its total applicable personnel. | The Generator Owner or Generator Operator failed to provide annual generating unit-specific training as described in Requirement R5 to the greater of: - three applicable personnel at a single generating unit; or - more than 10%, but less than or equal to 15% of its total applicable personnel. | The Generator Owner or Generator Operator failed to provide annual generating unit-specific training as described in Requirement R5 to the greater of: - four or more applicable personnel at a single generating unit; or - more than 15% of its total applicable personnel. | [5 empty] | GO | GOP
Filed and Pending Regulatory Approval | EOP | EOP-012-2 | R6. | Each Generator Owner shall, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1 and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius),4 develop a Corrective Action Plan when the generating unit experiences a Generator Cold Weather Reliability Event. The Corrective Action Plan shall be developed within 150 days or by July 1, whichever is earlier, and contain at a minimum: |  |  | High | The Generator Owner developed a Corrective Action Plan, but not within 150 days or by July 1 as required in Requirement R6. | The Generator Owner's Corrective Action Plan failed to comply with one of the elements in Requirement R6, Parts 6.1 through 6.3. | The Generator Owner's Corrective Action Plan failed to comply with two of the elements in Requirement R6, Parts 6.1 through 6.3. | The Generator Owner's Corrective Action Plan failed to comply with three of the elements in Requirement R6, Parts 6.1 through 6.3. OR The Generator Owner did not develop a Corrective Action Plan, as required by Requirement R6. | [5 empty] | GO
Filed and Pending Regulatory Approval | EOP | EOP-012-2 | R7. | Each Generator Owner, for each Corrective Action Plan developed pursuant to Requirements R1, R2, R3, or R6, shall: |  |  | Medium | The Generator Owner implemented a Corrective Action Plan, but failed to update the Corrective Action Plan when corrective action(s) changed in accordance with Requirement R7. | The Generator Owner implemented a Corrective Action Plan, but failed to include a timetable for implementing the selected corrective actions meeting the criteria of Requirement R7 Part 7.1. | The Generator Owner implemented a Corrective Action Plan, but failed to implement the Corrective Action Plan within the specified timetable or failed to update the Corrective Action Plan, with justification, when timetable(s) exceeded the timelines in Requirement R7 Part 7.1. | The Generator Owner failed to implement a Corrective Action Plan or failed to document in a declaration why corrective actions are not being implemented in accordance with Requirement R7. | [5 empty] | GO
Filed and Pending Regulatory Approval | EOP | EOP-012-2 | R8. | Each Generator Owner that creates a Generator Cold Weather Constraint declaration shall: |  |  | Medium | N/A | N/A | The Generator Owner failed to comply with one of the elements in Requirement R8, Parts 8.1 through 8.2. | The Generator Owner failed to comply with all of the elements in Requirement R8, Parts 8.1 through 8.2. | [5 empty] | GO
Filed and Pending Regulatory Approval | EOP | EOP-012-2 | R3. | Applicable to generating unit(s) in commercial operation prior to October 1, 2027: Each Generator Owner, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1, and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius),2 shall: - Implement freeze protection measures to protect Generator Cold Weather Critical Components that provide the capability to operate at the unit(s)' Extreme Cold Weather Temperature; or - Develop a Corrective Action Plan to add new or modify existing freeze protection measures to provide the capability to operate at the unit(s)' Extreme Cold Weather Temperature. |  |  | Medium | The Generator Owner did not have freeze protection measure(s) meeting the criteria in Requirement R3 for 5% or less of its applicable units. OR The Generator Owner did not develop a Corrective Action Plan as required by Requirement R3 for 5% or less of its applicable units. | The Generator Owner did not have freeze protection measure(s) meeting the criteria in Requirement R3 for more than 5%, but less than or equal to 10% of its applicable units. OR The Generator Owner did not develop a Corrective Action Plan as required by Requirement R3 for more than 5%, but less than or equal to 10% of its applicable units. | The Generator Owner did not have freeze protection measure(s) meeting the criteria in Requirement R3 for more than 10%, but less than or equal to 20% of its applicable units. OR The Generator Owner did not develop a Corrective Action Plan as required by Requirement R3 for more than 10%, but less than or equal to 20% of its applicable units. | The Generator Owner did not have freeze protection measure(s) meeting the criteria in Requirement R3 for more than 20% of its applicable units. OR The Generator Owner did not develop a Corrective Action Plan as required by Requirement R3 for more than 20% of its applicable units. | [5 empty] | GO
Inactive | FAC | FAC-001-0 | R1. | The Transmission Owner shall document, maintain, and publish facility connection requirements to ensure compliance with NERC Reliability Standards and applicable Regional Reliability Organization, subregional, Power Pool, and individual Transmission Owner planning criteria and facility connection requirements. The Transmission Owner’s facility connection requirements shall address connection requirements for: | 2007-06-18 | 2013-11-24 | Medium | [22 empty] | TO
Inactive | FAC | FAC-001-0 | R2. | The Transmission Owner’s facility connection requirements shall address, but are not limited to, the following items: | 2007-06-18 | 2013-11-24 | Medium | [22 empty] | TO
Inactive | FAC | FAC-001-0 | R3. | The Transmission Owner shall maintain and update its facility connection requirements as required. The Transmission Owner shall make documentation of these requirements available to the users of the transmission system, the Regional Reliability Organization, and NERC on request (five business days). | 2007-06-18 | 2013-11-24 | Medium | [22 empty] | TO
Inactive | FAC | FAC-001-1 | R1. | The Transmission Owner shall document, maintain, and publish Facility connection requirements to ensure compliance with NERC Reliability Standards and applicable Regional Entity, subregional, Power Pool, and individual Transmission Owner planning criteria and Facility connection requirements. The Transmission Owner’s Facility connection requirements shall address connection requirements for: 1.1. Generation Facilities, 1.2. Transmission Facilities, and 1.3. End-user Facilities | 2013-11-25 | 2015-12-31 | Medium | Not Applicable. | The Transmission Owner failed to do one of the following: Document or maintain or publish Facility connection requirements as specified in the Requirement OR Failed to include one (1) of the components as specified in R1.1, R1.2 or R1.3. | The Transmission Owner failed to do one of the following: Failed to include (2) of the components as specified in R1.1, R1.2 or R1.3 OR Failed to document or maintain or publish its Facility connection requirements as specified in the Requirement and failed to include one (1) of the components as specified in R1.1, R1.2 or R1.3. | The Transmission Owner did not develop Facility connection requirements. | [18 empty] | TO
Inactive | FAC | FAC-001-1 | R2. | Each applicable Generator Owner shall, within 45 days of having an executed Agreement to evaluate the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the interconnected Transmission systems (under FAC-002-1), document and publish its Facility connection requirements to ensure compliance with NERC Reliability Standards and applicable Regional Entity, subregional, Power Pool, and individual Transmission Owner planning criteria and Facility connection requirements. | 2013-11-25 | 2015-12-31 | Medium | The Generator Owner failed to document and publish Facility connection requirements until more than 45 calendar days but less than or equal to 60 calendar days after having an Agreement to evaluate the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the interconnected Transmission systems. | The Generator Owner failed to document and publish Facility connection requirements until more than 60 calendar days but less than or equal to 70 calendar days after having an Agreement to evaluate the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the interconnected Transmission systems. | The Generator Owner failed to document and publish Facility connection requirements until more than 70 calendar days but less than or equal to 80 calendar days after having an Agreement to evaluate the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the interconnected Transmission systems. | The Generator Owner failed to document and publish Facility connection requirements until more than 80 days after having an Agreement to evaluate the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the interconnected Transmission systems. | [5 empty] | GO
Inactive | FAC | FAC-001-1 | R3. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall address the following items in its Facility connection requirements: 3.1. Provide a written summary of its plans to achieve the required system performance as described in Requirements R1 or R2 throughout the planning horizon: 3.1.1. Procedures for coordinated joint studies of new Facilities and their impacts on the interconnected Transmission systems. 3.1.2. Procedures for notification of new or modified Facilities to others (those responsible for the reliability of the interconnected Transmission systems) as soon as feasible. 3.1.3. Voltage level and MW and MVAR capacity or demand at point of connection. 3.1.4. Breaker duty and surge protection. 3.1.5. System protection and coordination. 3.1.6. Metering and telecommunications. 3.1.7. Grounding and safety issues. 3.1.8. Insulation and insulation coordination. 3.1.9. Voltage, Reactive Power, and power factor control. 3.1.10. Power quality impacts. 3.1.11. Equipment Ratings. 3.1.12. Synchronizing of Facilities. 3.1.13. Maintenance coordination. 3.1.14. Operational issues (abnormal frequency and voltages). 3.1.15. Inspection requirements for existing or new Facilities. 3.1.16. Communications and procedures during normal and emergency operating conditions. | 2013-11-25 | 2015-12-31 | Medium | The responsible entity’s Facility connection requirements failed to address one of the parts listed in Requirement R3, parts 3.1.1 through 3.1.16. | The responsible entity’s Facility connection requirements failed to address two of the parts listed in Requirement R3, parts 3.1.1 through 3.1.16. | The responsible entity’s Facility connection requirements failed to address three of the parts listed in Requirement R3, parts 3.1.1 through 3.1.16. | The responsible entity’s Facility connection requirements failed to address four or more of the parts listed in Requirement R3, parts 3.1.1 through 3.1.16. | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-001-1 | R4. | The Transmission Owner shall maintain and update its Facility connection requirements as required. The Transmission Owner shall make documentation of these requirements available to the users of the transmission system, the Regional Entity, and ERO on request (five business days). | 2013-11-25 | 2015-12-31 | Medium | The responsible entity made the requirements available more than five business days but less than or equal to 10 business days after a request. | The responsible entity made the requirements available more than 10 business days but less than or equal to 20 business days after a request. | The responsible entity made the requirements available more than 20 business days less than or equal to 30 business days after a request. | The responsible entity made the requirements available more than 30 business days after a request. | [18 empty] | TO
Inactive | FAC | FAC-001-2 | R1. | Each Transmission Owner shall document Facility interconnection requirements, update them as needed, and make them available upon request. Each Transmission Owner’s Facility interconnection requirements shall address interconnection requirements for: | 2016-01-01 | 2018-12-31 | Low | N/A | The Transmission Owner documented Facility interconnection requirements and updated them as needed, but failed to make them available upon request. OR The Transmission Owner documented Facility interconnection requirements and made them available upon request, but failed to update them as needed. OR The Transmission Owner documented Facility interconnection requirements, updated them as needed, and made them available upon request, but failed to address interconnection requirements for one of the Facilities as specified in R1, Parts 1.1, 1.2, or 1.3. | The Transmission Owner documented Facility interconnection requirements, but failed to update them as needed and failed to make them available upon request. OR The Transmission Owner documented Facility interconnection requirements, updated them as needed, and made them available upon request, but failed to address interconnection requirements for two of the Facilities as specified in R1, Parts 1.1, 1.2, or 1.3. | The Transmission Owner did not document Facility interconnection requirements. | [18 empty] | TO
Inactive | FAC | FAC-001-2 | R2. | Each applicable Generator Owner shall document Facility interconnection requirements and make them available upon request within 45 calendar days of full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | 2016-01-01 | 2018-12-31 | Low | The applicable Generator Owner failed to document Facility interconnection requirements and make them available upon request until more than 45 calendar days but less than or equal to 60 calendar days after full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | The applicable Generator Owner failed to document Facility interconnection requirements and make them available upon request until more than 60 calendar days but less than or equal to 70 calendar days after full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | The applicable Generator Owner failed to document Facility interconnection requirements and make them available upon request until more than 70 calendar days but less than or equal to 80 calendar days after full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | The applicable Generator Owner failed to document Facility interconnection requirements and make them available upon request until more than 80 calendar days after full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | [5 empty] | GO
Inactive | FAC | FAC-001-2 | R3. | Each Transmission Owner shall address the following items in its Facility interconnection requirements: | 2016-01-01 | 2018-12-31 | Low | N/A | N/A | The Transmission Owner addressed either R3, Part 3.1 or Part 3.2 in its Facility interconnection requirements, but did not address both. | The Transmission Owner addressed neither R3, Part 3.1 nor Part 3.2 in its Facility interconnection requirements. | [18 empty] | TO
Inactive | FAC | FAC-001-2 | R4. | Each applicable Generator Owner shall address the following items in its Facility interconnection requirements: | 2016-01-01 | 2018-12-31 | Low | N/A | N/A | The applicable Generator Owner addressed either R4, Part 4.1 or Part 4.2 in its Facility interconnection requirements, but did not address both. | The applicable Generator Owner addressed neither R4, Part 4.1 nor Part 4.2 in its Facility interconnection requirements. | [5 empty] | GO
Inactive | FAC | FAC-001-3 | R1. | Each Transmission Owner shall document Facility interconnection requirements, update them as needed, and make them available upon request. Each Transmission Owner’s Facility interconnection requirements shall address interconnection requirements for | 2017-11-27 | 2023-12-31 | Low | N/A | The Transmission Owner documented Facility interconnection requirements and updated them as needed, but failed to make them available upon request. OR The Transmission Owner documented Facility interconnection requirements and made them available upon req them available upon request, but failed to update them as needed. OR The Transmission Owner documented Facility interconnection requirements, updated them as needed, and made them available upon request, but failed to address interconnection requirements for one of the Facilities as specified in R1, Parts 1.1, 1.2, or 1.3. | The Transmission Owner documented Facility interconnection requirements, but failed to update them as needed and failed to make them available upon request. OR The Transmission Owner documented Facility interconnection requirements, updated them as needed, and made them available upon request, but failed to address interconnection requirements for two of the Facilities as specified in R1, Parts 1.1, 1.2, or 1.3. | The Transmission Owner did not document Facility interconnection requirements. | [18 empty] | TO
Inactive | FAC | FAC-001-3 | R2. | Each applicable Generator Owner shall document Facility interconnection requirements and make them available upon request within 45 calendar days of full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | 2019-01-01 | 2023-12-31 | Low | The applicable Generator Owner failed to document Facility interconnection requirements and make them available upon request until more than 45 calendar days but less than or equal to 60 calendar days after full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | The applicable Generator Owner failed to document Facility interconnection requirements and make them available upon request until more than 60 calendar days but less than or equal to 70 calendar days after full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | The applicable Generator Owner failed to document Facility interconnection requirements and make them available upon request until more than 70 calendar days but less than or equal to 80 calendar days after full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | The applicable Generator Owner failed to document Facility interconnection requirements and make them available upon request until more than 80 calendar days after full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | [5 empty] | GO
Inactive | FAC | FAC-001-3 | R3. | Each Transmission Owner shall address the following items in its Facility interconnection requirements: | 2019-01-01 | 2023-12-31 | Low | N/A | The Transmission Owner failed to address one part of Requirement R3 Part 3.1 through Part 3.3. | The Transmission Owner failed to address two parts of Requirement R3 Part 3.1 through Part 3.3. | The Transmission Owner failed to address Requirement R3 Part 3.1 through Part 3.3. | [18 empty] | TO
Inactive | FAC | FAC-001-3 | R4. | Each applicable Generator Owner shall address the following items in its Facility interconnection requirements: | 2019-01-01 | 2023-12-31 | Low | N/A | The Generator Owner failed to address one part of Requirement R4 Part 4.1 through Part 4.3. | The Generator Owner failed to address two parts of Requirement R4 Part 4.1 through Part 4.3. | The Generator Owner failed to address Requirement R4 Part 4.1 through Part 4.3. | [5 empty] | GO
Mandatory Subject to Enforcement | FAC | FAC-001-4 | R1. | Each Transmission Owner shall document Facility interconnection requirements, update them as needed, and make them available upon request. Each Transmission Owner’s Facility interconnection requirements shall address interconnection requirements for: | 2024-01-01 |  | Low | N/A | The Transmission Owner documented Facility interconnection requirements and updated them as needed, but failed to make them available upon request. OR The Transmission Owner documented Facility interconnection requirements and made them available upon request, but failed to update them as needed. OR The Transmission Owner documented Facility interconnection requirements,updated them as needed, and made them available upon request, but failed to address interconnection requirements for one of the Facilities as specified in R1, Parts 1.1, 1.2, or 1.3. | The Transmission Owner documented Facility interconnection requirements, but failed to update them as needed and failed to make them available upon request. OR The Transmission Owner documented Facility interconnection requirements, updated them as needed, and made them available upon request, but failed to address interconnection requirements for two of the Facilities as specified in R1, Parts 1.1, 1.2, or 1.3. | The Transmission Owner did not document Facility interconnection requirements. | [18 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-001-4 | R2. | Each applicable Generator Owner shall document Facility interconnection requirements and make them available upon request within 45 calendar days of full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | 2024-01-01 |  | Low | The applicable Generator Owner failed to document Facility interconnection requirements and make them available upon request until more than 45 calendar days but less than or equal to 60 calendar days after full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | The applicable Generator Owner failed to document Facility interconnection requirements and make them available upon request until more than 60 calendar days but less than or equal to 70 calendar days after full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | The applicable Generator Owner failed to document Facility interconnection requirements and make them available upon request until more than 70 calendar days but less than or equal to 80 calendar days after full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | The applicable Generator Owner failed to document Facility interconnection requirements and make them available upon request until more than 80 calendar days after full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | [5 empty] | GO
Mandatory Subject to Enforcement | FAC | FAC-001-4 | R3. | Each Transmission Owner shall address the following items in its Facility interconnection requirements | 2024-01-01 |  | Low | N/A | The Transmission Owner failed to address one part of Requirement R3 (Part 3.1 through Part 3.3). | The Transmission Owner failed to address two parts of Requirement R3 (Part 3.1 through Part 3.3). | The Transmission Owner failed to address three parts of Requirement R3 (Part 3.1 through Part 3.3). | [18 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-001-4 | R4. | Each applicable Generator Owner shall address the following items in its Facility interconnection requirements: | 2024-01-01 |  | Low | N/A | The Generator Owner failed to address one part of Requirement R4 (Part 4.1 through Part 4.3). | The Generator Owner failed to address two parts of Requirement R4 (Part 4.1 through Part 4.3). | The Generator Owner failed to address three parts of Requirement R4 (Part 4.1 through Part 4.3). | [5 empty] | GO
Inactive | FAC | FAC-002-0 | R1. | The Generator Owner, Transmission Owner, Distribution Provider, and Load-Serving Entity seeking to integrate generation facilities, transmission facilities, and electricity end-user facilities shall each coordinate and cooperate on its assessments with its Transmission Planner and Planning Authority. The assessment shall include: | 2007-06-18 | 2011-09-30 | Medium | [6 empty] | DP |  |  | GO |  |  | LSE | [9 empty] | TO
Inactive | FAC | FAC-002-0 | R2. | The Planning Authority, Transmission Planner, Generator Owner, Transmission Owner, Load-Serving Entity, and Distribution Provider shall each retain its documentation (of its evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems) for three years and shall provide the documentation to the Regional Reliability Organization(s) Regional Reliability Organization(s) and NERC on request (within 30 calendar days). | 2007-06-18 | 2011-09-30 | Low | [6 empty] | DP |  |  | GO |  |  | LSE |  | PCPA | [7 empty] | TO |  | TP
Inactive | FAC | FAC-002-1 | R1. | The Generator Owner, Transmission Owner, Distribution Provider, and Load-Serving Entity seeking to integrate generation facilities, transmission facilities, and electricity end-user facilities shall each coordinate and cooperate on its assessments with its Transmission Planner and Planning Authority. The assessment shall include: | 2011-10-01 | 2015-12-31 | Medium | [6 empty] | DP |  |  | GO |  |  | LSE | [9 empty] | TO
Inactive | FAC | FAC-002-1 | R2. | The Planning Authority, Transmission Planner, Generator Owner, Transmission Owner, Load-Serving Entity, and Distribution Provider shall each retain its documentation (of its evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems) for three years and shall provide the documentation to the Regional Reliability Organization(s) and NERC on request (within 30 calendar days). | 2011-10-01 | 2014-01-21 | Low | [6 empty] | DP |  |  | GO |  |  | LSE |  | PCPA | [7 empty] | TO |  | TP
Inactive | FAC | FAC-002-2 | R1. | Each Transmission Planner and each Planning Coordinator shall study the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities and (ii) materially modifying existing interconnections of generation, transmission, or electricity end-user Facilities. The following shall be studied: | 2016-01-01 | 2021-03-31 | Medium | The Transmission Planner or Planning Coordinator studied the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities, and (ii) materially modifying existing interconnections of generation, transmission, or electricity end-user Facilities, but failed to study one of the Parts (R1, 1.1-1.4). | The Transmission Planner or Planning Coordinator studied the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities, and (ii) materially modifying existing interconnections of generation, transmission, or electricity end-user Facilities but failed to study two of the Parts (R1, 1.1-1.4). | The Transmission Planner or Planning Coordinator studied the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities, and (ii) materially modifying existing interconnections of generation, transmission, or electricity end-user Facilities but failed to study three of the Parts (R1, 1.1-1.4). | The Transmission Planner or Planning Coordinator failed to study the reliability impact of: interconnecting new generation, transmission, or electricity end-user Facilities, and (ii) materially modifying existing interconnections of, generation, transmission, or electricity end-user Facilities. | [10 empty] | PCPA | [9 empty] | TP
Inactive | FAC | FAC-002-2 | R2. | Each Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | 2016-01-01 | 2021-03-31 | Medium | The Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in one of the Parts (R1, 1.1-1.4). | The Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in two of the Parts (R1, 1.1-1.4). | The Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in three of the Parts (R1, 1.1-1.4). | The Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, failed to coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator. | [5 empty] | GO
Inactive | FAC | FAC-002-2 | R3. | Each Transmission Owner, each Distribution Provider, and each Load-Serving Entity seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | 2016-01-01 | 2021-03-31 | Medium | The Transmission Owner, Distribution Provider, or Load-Serving Entity seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in one of the Parts (R1, 1.1-1.4). | The Transmission Owner, Distribution Provider, or Load-Serving Entity seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in two of the Parts (R1, 1.1-1.4). | The Transmission Owner, Distribution Provider, or Load-Serving Entity seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in three of the Parts (R1, 1.1-1.4). | The Transmission Owner, Distribution Provider, or Load-Serving Entity seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, failed to coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator. |  |  | DP | [5 empty] | LSE | [9 empty] | TO
Inactive | FAC | FAC-002-2 | R4. | Each Transmission Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested new or materially modified interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | 2016-01-01 | 2021-03-31 | Medium | The Transmission Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested new or materially modified interconnections to its Facilities, but failed to provide data necessary to perform studies as described in one of the Parts (R1, 1.1-1.4). | The Transmission Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested new or materially modified interconnections to its Facilities, but failed to provide data necessary to perform studies as described in two of the Parts (R1, 1.1-1.4). | The Transmission Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested new or materially modified interconnections to its Facilities, but failed to provide data necessary to perform studies as described in three of the Parts (R1, 1.1-1.4). | The Transmission Owner failed to coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator regarding requested new or materially modified interconnections to its Facilities. | [18 empty] | TO
Inactive | FAC | FAC-002-2 | R5. | Each applicable Generator Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | 2016-01-01 | 2021-03-31 | Medium | The applicable Generator Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested interconnections to its Facilities, but failed to provide data necessary to perform studies as described in one of the Parts (R1, 1.1-1.4). | The applicable Generator Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested interconnections to its Facilities, but failed to provide data necessary to perform studies as described in two of the Parts (R1, 1.1-1.4). | The applicable Generator Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested interconnections to its Facilities, but failed to provide data necessary to perform studies as described in three of the Parts (R1, 1.1-1.4). | The applicable Generator Owner failed to coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator regarding requested interconnections to its Facilities. | [5 empty] | GO
Inactive | FAC | FAC-002-3 | R1. | Each Transmission Planner and each Planning Coordinator shall study the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities and (ii) materially modifying existing interconnections of generation, transmission, or electricity end-user Facilities. The following shall be studied: | 2021-04-01 | 2023-12-31 | Medium | The Transmission Planner or Planning Coordinator studied the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities, and (ii) materially modifying existing interconnections of generation, transmission, or electricity end-user Facilities, but failed to study one of the Parts (R1, 1.1-1.4). | The Transmission Planner or Planning Coordinator studied the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities, and (ii) materially modifying existing interconnections of generation, transmission, or electricity end-user Facilities but failed to study two of the Parts (R1, 1.1-1.4). | The Transmission Planner or Planning Coordinator studied the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities, and (ii) materially modifying existing interconnections of generation, transmission, or electricity end-user Facilities but failed to study three of the Parts (R1, 1.1-1.4). | The Transmission Planner or Planning Coordinator failed to study the reliability impact of: interconnecting new generation, transmission, or electricity end-user Facilities, and (ii) materially modifying existing interconnections of, generation, transmission, or electricity end-user Facilities. | [10 empty] | PCPA | [9 empty] | TP
Inactive | FAC | FAC-002-3 | R2. | Each Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | 2021-04-01 | 2023-12-31 | Medium | The Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in one of the Parts (R1, 1.1-1.4). | The Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in two of the Parts (R1, 1.1-1.4). | The Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in three of the Parts (R1, 1.1-1.4). | The Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, failed to coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator. | [5 empty] | GO
Inactive | FAC | FAC-002-3 | R3. | Each Transmission Owner and each Distribution Provider seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | 2021-04-01 | 2023-12-31 | Medium | The Transmission Owner or Distribution Provider seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in one of the Parts (R1, 1.1-1.4). | The Transmission Owner, or Distribution Provider seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in two of the Parts (R1, 1.1-1.4). | The Transmission Owner or Distribution Provider seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in three of the Parts (R1, 1.1-1.4). | The Transmission Owner, or Distribution Provider seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, failed to coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator. |  |  | DP | [15 empty] | TO
Inactive | FAC | FAC-002-3 | R4. | Each Transmission Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested new or materially modified interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | 2021-04-01 | 2023-12-31 | Medium | The Transmission Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested new or materially modified interconnections to its Facilities, but failed to provide data necessary to perform studies as described in one of the Parts (R1, 1.1-1.4). | The Transmission Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested new or materially modified interconnections to its Facilities, but failed to provide data necessary to perform studies as described in two of the Parts (R1, 1.1-1.4). | The Transmission Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested new or materially modified interconnections to its Facilities, but failed to provide data necessary to perform studies as described in three of the Parts (R1, 1.1-1.4). | The Transmission Owner failed to coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator regarding requested new or materially modified interconnections to its Facilities. | [18 empty] | TO
Inactive | FAC | FAC-002-3 | R5. | R5. Each applicable Generator Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | 2021-04-01 | 2023-12-31 | Medium | The applicable Generator Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested interconnections to its Facilities, but failed to provide data necessary to perform studies as described in one of the Parts (R1, 1.1-1.4). | The applicable Generator Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested interconnections to its Facilities, but failed to provide data necessary to perform studies as described in two of the Parts (R1, 1.1-1.4). | The applicable Generator Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested interconnections to its Facilities, but failed to provide data necessary to perform studies as described in three of the Parts (R1, 1.1-1.4). | The applicable Generator Owner failed to coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator regarding requested interconnections to its Facilities. | [5 empty] | GO
Mandatory Subject to Enforcement | FAC | FAC-002-4 | R1. | Each Transmission Planner and each Planning Coordinator shall study the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities and (ii) existing interconnections of generation, transmission, or electricity end-user Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6. The following shall be studied: | 2024-01-01 |  | Medium | The Transmission Planner or Planning Coordinator studied the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities, and (ii) existing interconnections of generation, transmission, or electricity end-user Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, but failed to study one of the Parts (R1, 1.1-1.4). | The Transmission Planner or Planning Coordinator studied the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities, and (ii) existing interconnections of generation, transmission, or electricity end-user Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, but failed to study two of the Parts (R1, 1.1-1.4). | The Transmission Planner or Planning Coordinator studied the reliability impact of: (i) interconnecting new generation, transmission, or electricity end-user Facilities, and (ii) existing interconnections of generation, transmission, or electricity end-user Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, but failed to study three of the Parts (R1, 1.1-1.4). | The Transmission Planner or Planning Coordinator failed to study the reliability impact of: interconnecting new generation, transmission, or electricity end-user Facilities, and (ii) existing interconnections of, generation, transmission, or electricity end-user Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | FAC | FAC-002-4 | R2. | Each Generator Owner seeking to interconnect new generation Facilities, or existing interconnections of generation Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | 2024-01-01 |  | Medium | The Generator Owner seeking to interconnect new generation Facilities, or existing interconnections of generation Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in one of the Parts (R1, 1.1-1.4). | The Generator Owner seeking to interconnect new generation Facilities, or existing interconnections of generation Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in two of the Parts (R1, 1.1-1.4). | The Generator Owner seeking to interconnect new generation Facilities, or existing interconnections of generation Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in three of the Parts (R1, 1.1-1.4). | The Generator Owner seeking to interconnect new generation Facilities, or existing interconnections of generation Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, failed to coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator. | [5 empty] | GO
Mandatory Subject to Enforcement | FAC | FAC-002-4 | R3. | Each Transmission Owner and each Distribution Provider seeking to interconnect new transmission Facilities or electricity end-user Facilities, or existing interconnections of transmission Facilities or electricity end-user Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | 2024-01-01 |  | Medium | The Transmission Owner or Distribution Provider seeking to interconnect new transmission Facilities or electricity end-user Facilities, or existing interconnections of transmission Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, or electricity end-user Facilities, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in one of the Parts (R1, 1.1-1.4). | The Transmission Owner, or Distribution Provider seeking to interconnect new transmission Facilities or electricity end-user Facilities, or existing interconnections of transmission Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, or electricity end-user Facilities, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in two of the Parts (R1, 1.1-1.4). | The Transmission Owner or Distribution Provider seeking to interconnect new transmission Facilities or electricity end-user Facilities, or existing interconnections of transmission Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, or electricity end-user Facilities, coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator, but failed to provide data necessary to perform studies as described in three of the Parts (R1, 1.1-1.4). | The Transmission Owner, or Distribution Provider seeking to interconnect new transmission Facilities or electricity end-user Facilities, or existing interconnections of transmission Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, or electricity end-user Facilities, failed to coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator. |  |  | DP | [15 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-002-4 | R4. | Each Transmission Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested new or existing interconnections seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. | 2024-01-01 |  | Medium | The Transmission Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested new or existing interconnections seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6to its Facilities, but failed to provide data necessary to perform studies as described in one of the Parts (R1, 1.1-1.4). | The Transmission Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested new or existing interconnections seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6to its Facilities, but failed to provide data necessary to perform studies as described in two of the Parts (R1, 1.1-1.4). | The Transmission Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested new or existing interconnections seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6to its Facilities, but failed to provide data necessary to perform studies as described in three of the Parts (R1, 1.1-1.4). | The Transmission Owner failed to coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator regarding requested new or existing interconnections seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6to its Facilities. | [18 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-002-4 | R5. | Each applicable Generator Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4 | 2024-01-01 |  | Medium | The applicable Generator Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested interconnections to its Facilities, but failed to provide data necessary to perform studies as described in one of the Parts (R1, 1.1-1.4). | The applicable Generator Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested interconnections to its Facilities, but failed to provide data necessary to perform studies as described in two of the Parts (R1, 1.1-1.4). | The applicable Generator Owner coordinated and cooperated on studies with its Transmission Planner or Planning Coordinator regarding requested interconnections to its Facilities, but failed to provide data necessary to perform studies as described in three of the Parts (R1, 1.1-1.4). | The applicable Generator Owner failed to coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator regarding requested interconnections to its Facilities. | [5 empty] | GO
Mandatory Subject to Enforcement | FAC | FAC-002-4 | R6. | Each Planning Coordinator shall maintain a publicly available definition of qualified change for the purposes of facility interconnection. | 2024-01-01 |  | Low | N/A | N/A | N/A | The Planning Coordinator did not maintain a publicly available definition of qualified change for the purposes of facility interconnection. | [10 empty] | PCPA
Inactive | FAC | FAC-003-0 | R1. | Each Transmission Owner shall have a vegetation management program to prevent transmission line contact with vegetation. The vegetation management program shall include the following three elements: |  | 2006-04-07 | [10 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-003-0 | R2. | Each Transmission Owner shall report to its Regional Reliability Organization all vegetationrelated outages on transmission circuits 200 kV and higher and any other lower voltage lines designated by the Regional Reliability Organization to be critical to the reliability of the electric system. |  | 2006-04-07 | [10 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-003-1 | R1. | The Transmission owner shall prepare, and keep current, a formal transmission vegetation management (TVMP). The TVMP shall include the Transmission Owner's objectives, practices, approved procedures, and work specifications. | 2007-06-18 | 2014-06-30 | High | [22 empty] | TO
Inactive | FAC | FAC-003-1 | R2. | The Transmission Owner shall create and implement an annual plan for vegetation management work to ensure the reliability of the system. The plan shall describe the methods used, such as manual clearing, mechanical clearing, herbicide treatment, or other actions. The plan should be flexible enough to adjust to changing conditions, taking into consideration anticipated growth of vegetation and all other environmental factors that may have an impact on the reliability of the transmission systems. Adjustments to the plan shall be documented as they occur. The plan should take into consideration the time required to obtain permissions or permits from landowners or regulatory authorities. Each Transmission Owner shall have systems and procedures for documenting and tracking the planned vegetation management work and ensuring that the vegetation management work was completed according to work specifications. | 2007-06-18 | 2014-06-30 | High | [22 empty] | TO
Inactive | FAC | FAC-003-1 | R3. | The Transmission Owner shall report quarterly to its RRO, or the RRO’s designee, sustained transmission line outages determined by the Transmission Owner to have been caused by vegetation. | 2007-06-18 | 2014-06-30 | Low | [22 empty] | TO
Inactive | FAC | FAC-003-1 | R4. | The RRO shall report the outage information provided to it by Transmission Owner’s, as required by Requirement 3, quarterly to NERC, as well as any actions taken by the RRO as a result of any of the reported outages. | 2007-06-18 | 2014-06-30 | Low | [19 empty] | RRO
Inactive | FAC | FAC-003-2 | R1. | Each Transmission Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below 1. An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Realtime, absent a Sustained Outage, 2. An encroachment due to a fall-in from inside the ROW that caused a vegetationrelated Sustained Outage, 3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 4. An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. | 2014-07-01 | 2013-11-25 | High | N/A | N/A | The Transmission Owner failed to manage vegetation to prevent encroachment into the MVCD of a line identified as an element of an IROL or Major WECC transfer path and encroachment into the MVCD as identified in FAC-003-Table 2 was observed in real time absent a Sustained Outage. | The Transmission Owner failed to manage vegetation to prevent encroachment into the MVCD of a line identified as an element of an IROL or Major WECC transfer path and a vegetation-related Sustained Outage was caused by one of the following: - A fall-in from inside the active transmission line ROW • Blowing together of applicable lines and vegetation located inside the active transmission line ROW • A grow-in | [18 empty] | TO
Inactive | FAC | FAC-003-2 | R2. | Each Transmission Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below: 1. An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage, 2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 3. An encroachment due to blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 4. An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage | 2014-07-01 | 2013-11-25 | High | N/A | N/A | The Transmission Owner failed to manage vegetation to prevent encroachment into the MVCD of a line not identified as an element of an IROL or Major WECC transfer path and encroachment into the MVCD as identified in FAC-003-Table 2 was observed in real time absent a Sustained Outage. | The Transmission Owner failed to manage vegetation to prevent encroachment into the MVCD of a line not identified as an element of an IROL or Major WECC transfer path and a vegetation-related Sustained Outage was caused by one of the following: - A fall-in from inside the active transmission line ROW • Blowing together of applicable lines and vegetation located inside the active transmission line ROW • A grow-in | [18 empty] | TO
Inactive | FAC | FAC-003-2 | R3. | Each Transmission Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: 3.1. Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; 3.2. Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. | 2014-07-01 | 2013-11-25 | Low | N/A | The Transmission Owner has maintenance strategies or documented procedures or processes or specifications but has not accounted for the inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency, for the Transmission Owner’s applicable lines. (Requirement R3, Part 3.2) | The Transmission Owner has maintenance strategies or documented procedures or processes or specifications but has not accounted for the movement of transmission line conductors under their Rating and all Rated Electrical Operating Conditions, for the Transmission Owner’s applicable lines. Requirement R3, Part 3.1) | The Transmission Owner does not have any maintenance strategies or documented procedures or processes or specifications used to prevent the encroachment of vegetation into the MVCD, for the Transmission Owner’s applicable lines. | [18 empty] | TO
Inactive | FAC | FAC-003-2 | R4. | Each Transmission Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the Transmission Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment. | 2014-07-01 | 2013-11-25 | Medium | N/A | N/A | The Transmission Owner experienced a confirmed vegetation threat and notified the control center holding switching authority for that applicable line, but there was intentional delay in that notification. | The Transmission Owner experienced a confirmed vegetation threat and did not notify the control center holding switching authority for that applicable line. | [18 empty] | TO
Inactive | FAC | FAC-003-2 | R5. | When a Transmission Owner is constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the Transmission Owner shall take corrective action to ensure continued vegetation management to prevent encroachments. | 2014-07-01 | 2013-11-25 | Medium | N/A | N/A | N/A | The Transmission Owner did not take corrective action when it was constrained from performing planned vegetation work where an applicable line was put at potential risk. | [18 empty] | TO
Inactive | FAC | FAC-003-2 | R6. | Each Transmission Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW. | 2014-07-01 | 2013-11-25 | Medium | The Transmission Owner failed to inspect 5% or less of its applicable lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) | The Transmission Owner failed to inspect more than 5% up to and including 10% of its applicable lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). | The Transmission Owner failed to inspect more than 10% up to and including 15% of its applicable lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). | The Transmission Owner failed to inspect more than 15% of its applicable lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). | [18 empty] | TO
Inactive | FAC | FAC-003-2 | R7. | Each Transmission Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) Examples of reasons for modification to annual plan may include: Change in expected growth rate/environmental factors; Circumstances that are beyond the control of a Transmission Owner; Rescheduling work between growing seasons; Crew or contractor availability/Mutual assistance agreements; Identified unanticipated high priority work; Weather conditions/Accessibility; Permitting delays; Land ownership changes/Change in land use by the landowner; Emerging technologies | 2014-07-01 | 2013-11-25 | Medium | The Transmission Owner failed to complete 5% or less of its annual vegetation work plan for its applicable lines (as finally modified). | The Transmission Owner failed to complete more than 5% and up to and including 10% of its annual vegetation work plan for its applicable lines (as finally modified). | The Transmission Owner failed to complete more than 10% and up to and including 15% of its annual vegetation work plan for its applicable lines (as finally modified). | The Transmission Owner failed to complete more than 15% of its annual vegetation work plan for its applicable lines (as finally modified). | [18 empty] | TO
Inactive | FAC | FAC-003-3 | R1. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below: 1. An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, 2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage 4. An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. | 2014-07-01 | 2016-09-30 | High | N/A | N/A | The responsible entity failed to manage vegetation to prevent encroachment into the MVCD of a line identified as an element of an IROL or Major WECC transfer path and encroachment into the MVCD as identified in FAC-003-Table 2 was observed in real time absent a Sustained Outage. | The responsible entity failed to manage vegetation to prevent encroachment into the MVCD of a line identified as an element of an IROL or Major WECC transfer path and a vegetation-related Sustained Outage was caused by one of the following: • A fall-in from inside the active transmission line ROW  Blowing together of applicable lines and vegetation located inside the active transmission line ROW  A grow-in | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-003-3 | R2. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below: 1. An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage, 2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 3. An encroachment due to blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 4. An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage. | 2014-07-01 | 2016-09-30 | Medium | N/A | N/A | The responsible entity failed to manage vegetation to prevent encroachment into the MVCD of a line not identified as an element of an IROL or Major WECC transfer path and encroachment into the MVCD as identified in FAC-003-Table 2 was observed in real time absent a Sustained Outage. | The responsible entity failed to manage vegetation to prevent encroachment into the MVCD of a line not identified as an element of an IROL or Major WECC transfer path and a vegetation-related Sustained Outage was caused by one of the following: • A fall-in from inside the active transmission line ROW  Blowing together of applicable lines and vegetation located inside the active transmission line ROW  A grow-in | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-003-3 | R3. | Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: [See Standard pdf for further information] | 2014-07-01 | 2016-09-30 | Low | N/A | The responsible entity has maintenance strategies or documented procedures or processes or specifications but has not accounted for the inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency, for the responsible entity’s applicable lines. (Requirement R3, Part 3.2) | The responsible entity has maintenance strategies or documented procedures or processes or specifications but has not accounted for the movement of transmission line conductors under their Rating and all Rated Electrical Operating Conditions, for the responsible entity’s applicable lines. Requirement R3, Part 3.1) | The responsible entity does not have any maintenance strategies or documented procedures or processes or specifications used to prevent the encroachment of vegetation into the MVCD, for the responsible entity’s applicable lines. | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-003-3 | R4. | Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment. | 2014-07-01 | 2016-09-30 | Medium | N/A | N/A | The responsible entity experienced a confirmed vegetation threat and notified the control center holding switching authority for that applicable line, but there was intentional delay in that notification. | The responsible entity experienced a confirmed vegetation threat and did not notify the control center holding switching authority for that applicable line. | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-003-3 | R5. | When a applicable Transmission Owner and applicable Generator Owner is constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments. | 2014-07-01 | 2016-09-30 | Medium | N/A | N/A | N/A | The responsible entity did not take corrective action when it was constrained from performing planned vegetation work where an applicable line was put at potential risk. | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-003-3 | R6. | Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW. | 2014-07-01 | 2016-09-30 | Medium | The responsible entity failed to inspect 5% or less of its applicable lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) | The responsible entity failed to inspect more than 5% up to and including 10% of its applicable lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). | The responsible entity failed to inspect more than 10% up to and including 15% of its applicable lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). | The responsible entity failed to inspect more than 15% of its applicable lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-003-3 | R7. | Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) Examples of reasons for modification to annual plan may include: • Change in expected growth rate/ environmental factors • Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner • Rescheduling work between growing seasons • Crew or contractor availability/ Mutual assistance agreements • Identified unanticipated high priority work • Weather conditions/Accessibility • Permitting delays • Land ownership changes/Change in land use by the landowner • Emerging technologies | 2014-07-01 | 2016-09-30 | Medium | The responsible entity failed to complete 5% or less of its annual vegetation work plan for its applicable lines (as finally modified). | The responsible entity failed to complete more than 5% and up to and including 10% of its annual vegetation work plan for its applicable lines (as finally modified). | The responsible entity failed to complete more than 10% and up to and including 15% of its annual vegetation work plan for its applicable lines (as finally modified). | The responsible entity failed to complete more than 15% of its annual vegetation work plan for its applicable lines (as finally modified). | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-003-4 | R1. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the Minimum Vegetation Clearance Distance (MVCD) of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below: (Footnote: This requirement does not apply to circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner subject to this reliability standard, including natural disasters such as earthquakes, fires, tornados, hurricanes, landslides, wind shear, fresh gale, major storms as defined either by the applicable Transmission Owner or applicable Generator Owner or an applicable regulatory body, ice storms, and floods; human or animal activity such as logging, animal severing tree, vehicle contact with tree, or installation, removal, or digging of vegetation. Nothing in this footnote should be construed to limit the Transmission Owner’s or applicable Generator Owner’s right to exercise its full legal rights on the ROW.) | 2016-10-01 | 2024-03-31 | High |  |  | The responsible entity failed to manage vegetation to prevent encroachment into the MVCD of a line identified as an element of an IROL or Major WECC transfer path and encroachment into the MVCD as identified in FAC-003-4-Table 2 was observed in real time absent a Sustained Outage. | The responsible entity failed to manage vegetation to prevent encroachment into the MVCD of a line identified as an element of an IROL or Major WECC transfer path and a vegetation-related Sustained Outage was caused by one of the following: • A fall-in from inside the active transmission line ROW • Blowing together of applicable lines and vegetation located inside the active transmission line ROW • A grow-in | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-003-4 | R2. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below: Footnote: This requirement does not apply to circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner subject to this reliability standard, including natural disasters such as earthquakes, fires, tornados, hurricanes, landslides, wind shear, fresh gale, major storms as defined either by the applicable Transmission Owner or applicable Generator Owner or an applicable regulatory body, ice storms, and floods; human or animal activity such as logging, animal severing tree, vehicle contact with tree, or installation, removal, or digging of vegetation. Nothing in this footnote should be construed to limit the Transmission Owner’s or applicable Generator Owner’s right to exercise its full legal rights on the ROW. | 2016-10-01 | 2024-03-31 | High |  |  | The responsible entity failed to manage vegetation to prevent encroachment into the MVCD of a line not identified as an element of an IROL or Major WECC transfer path and encroachment into the MVCD as identified in FAC-003-4-Table 2 was observed in real time absent a Sustained Outage. | The responsible entity failed to manage vegetation to prevent encroachment into the MVCD of a line not identified as an element of an IROL or Major WECC transfer path and a vegetation-related Sustained Outage was caused by one of the following: • A fall-in from inside the active transmission line ROW • Blowing together of applicable lines and vegetation located inside the active transmission line ROW • A grow-in | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-003-4 | R3. | Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: | 2016-10-01 | 2024-03-31 | Low |  | The responsible entity has maintenance strategies or documented procedures or processes or specifications but has not accounted for the inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency, for the responsible entity’s applicable lines. (Requirement R3, Part 3.2.) | The responsible entity has maintenance strategies or documented procedures or processes or specifications but has not accounted for the movement of transmission line conductors under their Rating and all Rated Electrical Operating Conditions, for the responsible entity’s applicable lines. (Requirement R3, Part 3.1.) | The responsible entity does not have any maintenance strategies or documented procedures or processes or specifications used to prevent the encroachment of vegetation into the MVCD, for the responsible entity’s applicable lines. | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-003-4 | R4. | Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment. | 2016-10-01 | 2024-03-31 | Medium |  |  | The responsible entity experienced a confirmed vegetation threat and notified the control center holding switching authority for that applicable line, but there was intentional delay in that notification. | The responsible entity experienced a confirmed vegetation threat and did not notify the control center holding switching authority for that applicable line. | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-003-4 | R5. | When an applicable Transmission Owner and an applicable Generator Owner are constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments. | 2016-10-01 | 2024-03-31 | Medium |  |  |  | The responsible entity did not take corrective action when it was constrained from performing planned vegetation work where an applicable line was put at potential risk. | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-003-4 | R6. | Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW (Footnote: When the applicable Transmission Owner or applicable Generator Owner is prevented from performing a Vegetation Inspection within the timeframe in R6 due to a natural disaster, the TO or GO is granted a time extension that is equivalent to the duration of the time the TO or GO was prevented from performing the Vegetation Inspection.) | 2016-10-01 | 2024-03-31 | Medium | The responsible entity failed to inspect 5% or less of its applicable lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) | The responsible entity failed to inspect more than 5% up to and including 10% of its applicable lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). | The responsible entity failed to inspect more than 10% up to and including 15% of its applicable lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). | The responsible entity failed to inspect more than 15% of its applicable lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-003-4 | R7. | Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). Examples of reasons for modification to annual plan may include. | 2016-10-01 | 2024-03-31 | Medium | The responsible entity failed to complete 5% or less of its annual vegetation work plan for its applicable lines (as finally modified). | The responsible entity failed to complete more than 5% and up to and including 10% of its annual vegetation work plan for its applicable lines (as finally modified). | The responsible entity failed to complete more than 10% and up to and including 15% of its annual vegetation work plan for its applicable lines (as finally modified). | The responsible entity failed to complete more than 15% of its annual vegetation work plan for its applicable lines (as finally modified). | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003-5 | R1. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the Minimum Vegetation Clearance Distance (MVCD) of its applicable line(s), operating within their Rating and all Rated Electrical Operating Conditions of the types shown below. Footnote: This requirement does not apply to circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner subject to this Reliability Standard, including natural disasters such as earthquakes, fires, tornados, hurricanes, landslides, wind shear, fresh gale, major storms as defined either by the applicable Transmission Owner or applicable Generator Owner or an applicable regulatory body, ice storms, and floods; human or animal activity such as logging, animal severing tree, vehicle contact with tree, or installation, removal, or digging of vegetation. Nothing in this footnote should be construed to limit the Transmission Owner’s or applicable Generator Owner’s right to exercise its full legal rights on the ROW. | 2024-04-01 |  | High |  |  | The responsible entity failed to manage vegetation to prevent encroachment into the MVCD of a line identified in the Applicability section 4.2 and 4.3 and encroachment into the MVCD as identified in FAC‐ 003‐5‐Table 2 was observed in real time absent a Sustained Outage. | The responsible entity failed to manage vegetation to prevent encroachment into the MVCD of a line identified in the Applicability section 4.2 and 4.3 and a vegetation‐ related Sustained Outage was caused by one of the following: · A fall‐in from inside the active transmission line ROW · Blowing together of applicable lines and vegetation located inside the active transmission line ROW · A grow‐in | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003-5 | R2. | Reserved for future use. | 2024-04-01
Mandatory Subject to Enforcement | FAC | FAC-003-5 | R3. | Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: | 2024-04-01 |  | Low |  | The responsible entity has maintenance strategies or documented procedures or processes or specifications but has not accounted for the inter‐relationships between vegetation growth rates, vegetation control methods, and inspection frequency, for the responsible entity’s applicable lines. (Requirement R3, Part 3.2.) | The responsible entity has maintenance strategies or documented procedures or processes or specifications but has not accounted for the movement of transmission line conductors under their Rating and all Rated Electrical Operating Conditions, for the responsible entity’s applicable lines. (Requirement R3, Part 3.1.) | The responsible entity does not have any maintenance strategies or documented procedures or processes or specifications used to prevent the encroachment of vegetation into the MVCD, for the responsible entity’s applicable lines. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003-5 | R4. | Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment. | 2024-04-01 |  | Medium |  |  | The responsible entity experienced a confirmed vegetation threat and notified the control center holding switching authority for that applicable line, but there was intentional delay in that notification. | The responsible entity experienced a confirmed vegetation threat and did not notify the control center holding switching authority for that applicable line. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003-5 | R5. | When an applicable Transmission Owner and an applicable Generator Owner are constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments. | 2024-04-01 |  | Medium |  |  |  | The responsible entity did not take corrective action when it was constrained from performing planned vegetation work where an applicable line was put at potential risk. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003-5 | R6. | Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice ‐ circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW. Footnote: When the applicable Transmission Owner or applicable Generator Owner is prevented from performing a Vegetation Inspection within the timeframe in R6 due to a natural disaster, the TO or GO is granted a time extension that is equivalent to the duration of the time the TO or GO was prevented from performing the Vegetation Inspection. | 2024-04-01 |  | Medium | The responsible entity failed to inspect 5% or less of its applicable lines (measured in units of choice ‐ circuit, pole line, line miles or kilometers, etc.) | The responsible entity failed to inspect more than 5% up to and including 10% of its applicable lines (measured in units of choice ‐ circuit, pole line, line miles or kilometers, etc.). | The responsible entity failed to inspect more than 10% up to and including 15% of its applicable lines (measured in units of choice ‐ circuit, pole line, line miles or kilometers, etc.). | The responsible entity failed to inspect more than 15% of its applicable lines (measured in units of choice ‐ circuit, pole line, line miles or kilometers, etc.). | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-003-5 | R7. | Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice ‐ circuit, pole line, line miles or kilometers, etc.). Examples of reasons for modification to annual plan may include: | 2024-04-01 |  | Medium | The responsible entity failed to complete 5% or less of its annual vegetation work plan for its applicable lines (as finally modified). | The responsible entity failed to complete more than 5% and up to and including 10% of its annual vegetation work plan for its applicable lines (as finally modified). | The responsible entity failed to complete more than 10% and up to and including 15% of its annual vegetation work plan for its applicable lines (as finally modified). | The responsible entity failed to complete more than 15% of its annual vegetation work plan for its applicable lines (as finally modified). | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-004-0 | R1. | The Transmission Owner and Generator Owner shall each document the methodology(ies) used to determine its electrical equipment and Facility Ratings. Further, the methodology(ies) shall comply with applicable Regional Reliability Organization requirements. The documentation shall address and include |  | 2006-08-01 | [10 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-004-0 | R2. | The Transmission Owner and Generator Owner shall provide documentation of the methodology(ies) used to determine its transmission equipment and Facility Ratings to the Regional Reliability Organization(s) and NERC on request (30 calendar days). |  | 2006-08-01 | [10 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-005-0 | R1. | The transmission Owner, and Generator Owner shall each have on file or be able to readily provide, a document or database identifying the Normal and Emergency Ratings of all of its transmission facilities (e.g., lines, transformers, terminal equipment, and storage devices) that are part of the interconnected transmission systems. Seasonal variations in Ratings shall be included as appropriate. |  | 2006-10-07 | [10 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-005-0 | R2. | The Transmission Owner and Generator Owner shall provide the Normal and Emergency Facility Ratings of all its transmission facilities to the Regional Reliability Organization(s) and NERC on request (30 calendar days). |  | 2006-10-07 | [10 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-008-1 | R1. | The Transmission Owner and Generator Owner shall each document its current methodology used for developing Facility Ratings (Facility Ratings Methodology) of its solely and jointly owned Facilities. The methodology shall include all of the following: | 2007-06-18 | 2012-12-31 | Low | [9 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-008-1 | R2. | The Transmission Owner and Generator Owner shall each make its Facility Ratings Methodology available for inspection and technical review by those Reliability Coordinators, Transmission Operators, Transmission Planners, and Planning Authorities that have responsibility for the area in which the associated Facilities are located, within 15 business days of receipt of a request. | 2007-06-18 | 2012-12-31 | Low | [9 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-008-1 | R3. | If a Reliability Coordinator, Transmission Operator, Transmission Planner, or Planning Authority provides written comments on its technical review of a Transmission Owner’s or Generator Owner’s Facility Ratings Methodology, the Transmission Owner or Generator Owner shall provide a written response to that commenting entity within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Facility Ratings Methodology and, if no change will be made to that Facility Ratings Methodology, the reason why. | 2007-06-18 | 2012-12-31 | Low | [9 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-008-2 | R1. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. [See standard for documentation requirements] |  | 2011-05-24 | Low | N/A | The Generator Owner’s Facility Rating documentation did not address Requirement R1, Part 1.1. | The Generator Owner’s Facility Rating documentation did not address Requirement R1, Part 1.2. | The Generator Owner failed to provide documentation for determining its Facility Ratings. | [5 empty] | GO
Inactive | FAC | FAC-008-2 | R2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. [See standard for methodology requirements] |  | 2011-05-24 | Low | The Generator Owner failed to include in its Facility Rating methodology one of the following Parts of Requirement R2: 2.1, 2.2.1, 2.2.2, 2.2.3, 2.2.4 | The Generator Owner failed to include in its Facility Rating methodology two of the following Parts of Requirement R2: 2.1, 2.2.1, 2.2.2, 2.2.3, 2.2.4 | The Generator Owner’s Facility Rating methodology did not address all the components of Requirement R2, Part 2.4. OR The Generator Owner failed to include in its Facility Rating Methodology, three of the following Parts of Requirement R2: 2.1, 2.2.1, 2.2.2, 2.2.3, 2.2.4 | The Generator Owner’s Facility Rating methodology failed to recognize a facility's rating based on the most limiting component rating as required in Requirement R2, Part 2.3 OR The Generator Owner failed to include in its Facility Rating Methodology four or more of the following Parts of Requirement R2: 2.1, 2.2.1, 2.2.2, 2.2.3, 2.2.4 | [5 empty] | GO
Inactive | FAC | FAC-008-2 | R3. | Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: [See standard for methodology requirements] |  | 2011-05-24 | Medium | The Transmission Owner failed to include in its Facility Rating methodology one of the following Parts of Requirement R3: 3.1, 3.2.1, 3.2.2, 3.2.3, 3.2.4 | The Transmission Owner failed to include in its Facility Rating methodology two of the following Parts of Requirement R3: 3.1, 3.2.1, 3.2.2, 3.2.3, 3.2.4 | The Transmission Owner’s Facility Rating methodology did not address either of the following Parts of Requirement R3: 3.4.1, 3.4.2 OR The Transmission Owner failed to include in its Facility Rating methodology three of the following Parts of Requirement R3: • 3.1 • 3.2.1 • 3.2.2 • 3.2.3 • 3.2.4 | The Transmission Owner’s Facility Rating methodology failed to recognize a Facility's rating based on the most limiting component rating as required in Requirement R3, Part 3.3 OR The Transmission Owner failed to include in its Facility Rating methodology four or more of the following Parts of Requirement R3: 3.1, 3.2.1, 3.2.2, 3.2.3, 3.2.4 | [18 empty] | TO
Inactive | FAC | FAC-008-2 | R4. | Each Transmission Owner shall make its Facility Ratings methodology and each Generator Owner shall each make its documentation for determining its Facility Ratings and its Facility Ratings methodology available for inspection and technical review by those Reliability Coordinators, Transmission Operators, Transmission Planners and Planning Coordinators that have responsibility for the area in which the associated Facilities are located, within 21 calendar days of receipt of a request. |  | 2011-05-24 | Low | The responsible entity made its Facility Ratings methodology or Facility Ratings documentation available within more than 21 calendar days but less than or equal to 31 calendar days after a request. | The responsible entity made its Facility Ratings methodology or Facility Ratings documentation available within more than 31 calendar days but less than or equal to 41 calendar days after a request. | The responsible entity made its Facility Rating methodology or Facility Ratings documentation available within more than 41 calendar days but less than or equal to 51 calendar days after a request. | The responsible entity failed to make its Facility Ratings methodology or Facility Ratings documentation available in more than 51 calendar days after a request. (R3) | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-008-2 | R5. | If a Reliability Coordinator, Transmission Operator, Transmission Planner or Planning Coordinator provides documented comments on its technical review of a Transmission Owner’s Facility Ratings methodology or Generator Owner’s documentation for determining its Facility Ratings and its Facility Rating methodology, the Transmission Owner or Generator Owner shall provide a response to that commenting entity within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Facility Ratings methodology and, if no change will be made to that Facility Ratings methodology, the reason why. |  | 2011-05-24 | Low | The responsible entity provided a response in more than 45 calendar days but less than or equal to 60 calendar days after a request. (R5) | The responsible entity provided a response in more than 60 calendar days but less than or equal to 70 calendar days after a request. OR The responsible entity provided a response within 45 calendar days, and the response indicated that a change will not be made to the Facility Ratings methodology or Facility Ratings documentation but did not indicate why no change will be made. (R5) | The responsible entity provided a response in more than 70 calendar days but less than or equal to 80 calendar days after a request. OR The responsible entity provided a response within 45 calendar days, but the response did not indicate whether a change will be made to the Facility Ratings methodology or Facility Ratings documentation. (R5) | The responsible entity failed to provide a response as required in more than 80 calendar days after the comments were received. (R5) | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-008-2 | R6. | Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. |  | 2011-05-24 | Medium | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for 5% or less of its solely owned and jointly owned Facilities. (R6) | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for more than 5% or more, but less than up to (and including) 10% of its solely owned and jointly owned Facilities. (R6) | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for more than 10% up to (and including) 15% of its solely owned and jointly owned Facilities. (R6) | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for more than15% of its solely owned and jointly owned Facilities. (R6) | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-008-2 | R7. | Each Transmission Owner and Generator Owner shall provide Facility Ratings for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities. |  | 2011-05-24 | Medium | The responsible entity provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by up to 15 calendar days. (R7) | The responsible entity provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by more than 15 calendar days but less than or equal to 25 calendar days. (R7) | The responsible entity provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by more than 25 calendar days but less than or equal to 35 calendar days. (R7) | The responsible entity provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by more than 35 calendar days. (R7) | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-008-3 | R1. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. [See standard for documentation requirements] | 2013-01-01 | 2021-09-30 | Low | N/A | The Generator Owner’s Facility Rating documentation did not address Requirement R1, Part 1.1. | The Generator Owner’s Facility Rating documentation did not address Requirement R1, Part 1.2. | The Generator Owner failed to provide documentation for determining its Facility Ratings. | [5 empty] | GO
Inactive | FAC | FAC-008-3 | R2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. [See standard for methodology requirements] | 2013-01-01 | 2021-09-30 | Medium | The Generator Owner failed to include in its Facility Rating methodology one of the following Parts of Requirement R2: 2.1, 2.2.1, 2.2.2, 2.2.3, 2.2.4 | The Generator Owner failed to include in its Facility Rating methodology two of the following Parts of Requirement R2: 2.1, 2.2.1, 2.2.2, 2.2.3, 2.2.4 | The Generator Owner’s Facility Rating methodology did not address all the components of Requirement R2, Part 2.4. OR The Generator Owner failed to include in its Facility Rating Methodology, three of the following Parts of Requirement R2: 2.1, 2.2.1, 2. | The Generator Owner’s Facility Rating methodology failed to recognize a facility's rating based on the most limiting component rating as required in Requirement R2, Part 2.3 OR The Generator Owner failed to include in its Facility Rating Methodology four or more of the following Parts of Requirement R2: • 2.1, 2.2.1, 2.2.2, 2.2.3, 2.2.4 | [5 empty] | GO
Inactive | FAC | FAC-008-3 | R3. | Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: [See standard for methodology requirements] | 2013-01-01 | 2021-09-30 | Medium | The Transmission Owner failed to include in its Facility Rating methodology one of the following Parts of Requirement R3: 3.1, 3.2.1, 3.2.2, 3.2.3, 3.2.4 | The Transmission Owner failed to include in its Facility Rating methodology two of the following Parts of Requirement R3: 3.1, 3.2.1, 3.2.2, 3.2.3, 3.2.4 | The Transmission Owner’s Facility Rating methodology did not address either of the following Parts of Requirement R3: 3.4.1, 3.4.2 OR The Transmission Owner failed to include in its Facility Rating methodology three of the following Parts of Requirement R3: 3.1, 3.2.1, 3.2.2, 3.2.3, 3.2.4 | The Transmission Owner’s Facility Rating methodology failed to recognize a Facility's rating based on the most limiting component rating as required in Requirement R3, Part 3.3 OR The Transmission Owner failed to include in its Facility Rating methodology four or more of the following Parts of Requirement R3: 3.1, 3.2.1, 3.2.2, 3.2.3, 3.2.4 | [18 empty] | TO
Inactive | FAC | FAC-008-3 | R4. | Each Transmission Owner shall make its Facility Ratings methodology and each Generator Owner shall each make its documentation for determining its Facility Ratings and its Facility Ratings methodology available for inspection and technical review by those Reliability Coordinators, Transmission Operators, Transmission Planners and Planning Coordinators that have responsibility for the area in which the associated Facilities are located, within 21 calendar days of receipt of a request. | 2013-01-01 | 2021-09-30 | Low | The responsible entity made its Facility Ratings methodology or Facility Ratings documentation available within more than 21 calendar days but less than or equal to 31 calendar days after a request. | The responsible entity made its Facility Ratings methodology or Facility Ratings documentation available within more than 31 calendar days but less than or equal to 41 calendar days after a request. | The responsible entity made its Facility Rating methodology or Facility Ratings documentation available within more than 41 calendar days but less than or equal to 51 calendar days after a request. | The responsible entity failed to make its Facility Ratings methodology or Facility Ratings documentation available in more than 51 calendar days after a request. (R3) | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-008-3 | R5. | If a Reliability Coordinator, Transmission Operator, Transmission Planner or Planning Coordinator provides documented comments on its technical review of a Transmission Owner’s Facility Ratings methodology or Generator Owner’s documentation for determining its Facility Ratings and its Facility Rating methodology, the Transmission Owner or Generator Owner shall provide a response to that commenting entity within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Facility Ratings methodology and, if no change will be made to that Facility Ratings methodology, the reason why. | 2013-01-01 | 2021-09-30 | Low | The responsible entity provided a response in more than 45 calendar days but less than or equal to 60 calendar days after a request. (R5) | The responsible entity provided a response in more than 60 calendar days but less than or equal to 70 calendar days after a request. OR The responsible entity provided a response within 45 calendar days, and the response indicated that a change will not be made to the Facility Ratings methodology or Facility Ratings documentation but did not indicate why no change will be made. (R5) | The responsible entity provided a response in more than 70 calendar days but less than or equal to 80 calendar days after a request. OR The responsible entity provided a response within 45 calendar days, but the response did not indicate whether a change will be made to the Facility Ratings methodology or Facility Ratings documentation. (R5) | The responsible entity failed to provide a response as required in more than 80 calendar days after the comments were received. (R5) | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-008-3 | R6. | Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. | 2013-01-01 | 2021-09-30 | Medium | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for 5% or less of its solely owned and jointly owned Facilities. (R6) | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for more than 5% or more, but less than up to (and including) 10% of its solely owned and jointly owned Facilities. (R6) | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for more than 10% up to (and including) 15% of its solely owned and jointly owned Facilities. (R6) | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for more than15% of its solely owned and jointly owned Facilities. (R6) | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-008-3 | R7. | Each Generator Owner shall provide Facility Ratings (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities. | 2013-01-01 | 2021-09-30 | Medium | The Generator Owner provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by up to and including 15 calendar days. | The Generator Owner provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by more than 15 calendar days but less than or equal to 25 calendar days. | The Generator Owner provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by more than 25 calendar days but less than or equal to 35 calendar days. | The Generator Owner provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by more than 35 calendar days. OR The Generator Owner failed to provide its Facility Ratings to the requesting entities. | [5 empty] | GO
Inactive | FAC | FAC-008-3 | R8. | Each Transmission Owner (and each Generator Owner subject to Requirement R2) shall provide requested information as specified below (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s): [See standard for requirements of providing requested information] | 2013-01-01 | 2021-09-30 | Medium | The responsible entity provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by up to and including 15 calendar days. (R8, Part 8.1) OR The responsible entity provided less than 100%, but not less than or equal to 95% of the required Rating information to all of the requesting entities. (R8, Part 8.1) OR The responsible entity provided the required Rating information to the requesting entity, but the information was provided up to and including 15 calendar days late. (R8, Part 8.2) OR The responsible entity provided less than 100%, but not less than or equal to 95% of the required Rating information to the requesting entity. (R8, Part 8.2) | The responsible entity provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by more than 15 calendar days but less than or equal to 25 calendar days. (R8, Part 8.1) OR The responsible entity provided less than 95%, but not less than or equal to 90% of the required Rating information to all of the requesting entities. (R8, Part 8.1) OR The responsible entity provided the required Rating information to the requesting entity, but did so more 15 calendar days but less than or equal to 25 calendar days late. (R8, Part 8.2) OR The responsible entity provided less than 95%, but not less than or equal to 90% of the required Rating information to the requesting entity. (R8, Part 8.2) | The responsible entity provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by more than 25 calendar days but less than or equal to 35 calendar days. (R8, Part 8.1) OR The responsible entity provided less than 90%, but not less than or equal to 85% of the required Rating information to all of the requesting entities. (R8, Part 8.1) OR The responsible entity provided the required Rating information to the requesting entity, but did so more than 25 calendar days but less than or equal to 35 calendar days late. (R8, Part 8.2) OR The responsible entity provided less than 90%, but no less than or equal to 85% of the required Rating information to the requesting entity. (R8, Part 8.2) | The responsible entity provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by more than 35 calendar days. (R8, Part 8.1) OR The responsible entity provided less than 85% of the required Rating information to all of the requesting entities. (R8, Part 8.1) OR The responsible entity provided the required Rating information to the requesting entity, but did so more than 35 calendar days late. (R8, Part 8.2) OR The responsible entity provided less than 85 % of the required Rating information to the requesting entity. (R8, Part 8.2) OR The responsible entity failed to provide its Rating information to the requesting entity. (R8, Part 8.1) | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-008-4 | R1. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. |  | 2021-02-04 | Low | N/A | The Generator Owner’s Facility Rating documentation did not address Requirement R1, Part 1.1. | The Generator Owner’s Facility Rating documentation did not address Requirement R1, Part 1.2. | The Generator Owner failed to provide documentation for determining its Facility Ratings. | [5 empty] | GO
Inactive | FAC | FAC-008-4 | R2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. |  | 2021-02-04 | Medium | The Generator Owner failed to include in its Facility Rating methodology one of the following Parts of Requirement R2: 2.1, 2.2.1., 2.2.2., 2.2.3., 2.2.4. | The Generator Owner failed to include in its Facility Rating methodology two of the following Parts of Requirement R2: 2.1, 2.2.1., 2.2.2., 2.2.3., 2.2.4. | The Generator Owner’s Facility Rating methodology did not address all the components of Requirement R2, Part 2.4. OR The Generator Owner failed to include in its Facility Rating Methodology, three of the following Parts of Requirement R2: 2.1, 2.2.1., 2.2.2., 2.2.3., 2.2.4. | The Generator Owner’s Facility Rating methodology failed to recognize a facility's rating based on the most limiting component rating as required in Requirement R2, Part 2.3 OR The Generator Owner failed to include in its Facility Rating Methodology four or more of the following Parts of Requirement R2: 2.1, 2.2.1., 2.2.2., 2.2.3., 2.2.4. | [5 empty] | GO
Inactive | FAC | FAC-008-4 | R3. | Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: |  | 2021-02-04 | Medium | The Transmission Owner failed to include in its Facility Rating methodology one of the following Parts of Requirement R3: 3.1, 3.2.1, 3.2.2, 3.2.3, 3.2.4 | The Transmission Owner failed to include in its Facility Rating methodology two of the following Parts of Requirement R3: 3.1, 3.2.1, 3.2.2, 3.2.3, 3.2.4 | The Transmission Owner’s Facility Rating methodology did not address either of the following Parts of Requirement R3: 3.4.1, 3.4.2 OR The Transmission Owner failed to include in its Facility Rating methodology three of the following Parts of Requirement R3: 3.1, 3.2.1, 3.2.2, 3.2.3, 3.2.4 | The Transmission Owner’s Facility Rating methodology failed to recognize a Facility's rating based on the most limiting component rating as required in Requirement R3, Part 3.3 OR The Transmission Owner failed to include in its Facility Rating methodology four or more of the following Parts of Requirement R3: 3.1, 3.2.1, 3.2.2, 3.2.3, 3.2.4 | [18 empty] | TO
Inactive | FAC | FAC-008-4 | R4. | Reserved. |  | 2021-02-04
Inactive | FAC | FAC-008-4 | R5. | Reserved. |  | 2021-02-04
Inactive | FAC | FAC-008-4 | R6. | Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. |  | 2021-02-04 | Medium | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for 5% or less of its solely owned and jointly owned Facilities. (R6) | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for more than 5% or more, but less than up to (and including) 10% of its solely owned and jointly owned Facilities. (R6) | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for more than 10% up to (and including) 15% of its solely owned and jointly owned Facilities. (R6) | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for more than15% of its solely owned and jointly owned Facilities. (R6) | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-008-4 | R7. | Reserved. |  | 2021-02-04
Inactive | FAC | FAC-008-4 | R8. | Reserved. |  | 2021-02-04
Mandatory Subject to Enforcement | FAC | FAC-008-5 | R1. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. | 2021-10-01 |  | Low | N/A | The Generator Owner’s Facility Rating documentation did not address Requirement R1, Part 1.1. | The Generator Owner’s Facility Rating documentation did not address Requirement R1, Part 1.2. | The Generator Owner failed to provide documentation for determining its Facility Ratings. | [5 empty] | GO
Mandatory Subject to Enforcement | FAC | FAC-008-5 | R2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. | 2021-10-01 |  | Medium | The Generator Owner failed to include in its Facility Rating methodology one of the following Parts of Requirement R2: • 2.1. • 2.2.1 • 2.2.2 • 2.2.3 • 2.2.4 | The Generator Owner failed to include in its Facility Rating methodology two of the following Parts of Requirement R2: • 2.1 • 2.2.1 • 2.2.2 • 2.2.3 • 2.2.4 | The Generator Owner’s Facility Rating methodology did not address all the components of Requirement R2, Part 2.4. OR The Generator Owner failed to include in its Facility Rating Methodology, three of the following Parts of Requirement R2: • 2.1. • 2.2.1 • 2.2.2 • 2.2.3 • 2.2.4 | The Generator Owner’s Facility Rating methodology failed to recognize a facility's rating based on the most limiting component rating as required in Requirement R2, Part 2.3 OR The Generator Owner failed to include in its Facility Rating Methodology four or more of the following Parts of Requirement R2: • 2.1 • 2.2.1 • 2.2.2 • 2.2.3 • 2.2.4 | [5 empty] | GO
Mandatory Subject to Enforcement | FAC | FAC-008-5 | R3. | Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: | 2021-10-01 |  | Medium | The Transmission Owner failed to include in its Facility Rating methodology one of the following Parts of Requirement R3: • 3.1 • 3.2.1 • 3.2.2 • 3.2.3 • 3.2.4 | The Transmission Owner failed to include in its Facility Rating methodology two of the following Parts of Requirement R3: • 3.1 • 3.2.1 • 3.2.2 • 3.2.3 • 3.2.4 | The Transmission Owner’s Facility Rating methodology did not address either of the following Parts of Requirement R3: • 3.4.1 • 3.4.2 OR The Transmission Owner failed to include in its Facility Rating methodology three of the following Parts of Requirement R3: • 3.1 • 3.2.1 • 3.2.2 • 3.2.3 • 3.2.4 | The Transmission Owner’s Facility Rating methodology failed to recognize a Facility's rating based on the most limiting component rating as required in Requirement R3, Part 3.3 OR The Transmission Owner failed to include in its Facility Rating methodology four or more of the following Parts of Requirement R3: • 3.1 • 3.2.1 • 3.2.2 • 3.2.3 • 3.2.4 | [18 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008-5 | R4. | Reserved. | 2021-10-01
Mandatory Subject to Enforcement | FAC | FAC-008-5 | R5. | Reserved. | 2021-10-01
Mandatory Subject to Enforcement | FAC | FAC-008-5 | R6. | Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. | 2021-10-01 |  | Medium | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for 5% or less of its solely owned and jointly owned Facilities. (R6) | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for more than 5% or more, but less than up to (and including) 10% of its solely owned and jointly owned Facilities. (R6) | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for more than 10% up to (and including) 15% of its solely owned and jointly owned Facilities. (R6) | The responsible entity failed to establish Facility Ratings consistent with the associated Facility Ratings methodology or documentation for determining the Facility Ratings for more than15% of its solely owned and jointly owned Facilities. (R6) | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-008-5 | R7. | Reserved. | 2021-10-01
Mandatory Subject to Enforcement | FAC | FAC-008-5 | R8. | Each Transmission Owner (and each Generator Owner subject to Requirement R2) shall provide requested information as specified below (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s): | 2021-10-01 |  | Medium | The responsible entity provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by up to and including 15 calendar days. (R8, Part 8.1) OR The responsible entity provided less than 100%, but not less than or equal to 95% of the required Rating information to all of the requesting entities. (R8, Part 8.1) OR The responsible entity provided the required Rating information to the requesting entity, but the information was provided up to and including 15 calendar days late. (R8, Part 8.2) OR The responsible entity provided less than 100%, but not less than or equal to 95% of the required Rating information to the requesting entity. (R8, Part 8.2) | The responsible entity provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by more than 15 calendar days but less than or equal to 25 calendar days. (R8, Part 8.1) OR The responsible entity provided less than 95%, but not less than or equal to 90% of the required Rating information to all of the requesting entities. (R8, Part 8.1) OR The responsible entity provided the required Rating information to the requesting entity, but did so more 15 calendar days but less than or equal to 25 calendar days late. (R8, Part 8.2) OR The responsible entity provided less than 95%, but not less than or equal to 90% of the required Rating information to the requesting entity. (R8, Part 8.2) | The responsible entity provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by more than 25 calendar days but less than or equal to 35 calendar days. (R8, Part 8.1) OR The responsible entity provided less than 90%, but not less than or equal to 85% of the required Rating information to all of the requesting entities. (R8, Part 8.1) OR The responsible entity provided the required Rating information to the requesting entity, but did so more than 25 calendar days but less than or equal to 35 calendar days late. (R8, Part 8.2) OR The responsible entity provided less than 90%, but no less than or equal to 85% of the required Rating information to the requesting entity. (R8, Part 8.2) | The responsible entity provided its Facility Ratings to all of the requesting entities but missed meeting the schedules by more than 35 calendar days. (R8, Part 8.1) OR The responsible entity provided less than 85% of the required Rating information to all of the requesting entities. (R8, Part 8.1) OR The responsible entity provided the required Rating information to the requesting entity, but did so more than 35 calendar days late. (R8, Part 8.2) OR The responsible entity provided less than 85 % of the required Rating information to the requesting entity. (R8, Part 8.2) OR The responsible entity failed to provide its Rating information to the requesting entity. (R8, Part 8.1) | [5 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-009-1 | R1. | The Transmission Owner and Generator Owner shall each establish Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings Methodology. | 2007-06-18 | 2012-12-31 | Medium | [9 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-009-1 | R2. | The Transmission Owner and Generator Owner shall each provide Facility Ratings for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities to its associated Reliability Coordinator(s), Planning Authority(ies), Transmission Planner(s), and Transmission Operator(s) as scheduled by such requesting entities. | 2007-06-18 | 2012-12-31 | Medium | [9 empty] | GO | [12 empty] | TO
Inactive | FAC | FAC-010-1 | R1. | The Planning Authority shall have a documented SOL Methodology for use in developing SOLs within its Planning Authority Area. This SOL Methodology shall: | 2008-07-01 | 2009-04-28 | Low | [14 empty] | PCPA
Inactive | FAC | FAC-010-1 | R2. | The Planning Authority’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | 2008-07-01 | 2009-04-28 | Low | [14 empty] | PCPA
Inactive | FAC | FAC-010-1 | R3. | The Planning Authority’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: | 2008-07-01 | 2009-04-28 | Low | [14 empty] | PCPA
Inactive | FAC | FAC-010-1 | R4. | The Planning Authority shall issue its SOL Methodology, and any change to that methodology, to all of the following prior to the effectiveness of the change: | 2008-07-01 | 2009-04-28 | Low | [14 empty] | PCPA
Inactive | FAC | FAC-010-1 | R5. | If a recipient of the SOL Methodology provides documented technical comments on the methodology, the Planning Authority shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the SOL Methodology and, if no change will be made to that SOL Methodology, the reason why. | 2008-07-01 | 2009-04-28 | Low | [14 empty] | PCPA
Inactive | FAC | FAC-010-2 | R1. | The Planning Authority shall have a documented SOL Methodology for use in developing SOLs within its Planning Authority Area. This SOL Methodology shall: | 2009-04-29 | 2010-04-18 | Low | Not applicable. | The Planning Authority has a documented SOL Methodology for use in developing SOLs within its Planning Authority Area, but it does not address R1.2 | The Planning Authority has a documented SOL Methodology for use in developing SOLs within its Planning Authority Area, but it does not address R1.3. | The Planning Authority has a documented SOL Methodology for use in developing SOLs within its Planning Authority Area, but it does not address R1.1. OR The Planning Authority has no documented SOL Methodology for use in developing SOLs within its Planning Authority Area. | [10 empty] | PCPA
Inactive | FAC | FAC-010-2 | R2. | The Planning Authority’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | 2009-04-29 | 2010-04-18 |  | The Planning Authority’s SOL Methodology requires that SOLs are set to meet BES performance following single and multiple contingencies, but does not address the pre-contingency state (R2.1) | The Planning Authority’s SOL Methodology requires that SOLs are set to meet BES performance in the precontingency state and following single contingencies, but does not address multiple contingencies. (R2.5-R2.6) | The Planning Authority’s SOL Methodology requires that SOLs are set to meet BES performance in the precontingency state and following multiple contingencies, but does not meet the performance for response to single contingencies. (R2.2 –R2.4) | The Planning Authority’s SOL Methodology requires that SOLs are set to meet BES performance in the precontingency state but does not require that SOLs be set to meet the BES performance specified for response to single contingencies (R2.2-R2.4) and does not require that SOLs be set to meet the BES performance specified for response to multiple contingencies. (R2.5-R2.6) | [10 empty] | PCPA
Inactive | FAC | FAC-010-2 | R3. | The Planning Authority’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: | 2009-04-29 | 2010-04-18 | Low | The Planning Authority has a methodology for determining SOLs that includes a description for all but one of the following: R3.1 through R3.6. | The Planning Authority has a methodology for determining SOLs that includes a description for all but two of the following: R3.1 through R3.6. | The Planning Authority has a methodology for determining SOLs that includes a description for all but three of the following: R3.1 through R3.6. | The Planning Authority has a methodology for determining SOLs that is missing a description of four or more of the following: R3.1 through R3.6. | [10 empty] | PCPA
Inactive | FAC | FAC-010-2 | R4. | The Planning Authority shall issue its SOL Methodology, and any change to that methodology, to all of the following prior to the effectiveness of the change: | 2009-04-29 | 2010-04-18 | Low | One or both of the following: The Planning Authority issued its SOL Methodology and changes to that methodology to all but one of the required entities. For a change in methodology, the changed methodology was provided up to 30 calendar days after the effectiveness of the change. | One of the following: The Planning Authority issued its SOL Methodology and changes to that methodology to all but one of the required entities AND for a change in methodology, the changed methodology was provided 30 calendar days or more, but less than 60 calendar days after the effectiveness of the change. OR The Planning Authority issued its SOL Methodology and changes to that methodology to all but two of the required entities AND for a change in methodology, the changed methodology was provided up to 30 calendar days after the effectiveness of the change. | One of the following: The Planning Authority issued its SOL Methodology and changes to that methodology to all but one of the required entities AND for a change in methodology, the changed methodology was provided 60 calendar days or more, but less than 90 calendar days after the effectiveness of the change. OR The Planning Authority issued its SOL Methodology and changes to that methodology to all but two of the required entities AND for a change in methodology, the changed methodology was provided 30 calendar days or more, but less than 60 calendar days after the effectiveness of the change. OR The Planning Authority issued its SOL Methodology and changes to that methodology to all but three of the required entities AND for a change in methodology, the changed methodology was provided up to 30 calendar days after the effectiveness of the change | One of the following: The Planning Authority failed to issue its SOL Methodology and changes to that methodology to more than three of the required entities. The Planning Authority issued its SOL Methodology and changes to that methodology to all but one of the required entities AND for a change in methodology, the changed methodology was provided 90 calendar days or more after the effectiveness of the change. OR The Planning Authority issued its SOL Methodology and changes to that methodology to all but two of the required entities AND for a change in methodology, the changed methodology was provided 60 calendar days or more, but less than 90 calendar days after the effectiveness of the change. OR The Planning Authority issued its SOL Methodology and changes to that methodology to all but three of the required entities AND for a change in methodology, the changed methodology was provided 30 calendar days or more, but less than 60 calendar days after the effectiveness of the change. The Planning Authority issued its SOL Methodology and changes to that methodology to all but four of the required entities AND for a change in methodology, the changed methodology was provided up to 30 calendar days after the effectiveness of the change. | [10 empty] | PCPA
Inactive | FAC | FAC-010-2 | R5. | If a recipient of the SOL Methodology provides documented technical comments on the methodology, the Planning Authority shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the SOL Methodology and, if no change will be made to that SOL Methodology, the reason why. | 2009-04-29 | 2010-04-18 | Low | The Planning Authority received documented technical comments on its SOL Methodology and provided a complete response in a time period that was longer than 45 calendar days but less than 60 calendar days. | The Planning Authority received documented technical comments on its SOL Methodology and provided a complete response in a time period that was 60 calendar days or longer but less than 75 calendar days. | The Planning Authority received documented technical comments on its SOL Methodology and provided a complete response in a time period that was 75 calendar days or longer but less than 90 calendar days. OR The Planning Authority’s response to documented technical comments on its SOL Methodology indicated that a change will not be made, but did not include an explanation of why the change will not be made. | The Planning Authority received documented technical comments on its SOL Methodology and provided a complete response in a time period that was 90 calendar days or longer. OR The Planning Authority’s response to documented technical comments on its SOL Methodology did not indicate whether a change will be made to the SOL Methodology. | [10 empty] | PCPA
Inactive | FAC | FAC-010-2.1 | R1. | The Planning Authority shall have a documented SOL Methodology for use in developing SOLs within its Planning Authority Area. This SOL Methodology shall: | 2010-04-19 | 2017-03-31 | Low | Not applicable. | The Planning Authority has a documented SOL Methodology for use in developing SOLs within its Planning Authority Area, but it does not address R1.2 | The Planning Authority has a documented SOL Methodology for use in developing SOLs within its Planning Authority Area, but it does not address R1.3. | The Planning Authority has a documented SOL Methodology for use in developing SOLs within its Planning Authority Area, but it does not address R1.1. OR The Planning Authority has no documented SOL Methodology for use in developing SOLs within its Planning Authority Area. | [10 empty] | PCPA
Inactive | FAC | FAC-010-2.1 | R2. | The Planning Authority’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | 2010-04-19 | 2017-03-31 |  | The Planning Authority’s SOL Methodology is missing one requirement as described in R2.1, R2.2, R2.3, R2.4, R2.5, or R2.6. | The Planning Authority’s SOL Methodology is missing two requirements as described in R2.1, R2.2, R2.3, R2.4, R2.5, or R2.6. | The Planning Authority’s SOL Methodology is missing three requirements as described in R2.1, R2.2, R2.3, R2.4, R2.5, or R2.6. | The Planning Authority’s SOL Methodology is missing four or more requirements as described in R2.1, R2.2, R2.3, R2.4, R2.5, or R2.6. | [10 empty] | PCPA
Inactive | FAC | FAC-010-2.1 | R3. | The Planning Authority’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: | 2010-04-19 | 2017-03-31 | Low | The Planning Authority has a methodology for determining SOLs that includes a description for all but one of the following: R3.1 through R3.6. | The Planning Authority has a methodology for determining SOLs that includes a description for all but two of the following: R3.1 through R3.6. | The Planning Authority has a methodology for determining SOLs that includes a description for all but three of the following: R3.1 through R3.6. | The Planning Authority has a methodology for determining SOLs that is missing a description of four or more of the following: R3.1 through R3.6. | [10 empty] | PCPA
Inactive | FAC | FAC-010-2.1 | R4. | The Planning Authority shall issue its SOL Methodology, and any change to that methodology, to all of the following prior to the effectiveness of the change: | 2010-04-19 | 2017-03-31 | Low | One or both of the following: The Planning Authority issued its SOL Methodology and changes to that methodology to all but one of the required entities. For a change in methodology, the changed methodology was provided up to 30 calendar days after the effectiveness of the change. | One of the following: The Planning Authority issued its SOL Methodology and changes to that methodology to all but one of the required entities AND for a change in methodology, the changed methodology was provided 30 calendar days or more, but less than 60 calendar days after the effectiveness of the change. OR The Planning Authority issued its SOL Methodology and changes to that methodology to all but two of the required entities AND for a change in methodology, the changed methodology was provided up to 30 calendar days after the effectiveness of the change. | One of the following: The Planning Authority issued its SOL Methodology and changes to that methodology to all but one of the required entities AND for a change in methodology, the changed methodology was provided 60 calendar days or more, but less than 90 calendar days after the effectiveness of the change. OR The Planning Authority issued its SOL Methodology and changes to that methodology to all but two of the required entities AND for a change in methodology, the changed methodology was provided 30 calendar days or more, but less than 60 calendar days after the effectiveness of the change. OR The Planning Authority issued its SOL Methodology and changes to that methodology to all but three of the required entities AND for a change in methodology, the changed methodology was provided up to 30 calendar days after the effectiveness of the change. | One of the following: The Planning Authority failed to issue its SOL Methodology and changes to that methodology to more than three of the required entities. The Planning Authority issued its SOL Methodology and changes to that methodology to all but one of the required entities AND for a change in methodology, the changed methodology was provided 90 calendar days or more after the effectiveness of the change. OR The Planning Authority issued its SOL Methodology and changes to that methodology to all but two of the required entities AND for a change in methodology, the changed methodology was provided 60 calendar days or more, but less than 90 calendar days after the effectiveness of the change. OR The Planning Authority issued its SOL Methodology and changes to that methodology to all but three of the required entities AND for a change in methodology, the changed methodology was provided 30 calendar days or more, but less than 60 calendar days after the effectiveness of the change. The Planning Authority issued its SOL Methodology and changes to that methodology to all but four of the required entities AND for a change in methodology, the changed methodology was provided up to 30 calendar days after the effectiveness of the change. | [10 empty] | PCPA
Inactive | FAC | FAC-010-2.1 | R5. | If a recipient of the SOL Methodology provides documented technical comments on the methodology, the Planning Authority shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the SOL Methodology and, if no change will be made to that SOL Methodology, the reason why. | 2010-04-19 | 2014-01-21 | Low | The Planning Authority received documented technical comments on its SOL Methodology and provided a complete response in a time period that was longer than 45 calendar days but less than 60 calendar days. | The Planning Authority received documented technical comments on its SOL Methodology and provided a complete response in a time period that was 60 calendar days or longer but less than 75 calendar days. | The Planning Authority received documented technical comments on its SOL Methodology and provided a complete response in a time period that was 75 calendar days or longer but less than 90 calendar days. OR The Planning Authority’s response to documented technical comments on its SOL Methodology indicated that a change will not be made, but did not include an explanation of why the change will not be made. | The Planning Authority received documented technical comments on its SOL Methodology and provided a complete response in a time period that was 90 calendar days or longer. OR The Planning Authority’s response to documented technical comments on its SOL Methodology did not indicate whether a change will be made to the SOL Methodology. | [10 empty] | PCPA
Inactive | FAC | FAC-010-3 | R1. | The Planning Authority shall have a documented SOL Methodology for use in developing SOLs within its Planning Authority Area. This SOL Methodology shall: | 2016-01-25 | 2024-03-31 | Low | N/A | The Planning Authority has a documented SOL Methodology for use in developing SOLs within its Planning Authority Area, but it does not address R1.2 | The Planning Authority has a documented SOL Methodology for use in developing SOLs within its Planning Authority Area, but it does not address R1.3. | The Planning Authority has a documented SOL Methodology for use in developing SOLs within its Planning Authority Area, but it does not address R1.1. OR The Planning Authority has no documented SOL Methodology for use in developing SOLs within its Planning Authority Area. | [10 empty] | PCPA
Inactive | FAC | FAC-010-3 | R2. | The Planning Authority’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | 2016-01-25 | 2024-03-31 |  | The Planning Authority’s SOL Methodology is missing one requirement as described in R2.1, R2.2, R2.3, R2.4, R2.5, or R2.6. | The Planning Authority’s SOL Methodology is missing two requirements as described in R2.1, R2.2, R2.3, R2.4, R2.5, or R2.6 | The Planning Authority’s SOL Methodology is missing three requirements as described in R2.1, R2.2, R2.3, R2.4, R2.5, or R2.6. | The Planning Authority’s SOL Methodology is missing four or more requirements as described in R2.1, R2.2-, R2.3, R2.4, R2.5, or R2.6 | [10 empty] | PCPA
Inactive | FAC | FAC-010-3 | R3. | The Planning Authority’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: | 2016-01-25 | 2024-03-31 | Low | The Planning Authority has a methodology for determining SOLs that includes a description for all but one of the following: R3.1 through R3.6. | The Planning Authority has a methodology for determining SOLs that includes a description for all but two of the following: R3.1 through R3.6. | The Planning Authority has a methodology for determining SOLs that includes a description for all but three of the following: R3.1 through R3.6. | The Planning Authority has a methodology for determining SOLs that is missing a description of four or more of the following: R3.1 through R3.6. | [10 empty] | PCPA
Inactive | FAC | FAC-010-3 | R4. | The Planning Authority shall issue its SOL Methodology, and any change to that methodology, to all of the following prior to the effectiveness of the change: | 2017-04-01 | 2024-03-31 | Low | One or both of the following: The Planning Authority issued its SOL Methodology and changes to that methodology to all but one of the required entities. For a change in methodology, the changed methodology was provided up to 30 calendar days after the effectiveness of the change. | One of the following: The Planning Authority issued its SOL Methodology and changes to that methodology to all but one of the required entities AND for a change in methodology, the changed methodology was provided 30 calendar days or more, but less than 60 calendar days after the effectiveness of the change. OR The Planning Authority issued its SOL Methodology and changes to that methodology to all but two of the required entities AND for a change in methodology, the changed methodology was provided up to 30 calendar days after the effectiveness of the change. | One of the following: The Planning Authority issued its SOL Methodology and changes to that methodology to all but one of the required entities AND for a change in methodology, the changed methodology was provided 60 calendar days or more, but less than 90 calendar days after the effectiveness of the change. OR The Planning Authority issued its SOL Methodology and changes to that methodology to all but two of the required entities AND for a change in methodology, the changed methodology was provided 30 calendar days or more, but less than 60 calendar days after the effectiveness of the change. OR The Planning Authority issued its SOL Methodology and changes to that methodology to all but three of the required entities AND for a change in methodology, the changed methodology was provided up to 30 calendar days after the effectiveness of the change. | One of the following: The Planning Authority failed to issue its SOL Methodology and changes to that methodology to more than three of the required entities. The Planning Authority issued its SOL Methodology and changes to that methodology to all but one of the required entities AND for a change in methodology, the changed methodology was provided 90 calendar days or more after the effectiveness of the change. OR The Planning Authority issued its SOL Methodology and changes to that methodology to all but two of the required entities AND for a change in methodology, the changed methodology was provided 60 calendar days or more, but less than 90 calendar days after the effectiveness of the change. OR The Planning Authority issued its SOL Methodology and changes to that methodology to all but three of the required entities AND for a change in methodology, the changed methodology was provided 30 calendar days or more, but less than 60 calendar days after the effectiveness of the change. | [10 empty] | PCPA
Inactive | FAC | FAC-011-1 | R1. | The Reliability Coordinator shall have a documented methodology for use in developing SOLs (SOL Methodology) within its Reliability Coordinator Area. This SOL Methodology shall: | 2008-10-01 | 2009-04-28 | Low | [16 empty] | RC
Inactive | FAC | FAC-011-1 | R2. | The Reliability Coordinator’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | 2008-10-01 | 2009-04-28 | Medium | [16 empty] | RC
Inactive | FAC | FAC-011-1 | R3. | The Reliability Coordinator’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: | 2008-10-01 | 2009-04-28 | Medium | [16 empty] | RC
Inactive | FAC | FAC-011-1 | R4. | The Reliability Coordinator shall issue its SOL Methodology and any changes to that methodology, prior to the effectiveness of the Methodology or of a change to the Methodology, to all of the following: | 2008-10-01 | 2009-04-28 | Low | [16 empty] | RC
Inactive | FAC | FAC-011-1 | R5. | If a recipient of the SOL Methodology provides documented technical comments on the methodology, the Reliability Coordinator shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the SOL Methodology and, if no change will be made to that SOL Methodology, the reason why. | 2008-10-01 | 2009-04-28 | Low | [16 empty] | RC
Inactive | FAC | FAC-011-2 | R1. | The Reliability Coordinator shall have a documented methodology for use in developing SOLs (SOL Methodology) within its Reliability Coordinator Area. This SOL Methodology shall: | 2009-04-29 | 2017-03-31 | Low | Not applicable. | The Reliability Coordinator has a documented SOL Methodology for use in developing SOLs within its Reliability Coordinator Area, but it does not address R1.2 | The Reliability Coordinator has a documented SOL Methodology for use in developing SOLs within its Reliability Coordinator Area, but it does not address R1.3. | The Reliability Coordinator has a documented SOL Methodology for use in developing SOLs within its Reliability Coordinator Area, but it does not address R1.1. OR The Reliability Coordinator has no documented SOL Methodology for use in developing SOLs within its Reliability Coordinator Area. | [12 empty] | RC
Inactive | FAC | FAC-011-2 | R2. | The Reliability Coordinator’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | 2009-04-29 | 2017-03-31 |  | The Reliability Coordinator‘s SOL Methodology requires that SOLs are set to meet BES performance following single contingencies, but does not require that SOLs are set to meet BES performance in the pre-contingency state. (R2.1) | Not applicable. | The Reliability Coordinator‘s SOL Methodology requires that SOLs are set to meet BES performance in the precontingency state, but does not require that SOLs are set to meet BES performance following single contingencies. (R2.2 – R2.4) | The Reliability Coordinator’s SOL Methodology does not require that SOLs are set to meet BES performance in the pre-contingency state and does not require that SOLs are set to meet BES performance following single contingencies. (R2.1 through R2.4) | [12 empty] | RC
Inactive | FAC | FAC-011-2 | R3. | The Reliability Coordinator’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: | 2009-04-29 | 2017-03-31 | Medium | The Reliability Coordinator’s SOL Methodology includes a description for all but one of the following: R3.1 through R3.7. | The Reliability Coordinator’s SOL Methodology includes a description for all but two of the following: R3.1 through R3.7. | The Reliability Coordinator’s SOL Methodology includes a description for all but three of the following: R3.1 through R3.7. | The Reliability Coordinator’s SOL Methodology is missing a description of four or more of the following: R3.1 through R3.7. | [12 empty] | RC
Inactive | FAC | FAC-011-2 | R4. | The Reliability Coordinator shall issue its SOL Methodology and any changes to that methodology, prior to the effectiveness of the Methodology or of a change to the Methodology, to all of the following: | 2009-04-29 | 2017-03-31 | Low | The Reliability Coordinator failed to issue its SOL Methodology and/or one or more changes to that methodology to one of the required entities specified in R4.1, R4.2, and R4.3. OR For a change in methodology, the changed methodology was provided to one or more of the required entities before the effectiveness of the change, but was provided to all the required entities no more than 10 calendar days after the effectiveness of the change. | The Reliability Coordinator failed to issue its SOL Methodology and/or one or more changes to that methodology to two of the required entities specified in R4.1, R4.2, and R4.3. OR For a change in methodology, the changed methodology was provided to one or more of the required entities more than 10 calendar days after the effectiveness of the change, but less than or equal to 20 days after the effectiveness of the change. | The Reliability Coordinator failed to issue its SOL Methodology and/or one or more changes to that methodology to three of the required entities specified in R4.1, R4.2, and R4.3. OR For a change in methodology, the changed methodology was provided to one or more of required entities more than 20 calendar days after the effectiveness of the change, but less than or equal to30 days after the effectiveness of the change | The Reliability Coordinator failed to issue its SOL Methodology and/or one or more changes to that methodology to four or more of the required entities specified in R4.1, R4.2, and R4.3 OR For a change in methodology, the changed methodology was provided to one or more of the required entities more than30 calendar days after the effectiveness of the change. | [12 empty] | RC
Inactive | FAC | FAC-011-2 | R5. | If a recipient of the SOL Methodology provides documented technical comments on the methodology, the Reliability Coordinator shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the SOL Methodology and, if no change will be made to that SOL Methodology, the reason why. | 2009-04-29 | 2014-01-21 | Low | The Reliability Coordinator received documented technical comments on its SOL Methodology and provided a complete response in a time period that was longer than 45 calendar days but less than 60 calendar days. | The Reliability Coordinator received documented technical comments on its SOL Methodology and provided a complete response in a time period that was 60 calendar days or longer but less than 75 calendar days. | The Reliability Coordinator received documented technical comments on its SOL Methodology and provided a complete response in a time period that was 75 calendar days or longer but less than 90 calendar days. OR The Reliability Coordinator’s response to documented technical comments on its SOL Methodology indicated that a change will not be made, but did not include an explanation of why the change will not be made. | The Reliability Coordinator received documented technical comments on its SOL Methodology and provided a complete response in a time period that was 90 calendar days or longer. OR The Reliability Coordinator’s response to documented technical comments on its SOL Methodology did not indicate whether a change will be made to the SOL Methodology. | [12 empty] | RC
Inactive | FAC | FAC-011-3 | R1. | The Reliability Coordinator shall have a documented methodology for use in developing SOLs (SOL Methodology) within its Reliability Coordinator Area. This SOL Methodology shall: | 2017-04-01 | 2024-03-31 | Low | N/A | The Reliability Coordinator has a documented SOL Methodology for use in developing SOLs within its Reliability Coordinator Area, but it does not address R1.2. | The Reliability Coordinator has a documented SOL Methodology for use in developing SOLs within its Reliability Coordinator Area, but it does not address R1.3. | The Reliability Coordinator has a documented SOL Methodology for use in developing SOLs within its Reliability Coordinator Area, but it does not address R1.1. OR The Reliability Coordinator has no documented SOL Methodology for use in developing SOLs within its Reliability Coordinator Area. | [12 empty] | RC
Inactive | FAC | FAC-011-3 | R2. | The Reliability Coordinator’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | 2017-04-01 | 2024-03-31 |  | The Reliability Coordinator‘s SOL Methodology requires that SOLs are set to meet BES performance following single contingencies, but does not require that SOLs are set to meet BES performance in the pre-contingency state. (R2.1) | Not applicable | The Reliability Coordinator‘s SOL Methodology requires that SOLs are set to meet BES performance in the pre-contingency state, but does not require that SOLs are set to meet BES performance following single contingencies. (R2.2 – R2.4) | The Reliability Coordinator’s SOL Methodology does not require that SOLs are set to meet BES performance in the pre-contingency state and does not require that SOLs are set to meet BES performance following single contingencies. (R2.1 through R2.4) | [12 empty] | RC
Inactive | FAC | FAC-011-3 | R3. | The Reliability Coordinator’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: | 2017-04-01 | 2024-03-31 | Medium | The Reliability Coordinator’s SOL Methodology includes a description for all but one of the following: R3.1 through R3.7. | The Reliability Coordinator’s SOL Methodology includes a description for all but two of the following: R3.1 through R3.7. | The Reliability Coordinator’s SOL Methodology includes a description for all but three of the following: R3.1 through R3.7. | The Reliability Coordinator’s SOL Methodology is missing a description of four or more of the following: R3.1 through R3.7. | [12 empty] | RC
Inactive | FAC | FAC-011-3 | R4. | The Reliability Coordinator shall issue its SOL Methodology and any changes to that methodology, prior to the effectiveness of the Methodology or of a change to the Methodology, to all of the following: | 2017-04-01 | 2024-03-31 | Low | The Reliability Coordinator failed to issue its SOL Methodology and/or one or more changes to that methodology to one of the required entities specified in R4.1, R4.2, and R4.3. OR For a change in methodology, the changed methodology was provided to one or more of the required entities before the effectiveness of the change, but was provided to all the required entities no more than 10 calendar days after the effectiveness of the change. | The Reliability Coordinator failed to issue its SOL Methodology and/or one or more changes to that methodology to two of the required entities specified in R4.1, R4.2, and R4.3. OR For a change in methodology, the changed methodology was provided to one or more of the required entities more than 10 calendar days after the effectiveness of the change, but less than or equal to 20 days after the effectiveness of the change. | The Reliability Coordinator failed to issue its SOL Methodology and/or one or more changes to that methodology to three of the required entities specified in R4.1, R4.2, and R4.3. OR For a change in methodology, the changed methodology was provided to one or more of required entities more than 20 calendar days after the effectiveness of the change, but less than or equal to30 days after the effectiveness of the change. | The Reliability Coordinator failed to issue its SOL Methodology and/or one or more changes to that methodology to four or more of the required entities specified in R4.1, R4.2, and R4.3 OR For a change in methodology, the changed methodology was provided to one or more of the required entities more than30 calendar days after the effectiveness of the change. | [12 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011-4 | R1. | Each Reliability Coordinator shall have a documented methodology for establishing SOLs (i.e., SOL methodology) within its Reliability Coordinator Area. | 2024-04-01 |  | Medium | N/A | N/A | N/A | The Reliability Coordinator did not have a documented SOL methodology for establishing SOLs within its Reliability Coordinator Area. | [12 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011-4 | R2. | Each Reliability Coordinator shall include in its SOL methodology the method for Transmission Operators to determine which owner-provided Facility Ratings are to be used in operations such that the Transmission Operator and its Reliability Coordinator use common Facility Ratings. | 2024-04-01 |  | Medium | N/A | N/A | The Reliability Coordinator included in its SOL methodology the method for Transmission Operators to determine which owner- provided Facility Ratings are to be used in operations, but the method did not address the use of common Facility Ratings between the Reliability Coordinator and the Transmission Operators in its Reliability Coordinator Area. | The Reliability Coordinator did not include in its SOL methodology the method for Transmission Operators to determine which owner- provided Facility Ratings are to be used in operations. | [12 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011-4 | R3. | Each Reliability Coordinator shall include in its SOL methodology the method for Transmission Operators to determine the System Voltage Limits to be used in operations. The method shall: | 2024-04-01 |  | Medium | The Reliability Coordinator failed to incorporate one of the Parts of Requirement R3 into its SOL methodology. | The Reliability Coordinator failed to incorporate two of the Parts of Requirement R3 into its SOL methodology. | The Reliability Coordinator failed to incorporate three of the Parts of Requirement R3 into its SOL methodology. | The Reliability Coordinator failed to incorporate four or more of the Parts of Requirement R3 into its SOL methodology. | [12 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011-4 | R4. | Each Reliability Coordinator shall include in its SOL methodology the method for determining the stability limits to be used in operations. The method shall: | 2024-04-01 |  | Medium | The Reliability Coordinator failed to incorporate one of the Parts of Requirement R4 into its SOL methodology. | The Reliability Coordinator failed to incorporate two of the Parts of Requirement R4 into its SOL methodology. | The Reliability Coordinator failed to incorporate three of the Parts of Requirement R4 into its SOL methodology. | The Reliability Coordinator failed to incorporate four or more of the Parts of Requirement R4 into its SOL methodology. | [12 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011-4 | R5. | Each Reliability Coordinator shall identify in its SOL methodology the set of Contingency events for use in determining stability limits and the set of Contingency events for use in performing Operational Planning Analysis (OPAs) and Real-time Assessments (RTAs). The SOL methodology for each set shall: | 2024-04-01 |  | Medium | N/A | N/A | The Reliability Coordinator failed to incorporate one of the Parts 5.2 or 5.3 of Requirement R5 into its SOL methodology. | The Reliability Coordinator failed to incorporate Part 5.1 of Requirement R5 into its SOL methodology. OR The Reliability Coordinator failed to incorporate Parts 5.2 and 5.3 of Requirement R5 into its SOL methodology. | [12 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011-4 | R6. | Each Reliability Coordinator shall include the following performance framework in its SOL methodology to determine SOL exceedances when performing Real-time monitoring, Real-time Assessments, and Operational Planning Analyses: | 2024-04-01 |  | High | The Reliability Coordinator failed to incorporate one of the Parts of Requirement R6 into its SOL methodology. | The Reliability Coordinator failed to incorporate two of the Parts of Requirement R6 into its SOL methodology. | The Reliability Coordinator failed to incorporate three of the Parts of Requirement R6 into its SOL methodology. | The Reliability Coordinator failed to incorporate four of the Parts of Requirement R6 into its SOL methodology. | [12 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011-4 | R7. | Each Reliability Coordinator shall include in its SOL methodology a risk-based approach for determining how SOL exceedances identified as part of Real-time monitoring and Real-time Assessments must be communicated and if so, the timeframe that communication must occur. The approach shall include: | 2024-04-01 |  | High | N/A | The Reliability Coordinator included in its SOL methodology, a risk-based approach for determining how SOL exceedances identified as part of Real- time monitoring and Real- time Assessments must be communicated and if so, with what priority, but failed to include one of the Parts 7.2.1 through 7.2.2. | The Reliability Coordinator included in its SOL methodology, a risk-based approach for determining how SOL exceedances identified as part of Real- time monitoring and Real- time Assessments must be communicated and if so, with what priority, but failed to include one of the Parts 7.1.1 through 7.1.5. | The Reliability Coordinator failed to include in its SOL methodology, a risk-based approach for determining how SOL exceedances identified as part of Real- time monitoring and Real- time Assessments must be communicated and if so, with what priority. | [12 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011-4 | R8. | Each Reliability Coordinator shall include in its SOL methodology: | 2024-04-01 |  | High | N/A | N/A | The Reliability Coordinator failed to include Part 8.1 (a description of how to identify the subset of SOLs that qualify as IROLs) in its SOL methodology. OR The Reliability Coordinator failed to include Part 8.2 (a criteria for determining when violating a SOL qualifies as an IROL in its SOL methodology. OR The Reliability Coordinator failed to include Part 8.2 (criteria for developing any associated IROL Tv) in its SOL methodology. | The Reliability Coordinator failed to include Parts 8.1 and 8.2 in its SOL methodology. | [12 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-011-4 | R9. | Each Reliability Coordinator shall provide its SOL methodology to: | 2024-04-01 |  | Low | The Reliability Coordinator failed to provide its new or revised SOL methodology to one of the parties specified in Requirement R9, Part 9.2 prior to the effective date OR The Reliability Coordinator provided its new or revised SOL methodology to a requesting Reliability Coordinator in accordance with Requirement R9, Part 9.1 but was late by less than or equal to 10 calendar days. | The Reliability Coordinator failed to provide its new or revised SOL methodology to two of the parties specified in Requirement R9, Part 9.2 prior to the effective date OR The Reliability Coordinator provided its new or revised SOL methodology to a requesting Reliability Coordinator in accordance with Requirement R9, Part 9.1, but was late by more than 10 calendar days but less than or equal to 20 calendar days. | The Reliability Coordinator failed to provide its new or revised SOL methodology to three of the parties specified in Requirement R9, Part 9.2 prior to the effective date OR The Reliability Coordinator provided its new or revised SOL methodology to a requesting Reliability Coordinator in accordance with Requirement R9, Part 9.1, but was late by more than 20 calendar days but less than or equal to 30 calendar days. | The Reliability Coordinator failed to provide its new or revised SOL methodology to four or more of the parties specified in Requirement R9, Part 9.2 prior to the effective date OR The Reliability Coordinator failed to provide its new or revised SOL methodology to one or more of the parties specified in Requirement R9, Part 9.2 OR The Reliability Coordinator provided its new or revised SOL methodology to a requesting Reliability Coordinator in accordance with Requirement R9, Part 9.1, but was late by more than 30 calendar days. OR The Reliability Coordinator failed to provide its new or revised SOL methodology to a requesting Reliability Coordinator in accordance with Requirement R9, Part 9.1. | [12 empty] | RC
Inactive | FAC | FAC-012-1 | R1. | The Reliability Coordinator and Planning Authority shall each document its current methodology used for developing its inter-regional and intra-regional Transfer Capabilities (Transfer Capability Methodology). The Transfer Capability Methodology shall include all of the following: |  | 2013-03-31 | Low | [14 empty] | PCPA |  | RC
Inactive | FAC | FAC-012-1 | R2. | The Reliability Coordinator shall issue its Transfer Capability Methodology, and any changes to that methodology, prior to the effectiveness of such changes, to all of the following: |  | 2013-03-31 | Low | [16 empty] | RC
Inactive | FAC | FAC-012-1 | R3. | The Planning Authority shall issue its Transfer Capability Methodology, and any changes to that methodology, prior to the effectiveness of such changes, to all of the following: |  | 2013-03-31 | Low | [14 empty] | PCPA
Inactive | FAC | FAC-012-1 | R4. | If a recipient of the Transfer Capability Methodology provides documented technical comments on the methodology, the Reliability Coordinator or Planning Authority shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Transfer Capability Methodology and, if no change will be made to that Transfer Capability Methodology, the reason why. |  | 2013-03-31 | Low | [14 empty] | PCPA |  | RC
Inactive | FAC | FAC-013-1 | R1. | The Reliability Coordinator and Planning Authority shall each establish a set of inter-regional and intra-regional Transfer Capabilities that is consistent with its current Transfer Capability Methodology. | 2007-06-18 | 2013-03-31 | Medium | The Reliability Coordinator or Planning Authority has established a set of Transfer Capabilities, but one or more Transfer Capabilities, but not more than 25% of all Transfer Capabilities required to be established, are not consistent with the current Tra | The Reliability Coordinator or Planning Authority has established a set of Transfer Capabilities, but more than 25% of those Transfer Capabilities, but not more than 50% of all Transfer Capabilities required to be established, are not consistent with the | The Reliability Coordinator or Planning Authority has established a set of Transfer Capabilities, but more than 50% of those Transfer Capabilities, but not more than 75% of all Transfer Capabilities required to be established, are not consistent with the | The Reliability Coordinator or Planning Authority has established a set of Transfer Capabilities, but more than 75% of those Transfer Capabilities are not consistent with the current Transfer Capability Methodology | [10 empty] | PCPA |  | RC
Inactive | FAC | FAC-013-1 | R2. | The Reliability Coordinator and Planning Authority shall each provide its inter-regional and intra-regional Transfer Capabilities to those entities that have a reliability-related need for such Transfer Capabilities and make a written request that includes a schedule for delivery of such Transfer Capabilities as follows: | 2007-06-18 | 2013-03-31 | Medium | The responsible entity failed to provide Transfer Capabilities to up to (and including) 5% of the required entities. | The responsible entity failed to provide Transfer Capabilities to more than 5% up to (and including) 10% of the required entities. | The responsible entity failed to provide Transfer Capabilities to more than 10% up to (and including) 15% of the required entities. | The responsible entity failed to provide Transfer Capabilities to more than 15% of the required entities. | [10 empty] | PCPA |  | RC
Inactive | FAC | FAC-013-2 | R1. | Each Planning Coordinator shall have a documented methodology it uses to perform an annual assessment of Transfer Capability in the Near-Term Transmission Planning Horizon (Transfer Capability methodology). The Transfer Capability methodology shall include, at a minimum, the following information: [See standard pdf for requirements of the Transfer Capability methodology] | 2013-04-01 | 2020-12-14 | Medium | The Planning Coordinator has a Transfer Capability methodology but failed to address one or two of the items listed in Requirement R1, Part 1.4. | The Planning Coordinator has a Transfer Capability methodology, but failed to incorporate one of the following Parts of Requirement R1 into that methodology: Part 1.1, Part 1.2, Part 1.3, Part 1.5 OR The Planning Coordinator has a Transfer Capability methodology but failed to address three of the items listed in Requirement R1, Part 1.4. | The Planning Coordinator has a Transfer Capability methodology, but failed to incorporate two of the following Parts of Requirement R1 into that methodology: Part 1.1, Part 1.2, Part 1.3, Part 1.5 OR The Planning Coordinator has a Transfer Capability methodology but failed to address four of the items listed in Requirement R1, Part 1.4. | The Planning Coordinator did not have a Transfer Capability methodology. OR The Planning Coordinator has a Transfer Capability methodology, but failed to incorporate three or more of the following Parts of Requirement R1 into that methodology: Part 1.1, Part 1.2, Part 1.3, Part 1.5 OR The Planning Coordinator has a Transfer Capability methodology but failed to address more than four of the items listed in Requirement R1, Part 1.4. | [10 empty] | PCPA
Inactive | FAC | FAC-013-2 | R2. | Each Planning Coordinator shall issue its Transfer Capability methodology, and any revisions to the Transfer Capability methodology, to the following entities subject to the following: [See standard pdf for requirements of issuing the Transfer Capability Methodology] | 2013-04-01 | 2020-12-14 | Low | The Planning Coordinator notified one or more of the parties specified in Requirement R2 of a new or revised Transfer Capability methodology after its implementation, but not more than 30 calendar days after its implementation. OR The Planning Coordinator provided the transfer Capability methodology more than 30 calendar days but not more than 60 calendar days after the receipt of a request. | The Planning Coordinator notified one or more of the parties specified in Requirement R2 of a new or revised Transfer Capability methodology more than 30 calendar days after its implementation, but not more than 60 calendar days after its implementation. OR The Planning Coordinator provided the Transfer Capability methodology more than 60 calendar days but not more than 90 calendar days after receipt of a request | The Planning Coordinator notified one or more of the parties specified in Requirement R2 of a new or revised Transfer Capability methodology more than 60 calendar days, but not more than 90 calendar days after its implementation. OR The Planning Coordinator provided the Transfer Capability methodology more than 90 calendar days but not more than 120 calendar days after receipt of a request. | The Planning Coordinator failed to notify one or more of the parties specified in Requirement R2 of a new or revised Transfer Capability methodology more than 90 calendar days after its implementation. OR The Planning Coordinator provided the Transfer Capability methodology more than 120 calendar days after receipt of a request. | [10 empty] | PCPA
Inactive | FAC | FAC-013-2 | R3. | If a recipient of the Transfer Capability methodology provides documented concerns with the methodology, the Planning Coordinator shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Transfer Capability methodology and, if no change will be made to that Transfer Capability methodology, the reason why. | 2013-04-01 | 2020-12-14 | Low | The Planning Coordinator provided a documented response to a documented concern with its Transfer Capability methodology as required in Requirement R3 more than 45 calendar days, but not more than 60 calendar days after receipt of the concern. | The Planning Coordinator provided a documented response to a documented concern with its Transfer Capability methodology as required in Requirement R3 more than 60 calendar days, but not more than 75 calendar days after receipt of the concern. | The Planning Coordinator provided a documented response to a documented concern with its Transfer Capability methodology as required in Requirement R3 more than 75 calendar days, but not more than 90 calendar days after receipt of the concern. | The Planning Coordinator failed to provide a documented response to a documented concern with its Transfer Capability methodology as required in Requirement R3 by more than 90 calendar days after receipt of the concern. OR The Planning Coordinator failed to respond to a documented concern with its Transfer Capability methodology. | [10 empty] | PCPA
Inactive | FAC | FAC-013-2 | R4. | During each calendar year, each Planning Coordinator shall conduct simulations and document an assessment based on those simulations in accordance with its Transfer Capability methodology for at least one year in the Near-Term Transmission Planning Horizon. | 2013-04-01 | 2020-12-14 | Medium | The Planning Coordinator conducted a Transfer Capability assessment outside the calendar year, but not by more than 30 calendar days. | The Planning Coordinator conducted a Transfer Capability assessment outside the calendar year, by more than 30 calendar days, but not by more than 60 calendar days. | The Planning Coordinator conducted a Transfer Capability assessment outside the calendar year, by more than 60 calendar days, but not by more than 90 calendar days. | The Planning Coordinator failed to conduct a Transfer Capability assessment outside the calendar year by more than 90 calendar days. OR The Planning Coordinator failed to conduct a Transfer Capability assessment. | [10 empty] | PCPA
Inactive | FAC | FAC-013-2 | R5. | Each Planning Coordinator shall make the documented Transfer Capability assessment results available within 45 calendar days of the completion of the assessment to the recipients of its Transfer Capability methodology pursuant to Requirement R2, Parts 2.1 and Part 2.2. However, if a functional entity that has a reliability related need for the results of the annual assessment of the Transfer Capabilities makes a written request for such an assessment after the completion of the assessment, the Planning Coordinator shall make the documented Transfer Capability assessment results available to that entity within 45 calendar days of receipt of the request | 2013-04-01 | 2020-12-14 | Low | The Planning Coordinator made its documented Transfer Capability assessment available to one or more of the recipients of its Transfer Capability methodology more than 45 calendar days after the requirements of R5,, but not more than 60 calendar days after completion of the assessment. | The Planning Coordinator made its Transfer Capability assessment available to one or more of the recipients of its Transfer Capability methodology more than 60 calendar days after the requirements of R5, but not more than 75 calendar days after completion of the assessment. | The Planning Coordinator made its Transfer Capability assessment available to one or more of the recipients of its Transfer Capability methodology more than 75 calendar days after the requirements of R5, but not more than 90 days after completion of the assessment. | The Planning Coordinator failed to make its documented Transfer Capability assessment available to one or more of the recipients of its Transfer Capability methodology more than 90 days after the requirements of R5. OR The Planning Coordinator failed to make its documented Transfer Capability assessment available to any of the recipients of its Transfer Capability methodology under the requirements of R5. | [10 empty] | PCPA
Inactive | FAC | FAC-013-2 | R6. | If a recipient of a documented Transfer Capability assessment requests data to support the assessment results, the Planning Coordinator shall provide such data to that entity within 45 calendar days of receipt of the request. The provision of such data shall be subject to the legal and regulatory obligations of the Planning Coordinator’s area regarding the disclosure of confidential and/or sensitive information. | 2013-04-01 | 2020-12-14 | Low | The Planning Coordinator provided the requested data as required in Requirement R6 more than 45 calendar days after receipt of the request for data, but not more than 60 calendar days after the receipt of the request for data. | The Planning Coordinator provided the requested data as required in Requirement R6 more than 60 calendar days after receipt of the request for data, but not more than 75 calendar days after the receipt of the request for data. | The Planning Coordinator provided the requested data as required in Requirement R6 more than 75 calendar days after receipt of the request for data, but not more than 90 calendar days after the receipt of the request for data. | The Planning Coordinator provided the requested data as required in Requirement R6 more than 90 after the receipt of the request for data. OR The Planning Coordinator failed to provide the requested data as required in Requirement R6. | [10 empty] | PCPA
Inactive | FAC | FAC-014-1 | R1. | The Reliability Coordinator shall ensure that SOLs, including Interconnection Reliability Operating Limits (IROLs), for its Reliability Coordinator Area are established and that the SOLs (including Interconnection Reliability Operating Limits) are consistent with its SOL Methodology. | 2009-01-01 | 2009-04-28 | Medium | [16 empty] | RC
Inactive | FAC | FAC-014-1 | R2. | The Transmission Operator shall establish SOLs (as directed by its Reliability Coordinator) for its portion of the Reliability Coordinator Area that are consistent with its Reliability Coordinator’s SOL Methodology. | 2009-01-01 | 2009-04-28 | Medium | [23 empty] | TOP
Inactive | FAC | FAC-014-1 | R3. | The Planning Authority shall establish SOLs, including IROLs, for its Planning Authority Area that are consistent with its SOL Methodology. | 2009-01-01 | 2009-04-28 | Medium | [14 empty] | PCPA
Inactive | FAC | FAC-014-1 | R4. | The Transmission Planner shall establish SOLs, including IROLs, for its Transmission Planning Area that are consistent with its Planning Authority’s SOL Methodology. | 2009-01-01 | 2009-04-28 | Medium | [24 empty] | TP
Inactive | FAC | FAC-014-1 | R5. | The Reliability Coordinator, Planning Authority and Transmission Planner shall each provide its SOLs and IROLs to those entities that have a reliability-related need for those limits and provide a written request that includes a schedule for delivery of those limits as follows: | 2009-01-01 | 2009-04-28 | High | [14 empty] | PCPA |  | RC | [7 empty] | TP
Inactive | FAC | FAC-014-1 | R6. | The Planning Authority shall identify the subset of multiple contingencies (if any), from Reliability Standard TPL-003 which result in stability limits. | 2009-01-01 | 2009-04-28 | Medium | [14 empty] | PCPA
Inactive | FAC | FAC-014-2 | R1. | The Reliability Coordinator shall ensure that SOLs, including Interconnection Reliability Operating Limits (IROLs), for its Reliability Coordinator Area are established and that the SOLs (including Interconnection Reliability Operating Limits) are consistent with its SOL Methodology. | 2009-04-29 | 2024-03-31 | Medium | There are SOLs, for the Reliability Coordinator Area, but from 1% up to but less than 25% of these SOLs are inconsistent with the Reliability Coordinator’s SOL Methodology. (R1) | There are SOLs, for the Reliability Coordinator Area, but 25% or more, but less than 50% of these SOLs are inconsistent with the Reliability Coordinator’s SOL Methodology. (R1) | There are SOLs, for the Reliability Coordinator Area, but 50% or more, but less than 75% of these SOLs are inconsistent with the Reliability Coordinator’s SOL Methodology. (R1) | There are SOLs for the Reliability Coordinator Area, but one or more of these the SOLs are inconsistent with the Reliability Coordinator’s SOL Methodology. (R1) | [12 empty] | RC
Inactive | FAC | FAC-014-2 | R2. | The Transmission Operator shall establish SOLs (as directed by its Reliability Coordinator) for its portion of the Reliability Coordinator Area that are consistent with its Reliability Coordinator’s SOL Methodology. | 2009-04-29 | 2024-03-31 | Medium | The Transmission Operator has established SOLs for its portion of the Reliability Coordinator Area, but from 1% up to but less than 25% of these SOLs are inconsistent with the Reliability Coordinator’s SOL Methodology. (R2) | The Transmission Operator has established SOLs for its portion of the Reliability Coordinator Area, but 25% or more, but less than 50% of these SOLs are inconsistent with the Reliability Coordinator’s SOL Methodology. (R2) | The Transmission Operator has established SOLs for its portion of the Reliability Coordinator Area, but 50% or more, but less than 75% of these SOLs are inconsistent with the Reliability Coordinator’s SOL Methodology. (R2) | The Transmission Operator has established SOLs for its portion of the Reliability Coordinator Area, but 75% or more of these SOLs are inconsistent with the Reliability Coordinator’s SOL Methodology. (R2) | [19 empty] | TOP
Inactive | FAC | FAC-014-2 | R3. | The Planning Authority shall establish SOLs, including IROLs, for its Planning Authority Area that are consistent with its SOL Methodology. | 2009-04-29 | 2024-03-31 | Medium | There are SOLs, for the Planning Coordinator Area, but from 1% up to, but less than, 25% of these SOLs are inconsistent with the Planning Coordinator’s SOL Methodology. (R3) | There are SOLs, for the Planning Coordinator Area, but 25% or more, but less than 50% of these SOLs are inconsistent with the Planning Coordinator’s SOL Methodology. (R3) | There are Sols for the Planning Coordinator Area, but 10% or more, but less than 75% of these SOLs are inconsistent with the Planning Coordinator’s SOL Methodology. (R3) | There are SOLs, for the Planning Coordinator Area, but 75% or more of these SOLs are inconsistent with the Planning Coordinator’s SOL Methodology. (R3) | [10 empty] | PCPA
Inactive | FAC | FAC-014-2 | R4. | The Transmission Planner shall establish SOLs, including IROLs, for its Transmission Planning Area that are consistent with its Planning Authority’s SOL Methodology. | 2009-04-29 | 2024-03-31 | Medium | The Transmission Planner has established SOLs for its portion of the Planning Coordinator Area, but up to 25% of these SOLs are inconsistent with the Planning Coordinator’s SOL Methodology. (R4) | The Transmission Planner has established SOLs for its portion of the Planning Coordinator Area, but 25% or more, but less than 50% of these SOLs are inconsistent with the Planning Coordinator’s SOL Methodology. (R4) | The Transmission Planner has established SOLs for its portion of the Reliability Coordinator Area, but 50% or more, but less than 75% of these SOLs are inconsistent with the Planning Coordinator’s SOL Methodology. (R4) | The Transmission Planner has established SOLs for its portion of the Planning Coordinator Area, but one or more of these SOLs are inconsistent with the Planning Coordinator’s SOL Methodology. (R4) | [20 empty] | TP
Inactive | FAC | FAC-014-2 | R5. | The Reliability Coordinator, Planning Authority, and Transmission Planner shall each provide its SOLs and IROLs to those entities that have a reliability-related need for those limits and provide a written request that includes a schedule for delivery of those limits as follows: | 2009-04-29 | 2024-03-31 | High | The responsible entity provided its SOLs to all the requesting entities but missed meeting one or more of the schedules by less than 15 calendar days. (R5) | One of the following: The responsible entity provided its SOLs to all but one of the requesting entities within the schedules provided. (R5) Or The responsible entity provided its SOLs to all the requesting entities but missed meeting one or more of the schedules for 15 or more but less than 30 calendar days. (R5) OR The supporting information provided with the IROLs does not address 5.1.4 | One of the following: The responsible entity provided its SOLs (including the subset of SOLs that are IROLs) to all but two of the requesting entities within the schedules provided. (R5) Or The responsible entity provided its SOLs to all the requesting entities but missed meeting one or more of the schedules for 30 or more but less than 45 calendar days. (R5) OR The supporting information provided with the IROLs does not address 5.1.3 | One of the following: The responsible entity failed to provide its SOLs to more than two of the requesting entities within 45 calendar days of the associated schedules. (R5) OR The supporting information provided with the IROLs does not address 5.1.1 and 5.1.2. | [10 empty] | PCPA |  | RC | [7 empty] | TP
Inactive | FAC | FAC-014-2 | R6. | The Planning Authority shall identify the subset of multiple contingencies (if any), from Reliability Standard TPL-003 which result in stability limits. | 2009-04-29 | 2024-03-31 | Medium | The Planning Authority failed to notify the Reliability Coordinator in accordance with R6.2 | Not applicable. | The Planning Authority identified the subset of multiple contingencies which result in stability limits but did not provide the list of multiple contingencies and associated limits to one Reliability Coordinator that monitors the Facilities associated with these limits. (R6.1) | The Planning Authority did not identify the subset of multiple contingencies which result in stability limits. (R6) OR The Planning Authority identified the subset of multiple contingencies which result in stability limits but did not provide the list of multiple contingencies and associated limits to more than one Reliability Coordinator that monitors the Facilities associated with these limits. (R6.1) | [10 empty] | PCPA
Mandatory Subject to Enforcement | FAC | FAC-014-3 | R1. | Each Reliability Coordinator shall establish Interconnection Reliability Operating Limits (IROLs) for its Reliability Coordinator Area in accordance with its System Operating Limit methodology (SOL methodology). | 2024-04-01 |  | High | N/A | N/A | N/A | The Reliability Coordinator failed to establish Interconnection Reliability Operating Limits (IROLs) for its Reliability Coordinator Area in accordance with its System Operating Limit Methodology (“SOL methodology”). | [12 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014-3 | R2. | Each Transmission Operator shall establish System Operating Limits (SOLs) for its portion of the Reliability Coordinator Area in accordance with its Reliability Coordinator’s SOL methodology. | 2024-04-01 |  | Medium | N/A | N/A | N/A | The Transmission Operator failed to establish SOLs for its portion of the Reliability Coordinator Area in accordance with its Reliability Coordinator’s SOL methodology. | [19 empty] | TOP
Mandatory Subject to Enforcement | FAC | FAC-014-3 | R3. | Each Transmission Operator shall provide its SOLs to its Reliability Coordinator. | 2024-04-01 |  | Medium | N/A | N/A | The Transmission Operator provided its SOLs to its Reliability Coordinator, but failed to provide its SOLs at the periodicity at which the Reliability Coordinator needs such information to perform its reliability functions. | The Transmission Operator failed to provide its SOLs to its Reliability Coordinator. | [19 empty] | TOP
Mandatory Subject to Enforcement | FAC | FAC-014-3 | R4. | Each Reliability Coordinator shall establish stability limits when an identified instability impacts adjacent Reliability Coordinator Areas or more than one Transmission Operator in its Reliability Coordinator Area in accordance with its SOL methodology. | 2024-04-01 |  | High | N/A | N/A | N/A | The Reliability Coordinator failed to establish stability limits to be used in operations when the limit impacts an adjacent Reliability Coordinator or more than one Transmission Operator in its Reliability Coordinator Area in accordance with its SOL methodology. | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | FAC | FAC-014-3 | R5. | Each Reliability Coordinator shall provide: | 2024-04-01 |  | High | The Reliability Coordinator failed to provide one of the items listed in Requirement R5, Parts 5.1 through 5.6. | The Reliability Coordinator failed to provide two of the items listed in Requirement R5, Parts 5.1 through 5.6. | The Reliability Coordinator failed to provide three of the items listed in Requirement R5, Parts 5.1 through 5.6. | The Reliability Coordinator failed to provide four or more of the items listed in Requirement R5, Parts 5.1 through 5.6. | [12 empty] | RC
Mandatory Subject to Enforcement | FAC | FAC-014-3 | R6. | Each Planning Coordinator and each Transmission Planner shall implement a documented process to use Facility Ratings, System steady-state voltage limits and stability criteria in its Planning Assessment of Near-Term Transmission Planning Horizon that are equally limiting or more limiting than the criteria for Facility Ratings, System Voltage Limits and stability described in its respective Reliability Coordinator’s SOL methodology. · The Planning Coordinator may use less limiting Facility Ratings, System steady-state voltage limits and stability criteria if it provides a technical rationale to each affected Transmission Planner, Transmission Operator and Reliability Coordinator. · The Transmission Planner may use less limiting Facility Ratings, System steady-state voltage limits and stability criteria if it provides a technical rationale to each affected Planning Coordinator, Transmission Operator and Reliability Coordinator. | 2024-04-01 |  | Medium | N/A | N/A | The Planning Coordinator or a Transmission Planner used less limiting Facility Ratings, System steady state voltage limits or stability criteria than the criteria for Facility Ratings, System Voltage Limits or stability described in its respective Reliability Coordinator’s SOL methodology, but failed to provide a technical rationale for allowing the use of less limiting Facility Ratings, System Voltage Limits or stability criteria. | The Planning Coordinator or a Transmission Planner failed to implement a process to ensure that Facility Ratings, System steady state voltage limits or stability criteria used in Planning Assessment are equally limiting or more limiting than the criteria for Facility Ratings, System Voltage Limits or stability described in its respective Reliability Coordinator’s SOL methodology. | [10 empty] | PCPA |  | RC | [6 empty] | TOP | TP
Mandatory Subject to Enforcement | FAC | FAC-014-3 | R7. | Each Planning Coordinator and each Transmission Planner shall annually communicate the following information for Corrective Action Plans developed to address any instability identified in its Planning Assessment of the Near-Term Transmission Planning Horizon to each impacted Transmission Operator and Reliability Coordinator. This communication shall include: | 2024-04-01 |  | Medium | The Planning Coordinator or a Transmission Planner communicated the identified instability to each impacted Reliability Coordinator and Transmission Operator, but the communication did not contain one of the elements listed in Requirement R7, Parts 7.1 through 7.5. | The Planning Coordinator or a Transmission Planner communicated the identified instability to each impacted Reliability Coordinator and Transmission Operator, but the communication did not contain two of the elements listed in Requirement R7, Parts 7.1 through 7.5. | The Planning Coordinator or a Transmission Planner communicated the identified instability to each impacted Reliability Coordinator and Transmission Operator, but the communication did not contain three elements listed in Requirement R7, Parts 7.1 through 7.5. | The Planning Coordinator or a Transmission Planner communicated the identified instability to each impacted Reliability Coordinator and Transmission Operator, but the communication did not contain four or more of the elements listed in Requirement R7, Parts 7.1 through 7.5. OR The Planning Coordinator or a Transmission Planner failed to communicate any identified instability, to each impacted Reliability Coordinator and Transmission Operator. | [10 empty] | PCPA |  | RC | [6 empty] | TOP | TP
Mandatory Subject to Enforcement | FAC | FAC-014-3 | R8. | Each Planning Coordinator and each Transmission Planner shall annually communicate to each impacted Transmission Owner and Generation Owner a list of their Facilities that comprise the planning event Contingency(ies) that would cause instability, Cascading or uncontrolled separation that adversely impacts the reliability of the BES as identified in its Planning Assessment of the Near‐Term Transmission Planning Horizon. | 2024-04-01 |  | Medium |  |  | The Planning Coordinator or a Transmission Planner provided the instability, Cascading or uncontrolled separation information listed in Requirement R8 to the applicable Transmission Owner, and Generation Owner, but failed to provide them annually. | The Planning Coordinator or a Transmission Planner failed to provide the instability, Cascading or uncontrolled separation information listed in Requirement R8 to the applicable Transmission Owner, and Generation Owner. | [5 empty] | GO |  |  |  |  | PCPA | [7 empty] | TO |  | TP
Inactive | FAC | FAC-501-WECC-1 | R1. | Transmission Owners shall have a TMIP detailing their inspection and maintenance requirements that apply to all transmission facilities necessary for System Operating Limits associated with each of the transmission paths identified in table titled “Major WECC Transfer Paths in the Bulk Electric System." R1.1. Transmission Owners shall annually review their TMIP and update as required. | 2011-07-01 | 2018-06-30 | Medium | N/A | [21 empty] | TO
Inactive | FAC | FAC-501-WECC-1 | R2. | Transmission Owners shall include the maintenance categories in Attachment 1-FAC-501-WECC-1 when developing their TMIP. | 2011-07-01 | 2018-06-30 | Medium | [22 empty] | TO
Inactive | FAC | FAC-501-WECC-1 | R3. | Transmission Owners shall implement and follow their TMIP. | 2011-07-01 | 2018-06-30 | Medium | [22 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-501-WECC-2 | R1. | Each Transmission Owner shall have a TMIP that includes, at a minimum, each of the items listed in Attachment A, Transmission Maintenance and Inspection Plan Content. | 2018-07-01 |  | Medium | The Transmission Owner’s TMIP did not include one of the items listed in Attachment A, as required in Requirement R1. | The Transmission Owner’s TMIP did not include two of the items listed in Attachment A, as required in Requirement R1. | The Transmission Owner’s TMIP did not include three of the items listed in Attachment A, as required in Requirement R1. | The Transmission Owner’s TMIP did not include four or more of the items listed in Attachment A, as required in Requirement R1. | [18 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-501-WECC-2 | R2. | Each Transmission Owner shall annually update its TMIP to reflect all changes to its TMIP. | 2018-07-01 |  | Medium | The Transmission Owner did not annually update its TMIP (within the 365 days following the last review), as required by R2. | The Transmission Owner did not update its TMIP within the last one year and 1 day (within the 366 days following the last review), as required by R2. | The Transmission Owner did not update its TMIP within the last two years and 1 day (within the 731 days following the last review), as required by R2. | The Transmission Owner did not update its TMIP within the last three years and 1 day (within the 1095 days following the last review), as required by R2. | [18 empty] | TO
Mandatory Subject to Enforcement | FAC | FAC-501-WECC-2 | R3. | Each Transmission Owner shall adhere to its TMIP. | 2018-07-01 |  | Medium | The Transmission Owner failed to adhere to: 1) one transmission line maintenance item, or 2) one station maintenance item, as contained in its TMIP, as required in R3. | The Transmission Owner failed to adhere to: 1) two transmission line maintenance items; or , 2) two station maintenance items; or 3) any combination of two items taken from the above list, for items contained in its TMIP, as required in R3. | The Transmission Owner failed to adhere to: 1) three transmission line maintenance items; or, 2) three station maintenance items; or 3) any combination of two items taken from the above list, for items contained in its TMIP, as required in R3. | The Transmission Owner failed to adhere to: 1) four or more transmission line maintenance items; or, 2) four or more station maintenance items; or, 3) any combination of four or more items taken from the above list, for items contained in its TMIP, as required in R3. | [18 empty] | TO
Pending Inactive | FAC | FAC-501-WECC-3 | R1. | Each Transmission Owner shall have a TMIP that includes, at a minimum, each of the items listed in Attachment A, Transmission Maintenance and Inspection Plan (TMIP) Content. |  |  | Medium | The Transmission Owner’s TMIP did not include one of the items listed in Attachment A, as required in Requirement R1. | The Transmission Owner’s TMIP did not include two of the items listed in Attachment A, as required in Requirement R1. | The Transmission Owner’s TMIP did not include three of the items listed in Attachment A, as required in Requirement R1. | The Transmission Owner’s TMIP did not include four or more of the items listed in Attachment A, as required in Requirement R1. | [18 empty] | TO
Pending Inactive | FAC | FAC-501-WECC-3 | R2. | Each Transmission Owner shall annually update its TMIP to reflect all changes to its TMIP. |  |  | Medium | The Transmission Owner did not annually update its TMIP (within the 365 days following the last review), as required by R2. | The Transmission Owner did not update its TMIP within the last one year and 1 day (within the 366 days following the last review), as required by R2. | The Transmission Owner did not update its TMIP within the last two years and 1 day (within the 731 days following the last review), as required by R2. | The Transmission Owner did not update its TMIP within the last three years and 1 day (within the 1095 days following the last review), as required by R2. | [18 empty] | TO
Pending Inactive | FAC | FAC-501-WECC-3 | R3. | Each Transmission Owner shall adhere to its TMIP. |  |  | Medium | The Transmission Owner failed to adhere to: 1) one transmission line maintenance item, or 2) one station maintenance item, as contained in its TMIP, as required in R3. | The Transmission Owner failed to adhere to:1) two transmission line maintenance items; or, 2) two station maintenance items; or 3) any combination of two items taken from the above list, for items contained in its TMIP, as required in R3. | The Transmission Owner failed to adhere to:1) three transmission line maintenance items; or, 2) three station maintenance items; or 3) any combination of three items taken from the above list, for items contained in its TMIP, as required in R3. | The Transmission Owner failed to adhere to:1) four or more transmission line maintenance items; or, 2) four or more station maintenance items; or, 3) any combination of four or more items taken from the above list, for items contained in its TMIP, as required in R3. | [18 empty] | TO
| FAC | FAC-501-WECC-4 | R1. | Each Transmission Owner shall have a TMIP that includes, at a minimum, each of the items listed in Attachment A, Transmission Maintenance and Inspection Plan (TMIP) Content. |  |  | Medium | The Transmission Owner’s TMIP did not include one of the items listed in Attachment A, as required in Requirement R1. | The Transmission Owner’s TMIP did not include two of the items listed in Attachment A, as required in Requirement R1. | The Transmission Owner’s TMIP did not include three of the items listed in Attachment A, as required in Requirement R1. | The Transmission Owner’s TMIP did not include four or more of the items listed in Attachment A, as required in Requirement R1. | [18 empty] | TO
| FAC | FAC-501-WECC-4 | R2. | Each Transmission Owner shall annually update its TMIP to reflect all changes to its TMIP. |  |  | Medium | The Transmission Owner did not annually update its TMIP (within the 365 days following the last review), as required by R2. | The Transmission Owner did not update its TMIP within the last one year and 1 day (within the 366 days following the last review), as required by R2. | The Transmission Owner did not update its TMIP within the last two years and 1 day (within the 731 days following the last review), as required by R2. | The Transmission Owner did not update its TMIP within the last three years and 1 day (within the 1095 days following the last review), as required by R2. | [18 empty] | TO
| FAC | FAC-501-WECC-4 | R3. | Each Transmission Owner shall adhere to its TMIP. |  |  | Medium | The Transmission Owner failed to adhere to: 1) one transmission line maintenance item, or 2) one station maintenance item, as contained in its TMIP, as required in R3. | The Transmission Owner failed to adhere to: 1) two transmission line maintenance items; or, 2) two station maintenance items; or 3) any combination of two items taken from the above list, for items contained in its TMIP, as required in R3. | The Transmission Owner failed to adhere to: 1) three transmission line maintenance items; or, 2) three station maintenance items; or 3) any combination of three items taken from the above list, for items contained in its TMIP, as required in R3. | The Transmission Owner failed to adhere to: 1) four or more transmission line maintenance items; or, 2) four or more station maintenance items; or, 3) any combination of four or more items taken from the above list, for items contained in its TMIP, as required in R3. | [18 empty] | TO
Inactive | INT | INT-001-0 | R1. | The Load-serving Purchasing-Selling Entity shall be responsible for ensuring Tags are submitted for: |  | 2007-01-01 | [16 empty] | PSE
Inactive | INT | INT-001-0 | R2. | The Sink Balancing Authority shall be responsible for ensuring a Tag is provided: |  | 2007-01-01 | [6 empty] | BA
Inactive | INT | INT-001-0 | R3. | The Purchasing Selling Entity responsible for submitting the Tag shall submit all Tags to the Sink Balancing Authority according to timing tables in Attachment 1-INT-001-0. |  | 2007-01-01 | [6 empty] | BA | [9 empty] | PSE
Inactive | INT | INT-001-0 | R4. | The Balancing Authority or Purchasing-Selling Entity responsible for submitting the Tag shall include the reliability data listed in Attachment 2-INT-001-0 in the Tag. |  | 2007-01-01 | [6 empty] | BA | [9 empty] | PSE
Inactive | INT | INT-001-0 | R5. | Each Purchasing-Selling Entity with title to an Interchange Transaction shall have, or shall arrange to have, personnel directly and immediately available for notification of Interchange Transaction changes. These personnel shall be available from the time that the title to the Interchange Transaction is acquired until the Interchange Transaction has been completed. |  | 2007-01-01 | [16 empty] | PSE
Inactive | INT | INT-001-1 | R1. | The Load-Serving, Purchasing-Selling Entity shall ensure that Arranged Interchange is submitted to the Interchange Authority for: |  | 2006-11-01 | [16 empty] | PSE
Inactive | INT | INT-001-1 | R2. | The Sink Balancing Authority shall ensure that Arranged Interchange is submitted to the Interchange Authority: |  | 2006-11-01 | [6 empty] | BA
Inactive | INT | INT-001-2 | R1. | The Load-Serving, Purchasing-Selling Entity shall ensure that Arranged Interchange is submitted to the Interchange Authority for: | 2007-06-18 | 2008-08-26 | Low | The Load-Serving, Purchasing-Selling Entity experienced one instance of failing to ensure that Arranged Interchange was submitted to the Interchange Authority for: (see below) | The Load-Serving, Purchasing-Selling Entity experienced two instances of failing to ensure that Arranged Interchange was submitted to the Interchange Authority for: (see below) | The Load-Serving, Purchasing-Selling Entity experienced three instances of failing to ensure that Arranged Interchange was submitted to the Interchange Authority for: (see below) | The Load-Serving, Purchasing-Selling Entity experienced four instances of failing to ensure that Arranged Interchange was submitted to the Interchange Authority for: (see below) | [11 empty] | PSE
Inactive | INT | INT-001-2 | R2. | The Sink Balancing Authority shall ensure that Arranged Interchange is submitted to the Interchange Authority: | 2007-06-18 | 2008-08-26 | Low | The Sink Balancing Authority experienced one instance of failing to ensure that Arranged Interchange was submitted to the Interchange Authority (see below) | The Sink Balancing Authority experienced two instances of failing to ensure that Arranged Interchange was submitted to the Interchange Authority (see below) | The Sink Balancing Authority experienced three instances of failing to ensure that Arranged Interchange was submitted to the Interchange Authority (see below) | The Sink Balancing Authority experienced four instances of failing to ensure that Arranged Interchange was submitted to the Interchange Authority (see below) |  | BA
Inactive | INT | INT-001-3 | R1. | The Load-Serving, Purchasing-Selling Entity shall ensure that Arranged Interchange is submitted to the Interchange Authority for: | 2008-08-27 | 2014-09-30 | Low | The Load-Serving, Purchasing-Selling Entity experienced one instance of failing to ensure that Arranged Interchange was submitted to the Interchange Authority for: (see below) | The Load-Serving, Purchasing-Selling Entity experienced two instances of failing to ensure that Arranged Interchange was submitted to the Interchange Authority for: (see below) | The Load-Serving, Purchasing-Selling Entity experienced three instances of failing to ensure that Arranged Interchange was submitted to the Interchange Authority for: (see below) | The Load-Serving, Purchasing-Selling Entity experienced four instances of failing to ensure that Arranged Interchange was submitted to the Interchange Authority for: (see below) | [11 empty] | PSE
Inactive | INT | INT-001-3 | R2. | The Sink Balancing Authority shall ensure that Arranged Interchange is submitted to the Interchange Authority: | 2008-08-27 | 2014-09-30 | Low | The Sink Balancing Authority experienced one instance of failing to ensure that Arranged Interchange was submitted to the Interchange Authority (see below) | The Sink Balancing Authority experienced two instances of failing to ensure that Arranged Interchange was submitted to the Interchange Authority (see below) | The Sink Balancing Authority experienced three instances of failing to ensure that Arranged Interchange was submitted to the Interchange Authority (see below) | The Sink Balancing Authority experienced four instances of failing to ensure that Arranged Interchange was submitted to the Interchange Authority (see below) |  | BA
Inactive | INT | INT-002-0 | R1. | The Sink Balancing Authority shall ensure that all Tags and any modifications to Tags are provided via a secure network to the following entities on the Scheduling Path: |  | 2007-01-01 | [6 empty] | BA
Inactive | INT | INT-002-0 | R2. | Transmission Service Providers on the Scheduling Path shall be responsible for assessing and approving or denying the Interchange Transaction based on established reliability criteria and adequacy of Interconnected Operating Services and transmission rights as well as the reasonableness of the Interchange Transaction Tag. The Transmission Service Provider shall verify and assess: |  | 2007-01-01 | [26 empty] | TSP
Inactive | INT | INT-002-0 | R3. | Balancing Authorities on the Scheduling Path shall be responsible for assessing and approving or denying the Interchange Transaction. The Balancing Authority shall verify and assess: |  | 2007-01-01 | [6 empty] | BA
Inactive | INT | INT-002-0 | R4. | Each Balancing Authority and Transmission Service Provider on the Scheduling Path shall communicate their approval or denial of the Interchange Transaction to the Sink Balancing Authority. |  | 2007-01-01 | [6 empty] | BA | [19 empty] | TSP
Inactive | INT | INT-002-0 | R5. | Upon receipt of approvals or denials from all of the individual Balancing Authorities and Transmission Service Providers, the Sink Balancing Authority shall communicate the composite approval status of the Interchange Transaction to the Purchasing-Selling Entity and all other Balancing Authorities and Transmission Service Providers on the Scheduling Path and through the Reliability analysis service to affected Transmission Operators and Reliability Coordinators. |  | 2007-01-01 | [6 empty] | BA
Inactive | INT | INT-003-0 | R1. | Each Receiving Balancing Authority shall confirm Interchange Schedules with the Sending Balancing Authority prior to implementation in the Balancing Authority’s ACE equation. |  | 2007-01-01 | [6 empty] | BA
Inactive | INT | INT-003-0 | R2. | Balancing Authorities shall implement Interchange Schedules only with Adjacent Balancing Authorities. |  | 2007-01-01 | [6 empty] | BA
Inactive | INT | INT-003-0 | R3. | Balancing Authorities shall begin and end Interchange Schedules at a time agreed to by the Source Balancing Authority, Sink Balancing Authority, and Intermediate Balancing Authorities. |  | 2007-01-01 | [6 empty] | BA
Inactive | INT | INT-003-0 | R4. | The Sink Balancing Authority shall be responsible for initiating implementation of each Interchange Transaction as tagged. Upon receiving composite approval from the Sink Balancing Authority, each Balancing Authority on the scheduling path shall enter confirmed Schedules into its Automatic Generation Control ACE equation. |  | 2007-01-01 | [6 empty] | BA
Inactive | INT | INT-003-0 | R5. | Balancing Authorities shall operate such that Interchange Schedules do not knowingly cause any other systems to violate established operating criteria. |  | 2007-01-01 | [6 empty] | BA
Inactive | INT | INT-003-0 | R6. | Balancing Authorities shall operate such that the maximum Net Interchange Schedule between any two Balancing Authorities does not exceed the lesser of: |  | 2007-01-01 | [6 empty] | BA
Inactive | INT | INT-003-1 | R1. | Each Receiving Balancing Authority shall confirm Interchange Schedules with the Sending Balancing Authority prior to implementation in the Balancing Authority’s ACE equation. |  | 2007-01-01 | [6 empty] | BA
Inactive | INT | INT-003-2 | R1. | Each Receiving Balancing Authority shall confirm Interchange Schedules with the Sending Balancing Authority prior to implementation in the Balancing Authority’s ACE equation. | 2007-06-18 | 2011-03-31 | Medium | There shall be a separate Lower VSL, if either of the following conditions exists: One instance of entering a schedule into its ACE equation without confirming the schedule as specified in R1, R1.1, R1.1.1 and R1.1.2. One instance of not coordinating the | There shall be a separate Moderate VSL, if either of the following conditions exists: Two instances of entering a schedule into its ACE equation without confirming the schedule as specified in R1, R1.1, R1.1.1 and R1.1.2. Two instances of not coordinating | There shall be a separate High VSL, if either of the following conditions exists: Three instances of entering a schedule into its ACE equation without confirming the schedule as specified in R1, R1.1, R1.1.1 and R1.1.2. Three instances of not coordinating | There shall be a separate Severe VSL, if either of the following conditions exists: Four or more instances of entering a schedule into its ACE equation without confirming the schedule as specified in R1, R1.1, R1.1.1 and R1.1.2. Four or more instances of |  | BA
Inactive | INT | INT-003-3 | R1. | Each Receiving Balancing Authority shall confirm Interchange Schedules with the Sending Balancing Authority prior to implementation in the Balancing Authority’s ACE equation. | 2011-04-01 | 2014-09-30 | Medium | There shall be a separate Lower VSL, if either of the following conditions exists: One instance of entering a schedule into its ACE equation without confirming the schedule as specified in R1, R1.1, R1.1.1 and R1.1.2. One instance of not coordinating the | There shall be a separate Moderate VSL, if either of the following conditions exists: Two instances of entering a schedule into its ACE equation without confirming the schedule as specified in R1, R1.1, R1.1.1 and R1.1.2. Two instances of not coordinating | There shall be a separate High VSL, if either of the following conditions exists: Three instances of entering a schedule into its ACE equation without confirming the schedule as specified in R1, R1.1, R1.1.1 and R1.1.2. Three instances of not coordinating | There shall be a separate Severe VSL, if either of the following conditions exists: Four or more instances of entering a schedule into its ACE equation without confirming the schedule as specified in R1, R1.1, R1.1.1 and R1.1.2. Four or more instances of |  | BA
Inactive | INT | INT-004-0 | R1. | If a Reliability Coordinator, Transmission Operator, or Source or Sink Balancing Authority, due to a reliability event, needs to modify an Interchange Transaction that is in progress or scheduled to be started, the entity shall, within 60 minutes of the start of the emergency Transaction, modify the Interchange Transaction tag, and shall communicate the modification to the Sink Balancing Authority. Reliability events may include: |  | 2007-01-01 | [6 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | INT | INT-004-0 | R2. | A Generator Operator or Load Serving Entity may request the Host Balancing Authority to modify an Interchange Transaction due to loss of generation or Load. |  | 2007-01-01 | [6 empty] | BA
Inactive | INT | INT-004-0 | R3. | Upon receipt of modification to an Interchange Transaction as described in Requirement R1, the Sink Balancing Authority (Source Balancing Authority in the case of a loss of generation) shall communicate the modified information about the Interchange Transaction, including its composite approval status, to all Balancing Authorities and Transmission Service Providers on the Transaction path and the Purchasing-Selling Entity responsible for the Transaction. |  | 2007-01-01 | [6 empty] | BA
Inactive | INT | INT-004-0 | R4. | At such time as the reliability event allows for the reloading of the transaction, the entity that initiated the curtailment shall release the limit on the Interchange Transaction tag to allow reloading the transaction and shall communicate the release of the limit to the Sink Balancing Authority. |  | 2007-01-01 | [6 empty] | BA
Inactive | INT | INT-004-0 | R5. | The Purchasing-Selling Entity responsible for tagging a Dynamic Interchange Schedule shall ensure the tag is updated for the next available scheduling hour and future hours when any one of the following occur: |  | 2007-01-01 | [16 empty] | PSE
Inactive | INT | INT-004-1 | R1. | At such time as the reliability event allows for the reloading of the transaction, the entity that initiated the curtailment shall release the limit on the Interchange Transaction tag to allow reloading the transaction and shall communicate the release of the limit to the Sink Balancing Authority. | 2007-06-18 | 2008-08-26 | Low | The entity that initiated the curtailment failed to communicate the transaction reload to the Sink Balancing Authority | The entity that initiated the curtailment failed to reload the transaction and failed to communicate to the Sink Balancing Authority | N/A | N/A |  | BA
Inactive | INT | INT-004-1 | R2. | The Purchasing-Selling Entity responsible for tagging a Dynamic Interchange Schedule shall ensure the tag is updated for the next available scheduling hour and future hours when any one of the following occurs: | 2007-06-18 | 2008-08-26 | Low | The Purchase-Selling entity failed to update the tags when required less than 25% of times it was required, as determined in R2.1, R2.2, or R2.3. | The Purchase-Selling entity failed to update the tags when required 25% or more and less than 50% of the times it was required, as determined in R2.1, R2.2, or R2.3. | The Purchase-Selling entity failed to update the tags when required 50% or more but less than75% of the times it was required, as determined in R2.1, R2.2, or R2.3. | The Purchase-Selling entity failed to update the tags when required 75% or more of the times it was required, as determined in R2.1, R2.2, or R2.3. | [11 empty] | PSE
Inactive | INT | INT-004-2 | R1. | At such time as the reliability event allows for the reloading of the transaction, the entity that initiated the curtailment shall release the limit on the Interchange Transaction tag to allow reloading the transaction and shall communicate the release of the limit to the Sink Balancing Authority. | 2008-08-27 | 2014-09-30 | Low | The entity that initiated the curtailment failed to communicate the transaction reload to the Sink Balancing Authority | The entity that initiated the curtailment failed to reload the transaction and failed to communicate to the Sink Balancing Authority |  |  |  | BA | [9 empty] | PSE | RC | [6 empty] | TOP
Inactive | INT | INT-004-2 | R2. | The Purchasing-Selling Entity responsible for tagging a Dynamic Interchange Schedule shall ensure the tag is updated for the next available scheduling hour and future hours when any one of the following occurs: | 2008-08-27 | 2014-09-30 | Low | The Purchase-Selling entity failed to update the tags when required less than 25% of times it was required, as determined in R2.1, R2.2, or R2.3. | The Purchase-Selling entity failed to update the tags when required 25% or more and less than 50% of the times it was required, as determined in R2.1, R2.2, or R2.3. | The Purchase-Selling entity failed to update the tags when required 50% or more but less than75% of the times it was required, as determined in R2.1, R2.2, or R2.3. | The Purchase-Selling entity failed to update the tags when required 75% or more of the times it was required, as determined in R2.1, R2.2, or R2.3. | [11 empty] | PSE
Inactive | INT | INT-004-3 | R1. | Each Purchasing-Selling Entity that secures energy to serve Load via a Dynamic Schedule or Pseudo-Tie shall ensure that a Request for Interchange is submitted as an on-time1 Arranged Interchange to the Sink Balancing Authority for that Dynamic Schedule or Pseudo-Tie, unless the information about the Pseudo-Tie is included in congestion management procedure(s) via an alternate method. | 2014-10-01 | 2014-11-25 | Low | N/A | N/A | N/A | The Purchasing-Selling Entity secured energy to serve Load via a Dynamic Schedule or Pseudo-Tie, but did not ensure that a Request for Interchange was submitted as on-time Arranged Interchange to the Sink Balancing Authority, and did not include information about the Pseudo-Tie in congestion management procedure(s) via an alternate method. | [11 empty] | PSE
Inactive | INT | INT-004-3 | R2. | The Purchasing-Selling Entity that submits a Request for Interchange in accordance with Requirement R1 shall ensure the Confirmed Interchange associated with that Dynamic Schedule or Pseudo-Tie is updated for future hours in order to support congestion management procedures if any one of the following occurs: [Please see the standard for more information] | 2014-10-01 | 2014-11-25 | Low | N/A | N/A | N/A | A deviation met or exceeded the criteria in Requirement R2 Parts 2.1- 2.3 and was expected to persist, but the Purchasing-Selling Entity did not ensure that the Confirmed Interchange associated with that Dynamic Schedule or Pseudo-Tie was updated for future hours. | [11 empty] | PSE
Inactive | INT | INT-004-3 | R3. | Each Balancing Authority shall only implement or operate a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication in order to support congestion management procedures. | 2014-10-01 | 2014-11-25 | Low | N/A | N/A | N/A | The Balancing Authority implemented or operated a Pseudo-Tie that was not included in the NAESB Electric Industry Registry publication. |  | BA
Inactive | INT | INT-004-3.1 | R1. | Each Purchasing-Selling Entity that secures energy to serve Load via a Dynamic Schedule or Pseudo-Tie shall ensure that a Request for Interchange is submitted as an on-time Arranged Interchange to the Sink Balancing Authority for that Dynamic Schedule or Pseudo-Tie, unless the information about the Pseudo-Tie is included in congestion management procedure(s) via an alternate method. | 2014-11-26 | 2020-12-14 | Low | N/A | N/A | N/A | The Purchasing-Selling Entity secured energy to serve Load via a Dynamic Schedule or Pseudo-Tie, but did not ensure that a Request for Interchange was submitted as on-time Arranged Interchange to the Sink Balancing Authority, and did not include information about the Pseudo-Tie in congestion management procedure(s) via an alternate method. | [11 empty] | PSE
Inactive | INT | INT-004-3.1 | R2. | The Purchasing-Selling Entity that submits a Request for Interchange in accordance with Requirement R1 shall ensure the Confirmed Interchange associated with that Dynamic Schedule or Pseudo-Tie is updated for future hours in order to support congestion management procedures if any one of the following occurs: [See standard for additional information.] | 2014-11-26 | 2020-12-14 | Low | N/A | N/A | N/A | A deviation met or exceeded the criteria in Requirement R2 Parts 2.1- 2.3 and was expected to persist, but the Purchasing-Selling Entity did not ensure that the Confirmed Interchange associated with that Dynamic Schedule or Pseudo-Tie was updated for future hours. | [11 empty] | PSE
Inactive | INT | INT-004-3.1 | R3. | Each Balancing Authority shall only implement or operate a Pseudo-Tie that is included in the NAESB Electric Industry Registry publication in order to support congestion management procedures. | 2014-11-26 | 2020-12-14 | Low | N/A | N/A | N/A | The Balancing Authority implemented or operated a Pseudo-Tie that was not included in the NAESB Electric Industry Registry publication. |  | BA
Inactive | INT | INT-005-1 | R1. | Prior to the expiration of the time period defined in the Timing Table, Column A, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment to all reliability entities involved in the Interchange. | 2007-06-18 | 2008-08-26 | Medium | The Interchange Authority experienced one occurrence of not distributing information to all involved reliability entities. | The Interchange Authority experienced two occurrences of not distributing information to all involved reliability entities | The Interchange Authority experienced three occurrences of not distributing information to all involved reliability entities | The Interchange Authority experienced four occurrences of not distributing information to all involved reliability entities | [7 empty] | IA
Inactive | INT | INT-005-2 | R1. | Prior to the expiration of the time period defined in the Timing Table, Column A, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment to all reliability entities involved in the Interchange. | 2008-08-27 | 2010-06-30 | Medium | The Interchange Authority experienced one occurrence of not distributing information to all involved reliability entities. | The Interchange Authority experienced two occurrences of not distributing information to all involved reliability entities | The Interchange Authority experienced three occurrences of not distributing information to all involved reliability entities | The Interchange Authority experienced four occurrences of not distributing information to all involved reliability entities | [7 empty] | IA
Inactive | INT | INT-005-3 | R1. | Prior to the expiration of the time period defined in the timing requirements tables in this standard, Column A, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment to all reliability entities involved in the Interchange. | 2010-07-01 | 2014-09-30 | Medium | [11 empty] | IA
Inactive | INT | INT-006-1 | R1. | Prior to the expiration of the reliability assessment period defined in the Timing Table, Column B, the Balancing Authority and Transmission Service Provider shall respond to a request from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange. | 2007-06-18 | 2008-08-26 | Low | The Responsible Entity failed on one occasion to respond to a request from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange. | The Responsible Entity failed on two occasions to respond to a request from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange. | The Responsible Entity failed on three occasions to respond to a request from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange. | The Responsible Entity failed on four occasions to respond to a request from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange. |  | BA | [19 empty] | TSP
Inactive | INT | INT-006-2 | R1. | Prior to the expiration of the reliability assessment period defined in the Timing Table, Column B, the Balancing Authority and Transmission Service Provider shall respond to a request from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange. | 2008-08-27 | 2010-06-30 | Low | The Responsible Entity failed on one occasion to respond to a request from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange. | The Responsible Entity failed on two occasions to respond to a request from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange. | The Responsible Entity failed on three occasions to respond to a request from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange. | The Responsible Entity failed on four occasions to respond to a request from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange. |  | BA | [19 empty] | TSP
Inactive | INT | INT-006-3 | R1. | Prior to the expiration of the reliability assessment period defined in the timing requirements tables in this standard, Column B, the Balancing Authority and Transmission Service Provider shall respond to each On-time Request for Interchange (RFI), and to each Emergency RFI and Reliability Adjustment RFI from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange. | 2010-07-01 | 2014-09-30 | Low | [5 empty] | BA | [19 empty] | TSP
Inactive | INT | INT-006-4 | R1. | Each Balancing Authority shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. [Please see the standard for more information] | 2014-10-01 | 2021-03-31 | Low | N/A | N/A | N/A | The Balancing Authority receiving an on-time Arranged Interchange or an emergency Arranged Interchange did not approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B. OR The Source or Sink Balancing Authority did not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout duration of the Arranged Interchange and did not deny the Arranged Interchange or curtail Confirmed Interchange. OR The Scheduling Path between the Balancing Authority and its Adjacent Balancing Authorities was invalid, and the Balancing Authority did not deny the Arranged Interchange or curtail Confirmed Interchange. |  | BA
Inactive | INT | INT-006-4 | R2. | Each Transmission Service Provider shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. [Please see the standard for more information] | 2014-10-01 | 2021-03-31 | Low | N/A | N/A | N/A | The Transmission Service Provider receiving an on-time Arranged Interchange or an emergency Arranged Interchange did not approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B OR The transmission path between the Transmission Service Provider and its adjacent Transmission Service Providers was invalid, and the Transmission Service Provider did not deny the Arranged Interchange or curtail Confirmed Interchange. | [21 empty] | TSP
Inactive | INT | INT-006-4 | R3. | The Source Balancing Authority and the Sink Balancing Authority receiving a Reliability Adjustment Arranged Interchange shall approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B. [Please see the standard for more information] | 2014-10-01 | 2021-03-31 | Low |  |  | The Source Balancing Authority or Sink Balancing Authority receiving a Reliability Adjustment Arranged Interchange denied it prior to the expiration of the time period defined in Attachment 1, Column B, but did not communicate that fact to its Reliability Coordinator within 10 minutes of the denial. | The Source Balancing Authority or Sink Balancing Authority receiving a Reliability Adjustment Arranged Interchange did not approve or deny it prior to the expiration of the time period definded in Attahment 1, Column B. |  | BA
Inactive | INT | INT-006-4 | R4. | Each Sink Balancing Authority shall confirm that none of the following conditions exist prior to transitioning an Arranged Interchange to Confirmed Interchange: • It is a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B has elapsed, and the Source Balancing Authority or the Sink Balancing Authority associated with the Arranged Interchange has not communicated its approval of the transition. • It is not a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B, has elapsed, and not all Balancing Authorities and Transmission Service Providers associated with the Arranged Interchange have communicated their approval of the transition. • It is not a Reliability Adjustment Arranged Interchange, the time period specified in Attachment 1, Column B, has elapsed, and any entity associated with the Arranged Interchange has communicated its denial of the transition. | 2014-10-01 | 2021-03-31 | Low | N/A | N/A | N/A | The Sink Balacing Authority failed to cnfirm that none of the conditions in Requirement 4 existed before transitioning an Arranged Interchange to Confirmed Interchange. |  | BA
Inactive | INT | INT-006-4 | R5. | For each Arranged Interchange that is transitioned to Confirmed Interchange, the Sink Balancing Authority shall notify the following entities of the on-time Confirmed Interchange such that the notification is delivered in time to be incorporated into scheduling systems prior to ramp start as specified in Attachment 1, Column D: [Please see the standard for more information] | 2014-10-01 | 2021-03-31 | Low |  |  | The Sink Balancing Authority did not notify any of the entities listed in Requirement R5 Parts 5.1-5.5 of the on-time Confirmed Interchange. | The Sink Balancing Authority did not notify any of the entities listed in Requiremnet R5 Parts 5.1-5.5 of the on-time Confirmed Interchange. OR The Sink Balancing Authority notified the entities listed in Requirement R5 Parts 5.1-5.5 of the one-time Confirmed Interchange, but did not notify one or more of the entities in time for the notifiacion to be incorporated into scheduling systems prior to ramp start as specified in Attachment 1, Column D. |  | BA
Mandatory Subject to Enforcement | INT | INT-006-5 | R1. | Each Balancing Authority shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. | 2021-04-01 |  | Low | N/A | N/A | N/A | The Balancing Authority receiving an on-time Arranged Interchange or an emergency Arranged Interchange did not approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B. OR The Source or Sink Balancing Authority did not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout duration of the Arranged Interchange and did not deny the Arranged Interchange or curtail Confirmed Interchange. OR The Scheduling Path between the Balancing Authority and its Adjacent Balancing Authorities was invalid, and the Balancing Authority did not deny the Arranged Interchange or curtail Confirmed Interchange.. |  | BA
Mandatory Subject to Enforcement | INT | INT-006-5 | R2. | Each Transmission Service Provider shall approve or deny each on-time Arranged Interchange or emergency Arranged Interchange that it receives and shall do so prior to the expiration of the time period defined in Attachment 1, Column B. | 2021-04-01 |  | Low | N/A | N/A | N/A | The Transmission Service Provider receiving an on-time Arranged Interchange or an emergency Arranged Interchange did not approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B. OR The transmission path between the Transmission Service Provider and its adjacent Transmission Service Providers was invalid, and the Transmission Service Provider did not deny the Arranged Interchange or curtail Confirmed Interchange. | [21 empty] | TSP
Mandatory Subject to Enforcement | INT | INT-006-5 | R3. | The Source Balancing Authority and the Sink Balancing Authority receiving a Reliability Adjustment Arranged Interchange shall approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B. | 2021-04-01 |  | Low | N/A | N/A | The Source Balancing Authority or Sink Balancing Authority receiving a Reliability Adjustment Arranged Interchange denied it prior to the expiration of the time period defined in Attachment 1, Column B. | The Source Balancing Authority or Sink Balancing Authority receiving a Reliability Adjustment Arranged Interchange did not approve or deny it prior to the expiration of the time period defined in Attachment 1, Column B. |  | BA
Mandatory Subject to Enforcement | INT | INT-006-5 | R4. | Reserved. | 2021-04-01
Mandatory Subject to Enforcement | INT | INT-006-5 | R5. | Reserved. | 2021-04-01
Inactive | INT | INT-007-1 | R1. | The Interchange Authority shall verify that Arranged Interchange is balanced and valid prior to transitioning Arranged Interchange to Confirmed Interchange by verifying the following: | 2007-06-18 | 2014-09-30 | Low | The Interchange Authority failed to verify one time, as indicated in R1.1, R1.2, R1.3, R1.3.1, R1.3.2, R1.3.3, or R1.3.4 that Arranged Interchange was balanced and valid prior to transitioning Arranged Interchange to Confirmed Interchange. | The Interchange Authority failed to verify two times, as indicated in R1.1, R1.2, R1.3, R1.3.1, R1.3.2, R1.3.3, or R1.3.4 that Arranged Interchange was balanced and valid prior to transitioning Arranged Interchange to Confirmed Interchange. | The Interchange Authority failed to verify three times, as indicated in R1.1, R1.2, R1.3, R1.3.1, R1.3.2, R1.3.3, or R1.3.4 that Arranged Interchange was balanced and valid prior to transitioning Arranged Interchange to Confirmed Interchange. | The Interchange Authority failed to verify four times, as indicated in R1.1, R1.2, R1.3, R1.3.1, R1.3.2, R1.3.3, or R1.3.4 that Arranged Interchange was balanced and valid prior to transitioning Arranged Interchange to Confirmed Interchange. | [7 empty] | IA
Inactive | INT | INT-008-1 | R1. | Prior to the expiration of the time period defined in the Timing Table, Column C, the Interchange Authority shall distribute to all Balancing Authorities (including Balancing Authorities on both sides of a direct current tie), Transmission Service Providers and Purchasing-Selling Entities involved in the Arranged Interchange whether or not the Arranged Interchange has transitioned to a Confirmed Interchange. | 2007-06-18 | 2008-08-26 | Low | The Interchange Authority experienced one occurrence of not distributing information to all involved reliability entities as deliniated in R1.1, R1.1.1 or R1.1.2. | The Interchange Authority experienced two occurrences of not distributing information to all involved reliability entities. | The Interchange Authority experienced three occurrences of not distributing information to all involved reliability entities. | The Interchange Authority experienced four occurrences of not distributing information to all involved reliability entities or no evidence provided. | [7 empty] | IA
Inactive | INT | INT-008-2 | R1. | Prior to the expiration of the time period defined in the Timing Table, Column C, the Interchange Authority shall distribute to all Balancing Authorities (including Balancing Authorities on both sides of a direct current tie), Transmission Service Providers and Purchasing-Selling Entities involved in the Arranged Interchange whether or not the Arranged Interchange has transitioned to a Confirmed Interchange. | 2008-08-27 | 2010-06-30 | Low | The Interchange Authority experienced one occurrence of not distributing information to all involved reliability entities as deliniated in R1.1, R1.1.1 or R1.1.2. | The Interchange Authority experienced two occurrences of not distributing information to all involved reliability entities. | The Interchange Authority experienced three occurrences of not distributing information to all involved reliability entities. | The Interchange Authority experienced four occurrences of not distributing information to all involved reliability entities or no evidence provided. | [7 empty] | IA
Inactive | INT | INT-008-3 | R1. | Prior to the expiration of the time period defined in the Timing Table, Column C, the Interchange Authority shall distribute to all Balancing Authorities (including Balancing Authorities on both sides of a direct current tie), Transmission Service Providers and Purchasing-Selling Entities involved in the Arranged Interchange whether or not the Arranged Interchange has transitioned to a Confirmed Interchange. | 2010-07-01 | 2014-09-30 | Low | [11 empty] | IA
Inactive | INT | INT-009-1 | R1. | The Balancing Authority shall implement Confirmed Interchange as received from the Interchange Authority. | 2007-06-18 | 2014-09-30 | Medium | The Balancing Authority experienced one occurrence of not implementing a Confirmed Interchange as received from the Interchange Authority. | The Balancing Authority experienced two occurrences of not implementing a Confirmed Interchange as received from the Interchange Authority. | The Balancing Authority experienced three occurrences of not implementing a Confirmed Interchange as received from the Interchange Authority. | The Balancing Authority experienced four occurrences of not implementing a Confirmed Interchange as received from the Interchange Authority. |  | BA
Inactive | INT | INT-009-2 | R1. | Each Balancing Authority shall agree with each of its Adjacent Balancing Authorities that its Composite Confirmed Interchange with that Adjacent Balancing Authority, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange per INT-010-2 not yet captured in the Composite Confirmed Interchange, is: [Please see the standard for more information] | 2014-10-01 | 2014-11-25 | Medium | [5 empty] | BA
Inactive | INT | INT-009-2 | R2. | The Attaining Balancing Authority and the Native Balancing Authority shall use a dynamic value emanating from an agreed upon common source to account for the Pseudo-Tie in the Actual Net Interchange (NIA) term of their respective control ACE (or alternate control process). | 2014-10-01 | 2014-11-25 | Medium | [5 empty] | BA
Inactive | INT | INT-009-2 | R3. | Each Balancing Authority in whose area the high-voltage direct current tie is controlled shall coordinate the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. | 2014-10-01 | 2014-11-25 | Medium | [5 empty] | BA
Inactive | INT | INT-009-2.1 | R1. | Each Balancing Authority shall agree with each of its Adjacent Balancing Authorities that its Composite Confirmed Interchange with that Adjacent Balancing Authority, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange per INT-010-2 not yet captured in the Composite Confirmed Interchange, is: | 2014-11-26 | 2021-03-31 | Medium | N/A | N/A | N/A | The Balancing Authority did not reach agreement with an Adjacent Balancing Authority on the magnitude or sign of its Composite Confirmed Interchange, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange per INT-010-2 not yet captured in the Composite Confirmed Interchange. |  | BA
Inactive | INT | INT-009-2.1 | R2. | The Attaining Balancing Authority and the Native Balancing Authority shall use a dynamic value emanating from an agreed upon common source to account for the Pseudo-Tie in the Actual Net Interchange (NIA) term of their respective control ACE (or alternate control process). | 2014-11-26 | 2021-03-31 | Medium | N/A | N/A | N/A | The Balancing Authority failed to use a dynamic value emanating from an agreed upon common source to account for the Pseudo-Tie in the Actual Net Interchange (NIA) term of their respective control ACE (or alternate control process). |  | BA
Inactive | INT | INT-009-2.1 | R3. | Each Balancing Authority in whose area the high-voltage direct current tie is controlled shall coordinate the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. | 2014-11-26 | 2021-03-31 | Medium | N/A | N/A | N/A | The Balancing Authority failed to coordinate the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. |  | BA
Mandatory Subject to Enforcement | INT | INT-009-3 | R1. | Each Balancing Authority shall agree with each of its Adjacent Balancing Authorities that its Composite Confirmed Interchange with that Adjacent Balancing Authority, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange not yet captured in the Composite Confirmed Interchange, is: | 2021-04-01 |  | Medium | N/A | N/A | N/A | The Balancing Authority did not reach agreement with an Adjacent Balancing Authority on the magnitude or sign of its Composite Confirmed Interchange, at mutually agreed upon time intervals, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange not yet captured in the Composite Confirmed Interchange. |  | BA
Mandatory Subject to Enforcement | INT | INT-009-3 | R2. | Reserved. | 2021-04-01
Mandatory Subject to Enforcement | INT | INT-009-3 | R3. | Each Balancing Authority in whose area the high-voltage direct current tie is controlled shall coordinate the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. | 2021-04-01 |  | Medium | N/A | N/A | N/A | The Balancing Authority failed to coordinate the Confirmed Interchange prior to its implementation with the Transmission Operator of the high-voltage direct current tie. |  | BA
Inactive | INT | INT-010-1 | R1. | The Balancing Authority that experiences a loss of resources covered by an energy sharing agreement shall ensure that a request for an Arranged Interchange is submitted with a start time no more than 60 minutes beyond the resource loss. If the use of the energy sharing agreement does not exceed 60 minutes from the time of the resource loss, no request for Arranged Interchange is required. | 2007-06-18 | 2014-09-30 | Low | The Balancing Authority that experienced a loss of resource covered by an energy sharing agreement failed one time to submit a request for an Arranged Interchange within the specified time period. | The Balancing Authority that experienced a loss of resource covered by an energy sharing agreement failed two times to submit request for an Arranged Interchange within the specified time period. | The Balancing Authority that experienced a loss of resource covered by an energy sharing agreement failed three times to submit a request for an Arranged Interchange within the specified time period. | The Balancing Authority that experienced a loss of resource covered by an energy sharing agreement failed four or more times to submit a request for an Arranged Interchange within the specified time period. |  | BA
Inactive | INT | INT-010-1 | R2. | For a modification to an existing Interchange schedule that is directed by a Reliability Coordinator for current or imminent reliability-related reasons, the Reliability Coordinator shall direct a Balancing Authority to submit the modified Arranged Interchange reflecting that modification within 60 minutes of the initiation of the event. | 2007-06-18 | 2014-09-30 | Low | The Reliability Coordinator failed one time to direct the submittal of a new or modified Arranged Interchange; or the Balancing Authority failed one time to submit the modified schedule as directed. | The Reliability Coordinator failed two times to direct the submittal of a new or modified Arranged Interchange; or the Balancing Authority failed two times to submit the modified schedule as directed. | The Reliability Coordinator failed three times to direct the submittal of a new or modified Arranged Interchange; or the Balancing Authority failed three times to submit the modified schedule as directed. | The Reliability Coordinator failed four times to direct the submittal of a new or modified Arranged Interchange; or the Balancing Authority failed four times to submit the modified schedule as directed. | [12 empty] | RC
Inactive | INT | INT-010-1 | R3. | For a new Interchange schedule that is directed by a Reliability Coordinator for current or imminent reliability-related reasons, the Reliability Coordinator shall direct a Balancing Authority to submit an Arranged Interchange reflecting that Interchange schedule within 60 minutes of the initiation of the event. | 2007-06-18 | 2014-09-30 | Low | The Reliability Coordinator failed one time to direct the submittal of a new or modified Arranged Interchange; or the Balancing Authority failed one time to submit a schedule as directed. | The Reliability Coordinator failed two times to direct the submittal of a new or modified Arranged Interchange ; or the Balancing Authority failed two times to submit a schedule as directed. | The Reliability Coordinator failed three times to direct the submittal of a new or modified Arranged Interchange ; or the Balancing Authority failed three times to submit a schedule as directed. | The Reliability Coordinator failed four times to direct the submittal of a new or modified Arranged Interchange; or the Balancing Authority failed four times or more to submit a schedule as directed. | [12 empty] | RC
Inactive | INT | INT-010-2 | R1. | The Balancing Authority that experiences a loss of resources covered by an energy sharing agreement or other reliability needs covered by an energy sharing agreement shall ensure that a Request for Interchange (RFI) is submitted with a start time no more than 60 minutes beyond the resource loss. If the use of the energy sharing agreement does not exceed 60 minutes from the time of the resource loss, no RFI is required. | 2014-10-01 | 2014-11-25 | Low | [5 empty] | BA
Inactive | INT | INT-010-2 | R2. | Each Sink Balancing Authority shall ensure that a Reliability Adjustment Arranged Interchange reflecting a modification is submitted within 60 minutes of the start of the modification if a Reliability Coordinator directs the modification of a Confirmed Interchange or Implemented Interchange for actual or anticipated reliability-related reasons. | 2014-10-01 | 2014-11-25 | Low | [5 empty] | BA
Inactive | INT | INT-010-2 | R3. | Each Sink Balancing Authority shall ensure that a Request for Interchange is submitted reflecting that Interchange Schedule within 60 minutes of the start of the scheduled Interchange if a Reliability Coordinator directs the scheduling of Interchange for actual or anticipated reliability-related reasons. | 2014-10-01 | 2014-11-25 | Low | [5 empty] | BA
Inactive | INT | INT-010-2.1 | R1. | The Balancing Authority that experiences a loss of resources covered by an energy sharing agreement or other reliability needs covered by an energy sharing agreement shall ensure that a Request for Interchange (RFI) is submitted with a start time no more than 60 minutes beyond the resource loss. If the use of the energy sharing agreement does not exceed 60 minutes from the time of the resource loss, no RFI is required. | 2014-11-26 | 2020-12-14 | Low | The Balancing Authority that experienced a loss of resources covered by an energy sharing agreement or other reliability needs covered by an energy sharing agreement ensured that a Request for Interchange was submitted, and it was submitted with a start time more than 60 minutes, but not more than 75 minutes, following the resource loss when the use of the energy sharing agreement exceeded 60 minutes. | The Balancing Authority that experienced a loss of resources covered by an energy sharing agreement or other reliability needs covered by an energy sharing agreement ensured that a Request for Interchange was submitted, and it was submitted with a start time more than 75 minutes, but not more than 90 minutes, following the resource loss when the use of the energy sharing agreement exceeded 60 minutes. | The Balancing Authority that experienced a loss of resources covered by an energy sharing agreement or other reliability needs covered by an energy sharing agreement ensured that a Request for Interchange was submitted, and it was submitted with a start time more than 90 minutes, but not more than 120 minutes, following the resource loss when the use of the energy sharing agreement exceeded 60 minutes. | The Balancing Authority that experienced a loss of resources covered by an energy sharing agreement or other reliability needs covered by an energy sharing agreement ensured that a Request for Interchange was submitted, and it was submitted with a start time more than 120 minutes following the resource loss when the use of the energy sharing agreement exceeded 60 minutes. OR The Balancing Authority that experienced a loss of resources covered by an energy sharing agreement or other reliability needs covered by an energy sharing agreement did not ensure that a Request for Interchange was submitted following the resource loss when the use of the energy sharing agreement exceeded 60 minutes. |  | BA
Inactive | INT | INT-010-2.1 | R2. | Each Sink Balancing Authority shall ensure that a Reliability Adjustment Arranged Interchange reflecting a modification is submitted within 60 minutes of the start of the modification if a Reliability Coordinator directs the modification of a Confirmed Interchange or Implemented Interchange for actual or anticipated reliability-related reasons. | 2014-11-26 | 2020-12-14 | Low | N/A | N/A | N/A | The Sink Balancing Authority did not ensure that a Reliability Adjustment Arranged Interchange reflecting a modification was submitted within 60 minutes following the start of that modification. |  | BA
Inactive | INT | INT-010-2.1 | R3. | Each Sink Balancing Authority shall ensure that a Request for Interchange is submitted reflecting that Interchange Schedule within 60 minutes of the start of the scheduled Interchange if a Reliability Coordinator directs the scheduling of Interchange for actual or anticipated reliability-related reasons. | 2014-11-26 | 2020-12-14 | Low | N/A | N/A | N/A | The Sink Balancing Authority did not ensure that a Request for Interchange reflecting the Interchange Schedule was submitted within 60 minutes following the start of that scheduled Interchange. |  | BA
Inactive | INT | INT-011-1 | R1. | Each Load-Serving Entity that uses Point to Point Transmission Service for intra-Balancing Authority Area transfers shall submit a Request for Interchange unless the information about intra-Balancing Authority transfers is included in congestion management procedure(s) via an alternate method. | 2014-10-01 | 2014-11-25 | Low | [12 empty] | LSE
Inactive | INT | INT-011-1.1 | R1. | Each Load-Serving Entity that uses Point to Point Transmission Service for intra-Balancing Authority Area transfers shall submit a Request for Interchange unless the information about intra-Balancing Authority transfers is included in congestion management procedure(s) via an alternate method. | 2014-11-26 | 2015-10-15 | Low | N/A | N/A | N/A | The Load-Serving Entity used Point to Point Transmission Service for an intra-Balancing Authority Area transfer, and did not submit a Request for Interchange for an intra-Balancing Authority transfer that is not included in congestion management procedure(s) via an alternate method. | [8 empty] | LSE
Inactive | IRO | IRO-001-0 | R1. | Each Regional Reliability Organization, subregion, or interregional coordinating group shall establish one or more Reliability Coordinators to continuously assess transmission reliability and coordinate emergency operations among the operating entities within the region and across the regional boundaries. |  | 2007-01-01 | [20 empty] | RRO
Inactive | IRO | IRO-001-0 | R2. | The Reliability Coordinator shall comply with a regional reliability plan approved by the NERC Operating Committee. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-001-0 | R3. | The Reliability Coordinator shall have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordinator Area to preserve the integrity and reliability of the Bulk Electric System. These actions shall be taken without delay, but no longer than 30 minutes. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-001-0 | R4. | Reliability Coordinators that delegate tasks to other entities shall have formal operating agreements with each entity to which tasks are delegated. The Reliability Coordinator shall verify that all delegated tasks are understood, communicated, and addressed within its Reliability Coordinator Area. All responsibilities for complying with NERC and regional standards applicable to Reliability Coordinators shall remain with the Reliability Coordinator. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-001-0 | R5. | The Reliability Coordinator shall list within its reliability plan all entities to which the Reliability Coordinator has delegated required tasks. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-001-0 | R6. | The Reliability Coordinator shall verify that all delegated tasks are carried out by NERCcertified Reliability Coordinator operating personnel. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-001-0 | R7. | The Reliability Coordinator shall have clear, comprehensive coordination agreements with adjacent Reliability Coordinators to ensure that System Operating Limit or Interconnection Reliability Operating Limit violation mitigation requiring actions in adjacent Reliability Coordinator Areas are coordinated. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-001-0 | R8. | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, the Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall immediately inform the Reliability Coordinator of the inability to perform the directive so that the Reliability Coordinator may implement alternate remedial actions. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-001-0 | R9. | The Reliability Coordinator shall act in the interests of reliability for the overall Reliability Coordinator Area and the Interconnection before the interests of any other entity. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-001-1 | R1. | Each Regional Reliability Organization, subregion, or interregional coordinating group shall establish one or more Reliability Coordinators to continuously assess transmission reliability and coordinate emergency operations among the operating entities within the region and across the regional boundaries. | 2007-06-18 | 2009-05-12 | High | The RRO, subregion or interregional coordinating group did not communicate the assignment of the Reliability Coordinators to operating entities clearly. | The RRO, subregion or interregional coordinating group did not clearly identify the coordination of Reliability Coordinator areas within the region. | The RRO, subregion or interregional coordinating group did not coordinate assignment of the Reliability Coordinators across regional boundaries. | The RRO, subregion or interregional coordinating group did not assign any Reliability Coordinators. | [15 empty] | RRO
Inactive | IRO | IRO-001-1 | R2. | The Reliability Coordinator shall comply with a regional reliability plan approved by the NERC Operating Committee. | 2007-06-18 | 2009-05-12 | High | The Reliability Coordinator has failed to follow the administrative portions of its regional reliability plan. | The Reliability Coordinator has failed to follow steps in its regional reliability plan that requires operator interventions or actions. | The Reliability Coordinator does not have a regional reliability plan approved by the NERC OC. | The Reliability Coordinator does not have an unapproved regional reliability plan. | [12 empty] | RC
Inactive | IRO | IRO-001-1 | R3. | The Reliability Coordinator shall have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordinator Area to preserve the integrity and reliability of the Bulk Electric System. These actions shall be taken without delay, but no longer than 30 minutes. | 2007-06-18 | 2009-05-12 | High |  |  | The Reliability Coordinator cannot demonstrate that it has clear authority to act or direct actions to preserve transmission security and reliability of the Bulk Electric System. | The Reliability Coordinator failed to take or direct to preserve the reliability and security of the Bulk Electric System within 30 minutes of identifying those actions. | [12 empty] | RC
Inactive | IRO | IRO-001-1 | R4. | Reliability Coordinators that delegate tasks to other entities shall have formal operating agreements with each entity to which tasks are delegated. The Reliability Coordinator shall verify that all delegated tasks are understood, communicated, and addressed within its Reliability Coordinator Area. All responsibilities for complying with NERC and regional standards applicable to Reliability Coordinators shall remain with the Reliability Coordinator. | 2007-06-18 | 2009-05-12 | Medium | 1. Less than 25% of the tasks are not documented in the agreement or | 1. More than 25% but 50% or less of the tasks are not documented in the agreement or | 1. More than 50% but 75% or less of the tasks are not documented in the agreement or | 1. There is no formal operating agreement for tasks delegated by the Reliability Coordinator, | [12 empty] | RC
Inactive | IRO | IRO-001-1 | R5. | The Reliability Coordinator shall list within its reliability plan all entities to which the Reliability Coordinator has delegated required tasks. | 2007-06-18 | 2009-05-12 | Low | 25% or less of the delegate entities are not identified in the reliability plan. | More than 25% but 50% or less of the delegate entities are not identified in the reliability plan. | More than 50% but 75% or less of the delegate entities are not identified in the reliability plan. | 1. There is no reliability plan or | [12 empty] | RC
Inactive | IRO | IRO-001-1 | R6. | The Reliability Coordinator shall verify that all delegated tasks are carried out by NERC-certified Reliability Coordinator operating personnel. | 2007-06-18 | 2009-05-12 | Medium |  | 1. The Reliability Coordinator has failed to demonstrate at least one delegated task was performed by NERC certified Reliability Coordinator operating personnel or | 1. The Reliability Coordinator has failed to demonstrate at least one delegated task was performed by NERC certified Reliability Coordinator operating personnel and did not require the delegate entity to have NERC certified Reliability Coordinator operat | The Reliability Coordinator has failed to demonstrate any delegated tasks were performed by NERC certified Reliability Coordinator operating personnel and did not require the delegate entity to have NERC certified Reliability Coordinator operating personn | [12 empty] | RC
Inactive | IRO | IRO-001-1 | R7. | The Reliability Coordinator shall have clear, comprehensive coordination agreements with adjacent Reliability Coordinators to ensure that System Operating Limit or Interconnection Reliability Operating Limit violation mitigation requiring actions in adjacent Reliability Coordinator Areas are coordinated. | 2007-06-18 | 2009-05-12 | High | The Reliability Coordinator has demonstrated the existence of coordination agreements with adjacent Reliability Coordinators but the agreements are not clear or comprehensive. | The Reliability Coordinator has demonstrated the existence of the coordination agreements with adjacent Reliability Coordinators but the agreements do not coordinate actions required in the adjacent Reliability Coordinator to mitigate SOL or IROL violatio | The Reliability Coordinator has demonstrated the existence of the coordination agreements with adjacent Reliability Coordinators but the agreements do not coordinate actions required in the adjacent Reliability Coordinator to mitigate SOL and IROL violati | The Reliability Coordinator has failed to demonstrate the existence of any coordination agreements with adjacent Reliability Coordinators. | [12 empty] | RC
Inactive | IRO | IRO-001-1 | R8. | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, the Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall immediately inform the Reliability Coordinator of the inability to perform the directive so that the Reliability Coordinator may implement alternate remedial actions. | 2007-06-18 | 2009-05-12 | High | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities followed the Reliability Coordinators directive with a delay not caused by equipment problems but di | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities followed the Reliability Coordinators directive with a delay not caused by equipment problems and di | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities followed the majority of the Reliability Coordinators directive and did not notify the Reliability C | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities did not follow the Reliability Coordinators directive and did not notify the Reliability Coordinator |  | BA |  |  |  |  | GOP |  | LSE |  |  | PSE | [7 empty] | TOP |  | TSP
Inactive | IRO | IRO-001-1 | R9. | The Reliability Coordinator shall act in the interests of reliability for the overall Reliability Coordinator Area and the Interconnection before the interests of any other entity. | 2007-06-18 | 2009-05-12 | High |  |  |  | The Reliability Coordinator did not act in the interests of reliability for the overall Reliability Coordinator Area and the Interconnection before the interests of one or more other entities. | [12 empty] | RC
Inactive | IRO | IRO-001-1.1 | R1. | Each Regional Reliability Organization, subregion, or interregional coordinating group shall establish one or more Reliability Coordinators to continuously assess transmission reliability and coordinate emergency operations among the operating entities within the region and across the regional boundaries. | 2009-05-13 | 2017-03-31 | High | [19 empty] | RRO
Inactive | IRO | IRO-001-1.1 | R2. | The Reliability Coordinator shall comply with a regional reliability plan approved by the NERC Operating Committee. | 2009-05-13 | 2017-03-31 | High | [16 empty] | RC
Inactive | IRO | IRO-001-1.1 | R3. | The Reliability Coordinator shall have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordinator Area to preserve the integrity and reliability of the Bulk Electric System. These actions shall be taken without delay, but no longer than 30 minutes. | 2009-05-13 | 2017-03-31 | High |  |  |  | The Reliability Coordinator failed to take or direct to preserve the reliability and security of the Bulk Electric System within 30 minutes of identifying those actions. | [12 empty] | RC
Inactive | IRO | IRO-001-1.1 | R4. | Reliability Coordinators that delegate tasks to other entities shall have formal operating agreements with each entity to which tasks are delegated. The Reliability Coordinator shall verify that all delegated tasks are understood, communicated, and addressed within its Reliability Coordinator Area. All responsibilities for complying with NERC and regional standards applicable to Reliability Coordinators shall remain with the Reliability Coordinator. | 2009-05-13 | 2017-03-31 | Medium | [16 empty] | RC
Inactive | IRO | IRO-001-1.1 | R5. | The Reliability Coordinator shall list within its reliability plan all entities to which the Reliability Coordinator has delegated required tasks. | 2009-05-13 | 2017-03-31 | Low | [16 empty] | RC
Inactive | IRO | IRO-001-1.1 | R6. | The Reliability Coordinator shall verify that all delegated tasks are carried out by NERC-certified Reliability Coordinator operating personnel. | 2009-05-13 | 2017-03-31 | Medium | [16 empty] | RC
Inactive | IRO | IRO-001-1.1 | R7. | The Reliability Coordinator shall have clear, comprehensive coordination agreements with adjacent Reliability Coordinators to ensure that System Operating Limit or Interconnection Reliability Operating Limit violation mitigation requiring actions in adjacent Reliability Coordinator Areas are coordinated. | 2009-05-13 | 2017-03-31 | High | [16 empty] | RC
Inactive | IRO | IRO-001-1.1 | R8. | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, the Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall immediately inform the Reliability Coordinator of the inability to perform the directive so that the Reliability Coordinator may implement alternate remedial actions. | 2009-05-13 | 2017-03-31 | High | [5 empty] | BA |  |  |  |  | GOP |  | LSE |  |  | PSE | [7 empty] | TOP |  | TSP
Inactive | IRO | IRO-001-1.1 | R9. | The Reliability Coordinator shall act in the interests of reliability for the overall Reliability Coordinator Area and the Interconnection before the interests of any other entity. | 2009-05-13 | 2017-03-31 | High | [16 empty] | RC
Inactive | IRO | IRO-001-2 | R1. | Each Regional Reliability Organization, subregion, or interregional coordinating group shall establish one or more Reliability Coordinators to continuously assess transmission reliability and coordinate emergency operations among the operating entities within the region and across the regional boundaries. |  | 2012-08-16 | High | N/A | N/A | N/A | N/A | [15 empty] | RRO
Inactive | IRO | IRO-001-2 | R2. | The Reliability Coordinator shall comply with a regional reliability plan approved by the NERC Operating Committee. |  | 2012-08-16 | High | N/A | N/A | N/A | The Reliability Coordinator did not comply with the regional reliability plan approved by the NERC Operating Committee. | [12 empty] | RC
Inactive | IRO | IRO-001-2 | R3. | The Reliability Coordinator shall have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordinator Area to preserve the integrity and reliability of the Bulk Electric System. These actions shall be taken without delay, but no longer than 30 minutes. |  | 2012-08-16 | High | N/A | N/A | The Reliability Coordinator cannot demonstrate that it has clear authority to act or direct actions to preserve transmission security and reliability of the Bulk Electric System. | The Reliability Coordinator failed to take or direct action to preserve the reliability and security of the Bulk Electric System within 30 minutes of identifying those actions. | [12 empty] | RC
Inactive | IRO | IRO-001-2 | R4. | Reliability Coordinators that delegate tasks to other entities shall have formal operating agreements with each entity to which tasks are delegated. The Reliability Coordinator shall verify that all delegated tasks are understood, communicated, and addressed within its Reliability Coordinator Area. All responsibilities for complying with NERC and regional standards applicable to Reliability Coordinators shall remain with the Reliability Coordinator. |  | 2012-08-16 | Medium |  | The Reliability Coordinator has delegated tasks to other entities and had formal operating agreements with each of these entities but could not verify that delegated tasks were understood, communicated, and addressed within its Reliability Coordinator Are |  | The Reliability Coordinator has delegated tasks to other entities but failed to have a formal operating agreement delegating tasks to each of these entities. | [12 empty] | RC
Inactive | IRO | IRO-001-2 | R5. | The Reliability Coordinator shall list within its reliability plan all entities to which the Reliability Coordinator has delegated required tasks. |  | 2012-08-16 | Low | 5% or less of the delegate entities are not identified in the reliability plan. | More than 5% up to (and including) 10% of the delegate entities are not identified in the reliability plan. | More than 10% up to (and including) 15% of the delegate entities are not identified in the reliability plan. | There is no reliability plan. OR More than 15% of the delegate entities are not identified in the reliability plan. | [12 empty] | RC
Inactive | IRO | IRO-001-2 | R6. | The Reliability Coordinator shall verify that all delegated tasks are carried out by NERC-certified Reliability Coordinator operating personnel. |  | 2012-08-16 | Medium | There is no reliability plan. OR More than 15% of the delegate entities are not identified in the reliability plan. | The Reliability Coordinator failed to demonstrate that more than 5% up to (and including) 10% of its delegated tasks were being performed by NERC certified Reliability Coordinator operating personnel | The Reliability Coordinator failed to demonstrate that more than 10% up to (and including) 15% of its delegated tasks were being performed by NERC certified Reliability Coordinator Operating personnel. | The Reliability Coordinator failed to demonstrate that more than 15% of its delegated tasks were being performed by NERC certified Reliability Coordinator operating personnel. | [12 empty] | RC
Inactive | IRO | IRO-001-2 | R7. | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, the Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall immediately inform the Reliability Coordinator of the inability to perform the directive so that the Reliability Coordinator may implement alternate remedial actions. |  | 2012-08-16 | High | N/A | The responsible entity could not comply with a directive due to qualified reasons (violation of safety, equipment or regulatory or statutory requirements) and did not immediately inform the Reliability Coordinator. | N/A | The responsible entity did not follow the Reliability Coordinator’s directive. |  | BA |  |  |  |  | GOP |  | LSE |  |  | PSE | [7 empty] | TOP |  | TSP
Inactive | IRO | IRO-001-2 | R8. | The Reliability Coordinator shall act in the interests of reliability for the overall Reliability Coordinator Area and the Interconnection before the interests of any other entity. |  | 2012-08-16 | High | N/A | N/A | N/A | The Reliability Coordinator did not act in the interests of reliability for the overall Reliability Coordinator Area and the Interconnection before the interests of one or more other entities. | [12 empty] | RC
Inactive | IRO | IRO-001-3 | R1. | Each Reliability Coordinator shall have the authority to act or direct others to act (which could include issuing Reliability Directives) to prevent identified events or mitigate the magnitude or duration of actual events that result in an Emergency or Adverse Reliability Impact. |  | 2016-01-26 | High | N/A | N/A | N/A | The Reliability Coordinator failed to take action or direct actions, to prevent an identified event that resulted in an Emergency or Adverse Reliability Impact. OR The Reliability Coordinator failed to take action or direct actions to mitigate the magnitude or duration of an event that resulted in an Emergency or Adverse Reliability Impact. | [12 empty] | RC
Inactive | IRO | IRO-001-3 | R2. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall comply with its Reliability Coordinator’s direction unless compliance with the direction cannot be physically implemented or unless such actions would violate safety, equipment, regulatory, or statutory requirements. |  | 2016-01-26 | High | N/A | N/A | N/A | The Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider did not comply with the Reliability Coordinator’s direction, and compliance with the direction could have been physically implemented and such actions would not have violated safety, equipment, regulatory, or statutory requirements. |  | BA | DP |  |  |  | GOP | [12 empty] | TOP
Inactive | IRO | IRO-001-3 | R3. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall inform its Reliability Coordinator upon recognition of its inability to perform as directed in accordance with Requirement R2. |  | 2016-01-26 | High | N/A | N/A | N/A | The Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider failed to inform its Reliability Coordinator upon recognition of its inability to perform as directed. |  | BA | DP |  |  |  | GOP | [12 empty] | TOP
Mandatory Subject to Enforcement | IRO | IRO-001-4 | R1. | Each Reliability Coordinator shall act to address the reliability of its Reliability Coordinator Area via direct actions or by issuing Operating Instructions. [Violation Risk Factor: | 2017-04-01 |  | High | N/A | N/A | N/A | The Reliability Coordinator failed to act to address the reliability of its Reliability Coordinator Area via direct actions or by issuing Operating Instructions. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-001-4 | R2. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall comply with its Reliability Coordinator’s Operating Instructions unless compliance with the Operating Instructions cannot be physically implemented or unless such actions would violate safety, equipment, regulatory, or statutory requirements. | 2017-04-01 |  | High | N/A | N/A | N/A | The responsible entity did not comply with the Reliability Coordinator’s Operating Instructions, and compliance with the Operating Instructions could have been physically implemented and such actions would not have violated safety, equipment, regulatory, or statutory requirements. |  | BA | DP |  |  |  | GOP | [12 empty] | TOP
Mandatory Subject to Enforcement | IRO | IRO-001-4 | R3. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall inform its Reliability Coordinator of its inability to perform the Operating Instruction issued by its Reliability Coordinator in Requirement R1. | 2017-04-01 |  | High | N/A | N/A | N/A | The responsible entity failed to inform its Reliability Coordinator upon recognition of its inability to perform an Operating Instruction issued by its Reliability Coordinator in Requirement R1 . |  | BA | DP |  |  |  | GOP | [12 empty] | TOP
Inactive | IRO | IRO-002-0 | R1. | Each Reliability Coordinator shall have adequate communications facilities (voice and data links) to appropriate entities within its Reliability Coordinator Area. These communications facilities shall be staffed and available to act in addressing a real-time emergency condition. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-002-0 | R2. | Each Reliability Coordinator shall determine the data requirements to support its reliability coordination tasks and shall request such data from its Transmission Operators, Balancing Authorities, Transmission Owners, Generation Owners, Generation Operators, and LoadServing Entities, or adjacent Reliability Coordinators. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-002-0 | R3. | Each Reliability Coordinator – or its Transmission Operators and Balancing Authorities – shall provide, or arrange provisions for, data exchange to other Reliability Coordinators or Transmission Operators and Balancing Authorities via a secure network. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-002-0 | R4. | Each Reliability Coordinator shall have multi-directional communications capabilities with its Transmission Operators and Balancing Authorities, and with neighboring Reliability Coordinators, for both voice and data exchange as required to meet reliability needs of the Interconnection. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-002-0 | R5. | Each Reliability Coordinator shall have detailed real-time monitoring capability of its Reliability Coordinator Area and sufficient monitoring capability of its surrounding Reliability Coordinator Areas to ensure that potential or actual System Operating Limit or Interconnection Reliability Operating Limit violations are identified. Each Reliability Coordinator shall have monitoring systems that provide information that can be easily understood and interpreted by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant and highly reliable infrastructure. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-002-0 | R6. | Each Reliability Coordinator shall monitor Bulk Electric System elements (generators, transmission lines, buses, transformers, breakers, etc.) that could result in SOL or IROL violations within its Reliability Coordinator Area. Each Reliability Coordinator shall monitor both real and reactive power system flows, and operating reserves, and the status of Bulk Electric System elements that are or could be critical to SOLs and IROLs and system restoration requirements within its Reliability Coordinator Area. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-002-0 | R7. | Each Reliability Coordinator shall have adequate analysis tools such as state estimation, preand post-contingency analysis capabilities (thermal, stability, and voltage), and wide-area overview displays |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-002-0 | R8. | Each Reliability Coordinator shall continuously monitor its Reliability Coordinator Area. Each Reliability Coordinator shall have provisions for backup facilities that shall be exercised if the main monitoring system is unavailable. Each Reliability Coordinator shall ensure SOL and IROL monitoring and derivations continue if the main monitoring system is unavailable. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-002-0 | R9. | Each Reliability Coordinator shall control its Reliability Coordinator analysis tools, including approvals for planned maintenance. Each Reliability Coordinator shall have procedures in place to mitigate the effects of analysis tool outages. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-002-1 | R1. | Each Reliability Coordinator shall have adequate communications facilities (voice and data links) to appropriate entities within its Reliability Coordinator Area. These communications facilities shall be staffed and available to act in addressing a real-time emergency condition. | 2007-06-18 | 2011-09-30 | High | The Reliability Coordinator has demonstrated communication facilities for both voice and data exist to all appropriate entities and that they are staffed and available but they are less than adequate. | The Reliability Coordinator has failed to demonstrate that is has: | The Reliability Coordinator has failed to demonstrate that is has: | The Reliability Coordinator has failed to demonstrate that is has: | [12 empty] | RC
Inactive | IRO | IRO-002-1 | R2. | Each Reliability Coordinator shall determine the data requirements to support its reliability coordination tasks and shall request such data from its Transmission Operators, Balancing Authorities, Transmission Owners, Generation Owners, Generation Operators, and Load-Serving Entities, or adjacent Reliability Coordinators. | 2007-06-18 | 2011-09-30 | Medium | The Reliability Coordinator demonstrated that it | The Reliability Coordinator demonstrated that it determined the majority but not all of its data requirements necessary to support its reliability coordination functions and requested that data from its Transmission Operators, Balancing Authorities, Trans | The Reliability Coordinator demonstrated that it determined | The Reliability Coordinator failed to demonstrate that it | [12 empty] | RC
Inactive | IRO | IRO-002-1 | R3. | Each Reliability Coordinator - or its Transmission Operators and Balancing Authorities - shall provide, or arrange provisions for, data exchange to other Reliability Coordinators or Transmission Operators and Balancing Authorities via a secure network. | 2007-06-18 | 2011-09-30 | Medium |  | The Reliability Coordinator or designated Transmission Operator and Balancing Authority has failed to demonstrate it provided or arranged provision for the exchange of data with one of the other Reliability Coordinators or Transmission Operators and Balan | The Reliability Coordinator or designated Transmission Operator and Balancing Authority has failed to demonstrate it provided or arranged provision for the exchange of data with two of the other Reliability Coordinators or Transmission Operators and Balan | The Reliability Coordinator or designated Transmission Operator and Balancing Authority has failed to demonstrate it provided or arranged provision for the exchange of data with three of the other Reliability Coordinators or Transmission Operators and Bal | [12 empty] | RC
Inactive | IRO | IRO-002-1 | R4. | Each Reliability Coordinator shall have multi-directional communications capabilities with its Transmission Operators and Balancing Authorities, and with neighboring Reliability Coordinators, for both voice and data exchange as required to meet reliability needs of the Interconnection. | 2007-06-18 | 2011-09-30 | High |  | The Reliability Coordinator has failed to demonstrate multi-directional communication capabilities to one of the Transmission Operators and Balancing Authorities in its Reliability Coordinator Area and with neighboring Reliability Coordinators. | The Reliability Coordinator has failed to demonstrate multi-directional communication capabilities to two or more of the Transmission Operators and Balancing Authorities in its Reliability Coordinator Area and with neighboring Reliability Coordinators. | The Reliability Coordinator has failed to demonstrate multi-directional communication capabilities to all of the Transmission Operators and Balancing Authorities in its Reliability Coordinator Area and with all neighboring Reliability Coordinators. | [12 empty] | RC
Inactive | IRO | IRO-002-1 | R5. | Each Reliability Coordinator shall have detailed real-time monitoring capability of its Reliability Coordinator Area and sufficient monitoring capability of its surrounding Reliability Coordinator Areas to ensure that potential or actual System Operating Limit or Interconnection Reliability Operating Limit violations are identified. Each Reliability Coordinator shall have monitoring systems that provide information that can be easily understood and interpreted by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant and highly reliable infrastructure. | 2007-06-18 | 2011-09-30 | High | The Reliability Coordinator's monitoring systems provide information in a way that is not easily understood and interpreted by the Reliability Coordinator's operating personnel or particular emphasis was not given to alarm management and awareness systems | The Reliability Coordinator has failed to demonstrate that is has detailed real-time monitoring capabilities in its Reliability Coordinator Area and sufficient monitoring capabilities of its surrounding Reliability Coordinator Areas to ensure that one pot | The Reliability Coordinator has failed to demonstrate that is has detailed real-time monitoring capabilities in its Reliability Coordinator Area and sufficient monitoring capabilities of its surrounding Reliability Coordinator Areas to ensure that two or | The Reliability Coordinator has failed to demonstrate that is has detailed real-time monitoring capabilities in its Reliability Coordinator Area and sufficient monitoring capabilities of its surrounding Reliability Coordinator Areas to ensure that all pot | [12 empty] | RC
Inactive | IRO | IRO-002-1 | R6. | Each Reliability Coordinator shall monitor Bulk Electric System elements (generators, transmission lines, buses, transformers, breakers, etc.) that could result in SOL or IROL violations within its Reliability Coordinator Area. Each Reliability Coordinator shall monitor both real and reactive power system flows, and operating reserves, and the status of Bulk Electric System elements that are or could be critical to SOLs and IROLs and system restoration requirements within its Reliability Coordinator Area. | 2007-06-18 | 2011-09-30 | High | The Reliability Coordinator failed to monitor: | The Reliability Coordinator failed to monitor: | The Reliability Coordinator failed to monitor: | The Reliability Coordinator failed to monitor: | [12 empty] | RC
Inactive | IRO | IRO-002-1 | R7. | Each Reliability Coordinator shall have adequate analysis tools such as state estimation, pre- and post-contingency analysis capabilities (thermal, stability, and voltage), and wide-area overview displays. | 2007-06-18 | 2011-09-30 | High | The Reliability Coordinator failed to demonstrate that it has: | The Reliability Coordinator failed to demonstrate that it has: | The Reliability Coordinator failed to demonstrate that it has: | The Reliability Coordinator failed to demonstrate that it has: | [12 empty] | RC
Inactive | IRO | IRO-002-1 | R8. | Each Reliability Coordinator shall continuously monitor its Reliability Coordinator Area. Each Reliability Coordinator shall have provisions for backup facilities that shall be exercised if the main monitoring system is unavailable. Each Reliability Coordinator shall ensure SOL and IROL monitoring and derivations continue if the main monitoring system is unavailable. | 2007-06-18 | 2011-09-30 | High | The Reliability Coordinator failed to demonstrate that: | The Reliability Coordinator failed to demonstrate that: | The Reliability Coordinator failed to demonstrate that: | The Reliability Coordinator failed to demonstrate that it continuously monitored its Reliability Authority Area. | [12 empty] | RC
Inactive | IRO | IRO-002-1 | R9. | Each Reliability Coordinator shall control its Reliability Coordinator analysis tools, including approvals for planned maintenance. Each Reliability Coordinator shall have procedures in place to mitigate the effects of analysis tool outages. | 2007-06-18 | 2011-09-30 | Medium | Reliability Coordinator has approval rights for planned maintenance outages of analysis tools but does not have approval rights for work on analysis tools that creates a greater risk of an unplanned outage of the tools. | Reliability Coordinator has approval rights for planned maintenance but does not have plans to mitigate the effects of outages of the analysis tools. | Reliability Coordinator has approval rights for planned maintenance but does not have plans to mitigate the effects of outages of the analysis tools and does not have approval rights for work on analysis tools that creates a greater risk of an unplanned o | Reliability Coordinator approval is not required for planned maintenance. | [12 empty] | RC
Inactive | IRO | IRO-002-2 | R1. | Each Reliability Coordinator shall have adequate communications facilities (voice and data links) to appropriate entities within its Reliability Coordinator Area. These communications facilities shall be staffed and available to act in addressing a real-time emergency condition. | 2011-10-01 | 2017-03-31 | High | The Reliability Coordinator has demonstrated communication facilities for both voice and data exist to all appropriate entities and that they are staffed and available but they are less than adequate. | The Reliability Coordinator has failed to demonstrate that is has: 1) Voice communication links with one appropriate entity or 2) Data links with one appropriate entity. | The Reliability Coordinator has failed to demonstrate that is has: 1) Voice communication links with two appropriate entities or 2) Data links with two appropriate entities. | The Reliability Coordinator has failed to demonstrate that is has: 1) Voice communication links with more than two appropriate entities or 2) Data links with more than two appropriate entities or 3) Communication facilities are not staffed or 4) Communication facilities are not ready. | [12 empty] | RC
Inactive | IRO | IRO-002-2 | R2. | Each Reliability Coordinator — or its Transmission Operators and Balancing Authorities — shall provide, or arrange provisions for, data exchange to other Reliability Coordinators or Transmission Operators and Balancing Authorities via a secure network. | 2011-10-01 | 2017-03-31 | Medium | N/A | The Reliability Coordinator or designated Transmission Operator and Balancing Authority has failed to demonstrate it provided or arranged provision for the exchange of data with one of the other Reliability Coordinators or Transmission Operators and Balancing Authorities. | The Reliability Coordinator or designated Transmission Operator and Balancing Authority has failed to demonstrate it provided or arranged provision for the exchange of data with two of the other Reliability Coordinators or Transmission Operators and Balancing Authorities. | The Reliability Coordinator or designated Transmission Operator and Balancing Authority has failed to demonstrate it provided or arranged provision for the exchange of data with three of the other Reliability Coordinators or Transmission Operators and Balancing Authorities. | [12 empty] | RC
Inactive | IRO | IRO-002-2 | R3. | Each Reliability Coordinator shall have multi-directional communications capabilities with its Transmission Operators and Balancing Authorities, and with neighboring Reliability Coordinators, for both voice and data exchange as required to meet reliability needs of the Interconnection. | 2011-10-01 | 2017-03-31 | Medium | N/A | The Reliability Coordinator has failed to demonstrate multi-directional communication capabilities to one of the Transmission Operators and Balancing Authorities in its Reliability Coordinator Area and with neighboring Reliability Coordinators. | The Reliability Coordinator has failed to demonstrate multi-directional communication capabilities to two or more of the Transmission Operators and Balancing Authorities in its Reliability Coordinator Area and with neighboring Reliability Coordinators. | The Reliability Coordinator has failed to demonstrate multi-directional communication capabilities to all of the Transmission Operators and Balancing Authorities in its Reliability Coordinator Area and with all neighboring Reliability Coordinators. | [12 empty] | RC
Inactive | IRO | IRO-002-2 | R4. | Each Reliability Coordinator shall have detailed real-time monitoring capability of its Reliability Coordinator Area and sufficient monitoring capability of its surrounding Reliability Coordinator Areas to ensure that potential or actual System Operating Limit or Interconnection Reliability Operating Limit violations are identified. Each Reliability Coordinator shall have monitoring systems that provide information that can be easily understood and interpreted by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant and highly reliable infrastructure. | 2011-10-01 | 2017-03-31 | High | The Reliability Coordinator's monitoring systems provide information in a way that is not easily understood and interpreted by the Reliability Coordinator's operating personnel or particular emphasis was not given to alarm management and awareness systems, automated data transfers and synchronized information systems. | The Reliability Coordinator has failed to demonstrate that is has detailed real-time monitoring capabilities in its Reliability Coordinator Area and sufficient monitoring capabilities of its surrounding Reliability Coordinator Areas to ensure that one potential or actual SOL or IROL violation is not identified. | The Reliability Coordinator has failed to demonstrate that is has detailed real-time monitoring capabilities in its Reliability Coordinator Area and sufficient monitoring capabilities of its surrounding Reliability Coordinator Areas to ensure that two or more potential and actual SOL and IROL violations are not identified. | The Reliability Coordinator has failed to demonstrate that is has detailed real-time monitoring capabilities in its Reliability Coordinator Area and sufficient monitoring capabilities of its surrounding Reliability Coordinator Areas to ensure that all potential and actual SOL and IROL violations are identified. | [12 empty] | RC
Inactive | IRO | IRO-002-2 | R5. | Each Reliability Coordinator shall monitor Bulk Electric System elements (generators, transmission lines, buses, transformers, breakers, etc.) that could result in SOL or IROL violations within its Reliability Coordinator Area. Each Reliability Coordinator shall monitor both real and reactive power system flows, and operating reserves, and the status of Bulk Electric System elements that are or could be critical to SOLs and IROLs and system restoration requirements within its Reliability Coordinator Area. | 2011-10-01 | 2017-03-31 | High | The Reliability Coordinator failed to monitor: 1) the status, real power flow or reactive power flow of Bulk Electric System elements that could result in one SOL violations or 2) or operating reserves for a small portion of the Reliability Authority Area. | The Reliability Coordinator failed to monitor: 1) the status, real power flow or reactive power flow of Bulk Electric System elements critical to assessing one IROL or to system restoration, 2) the status, real power flow or reactive power flow of Bulk Electric System elements that could result in multiple SOL violations, or 3) operating reserves | The Reliability Coordinator failed to monitor: 1) the status, real power flow or reactive power flow of Bulk Electric System elements critical to assessing two or more IROLs; or one IROL and to system restoration, 2) the status, real power flow or reactive power flow of Bulk Electric System elements that could result in multiple SOL violations and operating reserves, or 3) the status, real power flow or reactive power flow of Bulk Electric System elements critical to assessing one IROL or system restoration and operating reserves. | The Reliability Coordinator failed to monitor: 1) the status, real power flow or reactive power flow of Bulk Electric System elements critical to assessing all IROLs and to system restoration, or 2) the status, real power flow or reactive power flow of Bulk Electric System elements critical to assessing all SOL violations and operating reserves. | [12 empty] | RC
Inactive | IRO | IRO-002-2 | R6. | Each Reliability Coordinator shall have adequate analysis tools such as state estimation, pre- and post-contingency analysis capabilities (thermal, stability, and voltage), and wide-area overview displays. | 2011-10-01 | 2017-03-31 | High | The Reliability Coordinator failed to demonstrate that it has: 1) analysis tools capable of assessing all pre-contingency flows, 2) analysis tools capable of assessing all postcontingency flows, or 3) all necessary wide-area overview displays exist. | The Reliability Coordinator failed to demonstrate that it has: 1) analysis tools capable of assessing the majority of precontingency flows, 2) analysis tools capable of assessing the majority of post-contingency flows, or 3) the majority of necessary wide-area overview displays exist. | The Reliability Coordinator failed to demonstrate that it has: 1) analysis tools capable of assessing a minority of precontingency flows, 2) analysis tools capable of assessing a minority of postcontingency flows, or 3) a minority of necessary wide-area overview displays exist. | The Reliability Coordinator failed to demonstrate that it has: 1) analysis tools capable of assessing any precontingency flows, 2) analysis tools capable of assessing any postcontingency flows, or 3) any necessary wide-area overview displays exist. | [12 empty] | RC
Inactive | IRO | IRO-002-2 | R7. | Each Reliability Coordinator shall continuously monitor its Reliability Coordinator Area. Each Reliability Coordinator shall have provisions for backup facilities that shall be exercised if the main monitoring system is unavailable. Each Reliability Coordinator shall ensure SOL and IROL monitoring and derivations continue if the main monitoring system is unavailable. | 2011-10-01 | 2017-03-31 | High | The Reliability Coordinator failed to demonstrate that: 1) it or a delegated entity monitored SOLs when the main monitoring system was unavailable or 2) it has provisions to monitor SOLs when the main monitoring system is not available | The Reliability Coordinator failed to demonstrate that: 1) it or a delegated entity monitored one IROL when the main monitoring system was unavailable or 2) it has provisions to monitor one IROL when the main monitoring system is not available. | The Reliability Coordinator failed to demonstrate that: 1) it or a delegated entity monitored two or more IROLs when the main monitoring system was unavailable, 2) it or a delegated entity monitored SOLs and one IROL when the main monitoring system was unavailable 3) it has provisions to monitor two or more IROLs when the main monitoring system is not available, or 4) it has provisions to monitor SOLs and one IROL when the main monitoring system was unavailable. | The Reliability Coordinator failed to demonstrate that it continuously monitored its Reliability Authority Area. | [12 empty] | RC
Inactive | IRO | IRO-002-2 | R8. | Each Reliability Coordinator shall control its Reliability Coordinator analysis tools, including approvals for planned maintenance. Each Reliability Coordinator shall have procedures in place to mitigate the effects of analysis tool outages. | 2011-10-01 | 2017-03-31 | High | Reliability Coordinator has approval rights for planned maintenance outages of analysis tools but does not have approval rights for work on analysis tools that creates a greater risk of an unplanned outage of the tools. | Reliability Coordinator has approval rights for planned maintenance but does not have plans to mitigate the effects of outages of the analysis tools. | Reliability Coordinator has approval rights for planned maintenance but does not have plans to mitigate the effects of outages of the analysis tools and does not have approval rights for work on analysis tools that creates a greater risk of an unplanned outage of the tools | Reliability Coordinator approval is not required for planned maintenance. | [12 empty] | RC
Inactive | IRO | IRO-002-3 | R1. | Each Reliability Coordinator shall provide its System Operators with the authority to approve, deny or cancel planned outages of its own analysis tools. |  | 2016-01-26 | Medium | N/A | N/A | N/A | The Reliability Coordinator failed to provide its System Operator with the authority to approve, deny or cancel planned outages of its own analysis tools. | [12 empty] | RC
Inactive | IRO | IRO-002-3 | R2. | Each Reliability Coordinator shall have procedures in place to mitigate the effects of analysis tool outages. |  | 2016-01-26 | Medium | N/A | N/A | N/A | The Reliability Coordinator failed to have a procedure to mitigate the effects of analysis tool outages. | [12 empty] | RC
Inactive | IRO | IRO-002-4 | R1. | Each Reliability Coordinator shall have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | 2017-04-01 | 2017-09-30 | High | The Reliability Coordinator did not have data exchange capabilities with one applicable entity, or 5% or less of the applicable entities, whichever is greater. | The Reliability Coordinator did not have data exchange capabilities with two applicable entities, or more than 5% or less than or equal to 10% of the applicable entities, whichever is greater. | The Reliability Coordinator did not have data exchange capabilities with three applicable entities, or more than 10% or less than or equal to 15% of the applicable entities, whichever is greater. | The Reliability Coordinator did not have data exchange capabilities with four or more applicable entities or greater than 15% of the applicable entities, whichever is greater. | [12 empty] | RC
Inactive | IRO | IRO-002-4 | R2. | Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities | 2017-04-01 | 2017-09-30 | High | N/A | N/A | N/A | The Reliability Coordinator failed to provide its System Operator with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | [12 empty] | RC
Inactive | IRO | IRO-002-4 | R3. | Each Reliability Coordinator shall monitor Facilities, the status of Special Protection Systems, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | 2017-04-01 | 2017-09-30 | High | N/A | N/A | N/A | The Reliability Coordinator did not monitor Facilities, the status of Special Protection Systems, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | [12 empty] | RC
Inactive | IRO | IRO-002-4 | R4. | Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | 2017-04-01 | 2017-09-30 | High | N/A | N/A | N/A | The Reliability Coordinator did not have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | [12 empty] | RC
Inactive | IRO | IRO-002-5 | R1. | Each Reliability Coordinator shall have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | 2017-10-01 | 2019-12-31 | Medium | The Reliability Coordinator did not have data exchange capabilities for performing its Operational Planning Analyses with one applicable entity, or 5% or less of the applicable entities, whichever is greater. | The Reliability Coordinator did not have data exchange capabilities for performing its Operational Planning Analyses with two applicable entities, or more than 5% or less than or equal to 10% of the applicable entities, whichever is greater. | The Reliability Coordinator did not have data exchange capabilities for performing its Operational Planning Analyses with three applicable entities, or more than 10% or less than or equal to 15% of the applicable entities, whichever is greater. | The Reliability Coordinator did not have data exchange capabilities for performing its Operational Planning Analyses with four or more applicable entities or greater than 15% of the applicable entities, whichever is greater. | [12 empty] | RC
Inactive | IRO | IRO-002-5 | R2. | Each Reliability Coordinator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing its Real-time monitoring and Real-time Assessments. [Violation Risk Factor: | 2017-10-01 | 2019-12-31 | High | N/A | N/A | The Reliability Coordinator had data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, as specified in the requirement. | The Reliability Coordinator did not have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing Real-time monitoring and Real-time Assessments as specified in the requirement. | [12 empty] | RC
Inactive | IRO | IRO-002-5 | R3. | Each Reliability Coordinator shall test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Reliability Coordinator shall initiate action within two hours to restore redundant functionality. | 2017-10-01 | 2019-12-31 | Medium | The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Reliability Coordinator did not test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality; OR The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | [12 empty] | RC
Inactive | IRO | IRO-002-5 | R4. | Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | 2017-10-01 | 2019-12-31 | High | N/A | N/A | N/A | The Reliability Coordinator failed to provide its System Operator with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | [12 empty] | RC
Inactive | IRO | IRO-002-5 | R5. | Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | 2017-10-01 | 2019-12-31 | High | N/A | N/A | N/A | The Reliability Coordinator did not monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | [12 empty] | RC
Inactive | IRO | IRO-002-5 | R6. | Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | 2017-10-01 | 2019-12-31 | High | N/A | N/A | N/A | The Reliability Coordinator did not have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | [12 empty] | RC
Inactive | IRO | IRO-002-6 | R1. | Each Reliability Coordinator shall have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | 2020-01-01 | 2021-03-31 | Medium | The Reliability Coordinator did not have data exchange capabilities for performing its Operational Planning Analyses with one applicable entity, or 5% or less of the applicable entities, whichever is greater. | The Reliability Coordinator did not have data exchange capabilities for performing its Operational Planning Analyses with two applicable entities, or more than 5% or less than or equal to 10% of the applicable entities, whichever is greater. | The Reliability Coordinator did not have data exchange capabilities for performing its Operational Planning Analyses with three applicable entities, or more than 10% or less than or equal to 15% of the applicable entities, whichever is greater. | The Reliability Coordinator did not have data exchange capabilities for performing its Operational Planning Analyses with four or more applicable entities or greater than 15% of the applicable entities, whichever is greater. | [12 empty] | RC
Inactive | IRO | IRO-002-6 | R2. | Each Reliability Coordinator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing its Real-time monitoring and Real-time Assessments. | 2020-01-01 | 2021-03-31 | High | N/A | N/A | The Reliability Coordinator had data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, as specified in the requirement. | The Reliability Coordinator did not have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing Real-time monitoring and Real-time Assessments as specified in the requirement. | [12 empty] | RC
Inactive | IRO | IRO-002-6 | R3. | Each Reliability Coordinator shall test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Reliability Coordinator shall initiate action within two hours to restore redundant functionality. | 2020-01-01 | 2021-03-31 | Medium | The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Reliability Coordinator did not test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality; OR The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | [12 empty] | RC
Inactive | IRO | IRO-002-6 | R4. | Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | 2020-01-01 | 2021-03-31 | High | N/A | N/A | N/A | The Reliability Coordinator failed to provide its System Operator with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | [12 empty] | RC
Inactive | IRO | IRO-002-6 | R5. | Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | 2020-01-01 | 2021-03-31 | High | N/A | N/A | N/A | The Reliability Coordinator did not monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | [12 empty] | RC
Inactive | IRO | IRO-002-6 | R6. | Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | 2020-01-01 | 2021-03-31 | High | N/A | N/A | N/A | The Reliability Coordinator did not have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | [12 empty] | RC
Inactive | IRO | IRO-002-6 | D.A.7. | Each Reliability Coordinator shall, in coordination with other Reliability Coordinators, develop a common Interconnection-wide methodology to determine the modeling and monitoring of BES and non-BES Elements that are internal and external to its Reliability Coordinator Area, necessary for providing operational awareness of the impacts on Bulk Electric System Facilities within its Reliability Coordinator Area, including at a minimum: | 2020-01-01 | 2021-03-31 | High |  |  |  | The Reliability Coordinator did not develop the methodology as required in D.A.7. | [12 empty] | RC
Inactive | IRO | IRO-002-6 | D.A.8. | Each Reliability Coordinator shall use the methodology developed in D.A.7. | 2020-01-01 | 2021-03-31 | High |  |  |  | The Reliability Coordinator did not implement the methodology as required in D.A.8. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002-7 | R1. | Reserved. | 2021-04-01
Mandatory Subject to Enforcement | IRO | IRO-002-7 | R2. | Each Reliability Coordinator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing its Real-time monitoring and Real-time Assessments. | 2021-04-01 |  | High | N/A | N/A | The Reliability Coordinator had data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, as specified in the requirement. | The Reliability Coordinator did not have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing Real-time monitoring and Real-time Assessments as specified in the requirement. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002-7 | R3. | Each Reliability Coordinator shall test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Reliability Coordinator shall initiate action within two hours to restore redundant functionality. | 2021-04-01 |  | Medium | The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Reliability Coordinator did not test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality; OR The Reliability Coordinator tested its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002-7 | R4. | Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | 2021-04-01 |  | High | N/A | N/A | N/A | The Reliability Coordinator failed to provide its System Operator with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002-7 | R5. | Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | 2021-04-01 |  | High | N/A | N/A | N/A | The Reliability Coordinator did not monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002-7 | R6. | Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | 2021-04-01 |  | High | N/A | N/A | N/A | The Reliability Coordinator did not have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002-7 | D.A.7. | Each Reliability Coordinator shall, in coordination with other Reliability Coordinators, develop a common Interconnection-wide methodology to determine the modeling and monitoring of BES and non-BES Elements that are internal and external to its Reliability Coordinator Area, necessary for providing operational awareness of the impacts on Bulk Electric System Facilities within its Reliability Coordinator Area, including at a minimum: | 2021-04-01 |  | High |  |  |  | The Reliability Coordinator did not develop the methodology as required in D.A.7. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-002-7 | D.A.8. | Each Reliability Coordinator shall use the methodology developed in D.A.7. | 2021-04-01 |  | High |  |  |  | The Reliability Coordinator did not implement the methodology as required in D.A.8. | [12 empty] | RC
Inactive | IRO | IRO-003-0 | R1. | Each Reliability Coordinator shall monitor all Bulk Electric System facilities, which may include sub-transmission information, within its Reliability Coordinator Area and adjacent Reliability Coordinator Areas, as necessary to ensure that, at any time, regardless of prior planned or unplanned events, the Reliability Coordinator is able to determine any potential System Operating Limit and Interconnection Reliability Operating Limit violations within its Reliability Coordinator Area. |  | 2006-08-01 | [17 empty] | RC
Inactive | IRO | IRO-003-0 | R2. | When a Reliability Coordinator is aware of an operational concern, such as declining voltages, excessive reactive flows, or an IROL violation, in a neighboring Reliability Coordinator Area, it shall contact the Reliability Coordinator in whose area the operational concern was observed. The two Reliability Coordinators shall coordinate any actions, including emergency assistance, required to mitigate the operational concern. |  | 2006-08-01 | [17 empty] | RC
Inactive | IRO | IRO-003-0 | R3. | Each Reliability Coordinator shall know the current status of all critical facilities whose failure, degradation or disconnection could result in an SOL or IROL violation. Reliability Coordinators shall also know the status of any facilities that may be required to assist area restoration objectives. |  | 2006-08-01 | [17 empty] | RC
Inactive | IRO | IRO-003-1 | R1. | Each Reliability Coordinator shall monitor all Bulk Electric System facilities, which may include sub-transmission information, within its Reliability Coordinator Area and adjacent Reliability Coordinator Areas, as necessary to ensure that, at any time, regardless of prior planned or unplanned events, the Reliability Coordinator is able to determine any potential System Operating Limit and Interconnection Reliability Operating Limit violations within its Reliability Coordinator Area. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-003-1 | R2. | Each Reliability Coordinator shall know the current status of all critical facilities whose failure, degradation or disconnection could result in an SOL or IROL violation. Reliability Coordinators shall also know the status of any facilities that may be required to assist area restoration objectives. |  | 2007-01-01 | [17 empty] | RC
Inactive | IRO | IRO-003-2 | R1. | Each Reliability Coordinator shall monitor all Bulk Electric System facilities, which may include sub-transmission information, within its Reliability Coordinator Area and adjacent Reliability Coordinator Areas, as necessary to ensure that, at any time, regardless of prior planned or unplanned events, the Reliability Coordinator is able to determine any potential System Operating Limit and Interconnection Reliability Operating Limit violations within its Reliability Coordinator Area. | 2007-06-18 | 2017-03-31 | High | [16 empty] | RC
Inactive | IRO | IRO-003-2 | R2. | Each Reliability Coordinator shall know the current status of all critical facilities whose failure, degradation or disconnection could result in an SOL or IROL violation. Reliability Coordinators shall also know the status of any facilities that may be required to assist area restoration objectives. | 2007-06-18 | 2017-03-31 | High | [16 empty] | RC
Inactive | IRO | IRO-004-0 | R1. | Each Reliability Coordinator shall conduct next-day reliability analyses for its Reliability Coordinator Area to ensure that the Bulk Electric System can be operated reliably in anticipated normal and Contingency event conditions. The Reliability Coordinator shall conduct Contingency analysis studies to identify potential interface and other SOL and IROL violations, including overloaded transmission lines and transformers, voltage and stability limits, etc. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-004-0 | R2. | Each Reliability Coordinator shall pay particular attention to parallel flows to ensure one Reliability Coordinator Area does not place an unacceptable or undue Burden on an adjacent Reliability Coordinator Area. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-004-0 | R3. | Each Reliability Coordinator shall, in conjunction with its Transmission Operators and Balancing Authorities, develop action plans that may be required, including reconfiguration of the transmission system, re-dispatching of generation, reduction or curtailment of Interchange Transactions, or reducing load to return transmission loading to within acceptable SOLs or IROLs. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-004-0 | R4. | Each Transmission Operator, Balancing Authority, Transmission Owner, Generator Owner, Generator Operator, and Load-Serving Entity in the Reliability Coordinator Area shall provide information required for system studies, such as critical facility status, Load, generation, operating reserve projections, and known Interchange Transactions. This information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. |  | 2006-11-01 | [6 empty] | BA |  |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | IRO | IRO-004-0 | R5. | Each Reliability Coordinator shall share the results of its system studies, when conditions warrant or upon request, with other Reliability Coordinators and with Transmission Operators, Balancing Authorities, and Transmission Service Providers within its Reliability Coordinator Area. The Reliability Coordinator shall make study results available no later than 1500 Central Standard Time for the Eastern Interconnection and 1500 Pacific Standard Time for the Western Interconnection, unless circumstances warrant otherwise. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-004-0 | R6. | When conditions warrant, the Reliability Coordinator shall initiate a conference call or other appropriate communications to address the results of its reliability analyses. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-004-0 | R7. | If the results of these studies indicate potential SOL or IROL violations, the Reliability Coordinator shall issue the appropriate alerts via the Reliability Coordinator Information System (RCIS) and direct its Transmission Operators, Balancing Authorities and Transmission Service Providers to take any necessary action the Reliability Coordinator deems appropriate to address the potential SOL or IROL violation. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-004-0 | R8. | Each Transmission Operator, Balancing Authority, and Transmission Service Provider shall comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events. |  | 2006-11-01 | [6 empty] | BA | [17 empty] | TOP |  | TSP
Inactive | IRO | IRO-004-1 | R1. | Each Reliability Coordinator shall conduct next-day reliability analyses for its Reliability Coordinator Area to ensure that the Bulk Electric System can be operated reliably in anticipated normal and Contingency event conditions. The Reliability Coordinator shall conduct Contingency analysis studies to identify potential interface and other SOL and IROL violations, including overloaded transmission lines and transformers, voltage and stability limits, etc. | 2007-06-18 | 2011-09-30 | High | The Reliability Coordinator failed to conduct next-day reliability analyses or contingency analysis for its Reliability Coordinator Area for one (1) day during a calendar month. | The Reliability Coordinator failed to conduct next-day reliability analyses or contingency analysis for its Reliability Coordinator Area for two (2) to three (3) days during a calendar month. | The Reliability Coordinator failed to conduct next-day reliability analyses or contingency analysis for its Reliability Coordinator Area for four (4) to five (5) days during a calendar month. | The Reliability Coordinator failed to conduct next-day reliability analyses or contingency analysis for its Reliability Coordinator Area for more than five (5) days during a calendar month. | [12 empty] | RC
Inactive | IRO | IRO-004-1 | R2. | Each Reliability Coordinator shall pay particular attention to parallel flows to ensure one Reliability Coordinator Area does not place an unacceptable or undue Burden on an adjacent Reliability Coordinator Area. | 2007-06-18 | 2011-09-30 | High |  |  |  | The Reliability Coordinator failed to monitor parallel flows to ensure one Reliability Coordinator Area does not place an unacceptable or undue Burden on an adjacent Reliability Coordinator Area. | [12 empty] | RC
Inactive | IRO | IRO-004-1 | R3. | Each Reliability Coordinator shall, in conjunction with its Transmission Operators and Balancing Authorities, develop action plans that may be required, including reconfiguration of the transmission system, re-dispatching of generation, reduction or curtailment of Interchange Transactions, or reducing load to return transmission loading to within acceptable SOLs or IROLs. | 2007-06-18 | 2011-09-30 | High | The Reliability Coordinator, in conjunction with its Transmission Operators and Balancing Authorities, failed to develop action plans that may be required, including reconfiguration of the transmission system, re-dispatching of generation, reduction or cu | The Reliability Coordinator, in conjunction with its Transmission Operators and Balancing Authorities, failed to develop action plans that may be required, including reconfiguration of the transmission system, re-dispatching of generation, reduction or cu | The Reliability Coordinator, in conjunction with its Transmission Operators and Balancing Authorities, failed to develop action plans that may be required, including reconfiguration of the transmission system, re-dispatching of generation, reduction or cu | The Reliability Coordinator, in conjunction with its Transmission Operators and Balancing Authorities, failed to develop action plans that may be required, including reconfiguration of the transmission system, re-dispatching of generation, reduction or cu | [12 empty] | RC
Inactive | IRO | IRO-004-1 | R4. | Each Transmission Operator, Balancing Authority, Transmission Owner, Generator Owner, Generator Operator, and Load-Serving Entity in the Reliability Coordinator Area shall provide information required for system studies, such as critical facility status, Load, generation, operating reserve projections, and known Interchange Transactions. This information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. | 2007-06-18 | 2011-09-30 | High | The responsible entity in the Reliability Coordinator Area provided the information required for system studies, such as critical facility status, Load, generation, operating reserve projections, and known Interchange Transactions, but said information wa | The responsible entity in the Reliability Coordinator Area provided the information required for system studies, such as critical facility status, Load, generation, operating reserve projections, and known Interchange Transactions, but said information wa | The responsible entity in the Reliability Coordinator Area provided the information required for system studies, such as critical facility status, Load, generation, operating reserve projections, and known Interchange Transactions, but said information wa | The responsible entity in the Reliability Coordinator Area provided the information required for system studies, such as critical facility status, Load, generation, operating reserve projections, and known Interchange Transactions, but said information wa |  | BA |  |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP
Inactive | IRO | IRO-004-1 | R5. | Each Reliability Coordinator shall share the results of its system studies, when conditions warrant or upon request, with other Reliability Coordinators and with Transmission Operators, Balancing Authorities, and Transmission Service Providers within its Reliability Coordinator Area. The Reliability Coordinator shall make study results available no later than 1500 Central Standard Time for the Eastern Interconnection and 1500 Pacific Standard Time for the Western Interconnection, unless circumstances warrant otherwise. | 2007-06-18 | 2011-09-30 | High | The Reliability Coordinator failed to share the results of its system studies, when conditions warranted or was requested, with other Reliability Coordinators and with Transmission Operators, Balancing Authorities, and Transmission Service Providers withi | The Reliability Coordinator failed to share the results of its system studies, when conditions warranted or was requested, with other Reliability Coordinators and with Transmission Operators, Balancing Authorities, and Transmission Service Providers withi | The Reliability Coordinator failed to share the results of its system studies, when conditions warranted or was requested, with other Reliability Coordinators and with Transmission Operators, Balancing Authorities, and Transmission Service Providers withi | The Reliability Coordinator failed to share the results of its system studies, when conditions warranted or was requested, with other Reliability Coordinators and with Transmission Operators, Balancing Authorities, and Transmission Service Providers withi | [12 empty] | RC
Inactive | IRO | IRO-004-1 | R6. | If the results of these studies indicate potential SOL or IROL violations, the Reliability Coordinator shall direct its Transmission Operators, Balancing Authorities and Transmission Service Providers to take any necessary action the Reliability Coordinator deems appropriate to address the potential SOL or IROL violation. | 2007-06-18 | 2011-09-30 | High | The Reliability Coordinator failed to direct action to address a potential SOL or IROL violation on one (1) occasion during a calendar month. | The Reliability Coordinator failed to direct action to address a potential SOL or IROL violation on two (2) to three (3) occasions during a calendar month. | The reliability Coordinator failed to direct action to address a potential SOL or IROL violation on four (4) to five (5) occasions during a calendar month. | The Reliability Coordinator failed to direct action to address a potential SOL or IROL violation on more than five (5) occasions during a calendar month. | [12 empty] | RC
Inactive | IRO | IRO-004-1 | R7. | Each Transmission Operator, Balancing Authority, and Transmission Service Provider shall comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events. | 2007-06-18 | 2011-09-30 | High | The responsible entity failed to comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events on one (1) occasion during a calendar month. | The responsible entity failed to comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events on two (2) to three (3) occasions during a calendar | The responsible entity failed to comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events on four (4) to five (5) occasions during a calendar | The responsible entity failed to comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events on more than five (5) occasions during a calendar mo |  | BA | [17 empty] | TOP |  | TSP
Inactive | IRO | IRO-004-2 | R1. | Each Transmission Operator, Balancing Authority, and Transmission Service Provider shall comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events. | 2011-10-01 | 2017-03-31 | High | The responsible entity failed to comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events on one (1) occasion during a calendar month. | The responsible entity failed to comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events on two (2) to three (3) occasions during a calendar month. | The responsible entity failed to comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events on four (4) to five (5) occasions during a calendar month. | The responsible entity failed to comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events on more than five (5) occasions during a calendar month. |  | BA | [17 empty] | TOP |  | TSP
Inactive | IRO | IRO-005-0 | R1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-0 | R2. | Each Reliability Coordinator shall be aware of all Interchange Transactions that wheel through, source, or sink in its Reliability Coordinator Area, and make that Interchange Transaction information available to all Reliability Coordinators in the Interconnection. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-0 | R3. | As portions of the transmission system approach or exceed SOLs or IROLs, the Reliability Coordinator shall work with its Transmission Operators and Balancing Authorities to evaluate and assess any additional Interchange Schedules that would violate those limits. If a potential or actual IROL violation cannot be avoided through proactive intervention, the Reliability Coordinator shall initiate control actions or emergency procedures to relieve the violation without delay, and no longer than 30 minutes. The Reliability Coordinator shall ensure all resources, including load shedding, are available to address a potential or actual IROL violation. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-0 | R4. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-0 | R5. | Each Reliability Coordinator shall identify the cause of any potential or actual SOL or IROL violations. The Reliability Coordinator shall initiate the control action or emergency procedure to relieve the potential or actual IROL violation without delay, and no longer than 30 minutes. The Reliability Coordinator shall be able to utilize all resources, including load shedding, to address an IROL violation. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-0 | R6. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-0 | R7. | The Reliability Coordinator shall participate in NERC hotline discussions, assist in the assessment of reliability of the overall interconnected system, and coordinate actions in anticipated or actual emergency situations. The Reliability Coordinator shall disseminate such information within its Reliability Coordinator Area, as required. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-0 | R8. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-0 | R9. | The Reliability Coordinator shall coordinate with other Reliability Coordinators and Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with other Reliability Coordinators and Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-0 | R10. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-0 | R11. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. If a Frequency Error, Time Error, or inadvertent problem occurs outside of the Reliability Coordinator Area, the Reliability Coordinator shall initiate a NERC hotline call to discuss the Frequency Error, Time Error, or Inadvertent Interchange with other Reliability Coordinators. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-0 | R12. | Whenever a Special Protection System that may have an inter-Balancing Authority, interTransmission Operator, or inter-Reliability Coordinator Area impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. |  | 2006-11-01 | [6 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005-0 | R13. | Each Reliability Coordinator shall ensure that all Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities operate to prevent the likelihood that a disturbance, action, or nonaction in its Reliability Coordinator Area will result in a SOL or IROL violation in another area of the Interconnection. In instances where there is a difference in derived limits, the Reliability Coordinator and its Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-0 | R14. | Each Reliability Coordinator shall make known to Transmission Service Providers within its Reliability Coordinator Area, SOLs or IROLs within its wide-area view. The Transmission Service Providers shall respect these SOLs or IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-0 | R15. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area, and all impacted Reliability Coordinators within the Interconnection via the Reliability Coordinator Information System (RCIS) without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, and Reliability Coordinators when the transmission problem has been mitigated. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-0 | R16. | Each Reliability Coordinator shall confirm reliability assessment results and determine the effects within its own and adjacent Reliability Coordinator Areas. The Reliability Coordinator shall discuss options to mitigate potential or actual SOL or IROL violations and take actions as necessary to always act in the best interests of the Interconnection at all times. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-0 | R17. | When an IROL or SOL is exceeded, the Reliability Coordinator shall evaluate the local and wide-area impacts, both real-time and post-contingency, and determine if the actions being taken are appropriate and sufficient to return the system to within IROL in thirty minutes. If the actions being taken are not appropriate or sufficient, the Reliability Coordinator shall direct the Transmission Operator, Balancing Authority, Generator Operator, or Load-Serving Entity to return the system to within IROL or SOL. |  | 2006-11-01 | [17 empty] | RC
Inactive | IRO | IRO-005-1 | R1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: | 2007-06-18 | 2009-01-21 | High | The Reliability Coordinator failed to monitor one (1) of the elements listed in IRO-005-1 R1.1 through R1.10. | The Reliability Coordinator failed to monitor two (2) of the elements listed in IRO-005-1 R1.1 through R1.10. | The Reliability Coordinator failed to monitor three (3) of the elements listed in IRO-005-1 R1.1 through R1.10. | The Reliability Coordinator failed to monitor more than three (3) of the elements listed in IRO-005-1 R1.1 through R1.10. | [12 empty] | RC
Inactive | IRO | IRO-005-1 | R2. | Each Reliability Coordinator shall be aware of all Interchange Transactions that wheel through, source, or sink in its Reliability Coordinator Area, and make that Interchange Transaction information available to all Reliability Coordinators in the Interconnection. | 2007-06-18 | 2009-01-21 | High |  |  | The Reliability Coordinator was aware of all Interchange Transactions that wheeled through, sourced or sinked in its Reliability Coordinator Area, but failed to make that Interchange Transaction information available to all Reliability Coordinators in the | The Reliability Coordinator failed to be aware of all Interchange Transactions that wheeled through, sourced or sinked in its Reliability Coordinator Area, and failed to make that Interchange Transaction information available to all Reliability Coordinato | [12 empty] | RC
Inactive | IRO | IRO-005-1 | R3. | As portions of the transmission system approach or exceed SOLs or IROLs, the Reliability Coordinator shall work with its Transmission Operators and Balancing Authorities to evaluate and assess any additional Interchange Schedules that would violate those limits. If a potential or actual IROL violation cannot be avoided through proactive intervention, the Reliability Coordinator shall initiate control actions or emergency procedures to relieve the violation without delay, and no longer than 30 minutes. The Reliability Coordinator shall ensure all resources, including load shedding, are available to address a potential or actual IROL violation. | 2007-06-18 | 2009-01-21 | High |  | The Reliability Coordinator worked with its Transmission Operators and Balancing Authorities, as portions of the transmission system approached or exceeded SOLs or IROLs, to evaluate and assess any additional Interchange Schedules that would violate those | The Reliability Coordinator worked with its Transmission Operators and Balancing Authorities, as portions of the transmission system approached or exceeded SOLs or IROLs, to evaluate and assess any additional Interchange Schedules that would violate those | The Reliability Coordinator failed to work with its Transmission Operators and Balancing Authorities, as portions of the transmission system approached or exceeded SOLs or IROLs, to evaluate and assess any additional Interchange Schedules that would viola | [12 empty] | RC
Inactive | IRO | IRO-005-1 | R4. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | 2007-06-18 | 2009-01-21 | High |  | The Reliability Coordinator failed to direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. | The Reliability Coordinator failed to issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | The Reliability Coordinator failed to monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves was provided and available as required to meet the Control Performance Standard and Disturbance Control Standard r | [12 empty] | RC
Inactive | IRO | IRO-005-1 | R5. | Each Reliability Coordinator shall identify the cause of any potential or actual SOL or IROL violations. The Reliability Coordinator shall initiate the control action or emergency procedure to relieve the potential or actual IROL violation without delay, and no longer than 30 minutes. The Reliability Coordinator shall be able to utilize all resources, including load shedding, to address an IROL violation. | 2007-06-18 | 2009-01-21 | High |  |  | The Reliability Coordinator identified the cause of a potential or actual SOL or IROL violation, but failed to initiate a control action or emergency procedure to relieve the potential or actual IROL violation within 30 minutes. | The Reliability Coordinator failed to identify the cause of a potential or actual SOL or IROL violation and failed to initiate a control action or emergency procedure to relieve the potential or actual IROL violation. | [12 empty] | RC
Inactive | IRO | IRO-005-1 | R6. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. | 2007-06-18 | 2009-01-21 | High |  |  | The Reliability Coordinator ensured its Transmission Operators and Balancing Authorities were aware of Geo-Magnetic Disturbance (GMD) forecast information, but failed to assist, when needed, in the development of any required response plans. | The Reliability Coordinator failed to ensure its Transmission Operators and Balancing Authorities were aware of Geo-Magnetic Disturbance (GMD) forecast information. | [12 empty] | RC
Inactive | IRO | IRO-005-1 | R7. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. | 2007-06-18 | 2009-01-21 | High |  |  |  | The Reliability Coordinator failed to disseminate information within its Reliability Coordinator Area, when required. | [12 empty] | RC
Inactive | IRO | IRO-005-1 | R8. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. | 2007-06-18 | 2009-01-21 | High |  |  | The Reliability Coordinator monitored system frequency and its Balancing Authorities’ performance but failed to direct any necessary rebalancing to return to CPS and DCS compliance. | The Reliability Coordinator failed to monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance or the responsible entity failed to utilize all resources, including firm lo |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005-1 | R9. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real-time and next-day reliability analysis timeframes. | 2007-06-18 | 2009-01-21 | High |  | The Reliability Coordinator coordinated with Transmission Operators, Balancing Authorities, and Generator Operators, as needed, to develop action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations but failed to implement said plans, o | The Reliability Coordinator failed to coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations, or the Reliabil | The Reliability Coordinator failed to coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations and the Reliabil | [12 empty] | RC
Inactive | IRO | IRO-005-1 | R10. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. | 2007-06-18 | 2009-01-21 | High |  |  |  | The Reliability Coordinator failed to assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities, when necessary. | [12 empty] | RC
Inactive | IRO | IRO-005-1 | R11. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. | 2007-06-18 | 2009-01-21 | High |  | The Reliability Coordinator identified sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange and discussed corrective actions with the appropriate Balancing Authority but failed to direct th | The Reliability Coordinator identified sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange but failed to discuss corrective actions with the appropriate Balancing Authority. | The Reliability Coordinator failed to identify sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange. | [12 empty] | RC
Inactive | IRO | IRO-005-1 | R12. | Whenever a Special Protection System that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. | 2007-06-18 | 2009-01-21 | High |  |  |  | The Reliability Coordinator failed to be aware of the impact on inter-area flows of an inter-Balancing Authority or inter-Transmission Operator, following the operation of a Special Protection System that is armed (e.g., could potentially affect transmiss | [12 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005-1 | R13. | Each Reliability Coordinator shall ensure that all Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities operate to prevent the likelihood that a disturbance, action, or non-action in its Reliability Coordinator Area will result in a SOL or IROL violation in another area of the Interconnection. In instances where there is a difference in derived limits, the Reliability Coordinator and its Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. | 2007-06-18 | 2009-01-21 | High |  |  |  | The Reliability Coordinator failed to shall ensure that all Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities operated to prevent the likelihood that |  | BA |  |  |  |  | GOP |  | LSE |  |  | PSE | RC | [6 empty] | TOP |  | TSP
Inactive | IRO | IRO-005-1 | R14. | Each Reliability Coordinator shall make known to Transmission Service Providers within its Reliability Coordinator Area, SOLs or IROLs within its wide-area view. The Transmission Service Providers shall respect these SOLs or IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. | 2007-06-18 | 2009-01-21 | Medium |  |  |  | The Reliability Coordinator failed to make known to Transmission Service Providers within its Reliability Coordinator Area, SOLs or IROLs within its wide-area view, or the Transmission Service Providers failed to respect these SOLs or IROLs in accordance | [12 empty] | RC | [8 empty] | TSP
Inactive | IRO | IRO-005-1 | R15. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. | 2007-06-18 | 2009-01-21 | High |  | The Reliability Coordinator failed to notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem had been mitigated. |  | The Reliability Coordinator who foresaw a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area failed to issue an alert to all impacted Transmission Operators and Balancing Author | [12 empty] | RC
Inactive | IRO | IRO-005-1 | R16. | Each Reliability Coordinator shall confirm reliability assessment results and determine the effects within its own and adjacent Reliability Coordinator Areas. The Reliability Coordinator shall discuss options to mitigate potential or actual SOL or IROL violations and take actions as necessary to always act in the best interests of the Interconnection at all times. | 2007-06-18 | 2009-01-21 | High |  |  | The Reliability Coordinator confirmed the reliability assessment results and determine the effects within its own and adjacent Reliability Coordinator Areas and discussed options to mitigate potential or actual SOL or IROL violations, but failed to take a | The Reliability Coordinator failed to confirm reliability assessment results and determine the effects within its own and adjacent Reliability Coordinator Areas, or failed to discuss options to mitigate potential or actual SOL or IROL violations and take | [12 empty] | RC
Inactive | IRO | IRO-005-1 | R17. | When an IROL or SOL is exceeded, the Reliability Coordinator shall evaluate the local and wide-area impacts, both real-time and post-contingency, and determine if the actions being taken are appropriate and sufficient to return the system to within IROL in thirty minutes. If the actions being taken are not appropriate or sufficient, the Reliability Coordinator shall direct the Transmission Operator, Balancing Authority, Generator Operator, or Load-Serving Entity to return the system to within IROL or SOL. | 2007-06-18 | 2009-01-21 | High |  |  |  | The Reliability Coordinator either failed to evaluate the local and wide-area impacts of an IROL or SOL that was exceeded, in either real-time or post-contingency, or the Reliability Coordinator evaluated the local and wide-area impacts of an IROL or SOL | [12 empty] | RC
Inactive | IRO | IRO-005-2 | R1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: | 2009-01-22 | 2011-05-25 |  | The Reliability Coordinator failed to monitor one (1) of the elements listed in IRO-005-1 R1.1 through R1.10. | The Reliability Coordinator failed to monitor two (2) of the elements listed in IRO-005-1 R1.1 through R1.10. | The Reliability Coordinator failed to monitor three (3) of the elements listed in IRO-005-1 R1.1 through R1.10. | The Reliability Coordinator failed to monitor more than three (3) of the elements listed in IRO-005-1 R1.1 through R1.10. | [12 empty] | RC
Inactive | IRO | IRO-005-2 | R2. | Each Reliability Coordinator shall be aware of all Interchange Transactions that wheel through, source, or sink in its Reliability Coordinator Area, and make that Interchange Transaction information available to all Reliability Coordinators in the Interconnection. | 2009-01-22 | 2011-05-25 |  |  |  | The Reliability Coordinator was aware of all Interchange Transactions that wheeled through, sourced or sinked in its Reliability Coordinator Area, but failed to make that Interchange Transaction information available to all Reliability Coordinators in the | The Reliability Coordinator failed to be aware of all Interchange Transactions that wheeled through, sourced or sinked in its Reliability Coordinator Area, and failed to make that Interchange Transaction information available to all Reliability Coordinato | [12 empty] | RC
Inactive | IRO | IRO-005-2 | R3. | As portions of the transmission system approach or exceed SOLs or IROLs, the Reliability Coordinator shall work with its Transmission Operators and Balancing Authorities to evaluate and assess any additional Interchange Schedules that would violate those limits. If a potential or actual IROL violation cannot be avoided through proactive intervention, the Reliability Coordinator shall initiate control actions or emergency procedures to relieve the violation without delay, and no longer than 30 minutes. The Reliability Coordinator shall ensure all resources, including load shedding, are available to address a potential or actual IROL violation. | 2009-01-22 | 2011-05-25 |  |  | The Reliability Coordinator worked with its Transmission Operators and Balancing Authorities, as portions of the transmission system approached or exceeded SOLs or IROLs, to evaluate and assess any additional Interchange Schedules that would violate those | The Reliability Coordinator worked with its Transmission Operators and Balancing Authorities, as portions of the transmission system approached or exceeded SOLs or IROLs, to evaluate and assess any additional Interchange Schedules that would violate those | The Reliability Coordinator failed to work with its Transmission Operators and Balancing Authorities, as portions of the transmission system approached or exceeded SOLs or IROLs, to evaluate and assess any additional Interchange Schedules that would viola | [12 empty] | RC
Inactive | IRO | IRO-005-2 | R4. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | 2009-01-22 | 2011-05-25 |  |  | The Reliability Coordinator failed to direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. | The Reliability Coordinator failed to issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | The Reliability Coordinator failed to monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves was provided and available as required to meet the Control Performance Standard and Disturbance Control Standard r | [12 empty] | RC
Inactive | IRO | IRO-005-2 | R5. | Each Reliability Coordinator shall identify the cause of any potential or actual SOL or IROL violations. The Reliability Coordinator shall initiate the control action or emergency procedure to relieve the potential or actual IROL violation without delay, and no longer than 30 minutes. The Reliability Coordinator shall be able to utilize all resources, including load shedding, to address an IROL violation. | 2009-01-22 | 2011-05-25 |  |  |  | The Reliability Coordinator identified the cause of a potential or actual SOL or IROL violation, but failed to initiate a control action or emergency procedure to relieve the potential or actual IROL violation within 30 minutes. | The Reliability Coordinator failed to identify the cause of a potential or actual SOL or IROL violation and failed to initiate a control action or emergency procedure to relieve the potential or actual IROL violation. | [12 empty] | RC
Inactive | IRO | IRO-005-2 | R6. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. | 2009-01-22 | 2011-05-25 |  |  |  | The Reliability Coordinator ensured its Transmission Operators and Balancing Authorities were aware of Geo-Magnetic Disturbance (GMD) forecast information, but failed to assist, when needed, in the development of any required response plans. | The Reliability Coordinator failed to ensure its Transmission Operators and Balancing Authorities were aware of Geo-Magnetic Disturbance (GMD) forecast information. | [12 empty] | RC
Inactive | IRO | IRO-005-2 | R7. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. | 2009-01-22 | 2011-05-25 |  |  |  |  | The Reliability Coordinator failed to disseminate information within its Reliability Coordinator Area, when required. | [12 empty] | RC
Inactive | IRO | IRO-005-2 | R8. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. | 2009-01-22 | 2011-05-25 |  |  |  | The Reliability Coordinator monitored system frequency and its Balancing Authorities’ performance but failed to direct any necessary rebalancing to return to CPS and DCS compliance. | The Reliability Coordinator failed to monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance or the responsible entity failed to utilize all resources, including firm lo |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005-2 | R9. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. | 2009-01-22 | 2011-05-25 |  |  | The Reliability Coordinator coordinated with Transmission Operators, Balancing Authorities, and Generator Operators, as needed, to develop action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations but failed to implement said plans, o | The Reliability Coordinator failed to coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations, or the Reliabil | The Reliability Coordinator failed to coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations and the Reliabil | [12 empty] | RC
Inactive | IRO | IRO-005-2 | R10. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. | 2009-01-22 | 2011-05-25 |  |  |  |  | The Reliability Coordinator failed to assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities, when necessary. | [12 empty] | RC
Inactive | IRO | IRO-005-2 | R11. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. | 2009-01-22 | 2011-05-25 |  |  | The Reliability Coordinator identified sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange and discussed corrective actions with the appropriate Balancing Authority but failed to direct th | The Reliability Coordinator identified sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange but failed to discuss corrective actions with the appropriate Balancing Authority. | The Reliability Coordinator failed to identify sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange. | [12 empty] | RC
Inactive | IRO | IRO-005-2 | R12. | Whenever a Special Protection System that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. | 2009-01-22 | 2011-05-25 |  |  |  |  | The Reliability Coordinator failed to be aware of the impact on inter-area flows of an inter-Balancing Authority or inter-Transmission Operator, following the operation of a Special Protection System that is armed (e.g., could potentially affect transmiss | [12 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005-2 | R13. | Each Reliability Coordinator shall ensure that all Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities operate to prevent the likelihood that a disturbance, action, or nonaction in its Reliability Coordinator Area will result in a SOL or IROL violation in another area of the Interconnection. In instances where there is a difference in derived limits, the Reliability Coordinator and its Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. | 2009-01-22 | 2011-05-25 |  |  |  |  | The Reliability Coordinator failed to shall ensure that all Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities operated to prevent the likelihood that |  | BA |  |  |  |  | GOP |  | LSE |  |  | PSE | RC | [6 empty] | TOP |  | TSP
Inactive | IRO | IRO-005-2 | R14. | Each Reliability Coordinator shall make known to Transmission Service Providers within its Reliability Coordinator Area, SOLs or IROLs within its wide-area view. The Transmission Service Providers shall respect these SOLs or IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. | 2009-01-22 | 2011-05-25 |  |  |  |  | The Reliability Coordinator failed to make known to Transmission Service Providers within its Reliability Coordinator Area, SOLs or IROLs within its wide-area view, or the Transmission Service Providers failed to respect these SOLs or IROLs in accordance | [12 empty] | RC | [8 empty] | TSP
Inactive | IRO | IRO-005-2 | R15. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. | 2009-01-22 | 2011-05-25 |  |  | The Reliability Coordinator failed to notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem had been mitigated. |  | The Reliability Coordinator who foresaw a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area failed to issue an alert to all impacted Transmission Operators and Balancing Author | [12 empty] | RC
Inactive | IRO | IRO-005-2 | R16. | Each Reliability Coordinator shall confirm reliability assessment results and determine the effects within its own and adjacent Reliability Coordinator Areas. The Reliability Coordinator shall discuss options to mitigate potential or actual SOL or IROL violations and take actions as necessary to always act in the best interests of the Interconnection at all times. | 2009-01-22 | 2011-05-25 |  |  |  | The Reliability Coordinator confirmed the reliability assessment results and determine the effects within its own and adjacent Reliability Coordinator Areas and discussed options to mitigate potential or actual SOL or IROL violations, but failed to take a | The Reliability Coordinator failed to confirm reliability assessment results and determine the effects within its own and adjacent Reliability Coordinator Areas, or failed to discuss options to mitigate potential or actual SOL or IROL violations and take | [12 empty] | RC
Inactive | IRO | IRO-005-2 | R17. | When an IROL or SOL is exceeded, the Reliability Coordinator shall evaluate the local and wide-area impacts, both real-time and post-contingency, and determine if the actions being taken are appropriate and sufficient to return the system to within IROL in thirty minutes. If the actions being taken are not appropriate or sufficient, the Reliability Coordinator shall direct the Transmission Operator, Balancing Authority, Generator Operator, or Load-Serving Entity to return the system to within IROL or SOL. | 2009-01-22 | 2011-05-25 |  |  |  |  | The Reliability Coordinator either failed to evaluate the local and wide-area impacts of an IROL or SOL that was exceeded, in either real-time or post-contingency, or the Reliability Coordinator evaluated the local and wide-area impacts of an IROL or SOL | [12 empty] | RC
Inactive | IRO | IRO-005-2a | R1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: | 2011-05-26 | 2011-09-30 | High | The Reliability Coordinator failed to monitor one (1) of the elements listed in IRO-005-2 R1.1 through R1.10. | The Reliability Coordinator failed to monitor two (2) of the elements listed in IRO-005-2 R1.1 through R1.10. | The Reliability Coordinator failed to monitor three (3) of the elements listed in IRO-005-2 R1.1 through R1.10. | The Reliability Coordinator failed to monitor more than three (3) of the elements listed in IRO-005-2 R1.1 through R1.10. | [12 empty] | RC
Inactive | IRO | IRO-005-2a | R2. | Each Reliability Coordinator shall be aware of all Interchange Transactions that wheel through, source, or sink in its Reliability Coordinator Area, and make that Interchange Transaction information available to all Reliability Coordinators in the Interconnection. | 2011-05-26 | 2011-09-30 | High | N/A | N/A | The Reliability Coordinator was aware of all Interchange Transactions that wheeled through, sourced or sinked in its Reliability Coordinator Area, but failed to make that Interchange Transaction information available to all Reliability Coordinators in the | The Reliability Coordinator failed to be aware of all Interchange Transactions that wheeled through, sourced or sinked in its Reliability Coordinator Area, and failed to make that Interchange Transaction information available to all Reliability Coordinato | [12 empty] | RC
Inactive | IRO | IRO-005-2a | R3. | As portions of the transmission system approach or exceed SOLs or IROLs, the Reliability Coordinator shall work with its Transmission Operators and Balancing Authorities to evaluate and assess any additional Interchange Schedules that would violate those | 2011-05-26 | 2011-09-30 | High | N/A | The Reliability Coordinator worked with its Transmission Operators and Balancing Authorities, as portions of the transmission system approached or exceeded SOLs or IROLs, to evaluate and assess any additional Interchange Schedules that would violate those | The Reliability Coordinator worked with its Transmission Operators and Balancing Authorities, as portions of the transmission system approached or exceeded SOLs or IROLs, to evaluate and assess any additional Interchange Schedules that would violate those | The Reliability Coordinator failed to work with its Transmission Operators and Balancing Authorities, as portions of the transmission system approached or exceeded SOLs or IROLs, to evaluate and assess any additional Interchange Schedules that would viola | [12 empty] | RC
Inactive | IRO | IRO-005-2a | R4. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | 2011-05-26 | 2011-09-30 | High | N/A | The Reliability Coordinator failed to direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. | The Reliability Coordinator failed to issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | The Reliability Coordinator failed to monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves was provided and available as required to meet the Control Performance Standard and Disturbance Control Standard r | [12 empty] | RC
Inactive | IRO | IRO-005-2a | R5. | Each Reliability Coordinator shall identify the cause of any potential or actual SOL or IROL violations. The Reliability Coordinator shall initiate the control action or emergency procedure to relieve the potential or actual IROL violation without delay, and no longer than 30 minutes. The Reliability Coordinator shall be able to utilize all resources, including load shedding, to address an IROL violation. | 2011-05-26 | 2011-09-30 | High | N/A | N/A | The Reliability Coordinator identified the cause of a potential or actual SOL or IROL violation, but failed to initiate a control action or emergency procedure to relieve the potential or actual IROL violation within 30 minutes. | The Reliability Coordinator failed to identify the cause of a potential or actual SOL or IROL violation and failed to initiate a control action or emergency procedure to relieve the potential or actual IROL violation. | [12 empty] | RC
Inactive | IRO | IRO-005-2a | R6. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. | 2011-05-26 | 2011-09-30 | High | N/A | N/A | The Reliability Coordinator ensured its Transmission Operators and Balancing Authorities were aware of Geo-Magnetic Disturbance (GMD) forecast information, but failed to assist, when needed, in the development of any required response plans. | The Reliability Coordinator failed to ensure its Transmission Operators and Balancing Authorities were aware of Geo-Magnetic Disturbance (GMD) forecast information. | [12 empty] | RC
Inactive | IRO | IRO-005-2a | R7. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. | 2011-05-26 | 2011-09-30 | High | N/A | N/A | N/A | The Reliability Coordinator failed to disseminate information within its Reliability Coordinator Area, when required. | [12 empty] | RC
Inactive | IRO | IRO-005-2a | R8. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. | 2011-05-26 | 2011-09-30 | High | N/A | N/A | The Reliability Coordinator monitored system frequency and its Balancing Authorities’ performance but failed to direct any necessary rebalancing to return to CPS and DCS compliance. | The Reliability Coordinator failed to monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance or the responsible entity failed to utilize all resources, including firm lo |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005-2a | R9. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. | 2011-05-26 | 2011-09-30 | High | N/A | The Reliability Coordinator coordinated with Transmission Operators, Balancing Authorities, and Generator Operators, as needed, to develop action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations but failed to implement said plans, o | The Reliability Coordinator failed to coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations, or the Reliabil | The Reliability Coordinator failed to coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, IROL, CPS, or DCS violations and the Reliabil | [12 empty] | RC
Inactive | IRO | IRO-005-2a | R10. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. | 2011-05-26 | 2011-09-30 | High | N/A | N/A | N/A | The Reliability Coordinator failed to assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities, when necessary. | [12 empty] | RC
Inactive | IRO | IRO-005-2a | R11. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. | 2011-05-26 | 2011-09-30 | High | N/A | The Reliability Coordinator identified sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange and discussed corrective actions with the appropriate Balancing Authority but failed to direct th | The Reliability Coordinator identified sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange but failed to discuss corrective actions with the appropriate Balancing Authority. | The Reliability Coordinator failed to identify sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange. | [12 empty] | RC
Inactive | IRO | IRO-005-2a | R12. | Whenever a Special Protection System that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. | 2011-05-26 | 2011-09-30 | High | N/A | N/A | N/A | The Reliability Coordinator failed to be aware of the impact on inter-area flows of an inter-Balancing Authority or inter-Transmission Operator, following the operation of a Special Protection System that is armed (e.g., could potentially affect transmiss | [12 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005-2a | R13. | Each Reliability Coordinator shall ensure that all Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities operate to prevent the likelihood that a disturbance, action, or non-action in its Reliability Coordinator Area will result in a SOL or IROL violation in another area of the Interconnection. In instances where there is a difference in derived limits, the Reliability Coordinator and its Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. | 2011-05-26 | 2011-09-30 | High | N/A | N/A | N/A | The Reliability Coordinator failed to shall ensure that all Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities operated to prevent the likelihood that |  | BA |  |  |  |  | GOP |  | LSE |  |  | PSE | RC | [6 empty] | TOP |  | TSP
Inactive | IRO | IRO-005-2a | R14. | Each Reliability Coordinator shall make known to Transmission Service Providers within its Reliability Coordinator Area, SOLs or IROLs within its wide-area view. The Transmission Service Providers shall respect these SOLs or IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. | 2011-05-26 | 2011-09-30 | Medium | N/A | N/A | N/A | The Reliability Coordinator failed to make known to Transmission Service Providers within its Reliability Coordinator Area, SOLs or IROLs within its wide-area view, or the Transmission Service Providers failed to respect these SOLs or IROLs in accordance | [12 empty] | RC | [8 empty] | TSP
Inactive | IRO | IRO-005-2a | R15. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. | 2011-05-26 | 2011-09-30 | High | N/A | The Reliability Coordinator failed to notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem had been mitigated. | N/A | The Reliability Coordinator who foresaw a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area failed to issue an alert to all impacted Transmission Operators and Balancing Author | [12 empty] | RC
Inactive | IRO | IRO-005-2a | R16. | Each Reliability Coordinator shall confirm reliability assessment results and determine the effects within its own and adjacent Reliability Coordinator Areas. The Reliability Coordinator shall discuss options to mitigate potential or actual SOL or IROL violations and take actions as necessary to always act in the best interests of the Interconnection at all times. | 2011-05-26 | 2011-09-30 | High | N/A | N/A | The Reliability Coordinator confirmed the reliability assessment results and determine the effects within its own and adjacent Reliability Coordinator Areas and discussed options to mitigate potential or actual SOL or IROL violations, but failed to take a | The Reliability Coordinator failed to confirm reliability assessment results and determine the effects within its own and adjacent Reliability Coordinator Areas, or failed to discuss options to mitigate potential or actual SOL or IROL violations and take | [12 empty] | RC
Inactive | IRO | IRO-005-2a | R17. | When an IROL or SOL is exceeded, the Reliability Coordinator shall evaluate the local and wide-area impacts, both real-time and post-contingency, and determine if the actions being taken are appropriate and sufficient to return the system to within IROL in thirty minutes. If the actions being taken are not appropriate or sufficient, the Reliability Coordinator shall direct the Transmission Operator, Balancing Authority, Generator Operator, or Load-Serving Entity to return the system to within IROL or SOL. | 2011-05-26 | 2011-09-30 | High | N/A | N/A | N/A | The Reliability Coordinator either failed to evaluate the local and wide-area impacts of an IROL or SOL that was exceeded, in either real-time or post-contingency, or the Reliability Coordinator evaluated the local and wide-area impacts of an IROL or SOL | [12 empty] | RC
Inactive | IRO | IRO-005-3 | R1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: |  | 2011-05-25 |  | The Reliability Coordinator failed to monitor one (1) of the elements listed in IRO005-1 R1.1 through R1.10. | The Reliability Coordinator failed to monitor two (2) of the elements listed in IRO005-1 R1.1 through R1.10. | The Reliability Coordinator failed to monitor three (3) of the elements listed in IRO005-1 R1.1 through R1.10. | The Reliability Coordinator failed to monitor more than three (3) of the elements listed in IRO-005-1 R1.1 through R1.10. | [12 empty] | RC
Inactive | IRO | IRO-005-3 | R2. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. |  | 2011-05-25 |  | N/A | The Reliability Coordinator failed to direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. | The Reliability Coordinator failed to issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | The Reliability Coordinator failed to monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves was provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. | [12 empty] | RC
Inactive | IRO | IRO-005-3 | R3. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. |  | 2011-05-25 |  | N/A | N/A | The Reliability Coordinator ensured its Transmission Operators and Balancing Authorities were aware of Geo-Magnetic Disturbance (GMD) forecast information, but failed to assist, when needed, in the development of any required response plans. | The Reliability Coordinator failed to ensure its Transmission Operators and Balancing Authorities were aware of Geo-Magnetic Disturbance (GMD) forecast information. | [12 empty] | RC
Inactive | IRO | IRO-005-3 | R4. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. |  | 2011-05-25 |  | N/A | N/A | N/A | The Reliability Coordinator failed to disseminate information within itsReliability Coordinator Area, when required. | [12 empty] | RC
Inactive | IRO | IRO-005-3 | R5. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. |  | 2011-05-25 |  | N/A | N/A | The Reliability Coordinator monitored system frequency and its Balancing Authorities’ performance but failed to direct any necessary rebalancing to return to CPS and DCS compliance. | The Reliability Coordinator failed to monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance or the responsible entity failed to utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005-3 | R6. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. |  | 2011-05-25 |  | N/A | The Reliability Coordinator coordinated with Transmission Operators, Balancing Authorities, and Generator Operators, as needed, to develop action plans to mitigate potential or actual SOL, CPS, or DCS violations but failed to implement said plans, or the Reliability Coordinator coordinated pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in the real-time reliability analysis timeframe but failed to coordinate pending generation and transmission maintenance outages in the next-day reliability analysis timeframe. | The Reliability Coordinator failed to coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations, or the Reliability Coordinator failed to coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real-time and next-day reliability analysis timeframes. | The Reliability Coordinator failed to coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations and the Reliability Coordinator failed to coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real-time and next-day reliability analysis timeframes. | [12 empty] | RC
Inactive | IRO | IRO-005-3 | R7. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. |  | 2011-05-25 |  | N/A | N/A | N/A | The Reliability Coordinator failed to assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities, when necessary. | [12 empty] | RC
Inactive | IRO | IRO-005-3 | R8. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. |  | 2011-05-25 |  | N/A | The Reliability Coordinator identified sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange and discussed corrective actions with the appropriate Balancing Authority but failed to direct the Balancing Authority to comply with CPS and DCS. | The Reliability Coordinator identified sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange but failed to discuss corrective actions with the appropriate Balancing Authority. | The Reliability Coordinator failed to identify sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange. | [12 empty] | RC
Inactive | IRO | IRO-005-3 | R9. | Whenever a Special Protection System that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. |  | 2011-05-25 |  | N/A | N/A | N/A | The Reliability Coordinator failed to be aware of the impact on inter-area flows of an inter-Balancing Authority or inter-Transmission Operator, following the operation of a Special Protection System that is armed (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation), or the Transmission Operator failed to immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. | [12 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005-3 | R10. | In instances where there is a difference in derived limits, the Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. |  | 2011-05-25 |  | N/A | N/A | N/A | The responsible entity failed to operate the Bulk Electric System to the most limiting parameter in instances where there was a difference in derived limits. |  | BA |  |  |  |  | GOP |  | LSE |  |  | PSE | [7 empty] | TOP |  | TSP
Inactive | IRO | IRO-005-3 | R11. | The Transmission Service Provider shall respect SOLs and IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. |  | 2011-05-25 |  | N/A | N/A | N/A | The Transmission Service Provider failed to respect SOLs or IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. | [21 empty] | TSP
Inactive | IRO | IRO-005-3 | R12. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. |  | 2011-05-25 |  | N/A | The Reliability Coordinator failed to notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem had been mitigated. | N/A | The Reliability Coordinator who foresaw a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area failed to issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area, or the receiving Reliability Coordinator failed to disseminate this information to its impacted Transmission Operators and Balancing Authorities. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1a | R1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: | 2012-09-13 | 2017-03-31 |  | The Reliability Coordinator failed to monitor one (1) of the elements listed in IRO005-1 R1.1 through R1.10. | The Reliability Coordinator failed to monitor two (2) of the elements listed in IRO005-1 R1.1 through R1.10. | The Reliability Coordinator failed to monitor three (3) of the elements listed in IRO005-1 R1.1 through R1.10 | The Reliability Coordinator failed to monitor more than three (3) of the elements listed in IRO-005-1 R1.1 through R1.10. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1a | R2. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | 2012-09-13 | 2017-03-31 |  | N/A | The Reliability Coordinator failed to direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. | The Reliability Coordinator failed to issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | The Reliability Coordinator failed to monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves was provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1a | R3. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. | 2012-09-13 | 2017-03-31 |  | N/A | N/A | The Reliability Coordinator ensured its Transmission Operators and Balancing Authorities were aware of Geo-Magnetic Disturbance (GMD) forecast information, but failed to assist, when needed, in the development of any required response plans. | The Reliability Coordinator failed to ensure its Transmission Operators and Balancing Authorities were aware of Geo-Magnetic Disturbance (GMD) forecast information. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1a | R4. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. | 2012-09-13 | 2017-03-31 |  | N/A | N/A | N/A | The Reliability Coordinator failed to disseminate information within its Reliability Coordinator Area, when required. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1a | R5. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. | 2012-09-13 | 2017-03-31 |  | N/A | N/A | The Reliability Coordinator monitored system frequency and its Balancing Authorities’ performance but failed to direct any necessary rebalancing to return to CPS and DCS compliance. | The Reliability Coordinator failed to monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance or the responsible entity failed to utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005-3.1a | R6. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. | 2012-09-13 | 2017-03-31 |  | N/A | The Reliability Coordinator coordinated with Transmission Operators, Balancing Authorities, and Generator Operators, as needed, to develop action plans to mitigate potential or actual SOL, CPS, or DCS violations but failed to implement said plans. OR The Reliability Coordinator failed to coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in either the real-time reliability analysis time frame or the next-day reliability analysis time frame. | The Reliability Coordinator failed to coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations. OR The Reliability Coordinator failed to coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real-time and next-day reliability analysis timeframes. | The Reliability Coordinator failed to coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations and the Reliability Coordinator failed to coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real-time and next-day reliability analysis timeframes. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1a | R7. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. | 2012-09-13 | 2017-03-31 |  | N/A | N/A | N/A | The Reliability Coordinator failed to assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities, when necessary. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1a | R8. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. | 2012-09-13 | 2017-03-31 |  | N/A | The Reliability Coordinator identified sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange and discussed corrective actions with the appropriate Balancing Authority but failed to direct the Balancing Authority to comply with CPS and DCS. | The Reliability Coordinator identified sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange but failed to discuss corrective actions with the appropriate Balancing Authority. | The Reliability Coordinator failed to identify sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1a | R9. | Whenever a Special Protection System that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. | 2012-09-13 | 2017-03-31 |  | N/A | N/A | N/A | The Reliability Coordinator failed to be aware of the impact on inter-area flows of an inter-Balancing Authority or inter-Transmission Operator, following the operation of a Special Protection System that is armed (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation), or the Transmission Operator failed to immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. | [12 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005-3.1a | R10. | In instances where there is a difference in derived limits, the Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. | 2012-09-13 | 2017-03-31 |  | N/A | N/A | N/A | The responsible entity failed to operate the Bulk Electric System to the most limiting parameter in instances where there was a difference in derived limits. |  | BA |  |  |  |  | GOP |  | LSE |  |  | PSE | [7 empty] | TOP |  | TSP
Inactive | IRO | IRO-005-3.1a | R11. | The Transmission Service Provider shall respect SOLs and IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. | 2012-09-13 | 2017-03-31 |  | N/A | N/A | N/A | The Transmission Service Provider failed to respect SOLs or IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. | [21 empty] | TSP
Inactive | IRO | IRO-005-3.1a | R12. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. | 2012-09-13 | 2017-03-31 |  | N/A | The Reliability Coordinator failed to notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem had been mitigated. | N/A | The Reliability Coordinator who foresaw a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area failed to issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area, or the receiving Reliability Coordinator failed to disseminate this information to its impacted Transmission Operators and Balancing Authorities. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1(i)a | R1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: |  | 2014-11-13 |  | The Reliability Coordinator failed to monitor one (1) of the elements listed in IRO-005-3.1(i)a R1.1 through R1.10. | The Reliability Coordinator failed to monitor two (2) of the elements listed in IRO-005-3.1(i)a R1.1 through R1.10. | The Reliability Coordinator failed to monitor three (3) of the elements listed in IRO-005-3.1(i)a R1.1 through R1.10. | The Reliability Coordinator failed to monitor more than three (3) of the elements listed in IRO-005-3.1(i)a R1.1 through R1.10. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1(i)a | R2. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. |  | 2014-11-13 |  |  | The Reliability Coordinator failed to direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. | The Reliability Coordinator failed to issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | The Reliability Coordinator failed to monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves was provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1(i)a | R3. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. |  | 2014-11-13 |  |  |  | The Reliability Coordinator ensured its Transmission Operators and Balancing Authorities were aware of Geo-Magnetic Disturbance (GMD) forecast information, but failed to assist, when needed, in the development of any required response plans. | The Reliability Coordinator failed to ensure its Transmission Operators and Balancing Authorities were aware of Geo-Magnetic Disturbance (GMD) forecast information. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1(i)a | R4. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. |  | 2014-11-13 |  |  |  |  | The Reliability Coordinator failed to disseminate information within its Reliability Coordinator Area, when required. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1(i)a | R5. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. |  | 2014-11-13 |  |  |  | The Reliability Coordinator monitored system frequency and its Balancing Authorities’ performance but failed to direct any necessary rebalancing to return to CPS and DCS compliance. | The Reliability Coordinator failed to monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance or the responsible entity failed to utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1(i)a | R6. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. |  | 2014-11-13 |  |  | The Reliability Coordinator coordinated with Transmission Operators, Balancing Authorities, and Generator Operators, as needed, to develop action plans to mitigate potential or actual SOL, CPS, or DCS violations but failed to implement said plans. OR The Reliability Coordinator failed to coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in either the real- time reliability analysis time frame or the next-day reliability analysis. | The Reliability Coordinator failed to coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations. OR The Reliability Coordinator failed to coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real- time and next-day reliability analysis timeframes. | The Reliability Coordinator failed to coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations and the Reliability Coordinator failed to coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real- time and next-day reliability analysis timeframes. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1(i)a | R7. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. |  | 2014-11-13 |  |  |  |  | The Reliability Coordinator failed to assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities, when necessary. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1(i)a | R8. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. |  | 2014-11-13 |  |  | The Reliability Coordinator identified sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange and discussed corrective actions with the appropriate Balancing Authority but failed to direct the Balancing Authority to comply with CPS and DCS. | The Reliability Coordinator identified sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange but failed to discuss corrective actions with the appropriate Balancing Authority. | The Reliability Coordinator failed to identify sources of large Area Control Errors that were contributing to Frequency Error, Time Error, or Inadvertent Interchange. | [12 empty] | RC
Inactive | IRO | IRO-005-3.1(i)a | R9. | Whenever a Remedial Action Scheme that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Remedial Action Scheme on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Remedial Action Scheme including any degradation or potential failure to operate as expected. |  | 2014-11-13 |  |  |  |  | The Reliability Coordinator failed to be aware of the impact on inter-area flows of an inter-Balancing Authority or inter-Transmission Operator, following the operation of a Remedial Action Scheme that is armed (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation), or the Transmission Operator failed to immediately inform the Reliability Coordinator of the status of the Remedial Action Scheme including any degradation or potential failure to operate as expected. | [12 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005-3.1(i)a | R10. | In instances where there is a difference in derived limits, the Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. |  | 2014-11-13 |  |  |  |  | The responsible entity failed to operate the Bulk Electric System to the most limiting parameter in instances where there was a difference in derived limits. |  | BA |  |  |  |  | GOP |  | LSE |  |  | PSE | [7 empty] | TOP |  | TSP
Inactive | IRO | IRO-005-3.1(i)a | R11. | The Transmission Service Provider shall respect SOLs and IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. |  | 2014-11-13 |  |  |  |  | The Transmission Service Provider failed to respect SOLs or IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. | [21 empty] | TSP
Inactive | IRO | IRO-005-3.1(i)a | R12. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. |  | 2014-11-13 |  |  | The Reliability Coordinator failed to notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem had been mitigated. |  | The Reliability Coordinator who foresaw a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area failed to issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area, or the receiving Reliability Coordinator failed to disseminate this information to its impacted Transmission Operators and Balancing Authorities. | [12 empty] | RC
Inactive | IRO | IRO-005-3a | R1. | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: | 2011-10-01 | 2012-09-12 | [17 empty] | RC
Inactive | IRO | IRO-005-3a | R2. | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | 2011-10-01 | 2012-09-12 | [17 empty] | RC
Inactive | IRO | IRO-005-3a | R3. | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. | 2011-10-01 | 2012-09-12 | [17 empty] | RC
Inactive | IRO | IRO-005-3a | R4. | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. | 2011-10-01 | 2012-09-12 | [17 empty] | RC
Inactive | IRO | IRO-005-3a | R5. | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. | 2011-10-01 | 2012-09-12 | [6 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005-3a | R6. | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in both the real time and next-day reliability analysis timeframes. | 2011-10-01 | 2012-09-12 | [17 empty] | RC
Inactive | IRO | IRO-005-3a | R7. | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. | 2011-10-01 | 2012-09-12 | [17 empty] | RC
Inactive | IRO | IRO-005-3a | R8. | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. | 2011-10-01 | 2012-09-12 | [17 empty] | RC
Inactive | IRO | IRO-005-3a | R9. | Whenever a Special Protection System that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. | 2011-10-01 | 2012-09-12 | [17 empty] | RC | [6 empty] | TOP
Inactive | IRO | IRO-005-3a | R10. | In instances where there is a difference in derived limits, the Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. | 2011-10-01 | 2012-09-12 | [6 empty] | BA |  |  |  |  | GOP |  | LSE |  |  | PSE | [7 empty] | TOP |  | TSP
Inactive | IRO | IRO-005-3a | R11. | The Transmission Service Provider shall respect SOLs and IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. | 2011-10-01 | 2012-09-12 | [26 empty] | TSP
Inactive | IRO | IRO-005-3a | R12. | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. | 2011-10-01 | 2012-09-12 | [17 empty] | RC
Inactive | IRO | IRO-005-4 | R1. | When the results of an Operational Planning Analysis or Real-time Assessment indicate an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area, each Reliability Coordinator shall notify all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area. |  | 2016-01-26 | High | The Reliability Coordinator who identified an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area failed to issue an alert to one, but not all, impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area. | The Reliability Coordinator who identified an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area failed to issue an alert to two, but not all, impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area. | The Reliability Coordinator who identified an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area failed to issue an alert to three, but not all, impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area. | The Reliability Coordinator who identified an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area failed to issue an alert to more than three impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area (in cases where there are less than three impacted entities). | [12 empty] | RC
Inactive | IRO | IRO-005-4 | R2. | Each Reliability Coordinator that identifies an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area shall notify all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area when the problem has been mitigated. |  | 2016-01-26 | Medium | The Reliability Coordinator failed to notify one, but not all, impacted Transmission Operators, Balancing Authorities, when the transmission problem had been mitigated. | The Reliability Coordinator failed to notify two, but not all, impacted Transmission Operators, Balancing Authorities, when the transmission problem had been mitigated. | The Reliability Coordinator failed to notify three, but not all, impacted Transmission Operators, Balancing Authorities, when the transmission problem had been mitigated. | The Reliability Coordinator failed to notify more than three impacted Transmission Operators, Balancing Authorities, when the transmission problem had been mitigated. OR The Reliability Coordinator failed to notify more all impacted Transmission Operators, Balancing Authorities, when the transmission problem had been mitigated (in cases where there are less than three impacted entities). | [12 empty] | RC
Inactive | IRO | IRO-006-0 | R1. | A Reliability Coordinator shall take appropriate actions in accordance with established policies, procedures, authority, and expectations to relieve transmission loading. |  | 2005-08-08 | [17 empty] | RC
Inactive | IRO | IRO-006-0 | R2. | A Reliability Coordinator experiencing a potential or actual SOL or IROL violation within its Reliability Coordinator Area shall, at its discretion, select from either a “local” (Regional, Interregional, or subregional) transmission loading relief procedure or an Interconnection-wide procedure. |  | 2005-08-08 | [17 empty] | RC
Inactive | IRO | IRO-006-0 | R3. | The Reliability Coordinator may use local transmission loading relief or congestion management procedures, provided the Transmission Operator experiencing the potential or actual SOL or IROL violation is a party to those procedures. |  | 2005-08-08 | [17 empty] | RC
Inactive | IRO | IRO-006-0 | R4. | A Reliability Coordinator may implement a local transmission loading relief or congestion management procedure simultaneously with an Interconnection-wide procedure. However, the Reliability Coordinator shall follow the curtailments as directed by the Interconnection-wide procedure. A Reliability Coordinator desiring to use a local procedure as a substitute for curtailments as directed by the Interconnection-wide procedure shall have such use approved by the NERC Operating Committee. |  | 2005-08-08 | [17 empty] | RC
Inactive | IRO | IRO-006-0 | R5. | When implemented, all Reliability Coordinators shall comply with the provisions of the Interconnection-wide procedure including, for example, action by Reliability Coordinators in other Interconnections to curtail an Interchange Transaction that crosses an Interconnection boundary. |  | 2005-08-08 | [17 empty] | RC
Inactive | IRO | IRO-006-0 | R6. | During the implementation of relief procedures, and up to the point that emergency action is necessary, Reliability Coordinators and Balancing Authorities shall comply with interchange scheduling standards INT-001 through INT-004. |  | 2005-08-08 | [6 empty] | BA | [10 empty] | RC
Inactive | IRO | IRO-006-1 | R1. | A Reliability Coordinator shall take appropriate actions in accordance with established policies, procedures, authority, and expectations to relieve transmission loading. |  | 2006-09-29 | [17 empty] | RC
Inactive | IRO | IRO-006-1 | R2. | A Reliability Coordinator experiencing a potential or actual SOL or IROL violation within its Reliability Coordinator Area shall, at its discretion, select from either a “local” (Regional, Interregional, or subregional) transmission loading relief procedure or an Interconnection-wide procedure. |  | 2006-09-29 | [17 empty] | RC
Inactive | IRO | IRO-006-1 | R3. | The Reliability Coordinator may use local transmission loading relief or congestion management procedures, provided the Transmission Operator experiencing the potential or actual SOL or IROL violation is a party to those procedures. |  | 2006-09-29 | [17 empty] | RC
Inactive | IRO | IRO-006-1 | R4. | A Reliability Coordinator may implement a local transmission loading relief or congestion management procedure simultaneously with an Interconnection-wide procedure. However, the Reliability Coordinator shall follow the curtailments as directed by the Interconnection-wide procedure. A Reliability Coordinator desiring to use a local procedure as a substitute for curtailments as directed by the Interconnection-wide procedure shall have such use approved by the NERC Operating Committee. |  | 2006-09-29 | [17 empty] | RC
Inactive | IRO | IRO-006-1 | R5. | When implemented, all Reliability Coordinators shall comply with the provisions of the Interconnection-wide procedure including, for example, action by Reliability Coordinators in other Interconnections to curtail an Interchange Transaction that crosses an Interconnection boundary |  | 2006-09-29 | [17 empty] | RC
Inactive | IRO | IRO-006-1 | R6. | During the implementation of relief procedures, and up to the point that emergency action is necessary, Reliability Coordinators and Balancing Authorities shall comply with interchange scheduling standards INT-001 through INT-004. |  | 2006-09-29 | [6 empty] | BA | [10 empty] | RC
Inactive | IRO | IRO-006-2 | R1. | A Reliability Coordinator shall take appropriate actions in accordance with established policies, procedures, authority, and expectations to relieve transmission loading. |  | 2006-09-29 | [17 empty] | RC
Inactive | IRO | IRO-006-2 | R2. | A Reliability Coordinator experiencing a potential or actual SOL or IROL violation within its Reliability Coordinator Area shall, at its discretion, select from either a “local” (Regional, Interregional, or subregional) transmission loading relief procedure or an Interconnection-wide procedure. |  | 2006-09-29 | [17 empty] | RC
Inactive | IRO | IRO-006-2 | R3. | The Reliability Coordinator may use local transmission loading relief or congestion management procedures, provided the Transmission Operator experiencing the potential or actual SOL or IROL violation is a party to those procedures. |  | 2006-09-29 | [17 empty] | RC
Inactive | IRO | IRO-006-2 | R4. | A Reliability Coordinator may implement a local transmission loading relief or congestion management procedure simultaneously with an Interconnection-wide procedure. However, the Reliability Coordinator shall follow the curtailments as directed by the Interconnection-wide procedure. A Reliability Coordinator desiring to use a local procedure as a substitute for curtailments as directed by the Interconnection-wide procedure shall have such use approved by the NERC Operating Committee. |  | 2006-09-29 | [17 empty] | RC
Inactive | IRO | IRO-006-2 | R5. | When implemented, all Reliability Coordinators shall comply with the provisions of the Interconnection-wide procedure including, for example, action by Reliability Coordinators in other Interconnections to curtail an Interchange Transaction that crosses an Interconnection boundary. |  | 2006-09-29 | [17 empty] | RC
Inactive | IRO | IRO-006-2 | R6. | During the implementation of relief procedures, and up to the point that emergency action is necessary, Reliability Coordinators and Balancing Authorities shall comply with interchange scheduling standards INT-001 through INT-004. |  | 2006-09-29 | [6 empty] | BA | [10 empty] | RC
Inactive | IRO | IRO-006-3 | R1. | A Reliability Coordinator shall take appropriate actions in accordance with established policies, procedures, authority, and expectations to relieve transmission loading. | 2007-06-18 | 2009-04-22 | High |  |  |  | The Reliability Coordinator failed to take appropriate actions in accordance with established policies, procedures, authority, and expectations to relieve transmission loading. | [12 empty] | RC
Inactive | IRO | IRO-006-3 | R2. | A Reliability Coordinator experiencing a potential or actual SOL or IROL violation within its Reliability Coordinator Area shall, at its discretion, select from either a “local” (Regional, Interregional, or subregional) transmission loading relief procedure or an Interconnection-wide procedure. | 2007-06-18 | 2009-04-22 | High |  |  |  | The Reliability Coordinator experiencing a potential or actual SOL or IROL violation within its Reliability Coordinator Area failed to take actions based on either a “local” (Regional, Interregional, or subregional) transmission loading relief procedure o | [12 empty] | RC
Inactive | IRO | IRO-006-3 | R3. | The Reliability Coordinator may use local transmission loading relief or congestion management procedures, provided the Transmission Operator experiencing the potential or actual SOL or IROL violation is a party to those procedures. | 2007-06-18 | 2009-04-22 | High |  |  |  | The Reliability Coordinator used a local transmission loading relief or congestion management procedure when the Transmission Operator experiencing the potential or actual SOL or IROL violation was not a party to said procedures. | [12 empty] | RC
Inactive | IRO | IRO-006-3 | R4. | A Reliability Coordinator may implement a local transmission loading relief or congestion management procedure simultaneously with an Interconnection-wide procedure. However, the Reliability Coordinator shall follow the curtailments as directed by the Interconnection-wide procedure. A Reliability Coordinator desiring to use a local procedure as a substitute for curtailments as directed by the Interconnection-wide procedure shall have such use approved by the NERC Operating Committee. | 2007-06-18 | 2009-04-22 | High |  |  |  | A Reliability Coordinator implementing a local transmission loading relief or congestion management procedure simultaneously with an Interconnection-wide procedure failed to follow the curtailments as directed by the Interconnection-wide procedure, or the | [12 empty] | RC
Inactive | IRO | IRO-006-3 | R5. | When implemented, all Reliability Coordinators shall comply with the provisions of the Interconnection-wide procedure including, for example, action by Reliability Coordinators in other Interconnections to curtail an Interchange Transaction that crosses an Interconnection boundary. | 2007-06-18 | 2009-04-22 | High |  |  |  | The Reliability Coordinator failed to comply with the provisions of an Interconnection-wide procedure when the procedure was implemented. | [12 empty] | RC
Inactive | IRO | IRO-006-3 | R6. | During the implementation of relief procedures, and up to the point that emergency action is necessary, Reliability Coordinators and Balancing Authorities shall comply with interchange scheduling standards INT-001 through INT-004. | 2007-06-18 | 2009-04-22 | High |  | The applicable entity did not comply with one of the three required interchange scheduling standards (INT-001-2, INT-003-2 and INT-004-2). | The applicable entity did not comply with two of the three required interchange scheduling standards (INT-001-2, INT-003-2 and INT-004-2). | The applicable entity did not comply with any of the three required interchange scheduling standards (INT-001-2, INT-003-2 and INT-004-2). |  | BA | [10 empty] | RC
Inactive | IRO | IRO-006-4 | R1. | A Reliability Coordinator experiencing a potential or actual SOL or IROL violation within its Reliability Coordinator Area shall, with its authority and at its discretion, select one or more procedures to provide transmission loading relief. These procedures can be a ?local? (regional, interregional, or sub-regional) transmission loading relief procedure or one of the following Interconnection-wide procedures: [Time Horizon: Real-time Operations] | 2009-04-23 | 2009-12-09 | Medium | [16 empty] | RC
Inactive | IRO | IRO-006-4 | R2. | The Reliability Coordinator shall only use local transmission loading relief or congestion management procedures to which the Transmission Operator experiencing the potential or actual SOL or IROL violation is a party. [Time Horizon: Operations Planning] | 2009-04-23 | 2009-12-09 | Low | [16 empty] | RC
Inactive | IRO | IRO-006-4 | R3. | Each Reliability Coordinator with a relief obligation from an Interconnection-wide procedure shall follow the curtailments as directed by the Interconnection-wide procedure. A Reliability Coordinator desiring to use a local procedure as a substitute for curtailments as directed by the Interconnection-wide procedure shall obtain prior approval of the local procedure from the ERO. [Time Horizon: Operations Planning] | 2009-04-23 | 2009-12-09 | Low | [16 empty] | RC
Inactive | IRO | IRO-006-4 | R4. | When Interconnection-wide procedures are implemented to curtail Interchange Transactions that cross an Interconnection boundary, each Reliability Coordinator shall comply with the provisions of the Interconnection-wide procedure. [Time Horizon: Real-time Operations] | 2009-04-23 | 2009-12-09 | Medium | [16 empty] | RC
Inactive | IRO | IRO-006-4 | R5. | During the implementation of relief procedures, and up to the point that emergency action is necessary, Reliability Coordinators and Balancing Authorities shall comply with applicable Interchange scheduling standards. [Time Horizon: Real-time Operations] | 2009-04-23 | 2009-12-09 | Medium | [5 empty] | BA | [10 empty] | RC
Inactive | IRO | IRO-006-4.1 | R1. | A Reliability Coordinator experiencing a potential or actual SOL or IROL violation within its Reliability Coordinator Area shall, with its authority and at its discretion, select one or more procedures to provide transmission loading relief. These procedures can be a “local” (regional, interregional, or sub-regional) transmission loading relief procedure or one of the following Interconnection-wide procedures: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | 2009-12-10 | 2011-06-30 | High | For each TLR in the Eastern Interconnection, the Reliability Coordinator violates one (1) requirement of the applicable Interconnection-wide procedure | For each TLR in the Eastern Interconnection, the Reliability Coordinator violated two (2) to three (3) requirements of the applicable Interconnection-wide procedure | For each TLR in the Eastern Interconnection, the applicable Reliability Coordinator violated four (4) to five (5) requirements of the applicable Interconnection-wide procedure | For each TLR in the Eastern Interconnection, the Reliability Coordinator violated six (6) or more of the requirements of the applicable Interconnection-wide procedure. | [12 empty] | RC
Inactive | IRO | IRO-006-4.1 | R2. | The Reliability Coordinator shall only use local transmission loading relief or congestion management procedures to which the Transmission Operator experiencing the potential or actual SOL or IROL violation is a party. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | 2009-12-10 | 2011-06-30 | High | N/A | N/A | N/A | A Reliability Coordinator implemented local transmission loading relief or congestion management procedures to relieve congestion but the Transmission Operator experiencing the congestion was not a party to those procedure | [12 empty] | RC
Inactive | IRO | IRO-006-4.1 | R3. | Each Reliability Coordinator with a relief obligation from an Interconnection-wide procedure shall follow the curtailments as directed by the Interconnection-wide procedure. A Reliability Coordinator desiring to use a local procedure as a substitute for curtailments as directed by the Interconnection-wide procedure shall obtain prior approval of the local procedure from the ERO. [Violation Risk Factor: Low] [Time Horizon: Operations Planning] | 2009-12-10 | 2011-06-30 | High | N/A | N/A | N/A | A Reliability Coordinator implemented local transmission loading relief or congestion management procedures as a substitute for curtailment as directed by the Interconnection-wide procedure but the local procedure had not received prior approval from the | [12 empty] | RC
Inactive | IRO | IRO-006-4.1 | R4. | When Interconnection-wide procedures are implemented to curtail Interchange Transactions that cross an Interconnection boundary, each Reliability Coordinator shall comply with the provisions of the Interconnection-wide procedure. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | 2009-12-10 | 2011-06-30 | High | When requested to curtail an Interchange Transaction that crosses an Interconnection boundary utilizing an Interconnection-wide procedure, the responding Reliability Coordinator did not comply with the provisions of the Interconnection-wide procedure as r | N/A | N/A | N/A | [12 empty] | RC
Inactive | IRO | IRO-006-4.1 | R5. | During the implementation of relief procedures, and up to the point that emergency action is necessary, Reliability Coordinators and Balancing Authorities shall comply with applicable Interchange scheduling standards. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | 2009-12-10 | 2011-06-30 | Medium | The Reliability Coordinators or Balancing Authorities did not comply with applicable Interchange scheduling standards during the implementation of the relief procedures, up to the point emergency action is necessary | N/A | N/A | N/A |  | BA | [10 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-006-5 | R1. | Each Reliability Coordinator and Balancing Authority that receives a request pursuant to an Interconnection-wide transmission loading relief procedure (such as Eastern Interconnection TLR, WECC Unscheduled Flow Mitigation, or congestion management procedures from the ERCOT Protocols) from any Reliability Coordinator, Balancing Authority, or Transmission Operator in another Interconnection to curtail an Interchange Transaction that crosses an Interconnection boundary shall comply with the request, unless it provides a reliability reason to the requestor why it cannot comply with the request. | 2011-07-01 |  | High | N/A | N/A | N/A | The responsible entity received a request to curtail an Interchange Transaction crossing an Interconnection boundary pursuant to an Interconnection-wide transmission loading relief procedure from a Reliability Coordinator, Balancing Authority, or Transmission Operator, but the entity neither complied with the request, not provided a reliability reason why it could not comply with the request. |  | BA | [10 empty] | RC
Inactive | IRO | IRO-006-EAST-1 | R1. | R1. When acting or instructing others to act to mitigate the magnitude and duration of the instance of exceeding an IROL within that IROL’s TV, each Reliability Coordinator shall initiate, prior to or concurrently with the initiation of the Eastern Interconnection TLR procedure (or continuing management of this procedure if already initiated), one or more of the following actions: • Inter-area redispatch of generation • Intra-area redispatch of generation • Reconfiguration of the transmission system • Voluntary load reductions (e.g., Demand-side Management) • Controlled load reductions (e.g., load shedding) | 2011-07-01 | 2016-03-31 | High | N/A | N/A | N/A | When acting or instructing others to act to mitigate the magnitude and duration of the instance of exceeding an IROL within that IROL’s Tv, the Reliability Coordinator did not initiate one or more of the actions listed under R1 prior to or in conjunction with the initiation of the Eastern Interconnection TLR procedure (or continuing management of this procedure if already initiated). | [12 empty] | RC
Inactive | IRO | IRO-006-EAST-1 | R2. | To ensure operating entities are provided with information needed to maintain an awareness of changes to the Transmission System, when initiating the Eastern Interconnection TLR procedure to prevent or mitigate an SOL or IROL exceedance, and at least every clock hour (with the exception of TLR-1, where an hourly update is not required) after initiation up to and including the hour when the TLR level has been identified as TLR Level 0, the Reliability Coordinator shall identify: | 2011-07-01 | 2016-03-31 | Medium | The Reliability Coordinator initiating the Eastern Interconnection TLR procedure missed identifying the TLR Level and/or a list of congestion management actions to take as specified by the requirement for one clock hour during the period from initiation up to the hour when the TLR level was identified as TLR Level 0. | The Reliability Coordinator initiating the Eastern Interconnection TLR procedure missed identifying the TLR Level and/or a list of congestion management actions to take as specified by the requirement for two clock hours during the period from initiation up to the hour when the TLR level was identified as TLR Level 0. | The Reliability Coordinator initiating the Eastern Interconnection TLR procedure missed identifying the TLR Level and/or a list of congestion management actions to take as specified by the requirement for three clock hours during the period from initiation up to the hour when the TLR level was identified as TLR Level 0. | The Reliability Coordinator initiating the Eastern Interconnection TLR procedure missed identifying the TLR Level and/or a list of congestion management actions to take as specified by the requirement for four or more clock hours during the period from initiation up to the hour when the TLR level was identified as TLR Level 0. | [12 empty] | RC
Inactive | IRO | IRO-006-EAST-1 | R3. | Upon the identification of the TLR level and a list of congestion management actions to be implemented, the Reliability Coordinator initiating this TLR procedure shall: | 2011-07-01 | 2016-03-31 | Medium | The initiating Reliability Coordinator did not notify one or more Reliability Coordinators in the Eastern Interconnection of the TLR Level (3.1). | N/A | The initiating Reliability Coordinator did not communicate the list of congestion management actions to one or more of the Reliability Coordinators listed in Requirement R3, Part 3.2. OR The initiating Reliability Coordinator requested some, but not all, of the Reliability Coordinators identified in Requirement R3, Part 3.3 to implement the identified congestion management actions. | The initiating Reliability Coordinator requested none of the Reliability Coordinators identified in Requirement R3, Part 3.3 to implement the identified congestion management actions. | [12 empty] | RC
Inactive | IRO | IRO-006-EAST-1 | R4. | Each Reliability Coordinator that receives a request as described in Requirement R3, Part 3.3. shall, within 15 minutes of receiving the request, implement the congestion management actions requested by the issuing Reliability Coordinator as follows: • Instruct its Balancing Authorities to implement the Interchange Transaction schedule change requests. • Instruct its Balancing Authorities to implement the Network Integration Transmission Service and Native Load schedule changes for which the Balancing Authorities are responsible. • Instruct its Balancing Authorities to implement the Market Flow schedule changes for which the Balancing Authorities are responsible. • If an assessment determines shows that one or more of the congestion management actions communicated in Requirement R3, Part 3.3 will result in a reliability concern or will be ineffective, the Reliability Coordinator may replace those specific actions with alternate congestion management actions, provided that: o The alternate congestion management actions have been agreed to by the initiating Reliability Coordinator, and o The assessment shows that the alternate congestion management actions will not adversely affect reliability. | 2011-07-01 | 2016-03-31 | High | N/A | N/A | N/A | The responding Reliability Coordinator did not, within 15 minutes of receiving a request, either 1.) implement all the requested congestion management actions, or 2.) implement none or some of the requested congestion management actions and replace the remainder with alternate congestion management actions, provided that: assessment showed that the actions replaced would have resulted in a reliability concern or would have been ineffective, the alternate congestion management actions were agreed to by the initiating Reliability Coordinator, and assessment determined that the alternate congestion management actions would not adversely affect reliability. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-006-EAST-2 | R1. | Each Reliability Coordinator that initiates the Eastern Interconnection TLR procedure to prevent or mitigate an SOL or IROL exceedance shall identify the TLR level and the congestion management actions to be implemented, and shall update this information at least every clock hour (except TLR-1) after initiation up to and including the hour when the TLR level has been identified as TLR Level 0. Footnote: For more information on TLR levels, please see “Implementation Guideline for Reliability Coordinators: Eastern Interconnection TLR Levels Reference Document.” | 2016-04-01 |  | Medium | The Reliability Coordinator initiating the Eastern Interconnection TLR procedure missed identifying the TLR Level and/or a list of congestion management actions to take as specified by the requirement for one clock hour during the period from initiation up to the hour when the TLR level was identified as TLR Level 0. | The Reliability Coordinator initiating the Eastern Interconnection TLR procedure missed identifying the TLR Level and/or a list of congestion management actions to take as specified by the requirement for two clock hours during the period from initiation up to the hour when the TLR level was identified as TLR Level 0. | The Reliability Coordinator initiating the Eastern Interconnection TLR procedure missed identifying the TLR Level and/or a list of congestion management actions to take as specified by the requirement for three clock hours during the period from initiation up to the hour when the TLR level was identified as TLR Level 0. | The Reliability Coordinator initiating the Eastern Interconnection TLR procedure missed identifying the TLR Level and/or a list of congestion management actions to take as specified by the requirement for four or more clock hours during the period from initiation up to the hour when the TLR level was identified as TLR Level 0. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-006-EAST-2 | R2. | Each Reliability Coordinator with a Sink Balancing Authority that must implement congestion management actions pursuant to the Eastern Interconnection TLR procedure shall, within 15 minutes of receiving the request from the issuing Reliability Coordinator, instruct the Sink Balancing Authority to implement the congestion management actions, subject to the following exception: . Should an assessment determine that one or more of the congestion management actions communicated will result in a reliablity concern or will be ineffective, the Reliability Coordinator with a Sink Balancing Authority shall coordinate alternate congestion management actions with the issuing Reliabiltiy Coordinator. | 2016-04-01 |  | High |  |  |  | The responding Reliability Coordinator did not, within 15 minutes of receiving a request, either 1) instruct the Sink Balancing Authority to implement all the requested congestion management actions, or 2) coordinate alternate congestion management actions with the issuing Reliability Coordinator, provided that: assessment showed that the actions replaced would have resulted in a reliability concern or would have been ineffective. | [12 empty] | RC
Inactive | IRO | IRO-006-TRE-1 | R1. | The RC shall have procedures to identify and mitigate exceedances of identified Interconnection Reliability Operating Limits (IROL) and System Operating Limits (SOL) that will not be resolved by the automatic actions of the ERCOT Nodal market operations system. The procedures shall address, but not be limited to, one or more of the following: redispatch of generation; reconfiguration of the Transmission system; controlled load reductions (including both firm and non-firm load shedding). | 2012-07-01 | 2019-01-29 | Medium | N/A | N/A | N/A | The RC did not have procedures to identify and mitigate exceedances of identified IROLs and SOLs. | [12 empty] | RC
Inactive | IRO | IRO-006-TRE-1 | R2. | The RC shall act to identify and mitigate exceedances of identified Interconnection Reliability Operating Limits and System Operating Limits that will not be resolved by the automatic actions of the ERCOT Nodal market operations system, in accordance with the procedures required by R1. | 2012-07-01 | 2019-01-29 | High | N/A | N/A | The RC failed to follow its procedures in identifying and mitigating an exceedance of an SOL. | The RC failed to follow its procedures in identifying and mitigating an exceedance of an IROL. | [12 empty] | RC
Inactive | IRO | IRO-006-WECC-1 | R1. | Upon receiving a request of Step 4 or greater (see Attachment 1-IRO-006-WECC-1) from the Transmission Operator of a Qualified Transfer Path, the Reliability Coordinator shall approve (actively or passively) or deny that request within five minutes. [Time Horizon: Real-time Operations] | 2011-07-01 | 2014-06-30 | Medium | N/A | N/A | N/A | There was one instance during a calendar month in which the Reliability Coordinator approved (actively or passively) or denied a Step 4 or greater request greater than five minutes after receipt of notification from the Transmission Operator of a Qualified Transfer Path. | [12 empty] | RC
Inactive | IRO | IRO-006-WECC-1 | R2. | The Balancing Authorities shall approve curtailment requests to the schedules as submitted, implement alternative actions, or a combination there of that collectively meets the Relief Requirement.[Time Horizon: Real-time Operations] | 2011-07-01 | 2014-06-30 | Medium | [5 empty] | BA
Inactive | IRO | IRO-006-WECC-2 | R1. | Each Reliability Coordinator shall approve or deny a request within five minutes of receiving the request for unscheduled flow transmission relief from the Transmission Operator of a Qualified Transfer Path that will result in the calculation of a Relief Requirement. | 2014-07-01 | 2019-09-30 | Medium | N/A | N/A | N/A | There shall be a Severe level of non-compliance if there is one instance during a calendar month in which the Reliability Coordinator approved (actively or passively) or denied a request for unscheduled flow transmission relief from the Transmission Operator of a Qualified Transfer Path, greater than five minutes after receipt of notification from the Transmission Operator of a Qualified Transfer Path. | [12 empty] | RC
Inactive | IRO | IRO-006-WECC-2 | R2. | Each Balancing Authority shall perform any combination of the following actions meeting the Relief Requirement upon receiving a request for relief as described in Requirement R1: • Approve curtailment requests to the schedules as submitted • Implement alternative actions | 2014-07-01 | 2019-09-30 | Medium | There shall be a Lower Level of non-compliance if there is less than 100% Relief Requirement provided but greater than or equal to 90% Relief Requirement provided or the Relief Requirement was less than 5 MW and was not fully provided. | There shall be a Moderate Level of non-compliance if there is less than 90% Relief Requirement provided but greater than or equal to 75% Relief Requirement provided. | There shall be a High Level of non-compliance if there is less than 75% Relief Requirement provided but greater than or equal to 60% Relief Requirement provided. | There shall be a Severe Level of non-compliance if there is less than 60% Relief Requirement provided. |  | BA
Mandatory Subject to Enforcement | IRO | IRO-006-WECC-3 | R1. | Each Reliability Coordinator receiving a request for Curtailments for unscheduled flow transmission relief on a Qualified Path within its Reliability Coordinator Area shall either approve or deny that request within five minutes of receipt. | 2019-10-01 |  | Medium | Not Applicable | Not Applicable | Not Applicable | There shall be a Severe level of noncompliance if there is one instance during a calendar month in which the Reliability Coordinator approved (actively or passively) or denied a request for unscheduled flow transmission relief on a Qualified Path greater than five minutes after receipt that request. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-006-WECC-3 | R2. | Each Balancing Authority receiving an approved request for unscheduled flow transmission relief on a Qualified Path per Requirement R1, shall perform any of the following actions to meet that request: • Approve curtailment requests to the schedules as submitted • Implement alternative actions | 2019-10-01 |  | Medium | There shall be a Lower Level of noncompliance if there is less than 100% relief requirement provided but greater than or equal to 90% relief requirement provided or the relief requirement was less than 5 MW and was not fully provided. | There shall be a Moderate Level of noncompliance if there is less than 90% relief requirement provided but greater than or equal to 75% relief requirement provided. | There shall be a High Level of noncompliance if there is less than 75% relief requirement provided but greater than or equal to 60% relief requirement provided. | There shall be a Severe Level of noncompliance if there is less than 60% relief requirement provided. |  | BA
Inactive | IRO | IRO-008-1 | R1. | Each Reliability Coordinator shall perform an Operational Planning Analysis to assess whether the planned operations for the next day within its Wide Area, will exceed any of its Interconnection Reliability Operating Limits (IROLs) during anticipated normal and Contingency event conditions. | 2011-10-01 | 2017-03-31 | High | Performed an Operational Planning Analysis that covers all aspects of the requirement for all except one of 30 days. | Performed an Operational Planning Analysis that covers all aspects of the requirement for all except two of 30 days. | Performed an Operational Planning Analysis that covers all aspects of the requirement for all except three of 30 days. | Missed performing an Operational Planning Analysis that covers all aspects of the requirement for four or more of 30 days. | [12 empty] | RC
Inactive | IRO | IRO-008-1 | R2. | Each Reliability Coordinator shall perform a Real-Time Assessment at least once every 30 minutes to determine if its Wide Area is exceeding any IROLs or is expected to exceed any IROLs. | 2011-10-01 | 2017-03-31 | High | For any sample 24 hour period within the 30 day retention period, a Real-time Assessment was not conducted for one 30- minute period. within that 24- hour period (R2) | For any sample 24 hour period within the 30 day retention period, Real-time Assessments were not conducted for two 30- minute periods within that 24-hour period (R2) | For any sample 24 hour period within the 30 day retention period, Real-time Assessments were not conducted for three 30- minute periods within that 24-hour period (R2) | For any sample 24 hour period within the 30 day retention period, Real-time Assessments were not conducted for more than three 30-minute periods within that 24-hour period (R2) | [12 empty] | RC
Inactive | IRO | IRO-008-1 | R3. | When a Reliability Coordinator determines that the results of an Operational Planning Analysis or Real-Time Assessment indicates the need for specific operational actions to prevent or mitigate an instance of exceeding an IROL, the Reliability Coordinator shall share its results with those entities that are expected to take those actions. | 2011-10-01 | 2017-03-31 | Medium | N/A | N/A | N/A | The Reliability Coordinator failed to share the results of its analyses or assessments with any of the entities that were required to take action. | [12 empty] | RC
Inactive | IRO | IRO-008-2 | R1. | Each Reliability Coordinator shall perform an Operational Planning Analysis that will allow it to assess whether the planned operations for the next-day will exceed System Operating Limits (SOLs) and Interconnection Operating Reliability Limits (IROLs) within its Wide Area. | 2017-04-01 | 2024-03-31 | Medium | N/A | N/A | N/A | The Reliability Coordinator did not perform an Operational Planning Analysis allowing it to assess whether its planned operations for the next-day within its Wide Area will exceed any of its System Operating Limits (SOLs) and Interconnection Operating Reliability Limits (IROLs). | [12 empty] | RC
Inactive | IRO | IRO-008-2 | R2. | Each Reliability Coordinator shall have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational Planning Analysis as performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. | 2017-04-01 | 2024-03-31 | Medium | N/A | N/A | N/A | The Reliability Coordinator did not have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational Planning Analysis as performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. | [12 empty] | RC
Inactive | IRO | IRO-008-2 | R3. | Each Reliability Coordinator shall notify impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). | 2017-04-01 | 2024-03-31 | Medium | The Reliability Coordinator did not notify one impacted entity or 5% or less of the impacted entities whichever is greater identified in its Operating Plan(s) as to their role in that plan(s). | The Reliability Coordinator did not notify two impacted entities or more than 5% and less than or equal to 10% of the impacted entities whichever is greater, identified in its Operating Plan(s) as to their role in that plan(s). | The Reliability Coordinator did not notify three impacted entities or more than 10% and less than or equal to 15% of the impacted entities whichever is greater, identified in its Operating Plan(s) as to their role in that plan(s). | The Reliability Coordinator did not notify four or more impacted entities or more than 15% of the impacted entities identified in its Operating Plan(s) as to their role in that plan(s). For the Requirement R3 and R5 VSLs, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size. If a Reliability Coordinator has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation | [12 empty] | RC
Inactive | IRO | IRO-008-2 | R4. | Each Reliability Coordinator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | 2017-04-01 | 2024-03-31 | High | For any sample 24-hour period within the 30-day retention period, the Reliability Coordinator’s Real-time Assessment was not conducted for one 30-minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Reliability Coordinator’s Real-time Assessment was not conducted for two 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Reliability Coordinator’s Real-time Assessment was not conducted for three 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Reliability Coordinator’s Real-time Assessment was not conducted for three or more 30-minute periods within that 24-hour period. | [12 empty] | RC
Inactive | IRO | IRO-008-2 | R5. | Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the results of a Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area | 2017-04-01 | 2024-03-31 | High | The Reliability Coordinator did not notify one impacted Transmission Operator or Balancing Authority within its Reliability Coordinator Area or 5% or less of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area whichever is greater, when the results of its Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. | The Reliability Coordinator did not notify two impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area or more than 5% and less than or equal to 10% of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area whichever is greater, when the results of its Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. | The Reliability Coordinator did not notify three impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area or more than 10% and less than or equal to 15% of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area whichever is greater, when the results of its Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. | The Reliability Coordinator did not notify four or more impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area or more than 15% of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area identified in the Operating Plan(s) as to their role in the plan(s). OR The Reliability Coordinator did not notify the other impacted Reliability Coordinators, as indicated in its Operating Plan, when the results of its Real-time Assessment indicated an actual or expected condition that results in, or could result in a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (ROL) exceedance within its Wide Area. | [12 empty] | RC
Inactive | IRO | IRO-008-2 | R6. | Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. | 2017-04-01 | 2024-03-31 | Medium | The Reliability Coordinator did not notify one impacted Transmission Operator or Balancing Authority within its Reliability Coordinator Area or 5% or less of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area whichever is greater, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 was prevented or mitigated. OR The Reliability Coordinator did not notify one other impacted Reliability Coordinator as indicated in its Operating Plan when the System Operatiing Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 was prevents or mitigated. | The Reliability Coordinator did not notify two impacted Transmission Operators or Balancing Authorities within its Reliability Coordinator Area or more than 5% and less than or equal to 10% of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area whichever is greater, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R6 was prevented or mitigated. OR The Reliability Coordinator did not notify two other impacted Reliability Coordinators as indicated in its Operating Plan when the System Operating Limit (IROL) exceedance identified in Requirement R5 was prevented or mitigated. | The Reliability Coordinator did not notify three impacted Transmission Operators or Balancing Authorities within its Reliability Coordinator Area or more than 10% and less than or equal to 15% of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area whichever is greater, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R6 was prevented or mitigated. OR The Reliability Coordinator did not notify three other impacted Reliability Coordinators as indicated in its Operating Plan when the System Operating Limit (SOL) or Intrconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 was prevented or mitigated. | The Reliability Coordinator did not notify four or more impacted Transmission Operators or Balancing Authorities within its Reliability Coordinator Area or more than 15% of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 was prevented or mitigated. OR The Reliability Coordinator did not notify four or more other impacted Reliability Coordinators as indicated in its Operating Plan when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requireement R5 was prevented or mitigated. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-008-3 | R1. | Each Reliability Coordinator shall perform an Operational Planning Analysis that will allow it to assess whether the planned operations for the next-day will exceed System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs) within its Wide Area. | 2024-04-01 |  | Medium | N/A | N/A | N/A | The Reliability Coordinator did not perform an Operational Planning Analysis allowing it to assess whether its planned operations for the next-day within its Wide Area will exceed any of its System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-008-3 | R2. | Each Reliability Coordinator shall have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational Planning Analysis as performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. | 2024-04-01 |  | Medium | N/A | N/A | N/A | The Reliability Coordinator did not have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational Planning Analysis as performed in Requirement R1 while considering the Operating Plans for the next- day provided by its Transmission Operators and Balancing Authorities. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-008-3 | R3. | Each Reliability Coordinator shall notify impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). | 2024-04-01 |  | Medium | The Reliability Coordinator did not notify one impacted entity or 5% or less of the impacted entities whichever is greater identified in its Operating Plan(s) as to their role in that plan(s). | The Reliability Coordinator did not notify two impacted entities or more than 5% and less than or equal to 10% of the impacted entities whichever is greater, identified in its Operating Plan(s) as to their role in that plan(s). | The Reliability Coordinator did not notify three impacted entities or more than 10% and less than or equal to 15% of the impacted entities whichever is greater, identified in its Operating Plan(s) as to their role in that plan(s). | The Reliability Coordinator did not notify four or more impacted entities or more than 15% of the impacted entities identified in its Operating Plan(s) as to their role in that plan(s). | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-008-3 | R4. | Each Reliability Coordinator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | 2024-04-01 |  | High | For any sample 24-hour period within the 30- day retention period, the Reliability Coordinator’s Real-time Assessment was not conducted for one 30- minute period within that 24- hour period. | For any sample 24-hour period within the 30-day retention period, the Reliability Coordinator’s Real-time Assessment was not conducted for two 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30- day retention period, the Reliability Coordinator’s Real-time Assessment was not conducted for three 30- minute periods within that 24- hour period. | For any sample 24-hour period within the 30-day retention period, the Reliability Coordinator’s Real-time Assessment was not conducted for three or more 30-minute periods within that 24-hour period. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-008-3 | R5. | Each Reliability Coordinator shall notify, in accordance with its SOL methodology, impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the results of a Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. | 2024-04-01 |  | High | The Reliability Coordinator did not notify, in accordance with its SOL methodology one impacted Transmission Operator or Balancing Authority within its Reliability Coordinator Area or 5% or less of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area whichever is greater, when the results of its Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. | The Reliability Coordinator did not notify, in accordance with its SOL methodology two impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area or more than 5% and less than or equal to 10% of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area whichever is greater, when the results of its Real- time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. | The Reliability Coordinator did not notify, in accordance with its SOL methodology three impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area or more than 10% and less than or equal to 15% of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area whichever is greater, when the results of its Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. | The Reliability Coordinator did not notify, in accordance with its SOL methodology four or more impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area or more than 15% of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area identified in the Operating Plan(s) as to their role in the plan(s). OR The Reliability Coordinator did not notify the other impacted Reliability Coordinators, as indicated in its Operating Plan, when the results of its Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-008-3 | R6. | Each Reliability Coordinator shall notify, in accordance with SOL methodology, impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. | 2024-04-01 |  | Medium | The Reliability Coordinator did not notify, in accordance with its SOL methodology one impacted Transmission Operator or Balancing Authority within its Reliability Coordinator Area or 5% or less of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area whichever is greater, when the System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 was prevented or mitigated. OR The Reliability Coordinator did not notify one other impacted Reliability Coordinator as indicated in its Operating Plan when the when the System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 was prevented or mitigated. | The Reliability Coordinator did not notify, in accordance with its SOL methodology two impacted Transmission Operators or Balancing Authorities within its Reliability Coordinator Area or more than 5% and less than or equal to 10% of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area whichever is greater, when the System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R6 was prevented or mitigated. OR The Reliability Coordinator did not notify two other impacted Reliability Coordinators as indicated in its Operating Plan when the System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 was prevented or mitigated. | The Reliability Coordinator did not notify, in accordance with its SOL methodology three impacted Transmission Operators or Balancing Authorities within its Reliability Coordinator Area or more than 10% and less than or equal to 15% of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area whichever is greater, when the System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 was prevented or mitigated. OR The Reliability Coordinator did not notify three other impacted Reliability Coordinators as indicated in its Operating Plan when the System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 was prevented or mitigated. | The Reliability Coordinator did not notify, in accordance with its SOL methodology four or more impacted Transmission Operators or Balancing Authorities within its Reliability Coordinator Area or more than 15% of the impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area when the System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 was prevented or mitigated. OR The Reliability Coordinator did not notify four or more other impacted Reliability Coordinators as indicated in its Operating Plan when the System Operating Limit (SOL) exceedance or an Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 was prevented or mitigated. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-008-3 | R7. | Each Reliability Coordinator shall use its SOL methodology when determining SOL exceedances for Real-time Assessments, Real-time monitoring, and Operational Planning Analysis. | 2024-04-01 |  | Medium |  |  |  | The Reliability Coordinator failed to use its SOL methodology when determining SOL exceedances for Real-time Assessments, Real-time monitoring, and Operational Planning Analysis. | [12 empty] | RC
Inactive | IRO | IRO-009-1 | R1. | For each IROL (in its Reliability Coordinator Area) that the Reliability Coordinator identifies one or more days prior to the current day, the Reliability Coordinator shall have one or more Operating Processes, Procedures, or Plans that identify actions it shall take or actions it shall direct others to take (up to and including load shedding) that can be implemented in time to prevent exceeding those IROLs. | 2011-10-01 | 2015-12-31 | Medium |  |  |  | An IROL in its Reliability Coordinator Area was identified one or more days in advance and the Reliability Coordinator does not have an Operating Process, Procedure, or Plan that identifies actions to prevent exceeding that IROL. (R1) | [12 empty] | RC
Inactive | IRO | IRO-009-1 | R2. | For each IROL (in its Reliability Coordinator Area) that the Reliability Coordinator identifies one or more days prior to the current day, the Reliability Coordinator shall have one or more Operating Processes, Procedures, or Plans that identify actions it shall take or actions it shall direct others to take (up to and including load shedding) to mitigate the magnitude and duration of exceeding that IROL such that the IROL is relieved within the IROL’s Tv. | 2011-10-01 | 2015-12-31 | Medium |  |  |  | An IROL in its Reliability Coordinator Area was identified one or more days in advance and the Reliability Coordinator does not have an Operating Process, Procedure, or Plan that identifies actions to mitigate exceeding that IROL within the IROL’s Tv. (R2) | [12 empty] | RC
Inactive | IRO | IRO-009-1 | R3. | When an assessment of actual or expected system conditions predicts that an IROL in its Reliability Coordinator Area will be exceeded, the Reliability Coordinator shall implement one or more Operating Processes, Procedures or Plans (not limited to the Operating Processes, Procedures, or Plans developed for Requirements R1) to prevent exceeding that IROL. | 2011-10-01 | 2015-12-31 | High |  |  |  | An assessment of actual or expected system conditions predicted that an IROL in the Reliability Coordinator’s Area would be exceeded, but no Operating Processes, Procedures, or Plans were implemented. (R3) | [12 empty] | RC
Inactive | IRO | IRO-009-1 | R4. | When actual system conditions show that there is an instance of exceeding an IROL in its Reliability Coordinator Area, the Reliability Coordinator shall, without delay, act or direct others to act to mitigate the magnitude and duration of the instance of exceeding that IROL within the IROL’s Tv. | 2011-10-01 | 2015-12-31 | High |  |  | Actual system conditions showed that there was an instance of exceeding an IROL in its Reliability Coordinator Area, and there was a delay of five minutes or more before acting or directing others to act to mitigate the magnitude and duration of the instance of exceeding that IROL, however the IROL was mitigated within the IROL Tv. (R4) | Actual system conditions showed that there was an instance of exceeding an IROL in its Reliability Coordinator Area, and that IROL was not resolved within the IROL’s Tv. (R4) | [12 empty] | RC
Inactive | IRO | IRO-009-1 | R5. | If unanimity cannot be reached on the value for an IROL or its Tv, each Reliability Coordinator that monitors that Facility (or group of Facilities) shall, without delay, use the most conservative of the values (the value with the least impact on reliability) under consideration. | 2011-10-01 | 2015-12-31 | High |  |  |  | There was a disagreement on the value of the IROL or its Tv and the most conservative limit under consideration was not used. (R5) | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-009-2 | R1. | For each IROL (in its Reliability Coordinator Area) that the Reliability Coordinator identifies one or more days prior to the current day, the Reliability Coordinator shall have one or more Operating Processes, Procedures, or Plans that identify actions the Reliability Coordinator shall take or actions the Reliability Coordinator shall direct others to take (up to and including load shedding): | 2016-01-01 |  | Medium |  |  |  | An IROL in its Reliability Coordinator Area was identified one or more days in advance and the Reliability Coordinator does not have an Operating Process, Procedure, or Plan that identifies actions to prevent that IROL exceedance (Part 1.1). OR An IROL in its Reliability Coordinator Area was identified one or more days in advance and the Reliability Coordinator does not have an Operating Process, Procedure, or Plan that identifies actions to mitigate that IROL exceedance within the IROL’s Tv. (Part 1.2). | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-009-2 | R2. | Each Reliability Coordinator shall initiate one or more Operating Processes, Procedures, or Plans (not limited to the Operating Processes, Procedures, or Plans developed for Requirement R1) that are intended to prevent an IROL exceedance, as identified in the Reliability Coordinator’s Real-time monitoring or Real-time Assessment. | 2016-01-01 |  | High |  |  |  | No Operating Processes, Procedures, or Plans were initiated that were intended to prevent a predicted IROL exceedance as identified in the Reliability Coordinator’s Real-time monitoring or Real-time Assessment. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-009-2 | R3. | Each Reliability Coordinator shall act or direct others to act so that the magnitude and duration of an IROL exceedance is mitigated within the IROL’s Tv, as identified in the Reliability Coordinator’s Real-time monitoring or Real-time Assessment. | 2016-01-01 |  | High |  |  |  | Actual system conditions showed that there was an IROL exceedance in its Reliability Coordinator Area, and that the IROL exceedance was not mitigated within the IROL’s Tv. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-009-2 | R4. | Each Reliability Coordinator shall operate to the most limiting IROL and Tv in instances where there is a difference in an IROL or its Tv between Reliability Coordinators that are responsible for that Facility (or group of Facilities). | 2016-01-01 |  | High |  |  |  | The most limiting IROL or its Tv was not operated to between Reliability Coordinators that are responsible for the Facility (or group of Facilities) associated with the IROL. | [12 empty] | RC
Inactive | IRO | IRO-010-1 | R1. | The Reliability Coordinator shall have a documented specification for data and information to build and maintain models to support Real-time monitoring, Operational Planning Analyses, and Real-time Assessments of its Reliability Coordinator Area to prevent instability, uncontrolled separation, and cascading outages. The specification shall include the following: (Time Horizon: Operations Planning) |  | 2009-08-05 | Low | [16 empty] | RC
Inactive | IRO | IRO-010-1 | R2. | The Reliability Coordinator shall distribute its data specification to entities that have Facilities monitored by the Reliability Coordinator and to entities that provide Facility status to the Reliability Coordinator. (Time Horizon: Operations Planning) |  | 2009-08-05 | Low | [16 empty] | RC
Inactive | IRO | IRO-010-1 | R3. | Each Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-serving Entity, Reliability Coordinator, Transmission Operator, and Transmission Owner shall provide data and information, as specified, to the Reliability Coordinator(s) with which it has a reliability relationship. (Time Horizon: Operations Planning; Same-day Operations; Real-time Operations) |  | 2009-08-05 | Medium | [5 empty] | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | IRO | IRO-010-1a | R1. | The Reliability Coordinator shall have a documented specification for data and information to build and maintain models to support Real-time monitoring, Operational Planning Analyses, and Real-time Assessments of its Reliability Coordinator Area to prevent instability, uncontrolled separation, and cascading outages. The specification shall include the following: | 2011-10-01 | 2017-03-31 | Low | Data specification is complete with the following exception: Missing the mutually agreeable format. (R1.2) | Data specification is complete with the following exception – no process for data provision when automated Real-Time system operating data is unavailable. (R1.4) | Data specification incomplete (missing either the list of required data (R1.1), or the timeframe for providing data. (R1.3) | No data specification (R1) | [12 empty] | RC
Inactive | IRO | IRO-010-1a | R2. | The Reliability Coordinator shall distribute its data specification to entities that have Facilities monitored by the Reliability Coordinator and to entities that provide Facility status to the Reliability Coordinator. | 2011-10-01 | 2017-03-31 | Low | Distributed its data specification to greater than or equal to 95% but less than 100% of the entities that have Facilities monitored by the Reliability Coordinator and the entities that provide the Reliability Coordinator with Facility status. | Distributed its data specification to greater than or equal to 85% but less than 95% of the entities that have Facilities monitored by the Reliability Coordinator and the entities that provide the Reliability Coordinator with Facility status. (R2) | Distributed its data specification to greater than or equal to 75% - but less then 85% of the entities that have Facilities monitored by the Reliability Coordinator and the entities that provide the Reliability Coordinator with Facility status. (R2) | Data specification distributed to less than 75% of the entities that have Facilities monitored by the Reliability Coordinator and the entities that provide the Reliability Coordinator with Facility status. (R2) | [12 empty] | RC
Inactive | IRO | IRO-010-1a | R3. | Each Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-serving Entity, Reliability Coordinator, Transmission Operator, and Transmission Owner shall provide data and information, as specified, to the Reliability Coordinator(s) with which it has a reliability relationship. | 2011-10-01 | 2017-03-31 | Medium | Provided greater than or equal to 95% but less then 100% of the data and information as specified. (R3) | Provided greater than or equal to 85% but less than 95% of the data and information as specified. (R3) | Provided greater than or equal to 75% but less then 85% of the data and information as specified. (R3) | Provided less than 75% of the data and information as specified. (R3) |  | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | IRO | IRO-010-2 | R1. | The Reliability Coordinator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include but not be limited to: | 2017-01-01 | 2021-03-31 | Low | The Reliability Coordinator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Reliability Coordinator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Reliability Coordinator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Reliability Coordinator did not include any of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Reliability Coordinator did not have a documented specification for the data necessary for it to preform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | [12 empty] | RC
Inactive | IRO | IRO-010-2 | R2. | The Reliability Coordinator shall distribute its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | 2017-01-01 | 2021-03-31 | Low | The Reliability Coordinator did not distribute its data specification as developed in Requirement R1 to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Reliability Coordinator did not distribute its data specification as developed in Requirement R1 to two entities, or more than 5% and less than or equal to 10% of the reliability entities, whichever is greater, that have data required by the Reliability Coordinator’s Operational Planning Analyses, and Real- time monitoring, and Real-time Assessments. | The Reliability Coordinator did not distribute its data specification as developed in Requirement R1 to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Reliability Coordinator did not distribute its data specification as developed in Requirement R1 to four or more entities, or more than 15% of the entities, whichever is greater, that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Note: For the Requirement R2 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | [12 empty] | RC
Inactive | IRO | IRO-010-2 | R3. | Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall satisfy the obligations of the documented specifications using: | 2017-04-01 | 2021-03-31 | Medium | The responsible entity receiving a data specification in Requirement R2 satisfied the obligations of the documented specifications for data but failed to follow one of the criteria shown in Parts 3.1 – 3.3. | The responsible entity receiving a data specification in Requirement R2 satisfied the obligations of the documented specifications for data but failed to follow two of the criteria shown in Parts 3.1 – 3.3. | The responsible entity receiving a data specification in Requirement R2 satisfied the obligations of the documented specifications for data but failed to follow any of the criteria shown in Parts 3.1 – 3.3. | The responsible entity receiving a data specification in Requirement R2 did not satisfy the obligations of the documented specifications for data. |  | BA | DP |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP
Inactive | IRO | IRO-010-3 | R1. | The Reliability Coordinator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include but not be limited to: | 2021-04-01 | 2023-03-31 | Low | The Reliability Coordinator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Reliability Coordinator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Reliability Coordinator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Reliability Coordinator did not include any of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Reliability Coordinator did not have a documented specification for the data necessary for it to preform its Operational Planning Analyses, Real-time monitoring, and Real-time. Assessments. | [12 empty] | RC
Inactive | IRO | IRO-010-3 | R2. | The Reliability Coordinator shall distribute its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | 2021-04-01 | 2023-03-31 | Low | The Reliability Coordinator did not distribute its data specification as developed in Requirement R1 to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Reliability Coordinator did not distribute its data specification as developed in Requirement R1 to Three entities, or more than 5% and less than or equal to 10% of the reliability entites, whichever is greater, that have data required by the Reliability Coordinator's Operational Planning Analyses, and Real-time monitoring, and Real-time Assesssments. | The Reliability Coordinator did not distribute its data specification as developed in Requirement R1 to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Reliability Coordinator did not distribute its data specification as developed in Requirement R1 to four or more entities, or more than 15% of the entities, whichever is greater, that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. Note: For the Requirement R2 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | [12 empty] | RC
Inactive | IRO | IRO-010-3 | R3. | Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall satisfy the obligations of the documented specifications using: | 2021-04-01 | 2023-03-31 | Medium | The responsible entity receiving a data specification in Requirement R2 satisfied the obligations of the documented specifications for data but failed to follow one of the criteria shown in Parts 3.1 – 3.3. | The responsible entity receiving a data specification in Requirement R2 satisfied the obligations of the documented specifications for data but failed to follow two of the criteria shown in Parts 3.1 – 3.3. | The responsible entity receiving a data specification in Requirement R2 satisfied the obligations of the documented specifications for data but failed to follow any of the criteria shown in Parts 3.1 – 3.3. | The responsible entity receiving a data specification in Requirement R2 did not satisfy the obligations of the documented specifications for data. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | IRO | IRO-010-4 | R1. | The Reliability Coordinator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include but not be limited to: | 2023-04-01 | 2025-06-30 | Low | The Reliability Coordinator did not include two or fewer of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Reliability Coordinator did not include three of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Reliability Coordinator did not include four of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Reliability Coordinator did not include any of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Reliability Coordinator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-010-4 | R2. | The Reliability Coordinator shall distribute its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real- time monitoring, and Real-time Assessments. | 2023-04-01 | 2025-06-30 | Low | The Reliability Coordinator did not distribute its data specification as developed in Requirement R1 to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Reliability Coordinator did not distribute its data specification as developed in Requirement R1 to two entities, or more than 5% and less than or equal to 10% of the reliability entities, whichever is greater, that have data required by the Reliability Coordinator’s Operational Planning Analyses, and Real- time monitoring, and Real-time Assessments. | The Reliability Coordinator did not distribute its data specification as developed in Requirement R1 to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Reliability Coordinator did not distribute its data specification as developed in Requirement R1 to four or more entities, or more than 15% of the entities, whichever is greater, that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-010-4 | R3. | Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall satisfy the obligations of the documented specifications using: | 2023-04-01 | 2025-06-30 | Medium | The responsible entity receiving a data specification in Requirement R2 satisfied the obligations of the documented specifications for data but failed to follow one of the criteria shown in Parts 3.1 – 3.3. | The responsible entity receiving a data specification in Requirement R2 satisfied the obligations of the documented specifications for data but failed to follow two of the criteria shown in Parts 3.1 – 3.3. | The responsible entity receiving a data specification in Requirement R2 satisfied the obligations of the documented specifications for data but failed to follow any of the criteria shown in Parts 3.1 – 3.3. | The responsible entity receiving a data specification in Requirement R2 did not satisfy the obligations of the documented specifications for data. |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Subject to Future Enforcement | IRO | IRO-010-5 | R1. | The Reliability Coordinator shall maintain documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. The specification shall include but not be limited to: | 2025-07-01 |  | Low | The Reliability Coordinator did not include one or two of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐time monitoring, and Real‐ time Assessments. | The Reliability Coordinator did not include three of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐time monitoring, and Real‐time Assessments. | The Reliability Coordinator did not include four of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐time monitoring, and Real‐time Assessments. | The Reliability Coordinator did not include any of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐time monitoring, and Real‐time Assessments. OR, The Reliability Coordinator did not have a documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐time monitoring, and Real‐time Assessments. | [12 empty] | RC
Subject to Future Enforcement | IRO | IRO-010-5 | R2. | The Reliability Coordinator shall distribute its data and information specification(s) to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. | 2025-07-01 |  | Low | The Reliability Coordinator did not distribute its specification(s) as developed in Requirement R1 to one entity, or 5% or less of the entities, whichever is greater, that have data and information required by the Reliability Coordinator’s Operational Planning Analyses, Real‐time monitoring, and Real‐ time Assessments. | The Reliability Coordinator did not distribute its specification(s) as developed in Requirement R1 to two entities, or more than 5% and less than or equal to 10% of the reliability entities, whichever is greater, that have data and information required by the Reliability Coordinator’s Operational Planning Analyses, and Real‐ time monitoring, and Real‐time Assessments. | The Reliability Coordinator did not distribute its specification(s) as developed in Requirement R1 to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data and information required by the Reliability Coordinator’s Operational Planning Analyses, Real‐time monitoring, and Real‐ time Assessments. | The Reliability Coordinator did not distribute its specification(s) as developed in Requirement R1 to four or more entities, or more than 15% of the entities, whichever is greater, that have data and information required by the Reliability Coordinator’s Operational Planning Analyses, Real‐time monitoring, and Real‐ time Assessments. | [12 empty] | RC
Subject to Future Enforcement | IRO | IRO-010-5 | R3. | Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Transmission Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R2 shall satisfy the obligations of the documented specifications . | 2025-07-01 |  | Medium | The responsible entity receiving a specification(s) in Requirement R2 satisfied the obligations of the documented specifications but failed to meet one of the parts in Requirement Part 1.5. | The responsible entity receiving a specification(s) in Requirement R2 satisfied the obligations of the documented specifications but failed to meet two of the parts in Requirement R1Part 1.5. | The responsible entity receiving a specification(s) in Requirement R2 satisfied the obligations of the documented specifications but failed to meet any of the parts in Requirement R1 Part 1.5. | The responsible entity receiving a specification(s) in Requirement R2 did not satisfy the obligations of the documented specifications . |  | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP
Inactive | IRO | IRO-014-1 | R1. | The Reliability Coordinator shall have Operating Procedures, Processes, or Plans in place for activities that require notification, exchange of information or coordination of actions with one or more other Reliability Coordinators to support Interconnection reliability. These Operating Procedures, Processes, or Plans shall address Scenarios that affect other Reliability Coordinator Areas as well as those developed in coordination with other Reliability Coordinators. | 2007-06-18 | 2017-03-31 | Medium |  |  | The Reliability Coordinator has Operating Procedures, Processes, or Plans in place for activities that require notification, exchange of information or coordination of actions with one or more other Reliability Coordinators to support Interconnection reli | The Reliability Coordinator failed to have Operating Procedures, Processes, or Plans in place for activities that require notification, exchange of information or coordination of actions with one or more other Reliability Coordinators to support Interconn | [12 empty] | RC
Inactive | IRO | IRO-014-1 | R2. | Each Reliability Coordinator’s Operating Procedure, Process, or Plan that requires one or more other Reliability Coordinators to take action (e.g., make notifications, exchange information, or coordinate actions) shall be: | 2007-06-18 | 2017-03-31 | Low | [16 empty] | RC
Inactive | IRO | IRO-014-1 | R3. | A Reliability Coordinator’s Operating Procedures, Processes, or Plans developed to support a Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan shall include: | 2007-06-18 | 2017-03-31 | Medium | [16 empty] | RC
Inactive | IRO | IRO-014-1 | R4. | Each of the Operating Procedures, Processes, and Plans addressed in Reliability Standard IRO-014 Requirement 1 and Requirement 3 shall: | 2007-06-18 | 2017-03-31 | Low | [16 empty] | RC
Inactive | IRO | IRO-014-2 | R1. | Each Reliability Coordinator shall have Operating Procedures, Operating Processes, or Operating Plans for activities that require notification, exchange of information or coordination of actions that may impact other Reliability Coordinator Areas to support Interconnection reliability. These Operating Procedures, Processes, or Plans shall collectively address the following: |  | 2016-01-26 | Medium | The Reliability Coordinator has Operating Procedures, Operating Processes, or Operating Plans in place for activities that require notification, exchange of information or coordination of actions with impacted Reliability Coordinators to support Interconnection reliability but failed to address one of the topical areas identified in Parts 1.1 through 1.7. | The Reliability Coordinator has Operating Procedures, Operating Processes, or Operating Plans in place for activities that require notification, exchange of information or coordination of actions with impacted Reliability Coordinators to support Interconnection reliability but failed to address two of the topical areas identified in Parts 1.1 through 1.7. | The Reliability Coordinator has Operating Procedures, Operating Processes, or Operating Plans in place for activities that require notification, exchange of information or coordination of actions with impacted Reliability Coordinators to support Interconnection reliability but failed to address three of the topical areas identified in Parts 1.1 through 1.7. | The Reliability Coordinator failed to have Operating Procedures, Operating Processes, or Operating Plans in place for activities that require notification, exchange of information or coordination of actions with impacted Reliability Coordinators to support Interconnection reliability to address three or more of the topical areas identified in Parts 1.1 through 1.7. | [12 empty] | RC
Inactive | IRO | IRO-014-2 | R2. | Each Reliability Coordinator shall maintain its Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 as follows: |  | 2016-01-26 | Low | N/A | The Reliability Coordinator Operating Procedures, Operating Processes, or Operating Plans identified in R1 but failed to distribute these to all Reliability Coordinators that are required to take action. | The Reliability Coordinator has Operating Procedures, Operating Processes, or Operating Plans identified in R1 but failed to obtain agreement from all Reliability Coordinators that are required to take action. OR Failed to review and update the Operating Procedures, Operating Processes, and Operating Plans identified in R1 annually. | The Reliability Coordinator has Operating Procedures, Operating Processes, or Operating Plans identified in R1 but failed to review and update annually and obtain written agreement from all Reliability Coordinators that are required to take action and failed to distribute these to all Reliability Coordinators that are required to take action. | [12 empty] | RC
Inactive | IRO | IRO-014-2 | R3. | Each Reliability Coordinator shall make notifications and exchange reliability–related information with other Reliability Coordinators in accordance with the Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1. |  | 2016-01-26 | Medium | N/A | N/A | The Reliability Coordinator failed to make notifications OR exchange reliability–related information with impacted Reliability Coordinators. | The Reliability Coordinator failed to make notifications AND exchange reliability–related information with impacted Reliability Coordinators. | [12 empty] | RC
Inactive | IRO | IRO-014-2 | R4. | Each Reliability Coordinator shall participate in agreed upon conference calls, at least weekly (per Requirement 1, Part 1.7) with other Reliability Coordinators within the same Interconnection. |  | 2016-01-26 | Low | N/A | N/A | N/A | The Reliability Coordinator failed to participate in an agreed upon (at least weekly) conference call with impacted Reliability Coordinators within the same Interconnection. | [12 empty] | RC
Inactive | IRO | IRO-014-2 | R5. | Each Reliability Coordinator, upon identification of an Adverse Reliability Impact, shall notify all other Reliability Coordinators. |  | 2016-01-26 | Medium | N/A | The Reliability Coordinator failed to notify one, but not all, of the impacted Reliability Coordinators upon identification of an Adverse Reliability Impact. | N/A | The Reliability Coordinator failed to notify more than one impacted Reliability Coordinators upon identification of an Adverse Reliability Impact. OR The Reliability Coordinator failed to notify the impacted Reliability Coordinator (when there is only one impacted Reliability Coordinator) upon identification of an Adverse Reliability Impact. | [12 empty] | RC
Inactive | IRO | IRO-014-2 | R6. | During each instance where Reliability Coordinators disagree on the existence of an Adverse Reliability Impact each impacted Reliability Coordinator shall operate as though the problem exists. |  | 2016-01-26 | High | N/A | N/A | N/A | The Reliability Coordinator failed to operate under the assumption that the Adverse Reliability Impact existed during an instance where Reliability Coordinators disagree on the existence of an Adverse Reliability Impact. | [12 empty] | RC
Inactive | IRO | IRO-014-2 | R7. | During those instances where Reliability Coordinators disagree on the existence of an Adverse Reliability Impact, the Reliability Coordinator that identified the Adverse Reliability Impact shall develop an action plan to resolve the Adverse Reliability Impact. |  | 2016-01-26 | High | N/A | N/A | N/A | The Reliability Coordinator that identified the Adverse Reliability Impact failed to develop an action plan to resolve the Adverse Reliability Impact during an instance where Reliability Coordinators disagreed on the existence of an Adverse Reliability Impact. | [12 empty] | RC
Inactive | IRO | IRO-014-2 | R8. | During those instances where Reliability Coordinators disagree on the existence of an Adverse Reliability Impact, each Reliability Coordinator shall implement the action plan developed by the Reliability Coordinator that identified the Adverse Reliability Impact unless such actions would violate safety, equipment, regulatory or statutory requirements. |  | 2016-01-26 | High | N/A | N/A | N/A | The Reliability Coordinator failed to implement the action plan developed by the Reliability Coordinator that identified the Adverse Reliability Impact during an instance where Reliability Coordinators disagreed on the existence of an Adverse Reliability Impact. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014-3 | R1. | Each Reliability Coordinator shall have and implement Operating Procedures, Operating Processes, or Operating Plans, for activities that require notification or coordination of actions that may impact adjacent Reliability Coordinator Areas, to support Interconnection reliability. These Operating Procedures, Operating Processes, or Operating Plans shall include, but are not limited to, the following: [See standard for additional information.] | 2017-04-01 |  | Medium | The Reliability Coordinator has Operating Procedures, Operating Processes, or Operating Plans in place for activities that require notification or coordination of actions with impacted adjacent Reliability Coordinators to support Interconnection reliability but failed to address one of the topical areas identified in Parts 1.1 through 1.5. | The Reliability Coordinator has Operating Procedures, Operating Processes, or Operating Plans in place for activities that require notification, or coordination of actions with impacted adjacent Reliability Coordinators to support Interconnection reliability but failed to address two of the topical areas identified in Parts 1.1 through 1.5. | The Reliability Coordinator has Operating Procedures, Operating Processes, or Operating Plans in place for activities that require notification, or coordination of actions with impacted adjacent Reliability Coordinators to support Interconnection reliability but failed to address three of the topical areas identified in Parts 1.1 through 1.5. | The Reliability Coordinator failed to have Operating Procedures, Operating Processes, or Operating Plans in place for activities that require notification, or coordination of actions with impacted adjacent Reliability Coordinators to support Interconnection reliability. OR The Reliability Coordinator failed to implement its Operating Procedures, Operating processes, or Operating Plans when activities required notification, or coordination of actions with impacted adjacent Reliability Cordinators to support Interconnection reliability. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014-3 | R2. | Each Reliability Coordinator shall maintain its Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 as follows: [See standard for additional information.] | 2017-04-01 |  | Low | N/A | The Reliability Coordinator has Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 but failed to address one of the parts specified in Requirement R2. | The Reliability Coordinator has Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 but failed to address two of the parts specified in Requirement R2. | The Reliability Coordinator has Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 but failed to address all three of the parts specified in Requirement R2. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014-3 | R3. | Each Reliability Coordinator, upon identification of an expected or actual Emergency in its Reliability Coordinator Area, shall notify other impacted Reliability Coordinators. | 2017-04-01 |  | Medium | The Reliability Coordinator did not notify one other impacted Reliability Coordinator upon identification of an expected or actual Emergency in its Reliability Coordinator Area. | The Reliability Coordinator did not notify two other impacted Reliability Coordinators upon identification of an expected or actual Emergency in its Reliability Coordinator Area. | The Reliability Coordinator did not notify three other impacted Reliability Coordinators upon identification of an expected or actual Emergency in its Reliability Coordinator Area. | The Reliability Coordinator did not notify four or more other impacted Reliability Coordinators upon identification of an expected or actual Emergency in its Reliability Coordinator Area. NOTE: For the Requirement R3 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size. If a Reliability Coordinator has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014-3 | R4. | Each impacted Reliability Coordinator shall operate as though the Emergency exists during each instance where Reliability Coordinators disagree on the existence of an Emergency. | 2017-04-01 |  | High | N/A | N/A | N/A | The Reliability Coordinator failed to operate as though the Emergency existed during an instance where Reliability Coordinators disagreed on the existence of an Emergency. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014-3 | R5. | Each Reliability Coordinator that Identifies an Emergency in its Reliability Coordinator Area shall develop an action plan to resolve the Emergency during those instances where impacted Reliability Coordinators disagree on the existence of an Emergency. | 2017-04-01 |  | High | N/A | N/A | N/A | The Reliability Coordinator that identifies the Emergency in its Reliability Coordinator Area failed to develop an action plan to resolve the Emergency during an instance where impacted Reliability Coordinators disagreed on the existence of Emergency. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014-3 | R6. | Each impacted Reliability Coordinator shall implement the action plan developed by the Reliability Coordinator that identifies the Emergency during those instances where Reliability Coordinators disagree on the existence of an Emergency, unless such actions would violate safety, equipment, regulatory, or statutory requirements. | 2017-04-01 |  | High | N/A | N/A | N/A | The impacted Reliability Coordinator failed to implement the action plan developed by the Reliability Coordinator that identifies the Emergency during an instance where Reliability Coordinators disagreed on the existence of the Emergency. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-014-3 | R7. | Each Reliability Coordinator shall assist Reliability Coordinators, if requested and able, provided that the requesting Reliability Coordinator has implemented its emergency procedures, unless such actions cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | 2017-04-01 |  | High | N/A | N/A | N/A | The Reliability Coordinator did not provide assistance to Reliability Coordinators, if requested and able, provided that the requesting Reliability Coordinator had implemented its emergency procedures, unless such actions could not physically be implemented or would have violated safety, equipment, regulatory, or statutory requirements. | [12 empty] | RC
Inactive | IRO | IRO-015-1 | R1. | The Reliability Coordinator shall follow its Operating Procedures, Processes, or Plans for making notifications and exchanging reliability-related information with other Reliability Coordinators. | 2007-06-18 | 2017-03-31 | Medium | [16 empty] | RC
Inactive | IRO | IRO-015-1 | R2. | The Reliability Coordinator shall participate in agreed upon conference calls and other communication forums with adjacent Reliability Coordinators. | 2007-06-18 | 2017-03-31 | Low | [16 empty] | RC
Inactive | IRO | IRO-015-1 | R3. | The Reliability Coordinator shall provide reliability-related information as requested by other Reliability Coordinators. | 2007-06-18 | 2017-03-31 | Medium | [16 empty] | RC
Inactive | IRO | IRO-016-1 | R1. | The Reliability Coordinator that identifies a potential, expected, or actual problem that requires the actions of one or more other Reliability Coordinators shall contact the other Reliability Coordinator(s) to confirm that there is a problem and then discuss options and decide upon a solution to prevent or resolve the identified problem. | 2007-06-18 | 2017-03-31 | Medium | [16 empty] | RC
Inactive | IRO | IRO-016-1 | R2. | The Reliability Coordinator shall document (via operator logs or other data sources) its actions taken for either the event or for the disagreement on the problem(s) or for both. | 2007-06-18 | 2014-01-21 | Low | [16 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-017-1 | R1. | Each Reliability Coordinator shall develop, implement, and maintain an outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. The outage coordination process shall: [See standard for additional information.] | 2017-04-01 |  | Medium | The Reliability Coordinator did develop, implement, and maintain an outage coordination process for generation and Transmission outages within its Reliability Coordinator Area but it was missing one of the parts specified in Requirement R1 (Parts 1.1 – 1.4). | The Reliability Coordinator did develop, implement, and maintain an outage coordination process for generation and Transmission outages within its Reliability Coordinator Area but it was missing two of the parts specified in Requirement R1 (Parts 1.1 – 1.4). | The Reliability Coordinator did develop, implement, and maintain an outage coordination process for generation and Transmission outages within its Reliability Coordinator Area but it was missing three of the parts specified in Requirement R1 (Parts 1.1 – 1.4). | The Reliability Coordinator did develop, implement, and maintain an outage coordination process for generation and Transmission outages within its Reliability Coordinator Area but it was missing three of the parts specified in Requirement R1 (Parts 1.1 – 1.4). OR The Reliability Coordinator did not develop, implement, and maintain an outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-017-1 | R2. | Each Transmission Operator and Balancing Authority shall perform the functions specified in its Reliability Coordinator’s outage coordination process. | 2017-04-01 |  | Medium | N/A | N/A | N/A | The Transmission Operator or Balancing Authority did not perform the functions specified in its Reliability Coordinator’s outage coordination process. |  | BA | [17 empty] | TOP
Mandatory Subject to Enforcement | IRO | IRO-017-1 | R3. | Each Planning Coordinator and Transmission Planner shall provide its Planning Assessment to impacted Reliability Coordinators. | 2017-04-01 |  | Medium | N/A | N/A | N/A | The Planning Coordinator or Transmission Planner did not provide its Planning Assessment to impacted Reliability Coordinators. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | IRO | IRO-017-1 | R4. | Each Planning Coordinator and Transmission Planner shall jointly develop solutions with its respective Reliability Coordinator(s) for identified issues or conflicts with planned outages in its Planning Assessment for the Near-Term Transmission Planning Horizon. | 2017-04-01 |  | Medium | N/A | N/A | N/A | The Planning Coordinator or Transmission Planner did not jointly develop solutions with its respective Reliability Coordinator(s) for identified issues or conflicts with planned outages in its Planning Assessment for the Near-term Transmission Planning Horizon. | [10 empty] | PCPA | [9 empty] | TP
Inactive | IRO | IRO-018-1 | R1. | Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | 2018-03-31 | Medium | N/A | The Reliability Coordinator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include one of the elements listed in Part 1.1 through Part 1.3. | The Reliability Coordinator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include two of the elements listed in Part 1.1 through Part 1.3. | The Reliability Coordinator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include any of the elements listed in Part 1.1 through Part 1.3; OR The Reliability Coordinator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. | [12 empty] | RC
Inactive | IRO | IRO-018-1 | R2. | Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | 2018-03-31 | Medium | N/A | The Reliability Coordinator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include one of the elements listed in Part 2.1 through Part 2.3. | The Reliability Coordinator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include two of the elements listed in Part 2.1 through Part 2.3. | The Reliability Coordinator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include any of the elements listed in Part 2.1 through Part 2.3; OR The Reliability Coordinator did not implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. | [12 empty] | RC
Inactive | IRO | IRO-018-1 | R3. | Each Reliability Coordinator shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. |  | 2018-03-31 | Medium | N/A | N/A | The Reliability Coordinator has an alarm process monitor but the alarm process monitor did not provide a notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor occurred. | The Reliability Coordinator does not have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-018-1(i) | R1. | Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: | 2018-04-01 |  | High | N/A | The Reliability Coordinator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include one of the elements listed in Part 1.1 through Part 1.3. | The Reliability Coordinator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include two of the elements listed in Part 1.1 through Part 1.3. | The Reliability Coordinator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include any of the elements listed in Part 1.1 through Part 1.3; OR The Reliability Coordinator did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-018-1(i) | R2. | Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: | 2018-04-01 |  | Medium | N/A | The Reliability Coordinator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include one of the elements listed in Part 2.1 through Part 2.3. | The Reliability Coordinator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include two of the elements listed in Part 2.1 through Part 2.3. | The Reliability Coordinator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include any of the elements listed in Part 2.1 through Part 2.3; OR The Reliability Coordinator did not implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. | [12 empty] | RC
Mandatory Subject to Enforcement | IRO | IRO-018-1(i) | R3. | Each Reliability Coordinator shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | 2018-04-01 |  | Medium | N/A | N/A | The Reliability Coordinator has an alarm process monitor but the alarm process monitor did not provide a notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor occurred. | The Reliability Coordinator does not have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | [12 empty] | RC
Inactive | IRO | IRO-STD-006-0 | WR1. | Curtailment of Contributing Schedules WECC’s Unscheduled Flow Mitigation Plan (Plan), which is on file with FERC and has been accepted by FERC (most recently prior to the date hereof on November 20, 2001 in Docket No. ER01-3085-000), 1/ specifies that members2/ shall comply with requests from (Qualified) Transfer Path Operators to take actions that will reduce unscheduled flow on the Qualified Path in accordance with the table entitled “WECC Unscheduled Flow Procedure Summary of Curtailment Actions,” which is located in Attachment 1 of the Plan. Plan Section 11: 11.1 When USF Accommodation, as specified in Section 7, together with coordinated operation of the Qualified Controllable Devices, as specified in Section 9, are insufficient to reduce the Actual Flow on the Qualified Transfer Path to below the Transfer Limit, the Transfer Path Operator shall request curtailments in Schedules that contribute to the USF through the Qualified Transfer Path according to the USF Reduction Procedure. 11.2 Responsible Entities shall comply in a timely manner with a Transfer Path Operator's request for Schedule Curtailments. 1/ Capitalized terms used in this section, unless separately defined in this standard, shall have the meaning specified in the Plan. 2/ Reliability Standard will apply to all Responsible Entities within theWestern Interconnection. Plan Attachment 1 Section 9: “h. Upon receipt of a curtailment request, Contributing Schedules which are subject to curtailments will be reduced (or equivalent alternative schedule adjustments will be effected) in accordance with the following procedures: i. Receivers of Contributing Schedules will initiate the requested schedule reductions unless an otherwise agreed upon procedure for schedule reduction achieving the equivalent effect on the Qualified Transfer Path is established by the Receiver and/or the Sender. ii. Responsible Entities may arrange among themselves to make curtailments called for by this USF Reduction Procedure in a manner other than prescribed provided that the arrangements are as effective as the identified schedule curtailment in reducing USF across the Qualified Transfer Path. Responsible Entities may make bilateral arrangements, which will enable a Responsible Entity with schedules on the affected Qualified Transfer Path to make the required curtailments in lieu of making larger curtailments in schedules over other parallel paths. Where alternative schedule adjustments are utilized, it is the Receiver's responsibility to cause schedule adjustments to be effected which provide the same reduction in flow across the Qualified Transfer Path as would have been achieved by the prescribed reduction in the Contributing Schedule. iii. The total amount of requested schedule reduction may be apportioned to the applicable schedules at the discretion of the Receiver subject to item iv below. iv. Irrespective of the schedules altered or the manner in which they are altered, each Responsible Entity's overall net reduction in Actual Flow across the constrained Qualified Transfer Path must be equivalent to or greater than the reduction which would have been achieved had the identified schedule reduction occurred as requested. v. System dispatchers or real-time schedulers should identify in advance those schedules that qualify for curtailment requests for all Qualified Transfer Paths. This will expedite implementation of this USF Reduction Procedure when requested. vi. While this USF Reduction Procedure does not expect receivers to curtail schedules which would result in loss of firm load, nothing in this USF Reduction Procedure shall relieve the receiver of the obligation to achieve the required reduction in USF across the constrained Qualified Transfer Path.” Contributing Schedule curtailments apply to schedules in place before initiation of the USF Procedure at Step 4 (First level Contributing Schedule Curtailment) or higher step. At the time a Step 4 Level 1 USF Action or higher step is initiated, Schedules are established by the existence of an “Implemented” NERC Transaction Tag. Restricted Transactions After the USF Event is declared, a transaction with greater than a 5% Transfer Distribution Factor (TDF) on the Qualified Path in the qualified direction will be considered a “Restricted Transaction.” Changes to Restricted Transactions, other thanthe specific curtailments used to comply with relief obligations, cannot be made unless some alternative action is taken to compensate for the full impact on the Qualified Path. This applies to: New transaction, and Extensions or Adjustments to existing transaction.” If two or more Qualified Paths become simultaneously constrained to the point where the curtailment of contributing schedules is necessary, schedule curtailments which relieve USF on one path but increase USF on any other curtailed path shall not be made, unless specific procedures or methods are provided to address this condition. The entity shall be compliant with this standard although the required curtailments were not made. | 2007-06-18 | 2011-06-30 | [6 empty] | BA | [6 empty] | LSE | [10 empty] | TOP
Inactive | MOD | MOD-001-0 | R1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and document a Regional TTC and ATC methodology. (Certain systems that are not required to post ATC values are exempt from this standard.) The Regional Reliability Organization’s TTC and ATC methodology shall include each of the following nine items, and shall explain its use in determining TTC and ATC values: |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-001-0 | R2. | The Regional Reliability Organization shall make the most recent version of the documentation of its TTC and ATC methodology available on a Web site accessible by NERC, the Regional Reliability Organizations, and transmission users. |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-001-1 | R1. | Each Transmission Operator shall select one of the methodologies listed below for calculating Available Transfer Capability (ATC) or Available Flowgate Capability (AFC) for each ATC Path per time period identified in R2 for those Facilities within its Transmission operating area: The Area Interchange Methodology, as described in MOD-028, The Rated System Path Methodology, as described in MOD-029, The Flowgate Methodology, as described in MOD-030 |  | 2010-09-16 | Low | N/A | N/A | N/A | The Transmission Operator did not select one of the specified methodologies for each ATC Path per time period identified in R2 for those Facilities within its Transmission operating area. | [19 empty] | TOP
Inactive | MOD | MOD-001-1 | R2. | Each Transmission Service Provider shall calculate ATC or AFC values as listed below using the methodology or methodologies selected by its Transmission Operator(s): |  | 2010-09-16 | Low | One or more of the following:  The Transmission Service Provider has calculated hourly ATC or AFC values for more than the next 30 hours but less than the next 48 hours.  Has calculated daily ATC or AFC values for more than the next 21 calendar days but less than the next 31 calendar days.  Has calculated monthly ATC or AFC values for more than the next 9 months but less than the next 12 months. | One or more of the following:  The Transmission Service Provider has calculated hourly ATC or AFC values for more than the next 20 hours but less than the next 31 hours.  Has calculated daily ATC or AFC values for more than the next 14 calendar days but less than the next 22 calendar days.  Has calculated monthly ATC or AFC values for more than the next 6 months but less than the next 10 months. | One or more of the following:  The Transmission Service Provider has calculated hourly ATC or AFC values for more than the next 10 hours but less than the next 21 hours.  Has calculated daily ATC or AFC values for more than the next 7 calendar days but less than the next 15 calendar days.  Has calculated monthly ATC or AFC values for more than the next 3 months but less than the next 7 months. | One or more of the following:  The Transmission Service Provider has calculated hourly ATC or AFC values for less than the next 11 hours.  Has calculated daily ATC or AFC values for less than the next 8 calendar days.  Has calculated monthly ATC or AFC values for less than the next 4 months.  Did not use the selected methodology(ies) to calculate ATC. | [21 empty] | TSP
Inactive | MOD | MOD-001-1 | R3. | Each Transmission Service Provider shall prepare and keep current an Available Transfer Capability Implementation Document (ATCID) that includes, at a minimum, the following information: |  | 2010-09-16 | Low | The Transmission Service Provider has an ATCID that does not incorporate changes made up to three months ago. | The Transmission Service Provider has an ATCID that does not incorporate changes made more than three months but not more than six months ago. | The Transmission Service Provider has an ATCID that does not incorporate changes made more than six months but not more than one year ago. OR The Transmission Service Provider has an ATCID, but it does not include one or two of the information items described in R3. | The Transmission Service Provider has an ATCID that does not incorporate changes made a year or more ago. OR The Transmission Service Provider does not have an ATCID, or its ATCID does not include three or more of the information items described in R3. | [21 empty] | TSP
Inactive | MOD | MOD-001-1 | R4. | The Transmission Service Provider shall notify the following entities before implementing a new or revised ATCID: |  | 2010-09-16 | Low | The Transmission Service Provider notified one or more of the parties specified in R4 of a new or modified ATCID after, but not more than 30 calendar days after, its implementation. | The Transmission Service Provider notified one or more of the parties specified in R4 of a new or modified ATCID more than 30, but not more than 60, calendar days after its implementation. | The Transmission Service Provider notified one or more of the parties specified in R4 of a new or modified ATCID more than 60, but not more than 90, calendar days after its implementation. | The Transmission Service Provider notified one or more of the parties specified in R4 of a new or modified ATCID more than 90 calendar days after its implementation. OR The Transmission Service Provider did not notify one or more of the parties specified in R4 of a new or modified ATCID for more than 90 calendar days after its implementation. | [21 empty] | TSP
Inactive | MOD | MOD-001-1 | R5. | The Transmission Service Provider shall make available the current ATCID to all of the entities specified in R4. |  | 2010-09-16 | Low | N/A | N/A | N/A | The Transmission Service Provider did not make the ATCID available to the parties described in R4. | [21 empty] | TSP
Inactive | MOD | MOD-001-1 | R6. | When calculating Total Transfer Capability (TTC) or Total Flowgate Capability (TFC) the Transmission Operator shall use assumptions no more limiting than those used in the planning of operations for the corresponding time period studied, providing such planning of operations has been performed for that time period. |  | 2010-09-16 | Low | The Transmission Operator determined TTC or TFC using assumptions more limiting than those used in planning of operations for the studied time period for more than zero ATC Paths or Flowgates, but not more than 5% of all ATC Paths or Flowgates or 1 ATC Path or Flowgate (whichever is greater). | The Transmission Operator determined TTC or TFC using assumptions more limiting than those used in planning of operations for the studied time period for more than 5% of all ATC Paths or Flowgates or 1 ATC Path or Flowgate (whichever is greater), but not more than 10% of all ATC Paths or Flowgates or 2 ATC Paths or Flowgates (whichever is greater). | The Transmission Operator determined TTC or TFC using assumptions more limiting than those used in planning of operations for the studied time period for more than 10% of all ATC Paths or Flowgates or 2 ATC Path or Flowgate (whichever is greater), but not more than 15% of all ATC Paths or Flowgates or 3 ATC Paths or Flowgates (whichever is greater). | The Transmission Operator determined TTC or TFC using assumptions more limiting than those used in planning of operations for the studied time period for more than 15% of all ATC Paths or Flowgates or more than 3 ATC Paths or Flowgates (whichever is greater). | [19 empty] | TOP
Inactive | MOD | MOD-001-1 | R7. | When calculating ATC or AFC the Transmission Service Provider shall use assumptions no more limiting than those used in the planning of operations for the corresponding time period studied, providing such planning of operations has been performed for that time period. |  | 2010-09-16 | Low | The Transmission Service Provider determined ATC or AFC using assumptions more limiting than those used in planning of operations for the studied time period for more than zero ATC Paths or Flowgates, but not more than 5% of all ATC Paths or Flowgates or 1 ATC Path or Flowgate (whichever is greater). | The Transmission Service Provider determined ATC or AFC using assumptions more limiting than those used in planning of operations for the studied time period for more than 5% of all ATC Paths or Flowgates or 1 ATC Path or Flowgate (whichever is greater), but not more than 10% of all ATC Paths or Flowgates or 2 ATC Paths or Flowgates (whichever is greater). | The Transmission Service Provider determined ATC or AFC using assumptions more limiting than those used in planning of operations for the studied time period for more than 10%, of all ATC Paths or Flowgates or 2 ATC Path or Flowgate (whichever is greater), but not more than 15% of all ATC Paths or Flowgates or 3 ATC Paths or Flowgates (whichever is greater). | The Transmission Service Provider determined ATC or AFC using assumptions more limiting than those used in planning of operations for the studied time period for more than 15% of all ATC Paths or Flowgates or more than 3 ATC Paths or Flowgates (whichever is greater). | [21 empty] | TSP
Inactive | MOD | MOD-001-1 | R8. | Each Transmission Service Provider that calculates ATC shall recalculate ATC at a minimum on the following frequency, unless none of the calculated values identified in the ATC equation have changed: |  | 2010-09-16 | Low | One or more of the following:  For Hourly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for one or more hours but not more than 15 hours, and was in excess of the 175- hour per year requirement.  For Daily, the values described in the ATC equation changed and the Transmission Service provider did not calculate for one or more calendar days but not more than 3 calendar days.  For Monthly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for seven or more calendar days, but less than 14 calendar days. | One or more of the following:  For Hourly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for more than 15 hours but not more than 20 hours, and was in excess of the 175- hour per year requirement.  For Daily, the values described in the ATC equation changed and the Transmission Service provider did not calculate for more than 3 calendar days but not more than 4 calendar days.  For Monthly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for 14 or more calendar days, but less than 21 calendar days. | One or more of the following:  For Hourly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for more than 20 hours but not more than 25 hours, and was in excess of the 175- hour per year requirement. For Daily, the values described in the ATC equation changed and the Transmission Service provider did not calculate for more than 4 calendar days but not more than 5 calendar days.  For Monthly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for 21 or more calendar days, but less than 28 calendar days. | One or more of the following:  For Hourly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for more than 25 hours, and was in excess of the 175- hour per year requirement.  For Daily, the values described in the ATC equation changed and the Transmission Service provider did not calculate for more than 5 calendar days.  For Monthly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for 28 or more calendar days. | [21 empty] | TSP
Inactive | MOD | MOD-001-1 | R9. | Within thirty calendar days of receiving a request by any Transmission Service Provider, Planning Coordinator, Reliability Coordinator, or Transmission Operator for data from the list below solely for use in the requestor’s ATC or AFC calculations, each Transmission Service Provider receiving said request shall begin to make the requested data available to the requestor, subject to the conditions specified in R9.1 and R9.2: [Time Horizon: Operations Planning] • Expected generation and Transmission outages, additions, and retirements. • Load forecasts. • Unit commitments and order of dispatch, to include all designated network resources and other resources that are committed or have the legal obligation to run, as they are expected to run, in one of the following formats chosen by the data provider: Dispatch Order, Participation Factors, Block Dispatch • Aggregated firm capacity set-aside for Network Integration Transmission Service and aggregated non-firm capacity set aside for Network Integration Transmission Service (i.e. Secondary Service). • Firm and non-firm Transmission reservations. • Aggregated capacity set-aside for Grandfathered obligations • Firm roll-over rights. • Any firm and non-firm adjustments applied by the Transmission Service Provider to reflect parallel path impacts. • Power flow models and underlying assumptions. • Contingencies, provided in one or more of the following formats: ? A list of Elements, A list of Flowgates,? A set of selection criteria that can be applied to the Transmission model used by the Transmission Operator and/or Transmission Service Provider • Facility Ratings.• Any other services that impact Existing Transmission Commitments (ETCs). • Values of Capacity Benefit Margin (CBM) and Transmission Reliability Margin (TRM) for all ATC Paths or Flowgates. • Values of Total Flowgate Capability (TFC) and AFC for any Flowgates considered by the Transmission Service Provider receiving the request when selling Transmission service. • Values of TTC and ATC for all ATC Paths for those Transmission Service Providers receiving the request that do not consider Flowgates when selling Transmission Service. • Source and sink identification and mapping to the model. |  | 2010-09-16 | Low | N/A | The Transmission Service Provider made the requested data items specified in R9 available to the requesting entities specified within the requirement, per the schedule specified in the request, subject to the limitations specified in R9, available more than 30 calendar days but less than 45 calendar days after receiving a request. | The Transmission Service Provider made the requested data items specified in R9 available to the requesting entities specified within the requirement, per the schedule specified in the request, subject to the limitations specified in R9, available 45 calendar days or more but less than 60 calendar days after receiving a request. | The Transmission Service Provider did not make the requested data items specified in R9 available to the requesting entities specified within the requirement, per the schedule specified in the request, subject to the limitations specified in R9, available for 60 calendar days or more after receiving a request. | [21 empty] | TSP
Inactive | MOD | MOD-001-1a | R1. | Each Transmission Operator shall select one of the methodologies listed below for calculating Available Transfer Capability (ATC) or Available Flowgate Capability (AFC) for each ATC Path per time period identified in R2 for those Facilities within its Transmission operating area: .The Area Interchange Methodology, as described in MOD-028 .The Rated System Path Methodology, as described in MOD-029 .The Flowgate Methodology, as described in MOD-030 Footnote: All ATC Paths do not have to use the same methodology and no particular ATC Path must use the same methodology for all time periods. | 2011-04-01 | 2024-02-01 | Medium |  |  | The Transmisison Operator did not select one of the specified methodologies for each ATC Path per time period identified in R2 for those Facilities within its Transmission operating area. | [20 empty] | TOP
Inactive | MOD | MOD-001-1a | R2. | Each Transmission Service Provider shall calculate ATC or AFC values as listed below using the methodology or methodologies selected by its Transmission Operator(s): [Time Horizon: Operations Planning] | 2011-04-01 | 2024-02-01 | Medium | One or more of the following: -The Transmission Service Provider has calculated hourly ATC or AFC Values for more than the next 30 hours but less than the next 48 hours. -Has calculated daily ATC or AFC values for more than the next 21 calendar days but less than the next 31 calendar days. -Has calculated monthly ATC or AFC values for more than the nex 9 months but less than the next 12 months. | One or more of the following: -The Transmission Service Provider has calculated hourly ATC or AFC values for more than the 20 hours but less than the next 31 hours. -Has calculated daily ATC or AFC values for more than the next 14 calandar days but less than the next 22 calendar days. -Has calculated monthly ATC or AFC values for more than the next 6 months but less than the next 10 months. | One or more of the following: -The Transmission Service Provider has calculated hourly ATC or AFC values for more than the next 10 hours but less than the next 21 hours. -Has calculated daily ATC or AFC values for more than the next 7 calendar days but less than the next 15 calendar days. -Has calculated monthly ATC or AFC values for more than the next 3 months but less than the next 7 months. | One or more of the following: -The Transmission Service Provider has clculated hourly ATC or AFC values for less than the next 11 hours. -Has calculated daily ATC or AFC values for less than the next 8 calendar days. -Has calculated monthly ATC or AFC values for less than the next 4 months. -Did not use the selected methodology(ies) to calculate ATC. | [21 empty] | TSP
Inactive | MOD | MOD-001-1a | R3. | Each Transmission Service Provider shall prepare and keep current an Available Transfer Capability Implementation Document (ATCID) that includes, at a minimum, the following information: [Time Horizon: Operations Planning] | 2011-04-01 | 2024-02-01 | Medium | The Transmission Service Provider has an ATCID that does not incorporate changes made up to three months ago. | The Transmission Service Provider has an ATCID that does not incorporate changes made more than three months but not more than six months ago. | The Transmission Service Provider has an ATCID that does not incorporate changes made more than six months but no more than one year ago. OR The Transmission Service Provider has an ATCID, but it does not include one or two of the information items described in R3. | The Transmission Service Provider has an ATCID that does not incorporate changes made a year or more ago. OR The Transmission Service Provider does not have an ATCID, or its ATCID does not include three or more of the information items described in R3. | [21 empty] | TSP
Inactive | MOD | MOD-001-1a | R4. | The Transmission Service Provider shall notify the following entities before implementing a new or revised ATCID: [Time Horizon: Operations Planning] | 2011-04-01 | 2024-02-01 | Low | The Transmission Service Provider notified one or more of the parties specified in R4 of a new or modified ATCID after, but not more than 30 calendar days after, its implementation. | The Transmission Service Provider notified one or more of the parties specified in R4 of a new or modified ATCID more than 30, but not more than 60, calandar days after its implementation. | The Transmission Service Provider notified one ormore of the parties specified in R4 of a new or modified ATCID more than 60, but not more than 90, calendar days after its implementation. | The Transmission Service Provider notified one or more of the parties specified in R4 of a new or modified ATCID more than 90 calendar days after its implementation. OR The Transmission Service Provider did not notify one or more of the parties specified in R4 of a new or modified ATCID for more than 90 calendar days after its implementation. | [21 empty] | TSP
Inactive | MOD | MOD-001-1a | R5. | The Transmission Service Provider shall make available the current ATCID to all of the entities specified in R4. [Time Horizon: Operations Planning] | 2011-04-01 | 2024-02-01 | Low |  |  |  | The Transmission Service Provider did not make the ATCID available to the parties described in R4. | [21 empty] | TSP
Inactive | MOD | MOD-001-1a | R6. | When calculating Total Transfer Capability (TTC) or Total Flowgate Capability (TFC) the Transmission Operator shall use assumptions no more limiting than those used in the planning of operations for the corresponding time period studied, providing such planning of operations has been performed for that time period. [Time Horizon: Operations Planning] | 2011-04-01 | 2024-02-01 | Medium | The Transmission Operator determined TTC or TFC using assumptions more limiting than those used in planning of operations for the studied time period for more than zero ATC Paths or Flowgates, but not more than 5% of all the ATC Paths or Flowgates or 1 ATC Path or Flowgate (whichever is greater). | The Transmission Operator determined TTC or TFC using assumptions more limiting than those used in planning of operations for the studied time period for more than 5% of all ATC Paths or Flowgates or 1 ATC Path or Flowgates (whichever is greater), but not more than 10% of all ATC Paths or Flowgates or 2 ATC Paths or Flowgates (whichever is greater). | The Transmission Operator determined TTC or TFC using assumptions more limiting than those used in planning of operations for the studied time period for more than 10% of all ATC Paths or Flowgates or 2% ATC Path or Flowgate (whichever is greater), but not more than 15% of all ATC Paths or Flowgates or 3 ATC Paths or Flowgates (whichever is greater). | The Transmission Operator determined TTC or TFC using assumptions more limiting than those used in planning of operations for the studied time period for more than 15% of all ATC Paths or Flowgates or more than 3 ATC Paths or Flowgates (whichever is greater). | [19 empty] | TOP
Inactive | MOD | MOD-001-1a | R7. | When calculating ATC or AFC the Transmission Service Provider shall use assumptions no more limiting than those used in the planning of operations for the corresponding time period studied, providing such planning of operations has been performed for that time period. [Time Horizon: Operations Planning] | 2011-04-01 | 2024-02-01 | Medium | The Transmission Service Provider determined ATC or AFC using assumptions more limiting than those used in planning of operations for the studied time period for more than zero ATC Paths or Flowgates, but not more than 5% of all ATC Paths or Flowgates or 1 ATC Path or Flowgate (whichever is greater). | The Transmission Service Provider determined ATC or AFC using assumptions more limiting than those used in planning of operations for the studied time period for more than 5% of all ATC Paths or Flowgates or 1 ATC Path or Flowgate (whichever is greater), but not more than 10% of all ATC Paths or Flowgates or 2 ATC Paths or Flowgates (whichever is greater). | The Transmission Service Provider determined ATC or AFC using assumptions more limiting than those used in planning of operations for the studied time period for more than 10%, of all ATC Paths or Flowgates or 2 ATC Path or Flowgate (whichever is greater), but not more than 15% of all ATC Paths or Flowgates or 3 ATC Paths or Flowgates (whichever is greater). | The Transmission Service Provider determined ATC or AFC using assumptions more limiting than those used in planning of operations for the studied time period for more than 15% of all ATC Paths or Flowgates or more than 3 ATC Paths or Flowgates (whichever is greater). | [21 empty] | TSP
Inactive | MOD | MOD-001-1a | R8. | Each Transmission Service Provider that calculates ATC shall recalculate ATC at a minimum on the following frequency, unless none of the calculated values identified in the ATC equation have changed: [Time Horizon: Operations Planning] | 2011-04-01 | 2024-02-01 | Medium | One or more of the following: ? For Hourly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for one or more hours but not more than 15 hours, and was in excess of the 175-hour per year requirement. ? For Daily, the values described in the ATC equation changed and the Transmission Service provider did not calculate for one or more calendar days but not more than 3 calendar days. ? For Monthly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for seven or more calendar days, but less than 14 calendar days. | One or more of the following: ? For Hourly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for more than 15 hours but not more than 20 hours, and was in excess of the 175-hour per year requirement. ? For Daily, the values described in the ATC equation changed and the Transmission Service provider did not calculate for more than 3 calendar days but not more than 4 calendar days. ? For Monthly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for 14 or more calendar days, but less than 21 calendar days. | One or more of the following: ? For Hourly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for more than 20 hours but not more than 25 hours, and was in excess of the 175-hour per year requirement. For Daily, the values described in the ATC equation changed and the Transmission Service provider did not calculate for more than 4 calendar days but not more than 5 calendar days. ? For Monthly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for 21 or more calendar days, but less than 28 calendar days. | One or more of the following: ? For Hourly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for more than 25 hours, and was in excess of the 175-hour per year requirement. ? For Daily, the values described in the ATC equation changed and the Transmission Service provider did not calculate for more than 5 calendar days. ? For Monthly, the values described in the ATC equation changed and the Transmission Service provider did not calculate for 28 or more calendar days. | [21 empty] | TSP
Inactive | MOD | MOD-001-1a | R9. | Within thirty calendar days of receiving a request by any Transmission Service Provider, Planning Coordinator, Reliability Coordinator, or Transmission Operator for data from the list below solely for use in the requestor’s ATC or AFC calculations, each Transmission Service Provider receiving said request shall begin to make the requested data available to the requestor, subject to the conditions specified in R9.1 and R9.2: [Time Horizon: Operations Planning] • Expected generation and Transmission outages, additions, and retirements. • Load forecasts. • Unit commitments and order of dispatch, to include all designated network resources and other resources that are committed or have the legal obligation to run, as they are expected to run, in one of the following formats chosen by the data provider: Dispatch Order, Participation Factors, Block Dispatch • Aggregated firm capacity set-aside for Network Integration Transmission Service and aggregated non-firm capacity set aside for Network Integration Transmission Service (i.e. Secondary Service). • Firm and non-firm Transmission reservations. • Aggregated capacity set-aside for Grandfathered obligations • Firm roll-over rights. • Any firm and non-firm adjustments applied by the Transmission Service Provider to reflect parallel path impacts. • Power flow models and underlying assumptions. • Contingencies, provided in one or more of the following formats: - A list of Elements, -A list of Flowgates,- A set of selection criteria that can be applied to the Transmission model used by the Transmission Operator and/or Transmission Service Provider • Facility Ratings.• Any other services that impact Existing Transmission Commitments (ETCs). • Values of Capacity Benefit Margin (CBM) and Transmission Reliability Margin (TRM) for all ATC Paths or Flowgates. • Values of Total Flowgate Capability (TFC) and AFC for any Flowgates considered by the Transmission Service Provider receiving the request when selling Transmission service. • Values of TTC and ATC for all ATC Paths for those Transmission Service Providers receiving the request that do not consider Flowgates when selling Transmission Service. • Source and sink identification and mapping to the model. | 2011-04-01 | 2024-02-01 | Medium | N/A | The Transmission Service Provider made the requested data items specified in R9 available to the requesting entities specified within the requirement, per the schedule specified in the request, subject to the limitations specified in R9, available more than 30 calendar days but less than 45 calendar days after receiving a request. | The Transmission Service Provider made the requested data items specified in R9 available to the requesting entities specified within the requirement, per the schedule specified in the request, subject to the limitations specified in R9, available 45 calendar days or more but less than 60 calendar days after receiving a request. | The Transmission Service Provider did not make the requested data items specified in R9 available to the requesting entities specified within the requirement, per the schedule specified in the request, subject to the limitations specified in R9, available for 60 calendar days or more after receiving a request. | [21 empty] | TSP
Inactive | MOD | MOD-001-2 | R1. | Each Transmission Operator that determines Total Flowgate Capability (TFC) or Total Transfer Capability (TTC) shall develop a written methodology (or methodologies) for determining TFC or TTC values. The methodology (or methodologies) shall reflect the Transmission Operator’s current practices for determining TFC or TTC values. |  | 2019-05-09 | Low | Each Transmission Operator that determines TFC or TTC has not described its method for accounting for one of the limitations listed in part 1.1 in its written methodology. (1.1) OR Each Transmission Operator that determines TFC or TTC has not described its method for accounting for one of the element listed in part 1.2 in its written methodology, provided that element impacts its TFC or TTC determination. (1.2) | Each Transmission Operator that determines TFC or TTC has not described its method for accounting for two of the limitations listed in part 1.1 in its written methodology. (1.1) OR Each Transmission Operator that determines TFC or TTC has not described its method for accounting for two, three, or four elements listed in part 1.2 in its written methodology, provided those elements impacts its TFC or TTC determination. (1.2) | Each Transmission Operator that determines TFC or TTC has not described its method for accounting for any of the limitations listed in part 1.1 in its written methodology. (1.1) OR Each Transmission Operator that determines TFC or TTC has not described its method for accounting for five, six, or seven elements of listed in part 1.2 in its written methodology, provided those elements impacts its TFC or TTC determination. (1.2) OR Each Transmission Operator that determines TFC or TTC has not described the process for including any reliability-related constraints that have been requested by another Transmission Operator, provided the constraints are also used in the requesting Transmission Operator’s TFC or TTC calculation and the request referenced part 1.3. (1.3) OR Each Transmission Operator that determines TFC or TTC has not used (i) an impact test process for including requested constraints, (ii) a process to account for requested constraints that have a five percent or greater distribution factor for a transfer between areas in the TTC determination, or (iii) a mutually agreed upon method for determining whether requested constraints need to be included in the TFC or TTC determination. (1.3.1, 1.3.2, 1.3.3) | Each Transmission Operator that determines TFC or TTC did not develop a written methodology for describing its current practices for determining TFC or TTC values. OR Each Transmission Operator that determines TFC or TTC developed a written methodology for determining TFC or TTC but the methodology did not reflect its current practices for determining TFC or TTC values. | [19 empty] | TOP
Inactive | MOD | MOD-001-2 | R2. | Each Transmission Service Provider that determines Available Flowgate Capability (AFC) or Available Transfer Capability (ATC) shall develop an Available Transfer Capability Implementation Document (ATCID) that describes the methodology (or methodologies) for determining AFC or ATC values. The methodology (or methodologies) shall reflect the Transmission Service Provider’s current practices for determining AFC or ATC values. |  | 2019-05-09 | Low | Each Transmission Service Provider that determines AFC or ATC has not described its method for accounting for one of the elements listed in part 2.1 in its written methodology, provided that element impacts its AFC or ATC determination. (2.1) | Each Transmission Service Provider that determines AFC or ATC has not described its method for accounting for two, three, or four elements listed in part 2.1 in its written methodology, provided the elements impact its AFC or ATC determination. (2.1) | Each Transmission Service Provider that determines AFC or ATC has not described its method for accounting for five, six, or seven elements listed in part 2.1 in its written methodology, provided the elements impact its AFC or ATC determination. (2.1) OR Each Transmission Service Provider that uses the Flowgate Methodology did not use the AFC determined by the Transmission Service Provider for reliability-related constraints identified in part 1.3. (2.2) | Each Transmission Service Provider that determines AFC or ATC did not develop an ATCID describing its AFC or ATC methodology. OR Each Transmission Service Provider that determines AFC or ATC did not reflect its current practices for determining AFC or ATC values in its ATCID. | [21 empty] | TSP
Inactive | MOD | MOD-001-2 | R3. | Each Transmission Service Provider that determines Capacity Benefit Margin (CBM) values shall develop a Capacity Benefit Margin Implementation Document (CBMID) that describes its method for determining CBM values. The method described in the CBMID shall reflect the Transmission Service Provider’s current practices for determining CBM values. |  | 2019-05-09 | Low | None | None | None | Each Transmission Service Provider that determines CBM values did not develop a CBMID describing its method for determining CBM values. OR Each Transmission Service Provider that determines CBM values did not reflect its current practices for determining CBM values in its CBMID. | [21 empty] | TSP
Inactive | MOD | MOD-001-2 | R4. | Each Transmission Operator that determines Transmission Reliability Margin (TRM) values shall develop a Transmission Reliability Margin Implementation Document (TRMID) that describes its method for determining TRM values. The method described in the TRMID shall reflect the Transmission Operator’s current practices for determining TRM values. |  | 2019-05-09 | Low | None | None | None | Each Transmission Operator that determines TRM values did not develop a TRMID describing its method for determining TRM values. OR Each Transmission Operator that determines TRM values did not reflect its current practices for determining TRM values in its TRMID. | [19 empty] | TOP
Inactive | MOD | MOD-001-2 | R5. | Within 45 calendar days of receiving a written request that references this specific requirement from a Planning Coordinator, Reliability Coordinator, Transmission Operator, Transmission Planner, Transmission Service Provider, or any other registered entity that demonstrates a reliability need, each Transmission Operator or Transmission Service Provider shall provide: |  | 2019-05-09 | Low | Each Transmission Operator or Transmission Service Provider did not respond in writing to a written request by one or more of the registered entities specified in Requirement R5 within 45 calendar days from the date of the request, but did respond in writing within 75 calendar days. | Each Transmission Operator or Transmission Service Provider did not respond in writing to a written request by one or more of the registered entities specified in Requirement R5 within 76 calendar days from the date of the request, but did respond in writing within 105 calendar days. | Each Transmission Operator or Transmission Service Provider did not respond in writing to a written request by one or more of the registered entities specified in Requirement R5 within 106 calendar days from the date of the request, but did respond in writing within 135 calendar days. | Each Transmission Operator or Transmission Service Provider failed to respond in writing to a written request by one or more of the registered entities specified in Requirement R5. | [19 empty] | TOP |  | TSP
Inactive | MOD | MOD-001-2 | R6. | Each Transmission Operator or Transmission Service Provider that receives a written request from another Transmission Operator or Transmission Service Provider for data related to AFC, ATC, TFC, or TTC determinations that (1) references this specific requirement, and (2) specifies that the requested data is for use in the requesting party’s AFC, ATC, TFC, or TTC determination shall take one of the actions below. |  | 2019-05-09 | Low | Each Transmission Operator or Transmission Service Provider did not respond to a written request for data by one or more of the registered entities specified in Requirement R6 by making the requested data available within 45 calendar days from the date of the request, but did respond within 75 calendar days. | Each Transmission Operator or Transmission Service Provider did not respond to a written request for data by one or more of the registered entities specified in Requirement R6 by making data available within 76 calendar days from the date of the request, but did respond within 105 calendar days. | Each Transmission Operator or Transmission Service Provider did not respond to a written request by one or more of the registered entities specified in Requirement R6 by making data available within 106 calendar days from the date of the request, but did respond within 135 calendar days. | Each Transmission Operator or Transmission Service Provider failed to respond to a written request for data by making data available to one or more of the entities specified in Requirement R6. | [19 empty] | TOP |  | TSP
Inactive | MOD | MOD-002-0 | R1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and implement a procedure to periodically review (at least annually) and ensure that the TTC and ATC calculations and resulting values of member Transmission Service Providers comply with the Regional TTC and ATC methodology and applicable Regional criteria. |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-002-0 | R2. | Each Regional Reliability Organization shall document the results of its periodic reviews of TTC and ATC. |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-002-0 | R3. | The Regional Reliability Organization shall provide the results of its most current reviews of TTC and ATC to NERC on request (within 30 calendar days). |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-003-0 | R1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and document a procedure on how transmission users can input their concerns or questions regarding the TTC and ATC methodology and values of the Transmission Service Provider(s), and how these concerns or questions will be addressed. The Regional Reliability Organization’s procedure shall specify the following: |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-003-0 | R2. | The Regional Reliability Organization shall post on a web site that is accessible by the Regional Reliability Organizations, NERC, and transmission users, its procedure for receiving and addressing concerns about the TTC and ATC methodology and TTC and ATC values of member Transmission Service Providers. |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-004-0 | R1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and document a Regional CBM methodology. The Regional Reliability Organization’s CBM methodology shall include each of the following ten items, and shall explain its use in determining CBM value. Other items that are Regional Reliability Organization specific or that are considered in each respective Regional Reliability Organization methodology shall also be explained along with their use in determining CBM values. |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-004-0 | R2. | The Regional Reliability Organization shall make the most recent version of the documentation of its CBM methodology available on a website accessible by NERC, the Regional Reliability Organizations, and transmission users. |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-004-1 | R1. | The Transmission Service Provider that maintains CBM shall prepare and keep current a “Capacity Benefit Margin Implementation Document” (CBMID) that includes, at a minimum, the following information: | 2011-04-01 | 2024-02-01 | Medium | The Transmission Service Provider that maintains CBM has a CBMID that does not incorporate changes that have been made within the last three months. | The Transmission Service Provider that maintains CBM has a CBMID that does not incorporate changes that have been made more than three, but not more than six, months ago. OR The CBM maintaining Transmission Service Provider’s CBMID does not address one of the sub requirements. | The Transmission Service Provider that maintains CBM has a CBMID that does not incorporate changes that have been made more than six, but not more than twelve, months ago. OR The CBM maintaining Transmission Service Provider’s CBMID does not address two of the sub requirements. | The Transmission Service Provider that maintains CBM has a CBMID that does not incorporate changes that have been made more than twelve months ago. OR The Transmission Service Provider that maintains CBM does not have a CBMID; OR The CBM maintaining Transmission Service Provider’s CBMID does not address three of the sub requirements. | [21 empty] | TSP
Inactive | MOD | MOD-004-1 | R2. | The Transmission Service Provider that maintains CBM shall make available its current CBMID to the Transmission Operators, Transmission Service Providers, Reliability Coordinators, Transmission Planners, Resource Planners, and Planning Coordinators that are within or adjacent to the Transmission Service Provider’s area, and to the Load Serving Entities and Balancing Authorities within the Transmission Service Provider’s area, and notify those entities of any changes to the CBMID prior to the effective date of the change. [Time Horizon: Operations Planning] | 2011-04-01 | 2024-02-01 | Medium | The Transmission Service Provider that maintains CBM notifies one or more of the entities specified in R2 of a change in the CBM ID after the effective date of the change, but not more than 30 calendar days after the effective date of the change. | The Transmission Service Provider that maintains CBM notifies one or more of the entities specified in R2 of a change in the CBM ID 30 or more calendar days but not more than 60 calendar days after the effective date of the change. | The Transmission Service Provider that maintains CBM notifies one or more of the entities specified in R2 of a change in the CBM ID 60 or more calendar days but not more than 90 calendar days after the effective date of the change. OR The Transmission Service Provider that maintains CBM made available the CBMID to at least one, but not all, of the entities specified in R2. | The Transmission Service Provider that maintains CBM notifies one or more of the entities specified in R2 of a change in the CBM ID more than 90 calendar days after the effective date of the change. OR The Transmission Service Provider that maintains CBM made available the CBMID to none of the entities specified in R2. | [21 empty] | TSP
Inactive | MOD | MOD-004-1 | R3. | Each Load-Serving Entity determining the need for Transmission capacity to be set aside as CBM for imports into a Balancing Authority Area shall determine that need by: | 2011-04-01 | 2024-02-01 | Medium |  | The Load-Serving Entity did not use one of the methods described in R3.1 OR The Load-Serving Entity did not identify paths or regions as described in R3.2 |  | The Load-Serving Entity did not use one of the methods described in R3.1 AND The Load-Serving Entity did not identify paths or regions as described in R3.2 | [8 empty] | LSE
Inactive | MOD | MOD-004-1 | R4. | Each Resource Planner determining the need for Transmission capacity to be set aside as CBM for imports into a Balancing Authority Area shall determine that need by: | 2011-04-01 | 2024-02-01 | Medium |  | The Resource Planner did not use one of the methods described in R4.1 OR The Resource Planner did not identify paths or regions as described in R4.2 |  | The Resource Planner did not use one of the methods described in R4.1 AND The Resource Planner did not identify paths or regions as described in R4.2 | [14 empty] | RP
Inactive | MOD | MOD-004-1 | R5. | At least every 13 months, the Transmission Service Provider that maintains CBM shall establish a CBM value for each ATC Path or Flowgate to be used for ATC or Available Flowgate Capability (AFC) calculations during the 13 full calendar months (months 2-14) following the current month (the month in which the Transmission Service Provider is establishing the CBM values). This value shall: [Time Horizon: Operations Planning] | 2011-04-01 | 2024-02-01 | Medium | The Transmission Service Provider that maintains CBM established CBM more than 13 months, but not more than 16 months, after the last time the values were established. | The Transmission Service Provider that maintains CBM established CBM more than 16 months, but not more than 19 months, after the last time the values were established. OR The Transmission Service Provider that maintains CBM did not consider one or more of the items described in R5.1 that was available. OR The Transmission Service Provider that maintains CBM did not base the allocation on one or more paths or regions as described in R5.2. | The Transmission Service Provider that maintains CBM established CBM more than 19 months, but not more than 22 months, after the last time the values were established. | The Transmission Service Provider that maintains CBM established CBM more than 22 months after the last time the values were established. OR The Transmission Service Provider that maintains CBM failed to establish an initial value for CBM. OR The Transmission Service Provider that maintains CBM did not consider one or more of the items described in R5.1 that was available, and did not base the allocation on one or more paths or regions as described in R5.2 | [21 empty] | TSP
Inactive | MOD | MOD-004-1 | R6. | At least every 13 months, the Transmission Planner shall establish a CBM value for each ATC Path or Flowgate to be used in planning during each of the full calendar years two through ten following the current year (the year in which the Transmission Planner is establishing the CBM values). This value shall: [Time Horizon: Long-term Planning] | 2011-04-01 | 2024-02-01 | Medium | The Transmission Planner with an associated Transmission Service Provider that maintains CBM established CBM for each of the years 2 through 10 more than 13 months, but not more than 16 months, after the last time the values were established. | The Transmission Planner with an associated Transmission Service Provider that maintains CBM established CBM for each of the years 2 through 10 more than 16 months, but not more than 19 months, after the last time the values were established. OR The Transmission Planner with an associated Transmission Service Provider that maintains CBM did not consider one or more of the items described in R6.1 that was available. OR The Transmission Planner with an associated Transmission Service Provider that maintains CBM did not base the allocation on one or more paths or regions as described in R6.2 | The Transmission Planner with an associated Transmission Service Provider that maintains CBM established CBM for each of the years 2 through 10 more than 19 months, but not more than 22 months, after the last time the values were established. | The Transmission Planner with an associated Transmission Service Provider that maintains CBM established CBM for each of the years 2 through 10 more than 22 months after the last time the values were established. OR The Transmission Planner with an associated Transmission Service Provider that maintains CBM failed to establish an initial value for CBM for each of the years 2 through 10. OR The Transmission Planner with an associated Transmission Service Provider that maintains CBM did not consider one or more of the items described in R6.1 that was available, and did not base the allocation on one or more paths or regions as described in R6.2 | [20 empty] | TP
Inactive | MOD | MOD-004-1 | R7. | Less than 31 calendar days after the establishment of CBM, the Transmission Service Provider that maintains CBM shall notify all the Load-Serving Entities and Resource Planners that determined they had a need for CBM on the Transmission Service Provider’s system of the amount of CBM set aside. [Time Horizon: Operations Planning] | 2011-04-01 | 2024-02-01 | Medium | The Transmission Service Provider that maintains CBM notified all the entities as required, but did so in 31 or more days, but less than 45 days. | The Transmission Service Provider that maintains CBM notified all the entities as required, but did so in 45 or more days, but less than 60 days. | The Transmission Service Provider that maintains CBM notified all the entities as required, but did so in 60 or more days, but less than 75 days. OR The Transmission Service Provider that maintains CBM notified at least one, but not all, of the entities as required. | The Transmission Service Provider that maintains CBM notified all the entities as required, but did so in 75 or more days, OR The Transmission Service Provider that maintains CBM notified none of the entities as required. | [21 empty] | TSP
Inactive | MOD | MOD-004-1 | R8. | Less than 31 calendar days after the establishment of CBM, the Transmission Planner shall notify all the Load-Serving Entities and Resource Planners that determined they had a need for CBM on the system being planned by the Transmission Planner of the amount of CBM set aside. [Time Horizon: Operations Planning] | 2011-04-01 | 2024-02-01 | Medium | The Transmission Planner with an associated Transmission Service Provider that maintains CBM notified all the entities as required, but did so in 31 or more days, but less than 45 days. | The Transmission Planner with an associated Transmission Service Provider that maintains CBM notified all the entities as required, but did so in 45 or more days, but less than 60 days. | The Transmission Planner with an associated Transmission Service Provider that maintains CBM notified all the entities as required, but did so in 60 or more days, but less than 75 days. OR The Transmission Planner with an associated Transmission Service Provider that maintains CBM notified at least one, but not all, of the entities as required. | The Transmission Planner with an associated Transmission Service Provider that maintains CBM notified all the entities as required, but did so in 75 or more days, OR The Transmission Planner with an associated Transmission Service Provider that maintains CBM notified none of the entities as required. | [20 empty] | TP
Inactive | MOD | MOD-004-1 | R9. | The Transmission Service Provider that maintains CBM and the Transmission Planner shall each provide (subject to confidentiality and security requirements) copies of the applicable supporting data, including any models, used for determining CBM or allocating CBM over each ATC Path or Flowgate to the following: [Time Horizon: Operations Planning, Long-term Planning] | 2011-04-01 | 2024-02-01 | Low | The Transmission Service Provider or Transmission Planner provided a requester specified in R9 with the supporting data, including models, used to allocate CBM more than 30, but not more than 45, days after the submission of the request. | The Transmission Service Provider or Transmission Planner provided a requester specified in R9 with the supporting data, including models, used to allocate CBM more than 45, but not more than 60, days after the submission of the request. | The Transmission Service Provider or Transmission Planner provided a requester specified in R9 with the supporting data, including models, used to allocate CBM more than 60, but not more than 75, days after the submission of the request. OR The Transmission Service Provider or Transmission Planner provided at least one, but not all, of the requesters specified in R9 with the supporting data, including models, used to allocate CBM. | The Transmission Service Provider or Transmission Planner provided a requester specified in R9 with the supporting data, including models, used to allocate CBM more than 75 days after the submission of the request. OR The Transmission Service Provider or Transmission Planner provided none of the requesters specified in R9 with the supporting data, including models, used to allocate CBM. | [20 empty] | TP | TSP
Inactive | MOD | MOD-004-1 | R10. | The Load-Serving Entity or Balancing Authority shall request to import energy over firm Transfer Capability set aside as CBM only when experiencing a declared NERC Energy Emergency Alert (EEA) 2 or higher. [Time Horizon: Same-day Operations] | 2011-04-01 | 2024-02-01 | Low | N/A | N/A | N/A | A Load-Serving Entity or Balancing Authority requested to schedule energy over CBM while not in an EEA 2 or higher. |  | BA | [6 empty] | LSE
Inactive | MOD | MOD-004-1 | R11. | When reviewing an Arranged Interchange using CBM, all Balancing Authorities and Transmission Service Providers shall waive, within the bounds of reliable operation, any Real-time timing and ramping requirements. [Time Horizon: Same-day Operations] | 2011-04-01 | 2024-02-01 | Medium | N/A | N/A | N/A | A Balancing Authority or Transmission Service Provider denied an Arranged Interchange using CBM based on timing or ramping requirements without a reliability reason to do so. |  | BA | [19 empty] | TSP
Inactive | MOD | MOD-004-1 | R12. | The Transmission Service Provider that maintains CBM shall approve, within the bounds of reliable operation, any Arranged Interchange using CBM that is submitted by an “energy deficient entity ” under an EEA 2 if: Footnote: See Attachment 1-EOP-002-0 for explanation. | 2011-04-01 | 2024-02-01 | Medium | N/A | N/A | N/A | The Transmission Service Provider failed to approve an Arranged Interchange for CBM that met the criteria described in R12 without a reliability reason to do so. | [21 empty] | TSP
Inactive | MOD | MOD-005-0 | R1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and implement a procedure to review (at least annually) the CBM calculations and the resulting values of member Transmission Service Providers to ensure that they comply with the Regional Reliability Organization’s CBM methodology. The procedure shall include the following four requirements: |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-005-0 | R2. | Each Regional Reliability Organization shall document its CBM procedure and shall make its CBM review procedure available to NERC on request (within 30 calendar days). |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-005-0 | R3. | The Regional Reliability Organization shall provide documentation of the results of the most current implementation of its CBM review procedure to NERC on request (within 30 calendar days). |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-006-0 | R1. | Each Transmission Service Provider shall document its procedure on the use of Capacity Benefit Margin (CBM) (scheduling of energy against a CBM reservation). The procedure shall include the following three components: | 2007-06-18 | 2009-05-12 | Low | [25 empty] | TSP
Inactive | MOD | MOD-006-0 | R2. | Each Transmission Service Provider shall make its CBM use procedure available on a web site accessible by the Regional Reliability Organizations, NERC, and transmission users. | 2007-06-18 | 2009-05-12 | Low | The Transmission Service Provider has demonstrated the procedure is available on the Web but is deficient with minor details. |  |  | The Transmission Service Provider has failed to provide the procedure on the Web as directed by the requirement. | [21 empty] | TSP
Inactive | MOD | MOD-006-0.1 | R1. | Each Transmission Service Provider shall document its procedure on the use of Capacity Benefit Margin (CBM) (scheduling of energy against a CBM reservation). The procedure shall include the following three components: | 2009-05-13 | 2011-03-31 | [26 empty] | TSP
Inactive | MOD | MOD-006-0.1 | R2. | Each Transmission Service Provider shall make its CBM use procedure available on a web site accessible by the Regional Reliability Organizations, NERC, and transmission users. | 2009-05-13 | 2011-03-31 | [26 empty] | TSP
Inactive | MOD | MOD-007-0 | R1. | Each Transmission Service Provider that uses CBM shall report (to the Regional Reliability Organization, NERC and the transmission users) the use of CBM by the Load-Serving Entities’ Loads on its system, except for CBM sales as Non-Firm Transmission Service. (This use of CBM shall be consistent with the Transmission Service Provider’s procedure for use of CBM.) | 2007-06-18 | 2011-03-31 | Low | [25 empty] | TSP
Inactive | MOD | MOD-007-0 | R2. | The Transmission Service Provider shall post the following three items within 15 calendar days after the use of CBM for an Energy Emergency. This posting shall be on a web site accessible by the Regional Reliability Organizations, NERC, and transmission users. | 2007-06-18 | 2011-03-31 | Low | . | [24 empty] | TSP
Inactive | MOD | MOD-008-0 | R1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and document a Regional TRM methodology. The Region’s TRM methodology shall specify or describe each of the following five items, and shall explain its use, if any, in determining TRM values. Other items that are Region-specific or that are considered in each respective Regional methodology shall also be explained along with their use in determining TRM values. |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-008-0 | R2. | The Regional Reliability Organization shall make its most recent version of the documentation of its TRM methodology available on a web site accessible by NERC, the Regional Reliability Organizations, and transmission users. |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-008-1 | R1. | Each Transmission Operator shall prepare and keep current a TRM Implementation Document (TRMID) that includes, as a minimum, the following information: [Time Horizon: Operations Planning] | 2011-04-01 | 2024-02-01 | Medium | The Transmission Operator has a TRMID that does not incorporate changes made up to three months ago. | The Transmission Operator has a TRMID that does not incorporate changes that have been made three or more months ago but less than six months ago. OR The Transmission Operator’s TRMID does not address one of the following: ? R1.1, R1.2, Any one or more of the following: R1.3.1, R1.3.2 or R1.3.3 | The Transmission Operator has a TRMID that does not incorporate changes that have been made six or more months ago but less than one year ago. OR The Transmission Operator’s TRMID does not address two of the following: R1.1, R1.2, Any one of the following: R1.3.1, R1.3.2 or R1.3.3 | The Transmission Operator has a TRMID that does not incorporate changes that have been made one year ago or more. OR The Transmission Operator does not have a TRMID. OR The Transmission Operator’s TRMID does not address three of the following: R1.1, R1.2, Any one or more of the following: R1.3.1, R1.3.2, or R1.3.3 | [19 empty] | TOP
Inactive | MOD | MOD-008-1 | R2. | Each Transmission Operator shall only use the components of uncertainty from R1.1 to establish TRM, and shall not include any of the components of Capacity Benefit Margin (CBM). Transmission capacity set aside for reserve sharing agreements can be included in TRM. [Time Horizon: Operations Planning] | 2011-04-01 | 2024-02-01 | Medium | N/A | N/A | N/A | One or both of the following: ? The Transmission Operator included elements of uncertainty not defined in R1 in their establishment of TRM. ? The Transmission Operator included components of CBM in TRM. | [19 empty] | TOP
Inactive | MOD | MOD-008-1 | R3. | Each Transmission Operator shall make available its TRMID, and if requested, underlying documentation (if any) used to determine TRM, in the format used by the Transmission Operator, to any of the following who make a written request no more than 30 calendar days after receiving the request. [Time Horizon: Operations Planning] Transmission Service Providers, Reliability Coordinators, Planning Coordinators, Transmission Planner, Transmission Operators | 2011-04-01 | 2024-02-01 | Low | The Transmission Operator made the TRMID available to a requesting entity specified in R3 but provided TRMID in more than 30 days but less than 45 days. | The Transmission Operator made the TRMID available to a requesting entity specified in R3 but provided TRMID in 45 days or more but less than 60 days. | The Transmission Operator made the TRMID available to a requesting entity specified in R3 but provided TRMID in 60 days or more but less than 90 days. | The Transmission Operator did not make the TRMID available for 90 days or more. | [19 empty] | TOP
Inactive | MOD | MOD-008-1 | R4. | Each Transmission Operator that maintains TRM shall establish TRM values in accordance with the TRMID at least once every 13 months. [Time Horizon: Operations Planning] | 2011-04-01 | 2024-02-01 | Medium | The Transmission Operator established TRM values on schedule BUT the values were incomplete or incorrect. Not more than 5% or 1 value (whichever is greater) were incorrect or missing. | The Transmission Operator did not establish TRM within thirteen months of the previous determination, and the last determination was not more than 15 months ago OR The Transmission Operator established TRM values on schedule BUT the values were incomplete. More than 5%, or 1 value (which ever is greater) were incorrect or missing, but not more than 10% or 2 values (whichever is greater). | The Transmission Operator did not establish TRM within 15 months of the previous determination, and the last determination was not more than 18 months ago. OR The Transmission Operator established TRM values on schedule BUT the values were incomplete or incorrect. More than 10% or 2 values (which ever is greater) were incorrect or missing, but not more than 15% or 3 values. | The Transmission Operator did not establish TRM OR The last determination of TRM was more than 18 months ago. OR The Transmission Operator established TRM values on schedule BUT the values were incomplete or incorrect. More than 15% or 3 values (which ever is greater) were incorrect or missing. | [19 empty] | TOP
Inactive | MOD | MOD-008-1 | R5. | The Transmission Operator that maintains TRM shall provide the TRM values to its Transmission Service Provider(s) and Transmission Planner(s) no more than seven calendar days after a TRM value is initially established or subsequently changed. [Time Horizon: Operations Planning] | 2011-04-01 | 2024-02-01 | Medium | The Transmission Operator did provide the TRM values to all entities specified in more then 7 days but less than 14 days. OR The Transmission Operator did provide TRM values on schedule BUT the values were incomplete or did not match those determined in R4. Not more than 5% or 1 value (which ever is greater) were incorrect or missing. | The Transmission Operator did provide the TRM values to all entities specified in 14 days or more, but less than 30 days. OR The Transmission Operator did provide TRM values on schedule BUT the values were incomplete or did not match those determined in R4. More than 5% or 1 value (which ever is greater) were incorrect or missing, but not more than 10% or 2 values (whichever is greater). | The Transmission Operator did provide the TRM values to all entities specified in 30 days or more, but less than 60 days. OR The Transmission Operator did provide TRM values on schedule BUT the values were incomplete or did not match those determined in R4. More than 10% or 2 values (which ever is greater) were incorrect or missing, but not more than 15% or 3 values. | The Transmission Operator did not provide the TRM values to all entities specified within 60 days of the change. OR The Transmission Operator did provide TRM values on schedule BUT the values were incomplete or did not match those determined in R4. More than 15% or 3 values (which ever is greater) were incorrect or missing. | [19 empty] | TOP
Inactive | MOD | MOD-009-0 | R1. | Each Regional Reliability Organization, in conjunction with its members, shall develop and implement a procedure to review Transmission Reliability Margin (TRM) calculations and resulting values of member Transmission Service Providers to ensure they comply with the Regional TRM methodology, and are periodically updated and available to transmission users. This procedure shall include the following four required elements: |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-009-0 | R2. | The Regional Reliability Organization shall make documentation of its Regional TRM review procedure available to NERC on request (within 30 calendar days). |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-009-0 | R3. | The Regional Reliability Organization shall make documentation of the results of the most current implementation of its TRM review procedure available to NERC on request (within 30 calendar days). |  | 2009-11-24 | Low | [19 empty] | RRO
Inactive | MOD | MOD-010-0 | R1. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-011-0_R1) shall provide appropriate equipment characteristics, system data, and existing and future Interchange Schedules in compliance with its respective Interconnection Regional steady-state modeling and simulation data requirements and reporting procedures as defined in Reliability Standard MOD-011-0_R1. | 2007-06-18 | 2016-06-30 | Medium | [9 empty] | GO | [8 empty] | RP |  |  |  | TO |  | TP
Inactive | MOD | MOD-010-0 | R2. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-011-0_R1) shall provide this steady-state modeling and simulation data to the Regional Reliability Organizations, NERC, and those entities specified within Reliability Standard MOD-011-0_R1. If no schedule exists, then these entities shall provide the data on request (30 calendar days). | 2007-06-18 | 2016-06-30 | Medium | [9 empty] | GO | [8 empty] | RP |  |  |  | TO |  | TP
Inactive | MOD | MOD-011-0 | R1. | The Regional Reliability Organizations within an Interconnection, in conjunction with the Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners, shall develop comprehensive steady-state data requirements and reporting procedures needed to model and analyze the steady-state conditions for each of the NERC Interconnections: Eastern, Western, and ERCOT. Within an Interconnection, the Regional Reliability Organizations shall jointly coordinate the development of the data requirements and reporting procedures for that Interconnection. The Interconnection-wide requirements shall include the following steady-state data requirements: |  | 2016-06-30 | High | [19 empty] | RRO
Inactive | MOD | MOD-011-0 | R2. | The Regional Reliability Organizations within an Interconnection shall document their Interconnection’s steady-state data requirements and reporting procedures, shall review those data requirements and reporting procedures (at least every five years), and shall make the data requirements and reporting procedures available on request (within five business days) to Regional Reliability Organizations, NERC, and all users of the interconnected transmission systems. |  | 2016-06-30 | Medium | [19 empty] | RRO
Inactive | MOD | MOD-012-0 | R1. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-013-0_R1) shall provide appropriate equipment characteristics and system data in compliance with the respective Interconnection-wide Regional dynamics system modeling and simulation data requirements and reporting procedures as defined in Reliability Standard MOD-013-0_R1. | 2007-06-18 | 2016-06-30 | Medium | [9 empty] | GO | [8 empty] | RP |  |  |  | TO |  | TP
Inactive | MOD | MOD-012-0 | R2. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-013-0_R1) shall provide dynamics system modeling and simulation data to its Regional Reliability Organization(s), NERC, and those entities specified within the applicable reporting procedures identified in Reliability Standard MOD-013-0_R1. If no schedule exists, then these entities shall provide data on request (30 calendar days). | 2007-06-18 | 2016-06-30 | Medium | [9 empty] | GO | [8 empty] | RP |  |  |  | TO |  | TP
Inactive | MOD | MOD-013-0 | R1. | The Regional Reliability Organization, in coordination with its Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners, shall develop comprehensive dynamics data requirements and reporting procedures needed to model and analyze the dynamic behavior or response of each of the NERC Interconnections: Eastern, Western, and ERCOT. Within an Interconnection, the Regional Reliability Organizations shall jointly coordinate on the development of the data requirements and reporting procedures for that Interconnection. Each set of Interconnection-wide dynamics data requirements shall include the following dynamics data requirements: |  | 2006-11-02 | [20 empty] | RRO
Inactive | MOD | MOD-013-0 | R2. | The Regional Reliability Organization shall participate in the documentation of its Interconnection’s data requirements and reporting procedures and, shall participate in the review of those data requirements and reporting procedures (at least every five years), and shall provide those data requirements and reporting procedures to Regional Reliability Organizations, NERC, and all users of the Interconnected systems on request (within five business days). |  | 2006-11-02 | [20 empty] | RRO
Inactive | MOD | MOD-013-1 | R1. | The Regional Reliability Organization, in coordination with its Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners, shall develop comprehensive dynamics data requirements and reporting procedures needed to model and analyze the dynamic behavior or response of each of the NERC Interconnections: Eastern, Western, and ERCOT. Within an Interconnection, the Regional Reliability Organizations shall jointly coordinate on the development of the data requirements and reporting procedures for that Interconnection. Each set of Interconnection-wide dynamics data requirements shall include the following dynamics data requirements: |  | 2016-06-30 | Medium | [19 empty] | RRO
Inactive | MOD | MOD-013-1 | R2. | The Regional Reliability Organization shall participate in the documentation of its Interconnection’s data requirements and reporting procedures and, shall participate in the review of those data requirements and reporting procedures (at least every five years), and shall provide those data requirements and reporting procedures to Regional Reliability Organizations, NERC, and all users of the Interconnected systems on request (within five business days). |  | 2016-06-30 | Low | [19 empty] | RRO
Inactive | MOD | MOD-014-0 | R1. | The Regional Reliability Organization(s) within each Interconnection shall coordinate and jointly develop and maintain a library of solved (converged) Interconnection-specific steadystate system models. The Interconnection-specific models shall include near- and longer-term planning horizons that are representative of system conditions for projected seasonal peak, minimum, and other appropriate system demand levels. |  | 2016-06-30 | Low | [19 empty] | RRO
Inactive | MOD | MOD-014-0 | R2. | The Regional Reliability Organization(s) within each Interconnection shall coordinate and jointly develop steady-state system models annually for selected study years, as determined by the Regional Reliability Organizations within its Interconnection. The Regional Reliability Organization shall provide the most recent solved (converged) Interconnection-specific steadystate models to NERC in accordance with each Interconnection’s schedule for submission. |  | 2016-06-30 | Low | [19 empty] | RRO
Inactive | MOD | MOD-015-0 | R1. | The Regional Reliability Organization(s) within each Interconnection shall coordinate and jointly develop and maintain a library of initialized (with no Faults or system Disturbances) Interconnection-specific dynamics system models linked to the steadystate system models, as appropriate, of Reliability Standard MOD-014-0_R1. |  | 2016-06-30 | Low | [19 empty] | RRO
Inactive | MOD | MOD-015-0 | R2. | The Regional Reliability Organization(s) within each Interconnection shall develop Interconnection dynamics system models for their Interconnection annually for selected study years as determined by the Regional Reliability Organization(s) within each Interconnection and shall provide the most recent initialized (approximately 25 seconds, no-fault) models to NERC in accordance with each Interconnection’s schedule for submission. |  | 2016-06-30 | Medium | [19 empty] | RRO
Inactive | MOD | MOD-015-0.1 | R1. | The Regional Reliability Organization(s) within each Interconnection shall coordinate and jointly develop and maintain a library of initialized (with no Faults or system Disturbances) Interconnection-specific dynamics system models linked to the steadystate system models, as appropriate, of Reliability Standard MOD-014-0_R1. |  | 2016-06-30 | [20 empty] | RRO
Inactive | MOD | MOD-015-0.1 | R2. | The Regional Reliability Organization(s) within each Interconnection shall develop Interconnection dynamics system models for their Interconnection annually for selected study years as determined by the Regional Reliability Organization(s) within each Interconnection and shall provide the most recent initialized (approximately 25 seconds, no-fault) models to NERC in accordance with each Interconnection’s schedule for submission. |  | 2016-06-30 | [20 empty] | RRO
Inactive | MOD | MOD-016-0 | R1. | The Planning Authority and Regional Reliability Organization shall have documentation identifying the scope and details of the actual and forecast (a) Demand data, (b) Net Energy for Load data, and (c) controllable DSM data to be reported for system modeling and reliability analyses. |  | 2006-11-02 | [15 empty] | PCPA |  |  |  |  | RRO
Inactive | MOD | MOD-016-0 | R2. | The documentation of the scope and details of the data reporting requirements shall be available on request (five business days). |  | 2006-11-02 | [15 empty] | PCPA |  |  |  |  | RRO
Inactive | MOD | MOD-016-1 | R1. | The Planning Authority and Regional Reliability Organization shall have documentation identifying the scope and details of the actual and forecast (a) Demand data, (b) Net Energy for Load data, and (c) controllable DSM data to be reported for system modeling and reliability analyses. | 2007-06-18 | 2009-05-12 | Low |  | The Planning Authority and Regional Reliability Organization has documentation identifying the scope and details of the actual and forecast data but failed to have documentation identifying the scope data and details for one (1) of the following actual an | The Planning Authority and Regional Reliability Organization has documentation identifying the scope and details of the actual and forecast data but failed to have documentation identifying the scope data and details for two (2) of the following actual an | The Planning Authority and Regional Reliability Organization has failed to have documentation identifying the scope and details of the actual and forecast data to be reported for system modeling and reliability analyses. | [10 empty] | PCPA |  |  |  |  | RRO
Inactive | MOD | MOD-016-1 | R2. | The Regional Reliability Organization shall distribute its documentation required in Requirement 1 and any changes to that documentation, to all Planning Authorities that work within its Region. | 2007-06-18 | 2009-05-12 | Low |  |  | The Regional Reliability Organization distributed its documentation as specified in R1 but failed to distribute any changes to that documentation, to all Planning Authorities that work within its Region. | The Regional Reliability Organization failed to distribute its documentation as specified in R1 to all Planning Authorities that work within its Region. | [15 empty] | RRO
Inactive | MOD | MOD-016-1 | R3. | The Planning Authority shall distribute its documentation required in R1 for reporting customer data and any changes to that documentation, to its Transmission Planners and Load-Serving Entities that work within its Planning Authority Area. | 2007-06-18 | 2009-05-12 | Low |  |  | The Planning Authority distributed its documentation as specified in R1 for reporting customer data but failed to distribute any changes to that documentation, to its Transmission Planners and | The Planning Authority failed to distribute its documentation as specified in R1 for reporting customer data to its Transmission Planners and | [10 empty] | PCPA
Inactive | MOD | MOD-016-1.1 | R1. | The Planning Authority and Regional Reliability Organization shall have documentation identifying the scope and details of the actual and forecast (a) Demand data, (b) Net Energy for Load data, and (c) controllable DSM data to be reported for system modeling and reliability analyses. | 2009-05-13 | 2016-06-30 | Low | [14 empty] | PCPA |  |  |  |  | RRO
Inactive | MOD | MOD-016-1.1 | R2. | The Regional Reliability Organization shall distribute its documentation required in Requirement 1 and any changes to that documentation, to all Planning Authorities that work within its Region. | 2009-05-13 | 2016-06-30 | Low | [19 empty] | RRO
Inactive | MOD | MOD-016-1.1 | R3. | The Planning Authority shall distribute its documentation required in R1 for reporting customer data and any changes to that documentation, to its Transmission Planners and Load-Serving Entities that work within its Planning Authority Area. | 2009-05-13 | 2016-06-30 | Low | [14 empty] | PCPA
Inactive | MOD | MOD-017-0 | R1. | The Load-Serving Entity, Planning Authority, and Resource Planner shall each provide the following information annually on an aggregated Regional, subregional, Power Pool, individual system, or Load-Serving Entity basis to NERC, the Regional Reliability Organizations, and any other entities specified by the documentation in Standard MOD-016-1_R 1. | 2007-06-18 | 2009-05-12 | Medium | The Load-Serving Entity, Planning Authority, and Resource Planner failed to provide one of the elements of information as specified in R1.1, R1.2, R1.3 or R1.4 on an annual basis. | The Load-Serving Entity, Planning Authority, and Resource Planner failed to provide two of the elements of information as specified in R1.1, R1.2, R1.3 or R1.4 on an annual basis. | The Load-Serving Entity, Planning Authority, and Resource Planner failed to provide three of the elements of information as specified in R1.1, R1.2, R1.3 or R1.4 on an annual basis. | The Load-Serving Entity, Planning Authority, and Resource Planner failed to provide all of the elements of information as specified in R1.1, R1.2, R1.3 or R1.4 on an annual basis. | [8 empty] | LSE |  | PCPA |  |  |  | RP
Inactive | MOD | MOD-017-0.1 | R1. | The Load-Serving Entity, Planning Authority and Resource Planner shall each provide the following information annually on an aggregated Regional, subregional, Power Pool, individual system, or Load-Serving Entity basis to NERC, the Regional Reliability Organizations, and any other entities specified by the documentation in Standard MOD-016-1_R1. | 2009-05-13 | 2016-06-30 | Medium | [12 empty] | LSE |  | PCPA |  |  |  | RP
Inactive | MOD | MOD-018-0 | R1. | The Load-Serving Entity, Planning Authority, Transmission Planner and Resource Planner’s report of actual and forecast demand data (reported on either an aggregated or dispersed basis) shall: | 2007-06-18 | 2016-06-30 | Medium | [12 empty] | LSE |  | PCPA |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-018-0 | R2. | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each report data associated with Reliability Standard MOD-018-0_R1 to NERC, the Regional Reliability Organization, Load-Serving Entity, Planning Authority, and Resource Planner on request (within 30 calendar days). | 2007-06-18 | 2016-06-30 | Low | [12 empty] | LSE |  | PCPA |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-019-0 | R1. | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each provide annually its forecasts of interruptible demands and Direct Control Load Management (DCLM) data for at least five years and up to ten years into the future, as requested, for summer and winter peak system conditions to NERC, the Regional Reliability Organizations, and other entities (Load-Serving Entities, Planning Authorities, and Resource Planners) as specified by the documentation in Reliability Standard MOD-016-1_R 1. | 2007-06-18 | 2009-05-12 | Medium | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner failed to provide annually less than or equal to 25% of the interruptible demands and Direct Control Load Management (DCLM) data for at least five years and up to ten | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner failed to provide annually greater than 25% but less than or equal to 50% of the interruptible demands and Direct Control Load Management (DCLM) data for at least fiv | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner failed to provide annually greater than 50% but less than or equal to 75% of the interruptible demands and Direct Control Load Management (DCLM) data for at least fiv | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner failed to provide annually greater than 75% of the interruptible demands and Direct Control Load Management (DCLM) data for at least five years and up to ten years i | [8 empty] | LSE |  | PCPA |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-019-0.1 | R1. | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each provide annually its forecasts of interruptible demands and Direct Control Load Management (DCLM) data for at least five years and up to ten years into the future, as requested, for summer and winter peak system conditions to NERC, the Regional Reliability Organizations, and other entities (Load-Serving Entities, Planning Authorities, and Resource Planners) as specified by the documentation in Reliability Standard MOD-016-1_R1. | 2009-05-13 | 2016-06-30 | Medium | [12 empty] | LSE |  | PCPA |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-020-0 | R1. | The Load-Serving Entity, Transmission Planner, and Resource Planner shall each make known its amount of interruptible demands and Direct Control Load Management (DCLM) to Transmission Operators, Balancing Authorities, and Reliability Coordinators on request within 30 calendar days. | 2007-06-18 | 2020-12-14 | Low | [12 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021-0 | R1. | The Load-Serving Entity, Transmission Planner, and Resource Planner’s forecasts shall each clearly document how the Demand and energy effects of DSM programs (such as conservation, time-of-use rates, interruptible Demands, and Direct Control Load Management) are addressed. | 2007-06-18 | 2009-12-09 | Low | Load-Serving Entity, Transmission Planner, and Resource Planner’s forecasts document how the Demand and energy effects of DSM programs but failed to document how one (1) of the following elements of the Demand and energy effects of DSM programs are addr | Load-Serving Entity, Transmission Planner, and Resource Planner’s forecasts document how the Demand and energy effects of DSM programs but failed to document how two (2) of the following elements of the Demand and energy effects of DSM programs are addres | Load-Serving Entity, Transmission Planner, and Resource Planner’s forecasts document how the Demand and energy effects of DSM programs but failed to document how three (3) of the following elements of the Demand and energy effects of DSM programs are addr | Load-Serving Entity, Transmission Planner, and Resource Planner’s forecasts failed to document how the Demand and energy effects of DSM programs are addressed. | [8 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021-0 | R2. | The Load-Serving Entity, Transmission Planner, and Resource Planner shall each include information detailing how Demand-Side Management measures are addressed in the forecasts of its Peak Demand and annual Net Energy for Load in the data reporting procedures of Standard MOD-016-0_R 1. | 2007-06-18 | 2009-12-09 | Low |  |  |  | The Load-Serving Entity, Transmission Planner, and Resource Planner failed to include information detailing how Demand-Side Management measures are addressed in the forecasts of its Peak Demand and annual Net Energy for Load in the data reporting procedur | [8 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021-0 | R3. | The Load-Serving Entity, Transmission Planner, and Resource Planner shall each make documentation on the treatment of its DSM programs available to NERC on request (within 30 calendar days). | 2007-06-18 | 2009-12-09 | Low | The Load-Serving Entity, Transmission Planner, and Resource Planner provided documentation on the treatment of its DSM programs more than 30 but less than 45 calendar days following the request from NERC. | The Load-Serving Entity, Transmission Planner, and Resource Planner provided documentation on the treatment of its DSM programs more than 45 but less than 60 calendar days following the request from NERC. | The Load-Serving Entity, Transmission Planner, and Resource Planner provided documentation on the treatment of its DSM programs more than 60 but less than 75 calendar days following the request from NERC. | The Load-Serving Entity, Transmission Planner, and Resource Planner failed to provide documentation on the treatment of its DSM programs more than 75 calendar days following the request from NERC. | [8 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021-0.1 | R1. | The Load-Serving Entity, Transmission Planner and Resource Planner’s forecasts shall each clearly document how the Demand and energy effects of DSM programs (such as conservation, time-of-use rates, interruptible Demands, and Direct Control Load Management) are addressed. | 2009-12-10 | 2011-03-31 | Low | Load-Serving Entity, Transmission Planner, and Resource Planner’s forecasts document how the Demand and energy effects of DSM programs but failed to document how one (1) of the following elements of the Demand and energy effects of DSM programs are addr | Load-Serving Entity, Transmission Planner, and Resource Planner’s forecasts document how the Demand and energy effects of DSM programs but failed to document how two (2) of the following elements of the Demand and energy effects of DSM programs are addres | Load-Serving Entity, Transmission Planner, and Resource Planner’s forecasts document how the Demand and energy effects of DSM programs but failed to document how three (3) of the following elements of the Demand and energy effects of DSM programs are addr | Load-Serving Entity, Transmission Planner, and Resource Planner’s forecasts failed to document how the Demand and energy effects of DSM programs are addressed. | [8 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021-0.1 | R2. | The Load-Serving Entity, Transmission Planner and Resource Planner shall each include information detailing how Demand-Side Management measures are addressed in the forecasts of its Peak Demand and annual Net Energy for Load in the data reporting procedures of Standard MOD-016-0_R1. | 2009-12-10 | 2011-03-31 | Low |  |  |  | The Load-Serving Entity, Transmission Planner, and Resource Planner failed to include information detailing how Demand-Side Management measures are addressed in the forecasts of its Peak Demand and annual Net Energy for Load in the data reporting procedur | [8 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021-0.1 | R3. | The Load-Serving Entity, Transmission Planner and Resource Planner shall each make documentation on the treatment of its DSM programs available to NERC on request (within 30 calendar days). | 2009-12-10 | 2011-03-31 | Low | The Load-Serving Entity, Transmission Planner, and Resource Planner provided documentation on the treatment of its DSM programs more than 30 but less than 45 calendar days following the request from NERC. | The Load-Serving Entity, Transmission Planner, and Resource Planner provided documentation on the treatment of its DSM programs more than 45 but less than 60 calendar days following the request from NERC. | The Load-Serving Entity, Transmission Planner, and Resource Planner provided documentation on the treatment of its DSM programs more than 60 but less than 75 calendar days following the request from NERC. | The Load-Serving Entity, Transmission Planner, and Resource Planner failed to provide documentation on the treatment of its DSM programs more than 75 calendar days following the request from NERC. | [8 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021-1 | R1. | The Load-Serving Entity, Transmission Planner and Resource Planner’s forecasts shall each clearly document how the Demand and energy effects of DSM programs (such as conservation, time-of-use rates, interruptible Demands, and Direct Control Load Management) are addressed. | 2011-04-01 | 2016-06-30 | Low | [12 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021-1 | R2. | The Load-Serving Entity, Transmission Planner and Resource Planner shall each include information detailing how Demand-Side Management measures are addressed in the forecasts of its Peak Demand and annual Net Energy for Load in the data reporting procedures of Standard MOD-016-0_R1. | 2011-04-01 | 2016-06-30 | Low | [12 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-021-1 | R3. | The Load-Serving Entity, Transmission Planner and Resource Planner shall each make documentation on the treatment of its DSM programs available to NERC on request (within 30 calendar days). | 2011-04-01 | 2016-06-30 | Low | [12 empty] | LSE | [5 empty] | RP | [5 empty] | TP
Inactive | MOD | MOD-024-1 | R1. | The Regional Reliability Organization shall establish and maintain procedures to address verification of generator gross and net Real Power capability. These procedures shall include the following: |  | 2016-06-30 | Medium | [19 empty] | RRO
Inactive | MOD | MOD-024-1 | R2. | The Regional Reliability Organization shall provide its generator gross and net Real Power capability verification and reporting procedures, and any changes to those procedures, to the Generator Owners, Generator Operators, Transmission Operators, Planning Authorities, and Transmission Planners affected by the procedure within 30 calendar days of the approval. |  | 2016-06-30 | Low | [19 empty] | RRO
Inactive | MOD | MOD-024-1 | R3. | The Generator Owner shall follow its Regional Reliability Organization’s procedures for verifying and reporting its gross and net Real Power generating capability per R1. |  | 2016-06-30 | Medium | [9 empty] | GO
Inactive | MOD | MOD-025-1 | R1. | The Regional Reliability Organization shall establish and maintain procedures to address verification of generator gross and net Reactive Power capability. These procedures shall include the following: |  | 2016-06-30 | Low | [19 empty] | RRO
Inactive | MOD | MOD-025-1 | R2. | The Regional Reliability Organization shall provide its generator gross and net Reactive Power capability verification and reporting procedures, and any changes to those procedures, to the Generator Owners, Generator Operators, Transmission Operators, Planning Authorities, and Transmission Planners affected by the procedure within 30 calendar days of the approval. |  | 2016-06-30 | Low | [19 empty] | RRO
Inactive | MOD | MOD-025-1 | R3. | The Generator Owner shall follow its Regional Reliability Organization’s procedures for verifying and reporting its gross and net Reactive Power generating capability per R1. |  | 2016-06-30 | Low | [9 empty] | GO
Mandatory Subject to Enforcement | MOD | MOD-025-2 | R1. | Each Generator Owner shall provide its Transmission Planner with verification of the Real Power capability of its applicable Facilities as follows: | 2016-07-01 |  | Medium | The Generator Owner verified and recorded the Real Power capability of its applicable generating unit, but submitted the data to its Transmission Planner more than 90 calendar days, but within 120 calendar days, of the date the data is recorded for a staged test or the date the data is selected for verification using historical operational data. OR The Generator Owner verified the Real Power capability, per Attachment 1 and submitted the data but was missing 1 to less than or equal to 33 percent of the data. OR The Generator Owner performed the Real Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1 or item 2 (5 year requirement) but did so in more than 66 calendar months but less than or equal to 69 months. OR The Generator Owner performed the Real Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1, 2 or 3 (12 calendar month requirement) but did so in more than 12 calendar months but less than or equal to 13 calendar months. | The Generator Owner verified and recorded the Real Power capability of its applicable generating unit, but submitted the data to its Transmission Planner more than 120 calendar days, but within 150 calendar days, of the date the data is recorded for a staged test or the date the data is selected for verification using historical operational data. OR The Generator Owner verified the Real Power capability, per Attachment 1 and submitted the data but was missing more than 33 to 66 percent of the data. OR The Generator Owner performed the Real Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1 or item 2 (5 year requirement) but did so in more than 69 calendar months but less than or equal to 72 months. OR The Generator Owner performed the Real Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1, 2 or 3 (12 calendar month requirement) but did so in more than 13 calendar months but less than or equal to 14 calendar months. | The Generator Owner verified and recorded the Real Power capability of its applicable generating unit, but submitted the data to its Transmission Planner more than 150 calendar days, but within 180 calendar days, of the date the data is recorded for a staged test or the date the data is selected for verification using historical operational data. OR The Generator Owner verified the Real Power capability, per Attachment 1 and submitted the data but was missing from 67 to 99 percent of the data. OR The Generator Owner performed the Real Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1 or item 2 (5 year requirement) but did so in more than 72 calendar months but less than or equal to 75 months. OR The Generator Owner performed the Real Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1, 2 or 3 (12 calendar month requirement) but did so in more than 14 calendar months but less than or equal to 15 calendar months. | The Generator Owner verified and recorded the Real Power capability of its applicable generating unit, but submitted the data to its Transmission Planner more than 180 calendar days of the date the data is recorded for a staged test or the date the data is selected for verification using historical operational data. OR The Generator Owner failed to verify the Real Power capability, per Attachment 1 of an applicable generating unit. OR The Generator Owner performed the Real Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1 or item 2 (5 year requirement) but did so in more than 75 calendar months. OR The Generator Owner performed the Real Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1, 2 or 3 (12 calendar month requirement) but did so in more than 15 calendar months. | [5 empty] | GO
Mandatory Subject to Enforcement | MOD | MOD-025-2 | R2. | Each Generator Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: | 2016-07-01 |  | Medium | The Generator Owner verified and recorded the Reactive Power capability of its applicable generating unit or applicable synchronous condenser, but submitted the data to its Transmission Planner more than 90 calendar days, but within 120 calendar days, of the date the data is recorded for a staged test or the date the data is selected for verification using historical operational data. OR The Generator Owner verified the Reactive Power capability, per Attachment 1 and submitted the data but was missing 1 to up to and including 33 percent of the data. OR The Generator Owner performed the Reactive Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1 or item 2 (5 year requirement) but did so in more than 66 calendar months but less than or equal to 69 months. OR The Generator Owner performed the Reactive Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1, 2 or 3 (12 calendar month requirement) but did so in more than 12 calendar months but less than or equal to 13 calendar months. | The Generator Owner verified and recorded the Reactive Power capability of its applicable generating unit or applicable synchronous condenser, but submitted the data to its Transmission Planner more than 120 calendar days, but within 150 calendar days, of the date the data is recorded for a staged test or the date the data is selected for verification using historical operational data. OR The Generator Owner verified the Reactive Power capability, per Attachment 1 and submitted the data but was missing 34 to 66 percent of the data. OR The Generator Owner performed the Reactive Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1 or item 2 (5 year requirement) but did so in more than 69 calendar months but less than or equal to 72 months. OR The Generator Owner performed the Reactive Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1, 2 or 3 (12 calendar month requirement) but did so in more than 13 calendar months but less than or equal to 14 calendar months. | The Generator Owner verified and recorded the Reactive Power capability of its applicable generating unit or applicable synchronous condenser, but submitted the data to its Transmission Planner more than 150 calendar days, but within 180 calendar days, of the date the data is recorded for a staged test or the date the data is selected for verification using historical operational data. OR The Generator Owner verified the Reactive Power capability, per Attachment 1 and submitted the data but was missing 67 to 99 percent of the data. OR The Generator Owner performed the Reactive Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1 or item 2 (5 year requirement) but did so in more than 72 calendar months but less than or equal to 75 months. OR The Generator Owner performed the Reactive Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1, 2 or 3 (12 calendar month requirement) but did so in more than 14 calendar months but less than or equal to 15 calendar months. | The Generator Owner verified and recorded the Reactive Power capability of its applicable generating unit or applicable synchronous condenser, but submitted the data to its Transmission Planner more than 180 calendar days of the date the data is recorded for a staged test or the date the data is selected for verification using historical operational data. OR The Generator Owner failed to verify the Reactive Power capability, per Attachment 1 of an applicable generating unit or synchronous condenser unit. OR The Generator Owner performed the Reactive Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1 or item 2 (5 year requirement) but did so in more than 75 calendar months. OR The Generator Owner performed the Reactive Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1, 2 or 3 (12 calendar month requirement) but did so in more than 15 calendar months. | [5 empty] | GO
Mandatory Subject to Enforcement | MOD | MOD-025-2 | R3. | Each Transmission Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: | 2016-07-01 |  | Medium | The Transmission Owner verified and recorded the Reactive Power capability of its applicable synchronous condenser, but submitted the data to its Transmission Planner more than 90 calendar days, but within 120 calendar days, of the date the data is recorded for a staged test or the date the data is selected for verification using historical operational data. OR The Transmission Owner verified the Reactive Power capability, per Attachment 1 and submitted the data but was missing 1 to up to and including 33 percent of the data. OR The Transmission Owner performed the Reactive Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1 or item 2 (5 year requirement) but did so in more than 66 calendar months but less than or equal to 69 months. OR The Transmission Owner performed the Reactive Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1, 2 or 3 (12 calendar month requirement) but did so in more than 12 calendar months but less than or equal to 13 calendar months. | The Transmission Owner verified and recorded the Reactive Power capability of its applicable synchronous condenser, but submitted the data to its Transmission Planner more than 120 calendar days, but within 150 calendar days, of the date the data is recorded for a staged test or the date the data is selected for verification using historical operational data. OR The Transmission Owner verified the Reactive Power capability, per Attachment 1 and submitted the data but was missing 34 to 66 percent of the data. OR The Transmission Owner performed the Reactive Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1 or item 2 (5 year requirement) but did so in more than 69 calendar months but less than or equal to 72 months. OR The Transmission Owner performed the Reactive Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1, 2 or 3 (12 calendar month requirement) but did so in more than 13 calendar months but less than or equal to 14 calendar months. | The Transmission Owner verified and recorded the Reactive Power capability of an applicable synchronous condenser unit, but submitted the data to its Transmission Planner more than 150 calendar days, but within 180 calendar days, of the date the data is recorded for a staged test or the date the data is selected for verification using historical operational data. OR The Transmission Owner verified the Reactive Power capability, per Attachment 1 and submitted the data but was missing 67 to 99 percent of the data. OR The Transmission Owner performed the Reactive Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1 or item 2 (5 year requirement) but did so in more than 72 calendar months but less than or equal to 75 months. OR The Transmission Owner performed the Reactive Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1, 2 or 3 (12 calendar month requirement) but did so in more than 14 calendar months but less than or equal to 15 calendar months. | The Transmission Owner verified and recorded the Reactive Power capability of its applicable synchronous condenser, but submitted the data to its Transmission Planner more than 180 calendar days of the date the data is recorded for a staged test or the date the data is selected for verification using historical operational data. OR The Transmission Owner failed to verify the Reactive Power capability, per Attachment 1 of an applicable synchronous condenser unit. OR The Transmission Owner performed the verification per Attachment 1, “Periodicity for conducting a new verification” item 1 or item 2 (5 year requirement) but did so in more than 75 calendar months. OR The Transmission Owner performed the Reactive Power verification per Attachment 1, “Periodicity for conducting a new verification” item 1, 2 or 3 (12 calendar month requirement) but did so in more than 15 calendar months. | [18 empty] | TO
Inactive | MOD | MOD-025-RFC-01 | R1. | Each Generator Owner shall verify the operating range of Reactive Power capability for each of its applicable units by operational tracking or by test at least every five years, (with no more than 66 calendar months between verifications) in accordance with MOD-025-RFC-01 Attachment 1. |  | 2012-11-07 | Medium | The Generator Owner verified the Reactive Power capability for a specific generator in accordance with MOD-025-RFC-01 Attachment 1, and the verification was late by 60 calendar days or less and the Generator Owner has no evidence to support a delay in con | The Generator Owner verified the Reactive Power capability for a specific generator in accordance with MOD-025-RFC-01 Attachment 1, and the verification was late by more than 60 calendar days but less than or equal to 70 calendar days late and the Generat | The Generator Owner verified the Reactive Power capability for a specific generator in accordance with MOD-025-RFC-01 Attachment 1, and the verification was late by more than70 calendar days but less than or equal to 80 calendar days late and the Generato | The Generator Owner verified the Reactive Power capability for a specific generator in accordance with MOD-025-RFC-01 Attachment 1, and the verification was late by more than 80 calendar days and the Generator Owner has no evidence to support a delay in c | [5 empty] | GO
Inactive | MOD | MOD-025-RFC-01 | R2. | Each Generator Owner shall provide the following data from the most recent Reactive Power capability verification within 30 calendar days of a written request from its Transmission Planner, Transmission Operator, Reliability Coordinator or Planning Coordinator. [See standard pdf for additional information] |  | 2012-11-07 | Low | The Generator Owner provided the data (as specified in Requirement R2, Parts 2.1, 2.2 and 2.3) from the most recent Reactive Power capability verification but provided the data more than 30 calendar days but less than or equal to 40 calendar days followin | The Generator Owner provided the data (as specified in Requirement R2, Parts 2.1, 2.2 and 2.3) from the most recent Reactive Power capability verification but provided the data more than 40 calendar days but less than or equal to 50 calendar days followin | The Generator Owner provided the data (as specified in Requirement R2, Parts 2.1, 2.2 and 2.3) from the most recent Reactive Power capability verification but provided the data more than 50 calendar days but less than or equal to 60 calendar days followin | The Generator Owner failed to provide the data (as specified in Requirement R2, Parts 2.1, 2.2 and 2.3) from the most recent Reactive Power capability verification more than 60 calendar days following the request. OR The Generator Owner provided the dat | [5 empty] | GO
Mandatory Subject to Enforcement | MOD | MOD-026-1 | R1. | Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: • Instructions on how to obtain the list of excitation control system or plant volt/var control function models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic excitation control system or plant volt/var control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific excitation control system or plant volt/var control function contained in the Transmission Planner’s dynamic database from the current (in-use) models, including generator MVA base. | 2014-07-01 |  | Low | The Transmission Planner provided the instructions and data to the Generator Owner more than 90 calendar days but less than or equal to 120 calendar days of receiving a written request. | The Transmission Planner provided the instructions and data to the Generator Owner more than 120 calendar days but less than or equal to 150 calendar days of receiving a written request. | The Transmission Planner provided the instructions and data to the Generator Owner more than 150 calendar days but less than or equal to 180 calendar days of receiving a written request. | The Transmission Planner failed to provide the instructions and data to the Generator Owner within 180 calendar days of receiving a written request. | [20 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-026-1 | R2. | Each Generator Owner shall provide for each applicable unit, a verified generator excitation control system or plant volt/var control function model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-026 Attachment 1. | 2018-07-01 |  | Medium | The Generator Owner provided its verified model(s), including documentation and data to its Transmission Planner after the timeframe specified in MOD-026 Attachment 1 but less than or equal to 90 calendar days late; OR The Generator Owner provided the Transmission Planner verified models that omitted one of the six Parts identified in Requirement R2, Parts 2.1.1 through 2.1.6. | The Generator Owner provided its verified model(s), including documentation and data to its Transmission Planner more than 90 calendar days but less than or equal to 180 calendar days late as specified by the periodicity timeframe in MOD-026 Attachment 1. OR The Generator Owner provided the Transmission Planner verified models that omitted two of the six Parts identified in Requirement R2, Parts 2.1.1 through 2.1.6. | The Generator Owner provided its verified model(s), including documentation and data to its Transmission Planner more than 180 calendar days but less than or equal to 270 calendar days late as specified by the periodicity timeframe in MOD-026 Attachment 1. OR The Generator Owner provided the Transmission Planner verified models that omitted three of the six Parts identified in Requirement R2, Parts 2.1.1 through 2.1.6. | The Generator Owner provided its verified model(s), including documentation and data more than 270 calendar days late to its Transmission Planner in accordance with the periodicity specified in MOD-026 Attachment 1. OR The Generator Owner failed to use model(s) acceptable to the Transmission Planner as specified in Requirement R2, Part 2.1. OR The Generator Owner provided the Transmission Planner verified model(s) but omitted four or more of the six parts identified in Requirement R2, Subparts 2.1.1 through 2.1.6. | [5 empty] | GO
Mandatory Subject to Enforcement | MOD | MOD-026-1 | R3. | Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit: • Written notification from its Transmission Planner (in accordance with Requirement R6) that the excitation control system or plant volt/var control function model is not usable, • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the excitation control system or plant volt/var control function model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated excitation control system or plant volt/var control function model response did not match the recorded response to a transmission system event. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). Footnote: If verification is performed, the 10-year period as outlined in MOD-026 Attachment 1 is reset. | 2014-07-01 |  | Low | The Generator Owner provided a written response more than 90 calendar days but less than or equal to 120 calendar days of receiving written notice. | The Generator Owner provided a written response more than 120 calendar days but less than or equal to 150 calendar days of receiving written notice. | The Generator Owner provided a written response more than 150 calendar days but less than or equal to 180 calendar days of receiving written notice. | The Generator Owner failed to provide a written response within 180 calendar days of receiving written notice. OR The Generator Owner's written response failed to contain either the technical basis for maintaining the current model, or a list of future model changes, or a plan to perform another model verification. | [5 empty] | GO
Mandatory Subject to Enforcement | MOD | MOD-026-1 | R4. | Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the excitation control system or plant volt/var control function that alter the equipment response characteristic. Footnote:Exciter, voltage regulator, plant volt/var or power system stabilizer control replacement including software alterations that alter excitation control system equipment response, plant digital control system addition or replacement, plant digital control system software alterations that alter excitation control system equipment response, plant volt/var function equipment addition or replacement (such as static var systems, capacitor banks, individual unit excitation systems, etc), a change in the voltage control mode (such as going from power factor control to automatic voltage control, etc), exciter, voltage regulator, impedance compensator, or power system stabilizer settings change. Automatic changes in settings that occur due to changes in operating mode do not apply to Requirement R4. | 2014-07-01 |  | Low | The Generator Owner provided revised model data or plans to perform model verification more than 180 calendar days but less than or equal to 210 calendar days of making changes to the excitation control system or plant volt/var control function that altered the equipment response characteristic. | The Generator Owner provided revised model data or plans to perform model verification more than 210 calendar days but less than or equal to 240 calendar days of making changes to the excitation control system or plant volt/var control function that altered the equipment response characteristic. | The Generator Owner provided revised model data or plans to perform model verification more than 240 calendar days but less than or equal to 270 calendar days of making changes to the excitation control system or plant volt/var control function that altered the equipment response characteristic. | The Generator Owner failed to provide revised model data or failed to provide plans to perform model verification within 270 calendar days of making changes to the excitation control system or plant volt/var control function that altered the equipment response characteristic. | [5 empty] | GO
Mandatory Subject to Enforcement | MOD | MOD-026-1 | R5. | Each Generator Owner shall provide a written response to its Transmission Planner, within 90 calendar days following receipt of a technically justified unit request from the Transmission Planner to perform a model review of a unit or plant that includes one of the following: • Details of plans to verify the model (in accordance with Requirement R2), or • Corrected model data including the source of revised model data such as discovery of manufacturer test values to replace generic model data or updating of data parameters based on an on-site review of the equipment. | 2014-07-01 |  | Low | The Generator Owner provided a written response more than 90 calendar days but less than or equal to 120 calendar days to the Transmission Planner following receipt of a technically justified request to perform a model review of an applicable unit. | The Generator Owner provided a written response more than 120 calendar days but less than or equal to 150 calendar days to the Transmission Planner following receipt of a technically justified request to perform a model review of an applicable unit. | The Generator Owner provided a written response more than 150 calendar days but less than or equal to 180 calendar days to the Transmission Planner following receipt of a technically justified request to perform a model review of an applicable unit. | The Generator Owner failed to provide a written response to the Transmission Planner within 180 calendar days following receipt of a technically justified request to perform a model review of an applicable unit. OR The Generator Owner’s written response failed to include one of the sub bullets of Requirement R5. | [5 empty] | GO
Mandatory Subject to Enforcement | MOD | MOD-026-1 | R6. | Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the verified excitation control system or plant volt/var control function model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 6.1 through 6.3) or is not usable. If the model is not usable, the Transmission Planner shall provide a technical description of why the model is not usable. | 2014-07-01 |  | Medium | The Transmission Planner provided a written response to the Generator Owner indicating whether the model is usable or not usable; including a technical description if the model is not usable, more than 90 calendar days but less than or equal to 120 calendar days of receiving verified model information; OR The Transmission Planner provided a written response to the Generator Owner within 90 calendar days indicating that the model is not usable; but did not include a technical description. | The Transmission Planner provided a written response to the Generator Owner indicating whether the model is usable or not usable; including a technical description if the model is not usable, more than 120 calendar days but less than or equal to 150 calendar days of receiving the verified model information. OR The Transmission Planner’s written response omitted confirmation for one of the specified model criteria listed in Requirement R6, Parts 6.1 through 6.3; OR The Transmission Planner provided a written response to the Generator Owner indicating that the model is not usable, but did not include a technical description and provided the response more than 90 calendar days but less than or equal to 120 calendar days of receiving verified model information. | The Transmission Planner provided a written response to the Generator Owner indicating whether the model is usable or not usable; including a technical description if the model is not usable, more than 150 calendar days but less than or equal to 180 calendar days of receiving the verified model information; OR The Transmission Planner’s written response omitted confirmation for two of the specified model criteria listed in Requirement R6, Parts 6.1 through 6.3; OR The Transmission Planner provided a written response to the Generator Owner indicating that the model is not usable, but did not include a technical description and provided the response more than 120 calendar days but less than or equal to 150 calendar days of receiving verified model information. | The Transmission Planner failed to provide a written response to the Generator Owner within 180 calendar days of receiving the verified model information. OR The Transmission Planner’s written response omitted confirmation for all specified model criteria listed in Requirement R6, Parts 6.1 through 6.3. OR The Transmission Planner provided a written response to the Generator Owner indicating that the model is not usable, but did not include a technical description and provided the response more than 150 calendar days after receiving verified model information. | [20 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-027-1 | R1. | Each Transmission Planner shall provide the following requested information to the Generator Owner within 90 calendar days of receiving a written request: • Instructions on how to obtain the list of turbine/governor and load control or active power/frequency control system models that are acceptable to the Transmission Planner for use in dynamic simulation, • Instructions on how to obtain the dynamic turbine/governor and load control or active power/frequency control function model library block diagrams and/or data sheets for models that are acceptable to the Transmission Planner, or • Model data for any of the Generator Owner’s existing applicable unit specific turbine/governor and load control or active power/frequency control system contained in the Transmission Planner’s dynamic database from the current (in-use) models. | 2014-07-01 |  | Low | The Transmission Planner provided the instructions and data to the Generator Owner more than 90 calendar days but less than or equal to 120 calendar days of receiving a written request. | The Transmission Planner provided the instructions and data to the Generator Owner more than 120 calendar days but less than or equal to 150 calendar days of receiving a written request. | The Transmission Planner provided the instructions and data to the Generator Owner more than 150 calendar days but less than or equal to 180 calendar days of receiving a written request. | The Transmission Planner failed to provide the instructions and data to the Generator Owner within 180 calendar days of receiving a written request. | [20 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-027-1 | R2. | Each Generator Owner shall provide, for each applicable unit, a verified turbine/governor and load control or active power/frequency control model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-027 Attachment 1. | 2014-07-01 |  | Medium | The Generator Owner provided its verified model(s) to its Transmission Planner after the periodicity timeframe specified in MOD-027 Attachment 1 but less than or equal to 90 calendar days late; OR The Generator Owner provided the Transmission Planner a verified model that omitted one of the five Parts identified in Requirement R2, Subparts 2.1.1, through 2.1.5. | The Generator Owner provided its verified model(s) to its Transmission Planner more than 90 calendar days but less than or equal to 180 calendar days late as specified by the periodicity timeframe in MOD-027 Attachment 1; OR The Generator Owner provided the Transmission Planner a verified model that omitted two of the five Parts identified in Requirement R2, Subparts 2.1.1, through 2.1.5. | The Generator Owner provided its verified model(s) to its Transmission Planner more than 180 calendar days but less than or equal to 270 calendar days late as specified by the periodicity timeframe in MOD-027 Attachment 1; OR The Generator Owner provided the Transmission Planner verified models that omitted three of the five Parts identified in Requirement R2, Subparts 2.1.1, through 2.1.5. | The Generator Owner provided its verified model(s) more than 270 calendar days late to its Transmission Planner in accordance with the periodicity specified in MOD-027 Attachment 1; OR The Generator Owner failed to use model(s) acceptable to the Transmission Planner as specified in Requirement R2, Part 2.1; OR The Generator Owner provided the Transmission Planner verified model(s) that omitted four or more of the five Parts identified in Requirement R2, Subparts 2.1.1, through 2.1.5. | [5 empty] | GO
Mandatory Subject to Enforcement | MOD | MOD-027-1 | R3. | Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit. • Written notification, from its Transmission Planner (in accordance with Requirement R5) that the turbine/governor and load control or active power/frequency control model is not “usable,” • Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the turbine/governor and load control or active power/frequency control model, or • Written comments and supporting evidence from its Transmission Planner indicating that the simulated turbine/governor and load control or active power/frequency control response did not approximate the recorded response for three or more transmission system events. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification (in accordance with Requirement R2). | 2014-07-01 |  | Low | The Generator Owner provided a written response more than 90 calendar days but less than or equal to 120 calendar days of receiving written notice. | The Generator Owner provided a written response more than 120 calendar days but less than or equal to 150 calendar days of receiving written notice. | The Generator Owner provided a written response more than 150 calendar days but less than or equal to 180 calendar days of receiving written notice. | The Generator Owner failed to provide a written response within 180 calendar days of receiving written notice; OR The Generator Owner's written response failed to contain either the technical basis for maintaining the current model, or a list of future model changes, or a plan to perform another model verification. | [5 empty] | GO
Mandatory Subject to Enforcement | MOD | MOD-027-1 | R4. | Each Generator Owner shall provide revised model data or plans to perform model verification (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the turbine/governor and load control or active power/frequency control system that alter the equipment response characteristic. Footnote: Control replacement or alteration including software alterations or plant digital control system addition or replacement, plant digital control system software alterations that alter droop, and/or dead band, and/or frequency response and/or a change in the frequency control mode (such as going from droop control to constant MW control, etc). | 2014-07-01 |  | Low | The Generator Owner provided revised model data or plans to perform model verification more than 180 calendar days but less than or equal to 210 calendar days of making changes to the turbine/governor and load control or active power/frequency control system that alter the equipment response characteristic. | The Generator Owner provided revised model data or plans to perform model verification more than 210 calendar days but less than or equal to 240 calendar days of making changes to the turbine/governor and load control or active power/frequency control system that alter the equipment response characteristic. | The Generator Owner provided revised model data or plans to perform model verification more than 240 calendar days but less than or equal to 270 calendar days of making changes to the turbine/governor and load control or active power/frequency control system that alter the equipment response characteristic. | The Generator Owner failed to provide revised model data or failed to provide plans to perform model verification within 270 calendar days of making changes to the turbine/governor and load control or active power/frequency control system that altered the equipment response characteristic. | [5 empty] | GO
Mandatory Subject to Enforcement | MOD | MOD-027-1 | R5. | Each Transmission Planner shall provide a written response to the Generator Owner within 90 calendar days of receiving the turbine/governor and load control or active power/frequency control system verified model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 5.1 through 5.3) or is not usable. If the model is not usable, the Transmission Planner shall provide a technical description of why the model is not usable. | 2014-07-01 |  | Medium | The Transmission Planner provided a written response to the Generator Owner indicating whether the model is usable or not usable, including a technical description if the model is not usable, more than 90 calendar days but less than or equal to 120 calendar days of receiving verified model information; OR The Transmission Planner provided a written response to the Generator Owner within 90 calendar days indicating that the model is not usable; but did not include a technical description. | The Transmission Planner provided a written response to the Generator Owner indicating whether the model is usable or not usable, including a technical description if the model is not usable, more than 120 calendar days but less than or equal to 150 calendar days of receiving the verified model information; OR The Transmission Planner’s written response omitted confirmation for one of the specified model criteria listed in Requirement R5, Parts 5.1 through 5.3. OR The Transmission Planner provided a written response to the Generator Owner indicating that the model is not usable, but did not include a technical description and provided the response more than 90 calendar days but less than or equal to 120 calendar days of receiving verified model information. | The Transmission Planner provided a written response to the Generator Owner indicating whether the model is usable or not usable, including a technical description if the model is not usable, more than 150 calendar days but less than or equal to 180 calendar days of receiving the verified model information; OR The Transmission Planner’s written response omitted confirmation for two of the specified model criteria listed in Requirement R5, Parts 5.1 through 5.3. OR The Transmission Planner provided a written response to the Generator Owner indicating that the model is not usable, but did not include a technical description and provided the response more than 120 calendar days but less than or equal to 150 calendar days of receiving verified model information. | The Transmission Planner failed to provide a written response to the Generator Owner within 180 calendar days of receiving the verified model information; OR The Transmission Planner provided a written response without including confirmation of all specified model criteria listed in Requirement R5, Parts 5.1 through 5.3. OR The Transmission Planner provided a written response to the Generator Owner indicating that the model is not usable, but did not include a technical description and provided the response more than 150 calendar days after receiving verified model information. | [20 empty] | TP
Inactive | MOD | MOD-028-1 | R1. | Each Transmission Service Provider shall include in its Available Transfer Capability Implementation Document (ATCID), at a minimum, the following information relative to its methodology for determining Total Transfer Capability (TTC): [Time Horizon: Operations Planning] | 2011-04-01 | 2013-09-30 | Medium | [25 empty] | TSP
Inactive | MOD | MOD-028-1 | R2. | When calculating TTC for ATC Paths, the Transmission Operator shall use a Transmission model that contains all of the following: [Time Horizon: Operations Planning] | 2011-04-01 | 2013-09-30 | Medium | [23 empty] | TOP
Inactive | MOD | MOD-028-1 | R3. | When calculating TTCs for ATC Paths, the Transmission Operator shall include the following data for the Transmission Service Provider’s area. The Transmission Operator shall also include the following data associated with Facilities that are explicitly represented in the Transmission model, as provided by adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed: [Time Horizon: Operations Planning] | 2011-04-01 | 2013-09-30 | Medium | [23 empty] | TOP
Inactive | MOD | MOD-028-1 | R4. | When calculating TTCs for ATC Paths, the Transmission Operator shall meet all of the following conditions: [Time Horizon: Operations Planning] | 2011-04-01 | 2013-09-30 | Medium | [23 empty] | TOP
Inactive | MOD | MOD-028-1 | R5. | Each Transmission Operator shall establish TTC for each ATC Path as defined below: [Time Horizon: Operations Planning] | 2011-04-01 | 2013-09-30 | Medium | [23 empty] | TOP
Inactive | MOD | MOD-028-1 | R6. | Each Transmission Operator shall establish TTC for each ATC Path using the following process: [Time Horizon: Operations Planning] | 2011-04-01 | 2013-09-30 | Medium | [23 empty] | TOP
Inactive | MOD | MOD-028-1 | R7. | The Transmission Operator shall provide the Transmission Service Provider of that ATC Path with the most current value for TTC for that ATC Path no more than: [Time Horizon: Operations Planning] | 2011-04-01 | 2013-09-30 | Medium | [23 empty] | TOP
Inactive | MOD | MOD-028-1 | R8. | When calculating Existing Transmission Commitments (ETCs) for firm commitments (ETCF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See standard for formula. | 2011-04-01 | 2013-09-30 | Medium | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M10 for the same period, and the absolute value difference was more than 15% of the value calculated in the measure or 15MW, whichever is greater, but not more than 25% of the value calculated in the measure or 25MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M10 for the same period, and the absolute value difference was more than 25% of the value calculated in the measure or 25MW, whichever is greater, but not more than 35% of the value calculated in the measure or 35MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M10 for the same period, and the absolute value difference was more than 35% of the value calculated in the measure or 35MW, whichever is greater, but not more than 45% of the value calculated in the measure or 45MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M10 for the same period, and the absolute value difference was more than 45% of the value calculated in the measure or 45MW, whichever is greater. | [21 empty] | TSP
Inactive | MOD | MOD-028-1 | R9. | When calculating ETC for non-firm commitments (ETCNF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See standard for formula. | 2011-04-01 | 2013-09-30 | Low | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M11 for the same period, and the absolute value difference was more than 15% of the value calculated in the measure or 15MW, whichever is greater, but not more than 25% of the value calculated in the measure or 25MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M11 for the same period, and the absolute value difference was more than 25% of the value calculated in the measure or 25MW, whichever is greater, but not more than 35% of the value calculated in the measure or 35MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M11 for the same period, and the absolute value difference was more than 35% of the value calculated in the measure or 35MW, whichever is greater, but not more than 45% of the value calculated in the measure or 45MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M11 for the same period, and the absolute value difference was more than 45% of the value calculated in the measure or 45MW, whichever is greater. | [21 empty] | TSP
Inactive | MOD | MOD-028-1 | R10. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall utilize the following algorithm: [Time Horizon: Operations Planning] See Standard for formula. | 2011-04-01 | 2013-09-30 | Medium | [25 empty] | TSP
Inactive | MOD | MOD-028-1 | R11. | When calculating non-firm ATC for a ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See Standard for formula. | 2011-04-01 | 2013-09-30 | Low | [25 empty] | TSP
Inactive | MOD | MOD-028-2 | R1. | Each Transmission Service Provider shall include in its Available Transfer Capability Implementation Document (ATCID), at a minimum, the following information relative to its methodology for determining Total Transfer Capability (TTC): | 2013-10-01 | 2024-02-01 | Low | The Transmission Service Provider has an ATCID but it is missing one of the following: • R1.1 • R1.2 • R1.3 •R1.4 • R1.5 (any one or more of its sub-subrequirements) | The Transmission Service Provider has an ATCID but it is missing two of the following: • R1.1 • R1.2 • R1.3 • R1.4 • R1.5 (any one or more of its sub-subrequirements) | The Transmission Service Provider has an ATCID but it is missing three of the following: • R1.1 • R1.2 • R1.3 • R1.4 • R1.5 (any one or more of its sub-subrequirements) | The Transmission Service Provider has an ATCID but it is missing more than three of the following: •R1.1 • R1.2 • R1.3 • R1.4 • R1.5 (any one or more of its sub-subrequirements) | [21 empty] | TSP
Inactive | MOD | MOD-028-2 | R2. | When calculating TTC for ATC Paths, the Transmission Operator shall use a Transmission model that contains all of the following: | 2013-10-01 | 2024-02-01 | Low | The Transmission Operator used one to ten Facility Ratings that were different from those specified by a Transmission or Generator Owner in their Transmission model. | The Transmission Operator used eleven to twenty Facility Ratings that were different from those specified by a Transmission or Generator Owner in their Transmission model. | One or both of the following: • The Transmission Operator used twenty-one to thirty Facility Ratings that were different from those specified by a Transmission or Generator Owner in their Transmission model. • The Transmission Operator did not use a Transmission model that includes modeling data and topology (or equivalent representation) for one adjacent Reliability Coordinator Area. | One or more of the following: • The Transmission Operator used more than thirty Facility Ratings that were different from those specified by a Transmission or Generator Owner in their Transmission model. • The Transmission Operator’s model includes equivalent representation of non-radial facilities greater than 161 KV for its own Reliability Coordinator Area •The Transmission Operator did not use a Transmission model that includes modeling data and topology (or equivalent representation) for two or more adjacent Reliabiltiy Coordinator Areas. | [19 empty] | TOP
Inactive | MOD | MOD-028-2 | R3. | When calculating TTCs for ATC Paths, the Transmission Operator shall include the following data for the Transmission Service Provider’s area. The Transmission Operator shall also include the following data associated with Facilities that are explicitly represented in the Transmission model, as provided by adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed: | 2013-10-01 | 2024-02-01 | Low | The Transmission Operator did not include in the TTC process one to ten expected generation and Transmission outages, additions or retirements as specified in the ATCID. | The Transmission Operator did not include in the TTC process eleven to twenty-five expected generation and Transmission outages, additions or retirements as specified in the ATCID. | The Transmission Operator did not include in the TTC process twenty-six to fifty expected generation and Transmission outages, additions or retirements as specified in the ATCID. | One or more of the following: • The Transmission Operator did not include in the TTC process more than fifty expected generation and Transmission outages, additions or retirements as specified in the ATCID. • The Transmission Operator did not include the Load forecast or unit commitments in its TTC calculation as described in R3. | [19 empty] | TOP
Inactive | MOD | MOD-028-2 | R4. | When calculating TTCs for ATC Paths, the Transmission Operator shall meet all of the following conditions: | 2013-10-01 | 2024-02-01 | Low | The Transmission Operator did not model reservations’ sources or sinks as described in R4.3 for more than zero reservations, but not more than 5% of all reservations; or 1 reservation, whichever is greater. | The Transmission Operator did not model reservations’ sources or sinks as described in R4.3 for more than 5%, but not more than 10% of all reservations; or 2 reservations, whichever is greater. | The Transmission Operator did not model reservations’ sources or sinks as described in R4.3 for more than 10%, but not more than 15% of all reservations; or 3 reservations, whichever is greater. | One or more of the following: • The Transmission Operator did not include in the TTC calculation the contingencies that met the criteria described in the ATCID. • The Transmission Operator did not respect contractual allocations of TTC. • The Transmisson Operator did not model reservations' sources or sinks as described in R4.3 for more than 15% of all reservations; or more than 3 reservations, whichever is greater. •The Transmission Operator did not use firm reservations to estimate interchange or did not utilize that estimate in the TTC calculation as described in R4.3. | [19 empty] | TOP
Inactive | MOD | MOD-028-2 | R5. | Each Transmission Operator shall establish TTC for each ATC Path as defined below: | 2013-10-01 | 2024-02-01 | Low | One or more of the following: • The Transmission Operator did not establish TTCs for use in hourly or daily ATCs within 7 calendar days but did establish the values within 10 calendar days • The Transmission Operator did not establish TTCs for use in monthly TTCs for use in monthly ATSc during a calendar month but did establish the values within the next consecutive calendar month. | One or more of the following: • The Transmission Operator did not establish TTCs for use in hourly or daily ATCs in 10 calendar days but did establish the values within 13 calendar days . The Transmission Operator did not establish TTCs for use in monthly ATCs during a two consecutive calendar month peroid but did establish the values within the third consecutive calendar month. | One or more of the following: • The Transmission Operator did not establish TTCs for used in hourly or daily ATCs in 13 calendar days but did establish the values within 16 calendar days • The Transmission Operator did not establish TTCs for use in monthly ATCs during a three consecutive calendar month period but did establish the values within the fourth consecutive calendar month. | One or more of the following: • The Transmission Operator did not establish TTCs for used in hourly or daily ATCs in 16 calendar days. • The Transmission Operator did not establish TTCs for use in monthly ATCs during a four or more consecutive calendar month period. • The Transmission Operator did not establish TTCs within 24 hours of the triggers defined in R5.3. | [19 empty] | TOP
Inactive | MOD | MOD-028-2 | R6. | Each Transmission Operator shall establish TTC for each ATC Path using the following process: | 2013-10-01 | 2024-02-01 | Low | N/A | N/A | N/A | The Transmission Operator did not calculate TTCs per the process specified in R6. | [19 empty] | TOP
Inactive | MOD | MOD-028-2 | R7. | The Transmission Operator shall provide the Transmission Service Provider of that ATC Path with the most current value for TTC for that ATC Path no more than: | 2013-10-01 | 2024-02-01 | Low | One or more of the following: • The Transmission Operator provided its Transmission Service Provider with its ATC Path TTCs used in hourly or daily ATC calculations more than one calendar day after their determination, but not been more than two calendar days after their determination. • The transmission Operator has not provided its Transmission Service Provider with its ATC Path TTCs used in monthly ATC calculations more than seven calendar days after their determination, but not more than 14 calendar days since their determination. | One or more of the following: • The Transmission Operator provided its Transmission Service Provider with its ATC Path TTCs used in hourly or daily ATC calculations more than two calendar days after their determination, but not been more than three calendar days after their determination. • The Transmisision Operator has not provided its Transmission Service Provider with its ATC Path TTCs used in monthly ATC calculations more than 14 calendar days after their determination, but not been more than 21 calendar days after their determination. | One or more of the following: • The Transmission Operator provided its Transmission Service Provider with its ATC Path TTCs used in hourly or daily ATC calculations more than three calendar days after their determination, but not been more than four calendar days after their determination. • The Transmission Operator has not provided its Transmission Service Provider with its ATC Path TTCs used in monthly ATC calculations more than 21 calendar days after their determination, but not been more than 28 calendar days after their determination. | One or more of the following: • The Transmission Operator provided its Transmission Service Provider with its ATC Path TTCs used in hourly or daily ATC calculations more than four calendar days after their determination. • The Transmission Operator did not provide its Transmission Service Provider with its ATC Path TTCs used in hourly or daily ATC calculations. • The Transmission Operator provided its Transmisssion Service Provider with its ATC Path TTCs used in monthly ATC calculations more than 28 calendar days after their determination. • The Transmission Operator did not provide its transmission Serivce Provider with its ATC Path TTCs used in monthly ATC calculations. | [19 empty] | TOP
Inactive | MOD | MOD-028-2 | R8. | When calculating Existing Transmission Commitments (ETCs) for firm commitments (ETCF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCF = NITSF + GFF + PTPF + RORF + OSF Where: NITSF is the firm capacity set aside for Network Integration Transmission Service (including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) on ATC Paths that serve as interfaces with other Balancing Authorities. GFF is the firm capacity set aside for Grandfathered Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPF is the firm capacity reserved for confirmed Point-to-Point Transmission Service. RORF is the capacity reserved for roll-over rights for Firm Transmission Service contracts granting Transmission Customers the right of first refusal to take or continue to take Transmission Service when the Transmission Customer’s Transmission Service contract expires or is eligible for renewal. OSF is the firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | 2013-10-01 | 2024-02-01 | Low | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M10 for the same period, and the absolute value difference was more than 15% of the value calculated in the measure or 15MW, whichever is greater, but not more than 25% of the value calculated in the measure or 25MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M10 for the same period, and the absolute value difference was more than 25% of the value calculated in the measure or 25MW, whichever is greater, but not more than 35% of the value calculated in the measrue or 35MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M10 for the same period, and the absolute value difference was more than 35% of the value calculated in the measure or 35MW, whichever is greater, but not more than 45% of the value calculated in the measure or 45MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M10 for the same period, and the absolute value difference was more than 45% of the value calculated in the measure or 45MW, whichever is greater. | [21 empty] | TSP
Inactive | MOD | MOD-028-2 | R9. | When calculating ETC for non-firm commitments (ETCNF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: ETCNF = NITSNF + GFNF + PTPNF + OSNF Where: NITSNF is the non-firm capacity set aside for Network Integration Transmission Service (i.e., secondary service , including the capacity used to serve bundled load within the Transmission Service Provider’s area with external sources) reserved on ATC Paths that serve as interfaces with other Balancing Authorities. GFNF is the non-firm capacity reserved for Grandfathered Non-Firm Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or safe harbor tariff on ATC Paths that serve as interfaces with other Balancing Authorities. PTPNF is non-firm capacity reserved for confirmed Point-to-Point Transmission Service. OSNF is the non-firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Non-Firm Transmission Service, including any other firm adjustments to reflect impacts from other ATC Paths of the Transmission Service Provider as specified in the ATCID. | 2013-10-01 | 2024-02-01 | Low | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M11 for the same period, and the absolute value difference was more than 15% of the value calculated in the measure or 15MW, whichever is greater, but not more than 25% of the value calculated in the measure or 25MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M11 for the same period, and the absolute value difference was more than 25% of the value calculated in the measure or 25MW, whichever is greater, but not more than 35% of the value calculated in the meassure or 35MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M11 for the same period, and the absolute value difference was more than 35% of the value calculated in the measure or 35MW, whichever is greater, but not more than 45% of the value calculated in the measrue or 45MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M11 for the same period, and the absolute value difference was more than 45% of the value calculated in the measure or 45MW, whichever is greater. | [21 empty] | TSP
Inactive | MOD | MOD-028-2 | R10. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall utilize the following algorithm: ATCF = TTC – ETCF – CBM – TRM + PostbacksF + counterflowsF Where: ATCF is the firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. CBM is the Capacity Benefit Margin for the ATC Path during that period. TRM is the Transmission Reliability Margin for the ATC Path during that period. PostbacksF¬ are changes to firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsF are adjustments to firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | 2013-10-01 | 2024-02-01 | Low | The Transmission Service Provider did not use all the elements defined in R10 when determining firm ATC, or used additional elements, for more than zero ATC Paths, but not more than 5% of all ATC Paths or 1 ATC Path (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R10 when determining firm ATC, or used additional elements, for more than 5% of all ATC Paths or 1 ATC Path (whichever is greater), but not more than 10% of all ATC Paths or 2 ATC Paths (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R10 when determining firm ATC, or used additional elements, for more than 10% of all ATC Paths or 2 ATC Paths (whichever is greater), but not more than 15% of all ATC Paths or 3 ATC Paths (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R10 when determining firm ATC, or used additional elements, for more than 15% of all ATC Paths or more than 3 ATC Paths (whichever is greater). | [21 empty] | TSP
Inactive | MOD | MOD-028-2 | R11. | When calculating non-firm ATC for a ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: ATCNF = TTC – ETCF - ETCNF – CBMS – TRMU + PostbacksNF + counterflowsNF Where: ATCNF is the non-firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm Transmission commitments for the ATC Path during that period. ETCNF is the sum of existing non-firm Transmission commitments for the ATC Path during that period. CBMS is the Capacity Benefit Margin for the ATC Path that has been scheduled without a separate reservation during that period. TRMU is the Transmission Reliability Margin for the ATC Path that has not been released for sale (unreleased) as non-firm capacity by the Transmission Service Provider during that period. PostbacksNF¬ are changes to non-firm ATC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsNF are adjustments to non-firm ATC as determined by the Transmission Service Provider and specified in the ATCID. | 2013-10-01 | 2024-02-01 | Low | The Transmission Service Provider did not use all the elements defined in R11 when determining non-firm ATC, or used additional elements, for more than zero ATC Paths, but not more than 5% of all ATC Paths or 1 ATC Path (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R11 when determining non-firm ATC, or used additional elements, for more than 5% of all ATC Paths or 1 ATC Path (whichever is greater), but not more than 10% of all ATC Paths or 2 ATC Paths (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R11 when determining non-firm ATC, or used additional elements, for more than 10% of all ATC Paths or 2 ATC Paths (whichever is greater), but not more than 15% of all ATC Paths or 3 ATC Paths (Whicheveris greater). | The Transmission Service Provider did not use all the elements defined in R11 when determining non-firm ATC, or used additional elements, for more than 15% of all ATC Paths or more than 3 ATC Paths (whichever is greater). | [21 empty] | TSP
Inactive | MOD | MOD-029-1 | R1. | When calculating TTCs for ATC Paths, the Transmission Operator shall use a Transmission model which satisfies the following requirements: [Time Horizon: Operations Planning] |  | 2010-09-16 | Low | [23 empty] | TOP
Inactive | MOD | MOD-029-1 | R2. | The Transmission Operator shall use the following process to determine TTC: [Time Horizon: Operations Planning] |  | 2010-09-16 | Low | [23 empty] | TOP
Inactive | MOD | MOD-029-1 | R3. | Each Transmission Operator shall establish the TTC at the lesser of the value calculated in R2 or any System Operating Limit (SOL) for that ATC Path. [Time Horizon: Operations Planning] |  | 2010-09-16 | Low | [23 empty] | TOP
Inactive | MOD | MOD-029-1 | R4. | Within seven calendar days of the finalization of the study report, the Transmission Operator shall make available to the Transmission Service Provider of the ATC Path, the most current value for TTC and the TTC study report documenting the assumptions used and steps taken in determining the current value for TTC for that ATC Path. [Time Horizon: Operations Planning] |  | 2010-09-16 | Low | [23 empty] | TOP
Inactive | MOD | MOD-029-1 | R5. | When calculating ETC for firm Existing Transmission Commitments (ETCF) for a specified period for an ATC Path, the Transmission Service Provider shall use the algorithm below: [Time Horizon: Operations Planning] See standard for formula. |  | 2010-09-16 | Low | [25 empty] | TSP
Inactive | MOD | MOD-029-1 | R6. | When calculating ETC for non-firm Existing Transmission Commitments (ETCNF) for all time horizons for an ATC Path the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See standard for formula. |  | 2010-09-16 | Low | [25 empty] | TSP
Inactive | MOD | MOD-029-1 | R7. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See standard for formula. |  | 2010-09-16 | Low | [25 empty] | TSP
Inactive | MOD | MOD-029-1 | R8. | When calculating non-firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See standard for formula. |  | 2010-09-16 | Low | [25 empty] | TSP
Inactive | MOD | MOD-029-1a | R1. | When calculating TTCs for ATC Paths, the Transmission Operator shall use a Transmission model which satisfies the following requirements: | 2011-04-01 | 2017-03-31 | Low | The Transmission Operator used a model that met all but one of the modeling requirements specified in R1.1. OR The Transmission Operator utilized one to ten Facility Ratings that were different from those specified by a Transmission Owner or Generation Owner in their Transmission model. (R1.2) | The Transmission Operator used a model that met all but two of the modeling requirements specified in R1.1. OR The Transmission Operator utilized eleven to twenty Facility Ratings that were different from those specified by a Transmission Owner or Generation Owner in their Transmission model. (R1.2) | The Transmission Operator used a model that met all but three of the modeling requirements specified in R1.1. OR The Transmission Operator utilized twenty-one to thirty Facility Ratings that were different from those specified by a Transmission Owner or Generation Owner in their Transmission model. (R1.2) | The Transmission Operator used a model that did not meet four or more of the modeling requirements specified in R1.1. OR The Transmission Operator utilized more than thirty Facility Ratings that were different from those specified by a Transmission Owner or Generation Owner in their Transmission model. (R1.2) | [19 empty] | TOP
Inactive | MOD | MOD-029-1a | R2. | The Transmission Operator shall use the following process to determine TTC: | 2011-04-01 | 2017-03-31 | Low | One or both of the following: • The Transmission Operator did not calculate TTC using one of the items in subrequirements R2.1-R2.6. • The Transmission Operator does not include one required item in the study report required in R2.8. | One or both of the following: • The Transmission Operator did not calculate TTC using two of the items in subrequirements R2.1-R2.6. • The Transmission Operator does not include two required items in the study report required in R2.8. | One or both of the following: • The Transmission Operator did not calculate TTC using three of the items in subrequirements R2.1-R2.6. • The Transmission Operator does not include three required items in the study report required in R2.8. | One or more of the following: • The Transmission Operator did not calculate TTC using four or more of the items in subrequirements R2.1-R2.6. • The Transmission Operator did not apply R2.7. • The Transmission Operator does not include four or more required items in the study report required in R2.8 | [19 empty] | TOP
Inactive | MOD | MOD-029-1a | R3. | Each Transmission Operator shall establish the TTC at the lesser of the value calculated in R2 or any System Operating Limit (SOL) for that ATC Path. | 2011-04-01 | 2017-03-31 | Low | The Transmission Operator did not specify the TTC as the lesser of the TTC calculated using the process described in R2 or any associated SOL for more than zero ATC Paths, BUT, not more than 1% of all ATC Paths or 1 ATC Path (whichever is greater). | The Transmission Operator did not specify the TTC as the lesser of the TTC calculated using the process described in R2 or any associated SOL for more than 1% of all ATC Paths or 1 ATC Path (whichever is greater), BUT not more than 2% of all ATC Paths or 2 ATC Paths (whichever is greater). | The Transmission Operator did not specify the TTC as the lesser of the TTC calculated using the process described in R2 or any associated SOL for more than 2% of all ATC Paths or 2 ATC Paths (whichever is greater), BUT not more than 5% of all ATC Paths or 3 ATC Paths (whichever is greater). | The Transmission Operator did not specify the TTC as the lesser of the TTC calculated using the process described in R2 or any associated SOL, for more than 5% of all ATC Paths or 3 ATC Paths (whichever is greater). | [19 empty] | TOP
Inactive | MOD | MOD-029-1a | R4. | Within seven calendar days of the finalization of the study report, the Transmission Operator shall make available to the Transmission Service Provider of the ATC Path, the most current value for TTC and the TTC study report documenting the assumptions used and steps taken in determining the current value for TTC for that ATC Path. | 2011-04-01 | 2017-03-31 | Low | The Transmission Operator provided the TTC and study report to the Transmission Service Provider more than seven, but not more than 14 calendar days after the report was finalized. | The Transmission Operator provided the TTC and study report to the Transmission Service Provider more than 14, but not more than 21 calendar days after the report was finalized. | The Transmission Operator provided the TTC and study report to the Transmission Service Provider more than 21, but not more than 28 calendar days after the report was finalized. | The Transmission Operator provided the TTC and study report to the Transmission Service Provider more than 28 calendar days after the report was finalized. | [19 empty] | TOP
Inactive | MOD | MOD-029-1a | R5. | When calculating ETC for firm Existing Transmission Commitments (ETCF) for a specified period for an ATC Path, the Transmission Service Provider shall use the algorithm below: See standard for formula. | 2011-04-01 | 2017-03-31 | Low | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M7 for the same period, and the absolute value difference was more than 15% of the value calculated in the measure or 15MW, whichever is greater, but not more than 25% of the value calculated in the measure or 25MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M7 for the same period, and the absolute value difference was more than 25% of the value calculated in the measure or 25MW, whichever is greater, but not more than 35% of the value calculated in the measure or 35MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M7 for the same period, and the absolute value difference was more than 35% of the value calculated in the measure or 35MW, whichever is greater, but not more than 45% of the value calculated in the measure or 45MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M7 for the same period, and the absolute value difference was more than 45% of the value calculated in the measure or 45MW, whichever is greater. | [21 empty] | TSP
Inactive | MOD | MOD-029-1a | R6. | When calculating ETC for non-firm Existing Transmission Commitments (ETCNF) for all time horizons for an ATC Path the Transmission Service Provider shall use the following algorithm: See standard for formula. ETCNF = NITSNF + GFNF + PTPNF + OSNF Where: NITSNF is the non-firm capacity set aside for Network Integration Transmission Service serving Load (i.e., secondary service), to include losses, and load growth not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. GFNF is the non-firm capacity set aside for grandfathered Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or “safe harbor tariff.” PTPNF is non-firm capacity reserved for confirmed Point-to-Point Transmission Service. OSNF is the non-firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using non-firm transmission service as specified in the ATCID. | 2011-04-01 | 2017-03-31 | Low | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M8 for the same period, and the absolute value difference was more than 15% of the value calculated in the measure or 15MW, whichever is greater, but not more than 25% of the value calculated in the measure or 25MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M8 for the same period, and the absolute value difference was more than 25% of the value calculated in the measure or 25MW, whichever is greater, but not more than 35% of the value calculated in the measure or 35MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M8 for the same period, and the absolute value difference was more than 35% of the value calculated in the measure or 35MW, whichever is greater, but not more than 45% of the value calculated in the measure or 45MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M8 for the same period, and the absolute value difference was more than 45% of the value calculated in the measure or 45MW, whichever is greater. | [21 empty] | TSP
Inactive | MOD | MOD-029-1a | R7. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: See standard for formula. : Lower] [Time Horizon: Operations Planning] ATCF = TTC – ETCF – CBM – TRM + PostbacksF + counterflowsF Where ATCF is the firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm commitments for the ATC Path during that period. CBM is the Capacity Benefit Margin for the ATC Path during that period. TRM is the Transmission Reliability Margin for the ATC Path during that period. PostbacksF are changes to firm Available Transfer Capability due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsF are adjustments to firm Available Transfer Capability as determined by the Transmission Service Provider and specified in their ATCID | 2011-04-01 | 2017-03-31 | Low | The Transmission Service Provider did not use all the elements defined in R7 when determining firm ATC, or used additional elements, for more than zero ATC Paths, but not more than 5% of all ATC Paths or 1 ATC Path (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R7 when determining firm ATC, or used additional elements, for more than 5% of all ATC Paths or 1 ATC Path (whichever is greater), but not more than 10% of all ATC Paths or 2 ATC Paths (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R7 when determining firm ATC, or used additional elements, for more than 10% of all ATC Paths or 2 ATC Paths (whichever is greater), but not more than 15% of all ATC Paths or 3 ATC Paths (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R7 when determining firm ATC, or used additional elements, for more than 15% of all ATC Paths or more than 3 ATC Paths (whichever is greater). | [21 empty] | TSP
Inactive | MOD | MOD-029-1a | R8. | When calculating non-firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: See standard for formula. ATCNF = TTC – ETCF – ETCNF – CBMS – TRMU + PostbacksNF + counterflowsNF Where: ATCNF is the non-firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm commitments for the ATC Path during that period. ETCNF is the sum of existing non-firm commitments for the ATC Path during that period. CBMS is the Capacity Benefit Margin for the ATC Path that has been scheduled during that period. TRMU is the Transmission Reliability Margin for the ATC Path that has not been released for sale (unreleased) as non-firm capacity by the Transmission Service Provider during that period. PostbacksNF are changes to non-firm Available Transfer Capability due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsNF are adjustments to non-firm Available Transfer Capability as determined by the Transmission Service Provider and specified in its ATCID. | 2011-04-01 | 2017-03-31 | Low | The Transmission Service Provider did not use all the elements defined in R8 when determining non-firm ATC, or used additional elements, for more than zero ATC Paths, but not more than 5% of all ATC Paths or 1 ATC Path (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R8 when determining non-firm ATC, or used additional elements, for more than 5% of all ATC Paths or 1 ATC Path (whichever is greater), but not more than 10% of all ATC Paths or 2 ATC Paths (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R8 when determining non-firm ATC, or used additional elements, for more than 10% of all ATC Paths or 2 ATC Paths (whichever is greater), but not more than 15% of all ATC Paths or 3 ATC Paths (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R8 when determining non-firm ATC, or used additional elements, for more than 15% of all ATC Paths or more than 3 ATC Paths (whichever is greater). | [21 empty] | TSP
Inactive | MOD | MOD-029-2a | R1. | When calculating TTCs for ATC Paths, the Transmission Operator shall use a Transmission model which satisfies the following requirements: | 2017-04-01 | 2024-02-01 | Low | The Transmission Operator used a model that met all but one of the modeling requirements specified in R1.1. OR The Transmission Operator utilized one to ten Facility Ratings that were different from those specified by a Transmission Owner or Generation Owner in their Transmission model. (R1.2) | The Transmission Operator used a model that met all but two of the modeling requirements specified in R1.1. OR The Transmission Operator utilized eleven to twenty Facility Ratings that were different from those specified by a Transmission Owner or Generation Owner in their Transmission model. (R1.2) | The Transmission Operator used a model that met all but three of the modeling requirements specified in R1.1. OR The Transmission Operator utilized twenty-one to thirty Facility Ratings that were different from those specified by a Transmission Owner or Generation Owner in their Transmission model. (R1.2) | The Transmission Operator used a model that did not meet four or more of the modeling requirements specified in R1.1. OR The Transmission Operator utilized more than thirty Facility Ratings that were different from those specified by a Transmission Owner or Generation Owner in their Transmission model. (R1.2) | [19 empty] | TOP
Inactive | MOD | MOD-029-2a | R2. | The Transmission Operator shall use the following process to determine TTC: | 2017-04-01 | 2024-02-01 | Low | One or both of the following:• The Transmission Operator did not calculate TTC using one of the items in sub-requirements R2.1-R2.6. • The Transmission Operator does not include one required item in the study report required in R2.8. | One or both of the following:• The Transmission Operator did not calculate TTC using two of the items in sub-requirements R2.1-R2.6. • The Transmission Operator does not include two required items in the study report required in R2.8. | One or both of the following:• The Transmission Operator did not calculate TTC using three of the items in sub-requirements R2.1-R2.6. • The Transmission Operator does not include three required items in the study report required in R2.8. | One or more of the following:• The Transmission Operator did not calculate TTC using four or more of the items in sub-requirements R2.1-R2.6. • The Transmission Operator did not apply R2.7. • The Transmission Operator does not include four or more required items in the study report required in R2.8 | [19 empty] | TOP
Inactive | MOD | MOD-029-2a | R3. | Each Transmission Operator shall establish the TTC at the lesser of the value calculated in R2 or any System Operating Limit (SOL) for that ATC Path. | 2017-04-01 | 2024-02-01 | Low | The Transmission Operator did not specify the TTC as the lesser of the TTC calculated using the process described in R2 or any associated SOL for more than zero ATC Paths, BUT, not more than 1% of all ATC Paths or 1 ATC Path (whichever is greater). | The Transmission Operator did not specify the TTC as the lesser of the TTC calculated using the process described in R2 or any associated SOL for more than 1% of all ATC Paths or 1 ATC Path (whichever is greater), BUT not more than 2% of all ATC Paths or 2 ATC Paths (whichever is greater). | The Transmission Operator did not specify the TTC as the lesser of the TTC calculated using the process described in R2 or any associated SOL for more than 2% of all ATC Paths or 2 ATC Paths (whichever is greater), BUT not more than 5% of all ATC Paths or 3 ATC Paths (whichever is greater). | The Transmission Operator did not specify the TTC as the lesser of the TTC calculated using the process described in R2 or any associated SOL, for more than 5% of all ATC Paths or 3 ATC Paths (whichever is greater). | [19 empty] | TOP
Inactive | MOD | MOD-029-2a | R4. | Within seven calendar days of the finalization of the study report, the Transmission Operator shall make available to the Transmission Service Provider of the ATC Path, the most current value for TTC and the TTC study report documenting the assumptions used and steps taken in determining the current value for TTC for that ATC Path. | 2017-04-01 | 2024-02-01 | Low | The Transmission Operator provided the TTC and study report to the Transmission Service Provider more than seven, but not more than 14 calendar days after the report was finalized. | The Transmission Operator provided the TTC and study report to the Transmission Service Provider more than 14, but not more than 21 calendar days after the report was finalized. | The Transmission Operator provided the TTC and study report to the Transmission Service Provider more than 21, but not more than 28 calendar days after the report was finalized. | The Transmission Operator provided the TTC and study report to the Transmission Service Provider more than 28 calendar days after the report was finalized. | [19 empty] | TOP
Inactive | MOD | MOD-029-2a | R5. | When calculating ETC for firm Existing Transmission Commitments (ETCF) for a specified period for an ATC Path, the Transmission Service Provider shall use the algorithm below: [See standard for additional information.] ETCF = NLF + NITSF + GFF + PTPF + RORF + OSF Where: NLF is the firm capacity set aside to serve peak Native Load forecast commitments for the time period being calculated, to include losses, and Native Load growth, not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. NITSF is the firm capacity reserved for Network Integration Transmission Service serving Load, to include losses, and Load growth, not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. GFF is the firm capacity set aside for grandfathered Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or “safe harbor tariff.” PTPF is the firm capacity reserved for confirmed Point-to-Point Transmission Service. RORF is the firm capacity reserved for Roll-over rights for contracts granting Transmission Customers the right of first refusal to take or continue to take Transmission Service when the Transmission Customer’s Transmission Service contract expires or is eligible for renewal. OSF is the firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using Firm Transmission Service as specified in the ATCID. | 2017-04-01 | 2024-02-01 | Low | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M7 for the same period, and the absolute value difference was more than 15% of the value calculated in the measure or 15MW, whichever is greater, but not more than 25% of the value calculated in the measure or 25MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M7 for the same period, and the absolute value difference was more than 25% of the value calculated in the measure or 25MW, whichever is greater, but not more than 35% of the value calculated in the measure or 35MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M7 for the same period, and the absolute value difference was more than 35% of the value calculated in the measure or 35MW, whichever is greater, but not more than 45% of the value calculated in the measure or 45MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M7 for the same period, and the absolute value difference was more than 45% of the value calculated in the measure or 45MW, whichever is greater. | [21 empty] | TSP
Inactive | MOD | MOD-029-2a | R6. | When calculating ETC for non-firm Existing Transmission Commitments (ETCNF) for all time horizons for an ATC Path the Transmission Service Provider shall use the following algorithm: [See standard for additional information.] ETCNF = NITSNF + GFNF + PTPNF + OSNF Where: NITSNF is the non-firm capacity set aside for Network Integration Transmission Service serving Load (i.e., secondary service), to include losses, and load growth not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. GFNF is the non-firm capacity set aside for grandfathered Transmission Service and contracts for energy and/or Transmission Service, where executed prior to the effective date of a Transmission Service Provider’s Open Access Transmission Tariff or “safe harbor tariff.” PTPNF is non-firm capacity reserved for confirmed Point-to-Point Transmission Service. OSNF is the non-firm capacity reserved for any other service(s), contract(s), or agreement(s) not specified above using non-firm transmission service as specified in the ATCID. | 2017-04-01 | 2024-02-01 | Low | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M8 for the same period, and the absolute value difference was more than 15% of the value calculated in the measure or 15MW, whichever is greater, but not more than 25% of the value calculated in the measure or 25MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M8 for the same period, and the absolute value difference was more than 25% of the value calculated in the measure or 25MW, whichever is greater, but not more than 35% of the value calculated in the measure or 35MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M8 for the same period, and the absolute value difference was more than 35% of the value calculated in the measure or 35MW, whichever is greater, but not more than 45% of the value calculated in the measure or 45MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M8 for the same period, and the absolute value difference was more than 45% of the value calculated in the measure or 45MW, whichever is greater. | [21 empty] | TSP
Inactive | MOD | MOD-029-2a | R7. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: [See standard for additional information.] ATCF = TTC – ETCF – CBM – TRM + PostbacksF + counterflowsF Where ATCF is the firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm commitments for the ATC Path during that period. CBM is the Capacity Benefit Margin for the ATC Path during that period. TRM is the Transmission Reliability Margin for the ATC Path during that period. PostbacksF¬ are changes to firm Available Transfer Capability due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsF are adjustments to firm Available Transfer Capability as determined by the Transmission Service Provider and specified in their ATCID. | 2017-04-01 | 2024-02-01 | Low | The Transmission Service Provider did not use all the elements defined in R7 when determining firm ATC, or used additional elements, for more than zero ATC Paths, but not more than 5% of all ATC Paths or 1 ATC Path (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R7 when determining firm ATC, or used additional elements, for more than 5% of all ATC Paths or 1 ATC Path (whichever is greater), but not more than 10% of all ATC Paths or 2 ATC Paths (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R7 when determining firm ATC, or used additional elements, for more than 10% of all ATC Paths or 2 ATC Paths (whichever is greater), but not more than 15% of all ATC Paths or 3 ATC Paths (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R7 when determining firm ATC, or used additional elements, for more than 15% of all ATC Paths or more than 3 ATC Paths (whichever is greater). | [21 empty] | TSP
Inactive | MOD | MOD-029-2a | R8. | When calculating non-firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: ATCNF = TTC – ETCF – ETCNF – CBMS – TRMU + PostbacksNF + counterflowsNF Where: ATCNF is the non-firm Available Transfer Capability for the ATC Path for that period. TTC is the Total Transfer Capability of the ATC Path for that period. ETCF is the sum of existing firm commitments for the ATC Path during that period. ETCNF is the sum of existing non-firm commitments for the ATC Path during that period. CBMS is the Capacity Benefit Margin for the ATC Path that has been scheduled during that period. TRMU is the Transmission Reliability Margin for the ATC Path that has not been released for sale (unreleased) as non-firm capacity by the Transmission Service Provider during that period. PostbacksNF¬ are changes to non-firm Available Transfer Capability due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsNF are adjustments to non-firm Available Transfer Capability as determined by the Transmission Service Provider and specified in its ATCID. | 2017-04-01 | 2024-02-01 | Low | The Transmission Service Provider did not use all the elements defined in R8 when determining non-firm ATC, or used additional elements, for more than zero ATC Paths, but not more than 5% of all ATC Paths or 1 ATC Path (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R8 when determining non-firm ATC, or used additional elements, for more than 5% of all ATC Paths or 1 ATC Path (whichever is greater), but not more than 10% of all ATC Paths or 2 ATC Paths (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R8 when determining non-firm ATC, or used additional elements, for more than 10% of all ATC Paths or 2 ATC Paths (whichever is greater), but not more than 15% of all ATC Paths or 3 ATC Paths (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R8 when determining non-firm ATC, or used additional elements, for more than 15% of all ATC Paths or more than 3 ATC Paths (whichever is greater). | [21 empty] | TSP
Inactive | MOD | MOD-030-1 | R1. | The Transmission Service Provider shall include in its “Available Transfer Capability Implementation Document” (ATCID). [Time Horizon: Operations Planning] |  | 2009-11-24 | Low | [25 empty] | TSP
Inactive | MOD | MOD-030-1 | R2. | The Transmission Operator shall perform the following: [Time Horizon: Operations Planning] |  | 2009-11-24 | Low | [23 empty] | TOP
Inactive | MOD | MOD-030-1 | R3. | The Transmission Operator shall make available to the Transmission Service Provider a Transmission model to determine Available Flowgate Capability (AFC) that meets the following criteria: [Time Horizon: Operations Planning] |  | 2009-11-24 | Low | [23 empty] | TOP
Inactive | MOD | MOD-030-1 | R4. | When calculating AFCs, the Transmission Service Provider shall represent the impact of Transmission Service as follows:[Time Horizon: Operations Planning] - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. |  | 2009-11-24 | Low | [25 empty] | TSP
Inactive | MOD | MOD-030-1 | R5. | When calculating AFCs, the Transmission Service Provider shall: [Time Horizon: Operations Planning] |  | 2009-11-24 | Low | [25 empty] | TSP
Inactive | MOD | MOD-030-1 | R6. | When calculating the impact of ETC for firm commitments (ETCFi) for all time periods for a Flowgate, the Transmission Service Provider shall sum the following: [Time Horizon: Operations Planning] |  | 2009-11-24 | Low | [25 empty] | TSP
Inactive | MOD | MOD-030-1 | R7. | When calculating the impact of ETC for non-firm commitments (ETCNFi) for all time periods for a Flowgate the Transmission Service Provider shall sum: [Time Horizon: Operations Planning] |  | 2009-11-24 | Low | [25 empty] | TSP
Inactive | MOD | MOD-030-1 | R8. | When calculating firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): [Time Horizon: Operations Planning] See standard for formula. |  | 2009-11-24 | Low | [25 empty] | TSP
Inactive | MOD | MOD-030-1 | R9. | When calculating non-firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): [Time Horizon: Operations Planning] See standard for formula. |  | 2009-11-24 | Low | [25 empty] | TSP
Inactive | MOD | MOD-030-1 | R10. | Each Transmission Service Provider shall recalculate AFC, utilizing the updated models described in R3.2, R3.3, and R5, at a minimum on the following frequency, unless none of the calculated values identified in the AFC equation have changed: [Time Horizon: Operations Planning] |  | 2009-11-24 | Low | [25 empty] | TSP
Inactive | MOD | MOD-030-1 | R11. | When converting Flowgate AFCs to ATCs (and TFCs to TTCs) for ATC Paths, the Transmission Service Provider shall convert those values based on the following algorithm: [Time Horizon: Operations Planning] See standard for formula. |  | 2009-11-24 | Low | [25 empty] | TSP
Inactive | MOD | MOD-030-2 | R1. | The Transmission Service Provider shall include in its “Available Transfer Capability Implementation Document” (ATCID): | 2011-04-01 | 2017-03-31 | Medium | The Transmission Service Provider does not include in its ATCID one or two of the subrequirements listed under R1.2, or the sub-requirement is incomplete. | The Transmission Service Provider does not include in its ATCID three of the subrequirements listed under R1.2, or the sub-requirement is incomplete. | The Transmission Service Provider does not include in its ATCID the information described in R1.1. OR The Transmission Service Provider does not include in its ATCID the information described in R1.2 (1.2.1, 1.2.2., 1.2.3, and 1.2.4 are missing). | The Transmission Service Provider does not include in its ATCID the information described in R1.1 and R1.2 (1.2.1, 1.2.2., 1.2.3, and 1.2.4 are missing). | [21 empty] | TSP
Inactive | MOD | MOD-030-2 | R2. | The Transmission Operator shall perform the following: | 2011-04-01 | 2017-03-31 | Medium | One or more of the following:  The Transmission Operator established its list of Flowgates less frequently than once per calendar year, but not more than three months late as described in R2.2.  The Transmission Operator established its list of Flowgates more than thirty days, but not more than sixty days, following a request to create, modify or delete a flowgate as described in R2.3.  The Transmission Operator has not updated its Flowgate TFC when notified by the Transmission Owner in more than 7 days, but it has not been more than 14 days since the notification (R2.5.1)  The Transmission Operator has not provided its Transmission Service Provider with its Flowgate TFCs within seven days (one week) of their determination, but is has not been more than 14 days (two weeks) since their determination. | One or more of the following:  The Transmission Operator did not include a Flowgate in their AFC calculations that met the criteria described in R2.1.  The Transmission Operator established its list of Flowgates more than three months late, but not more than six months late as described in R2.2.  The Transmission Operator established its list of Flowgates more than sixty days, but not more than ninety days, following a request to create, modify or delete a flowgate as described in R2.3.  The Transmission Operatorhas not updated its Flowgate TFCs at least once within a calendar year, and it has been not more than 15 months since the last update.  The Transmission Operator has not updated its Flowgate TFC when notified by the Transmission Owner in more than 14 days, but it has not been more than 21 days since the notification (R2.5.1)  The Transmission Operator has not provided its Transmission Service Provider with its Flowgate TFCs in more than 14 days (two weeks) of their determination, but is has not been more than 21 days (three weeks) since their determination. | One or more of the following:  The Transmission Operator did not include two to five Flowgates in their AFC calculations that met the criteria described in R2.1.  The Transmission Operator established its list of Flowgates more than six months late, but not more than nine months late as described in R2.2.  The Transmission Operator established its list of Flowgates more than ninety days, but not more than 120 days, following a request to create, modify or delete a flowgate as described in R2.3. The Transmission Operatorhas not updated its Flowgate TFCs at least once within a calendar year, and it has been more than 15 months but not more than 18 months since the last update.  The Transmission Operator has not updated its Flowgate TFCs when notified by the Transmission Owner in more than 21 days, but it has not been more than 28 days since the notification (R2.5.1)  The Transmission Operator has not provided its Transmission Service Provider with its Flowgate TFCs in more than 21 days (three weeks) of their determination, but is has not been more than 28 days (four weeks) since their determination. | One or more of the following:  The Transmission Operator did not include six or more Flowgates in their AFC calculations that met the criteria described in R2.1.  The Transmission Operator established its list of Flowgates more than nine months late as described in R2.2.  The Transmission Operator did not establish its list of internal Flowgates as described in R2.2.  The Transmission Operator established its list of Flowgates more than 120 days following a request to create, modify or delete a flowgate as described in R2.3.  The Transmission Operator did not establish its list of external Flowgates following a request to create, modify or delete an external flowgate as described in R2.3.  The Transmission Operator did not determine the TFC for a flowgate as described in R2.4.  The Transmission Operator has not updated its Flowgate TFCs at least once within a calendar year, and it has been more than 18 months since the last update. (R2.5)  The Transmission Operator has not updated its Flowgate TFCs when notified by the Transmission Owner in more than 28 calendar days (R2.5.1)  The Transmission Operator has not provided its Transmission Service Provider with its Flowgate TFCs in more than 28 days (4 weeks) of their determination. | [19 empty] | TOP
Inactive | MOD | MOD-030-2 | R3. | The Transmission Operator shall make available to the Transmission Service Provider a Transmission model to determine Available Flowgate Capability (AFC) that meets the following criteria: | 2011-04-01 | 2017-03-31 | Medium | One or more of the following:  The Transmission Operator used one to ten Facility Ratings that were different from those specified by a Transmission or Generator Owner in their Transmission model.  The Transmission Operator did not update the model per R3.2 for one or more calendar days but not more than 2 calendar days  The Transmission Operator did not update the model for per R3.3 for one or more months but not more than six weeks | One or more of the following:  The Transmission Operator used eleven to twenty Facility Ratings that were different from those specified by a Transmission or Generator Owner in their Transmission model.  The Transmission Operator did not update the model per R3.2 for more than 2 calendar days but not more than 3 calendar days  The Transmission Operator did not update the model for per R3.3 for more than six weeks but not more than eight weeks | One or more of the following:  The Transmission Operator used twenty-one to thirty Facility Ratings that were different from those specified by a Transmission or Generator Owner in their Transmission model.  The Transmission Operator did not update the model per R3.2 for more than 3 calendar days but not more than 4 calendar days  The Transmission Operator did not update the model for per R3.3 for more than eight weeks but not more than ten weeks | One or more of the following:  The Transmission Operator did not update the model per R3.2 for more than 4 calendar days  The Transmission Operator did not update the model for per R3.3 for more than ten weeks  The Transmission Operator used more than thirty Facility Ratings that were different from those specified by a Transmission or Generator Owner in their Transmission model.  The Transmission operator did not include in the Transmission model detailed modeling data and topology for its own Reliability Coordinator area.  The Transmission operator did not include in the Transmission modeling data and topology for immediately adjacent and beyond Reliability Coordinator area. | [19 empty] | TOP
Inactive | MOD | MOD-030-2 | R4. | When calculating AFCs, the Transmission Service Provider shall represent the impact of Transmission Service as follows: [Time Horizon: Operations Planning] - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. | 2011-04-01 | 2017-03-31 | Medium | The Transmission Service Provider did not represent the impact of Transmission Service as described in R4 for more than zero, but not more than 5% of all reservations; or more than zero, but not more than 1 reservation, whichever is greater.. | The Transmission Service Provider did not represent the impact of Transmission Service as described in R4 for more than 5%, but not more than 10% of all reservations; or more than 1, but not more than 2 reservations, whichever is greater.. | The Transmission Service Provider did not represent the impact of Transmission Service as described in R4 for more than 10%, but not more than 15% of all reservations; or more than 2, but not more than 3 reservations, whichever is greater.. | The Transmission Service Provider did not represent the impact of Transmission Service as described in R4 for more than 15% of all reservations; or more than 3 reservations, whichever is greater.. | [21 empty] | TSP
Inactive | MOD | MOD-030-2 | R5. | When calculating AFCs, the Transmission Service Provider shall: | 2011-04-01 | 2017-03-31 | Medium | The Transmission Service Provider did not include in the AFC process one to ten expected generation or Transmission outages, additions or retirements within the scope of the model as specified in the ATCID. | The Transmission Service Provider did not include in the AFC process eleven to twentyfive expected generation and Transmission outages, additions or retirements within the scope of the model as specified in the ATCID. | The Transmission Service Provider did not include in the AFC process twenty-six to fifty expected generation and Transmission outages, additions or retirements within the scope of the model as specified in the ATCID. | One or more of the following:  The Transmission Service Provider did not use the model provided by the Transmission Operator.  The Transmission Service Provider did not include in the AFC process more than fifty expected generation and Transmission outages, additions or retirements within the scope of the model as specified in the ATCID.  The Transmission Service provider did not use AFC provided by a third party. | [21 empty] | TSP
Inactive | MOD | MOD-030-2 | R6. | When calculating the impact of ETC for firm commitments (ETCFi) for all time periods for a Flowgate, the Transmission Service Provider shall sum the following: | 2011-04-01 | 2017-03-31 | Medium | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M13 for the same period, and the absolute value difference was more than 15% of the value calculated in the measure or 15MW, whichever is greater, but not more than 25% of the value calculated in the measure or 25MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M13 for the same period, and the absolute value difference was more than 25% of the value calculated in the measure or 25MW, whichever is greater, but not more than 35% of the value calculated in the measure or 35MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M13 for the same period, and the absolute value difference was more than 35% of the value calculated in the measure or 35MW, whichever is greater, but not more than 45% of the value calculated in the measure or 45MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M13 for the same period, and the absolute value difference was more than 45% of the value calculated in the measure or 45MW, whichever is greater. | [21 empty] | TSP
Inactive | MOD | MOD-030-2 | R7. | When calculating the impact of ETC for non-firm commitments (ETCNFi) for all time periods for a Flowgate the Transmission Service Provider shall sum: | 2011-04-01 | 2017-03-31 | Low | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M14 for the same period, and the absolute value difference was more than 15% of the value calculated in the measure or 15MW, whichever is greater, but not more than 25% of the value calculated in the measure or 25MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M14 for the same period, and the absolute value difference was more than 25% of the value calculated in the measure or 25MW, whichever is greater, but not more than 35% of the value calculated in the measure or 35MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M14 for the same period, and the absolute value difference was more than 35% of the value calculated in the measure or 35MW, whichever is greater, but not more than 45% of the value calculated in the measure or 45MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M14 for the same period, and the absolute value difference was more than 45% of the value calculated in the measure or 45MW, whichever is greater. | [21 empty] | TSP
Inactive | MOD | MOD-030-2 | R8. | When calculating firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): See Standard for Formula. AFCF = TFC – ETCFi – CBMi – TRMi + PostbacksFi + counterflowsFi Where: AFCF is the firm Available Flowgate Capability for the Flowgate for that period. TFC is the Total Flowgate Capability of the Flowgate. ETCFi is the sum of the impacts of existing firm Transmission commitments for the Flowgate during that period. CBMi is the impact of the Capacity Benefit Margin on the Flowgate during that period. TRMi is the impact of the Transmission Reliability Margin on the Flowgate during that period. PostbacksFi are changes to firm AFC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsFi are adjustments to firm AFC as determined by the Transmission Service Provider and specified in their ATCID. | 2011-04-01 | 2017-03-31 | Medium | The Transmission Service Provider did not use all the elements defined in R8 when determining firm AFC, or used additional elements, for more than zero Flowgates, but not more than 5% of all Flowgates or 1 Flowgate (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R8 when determining firm AFC, or used additional elements, for more than 5% of all Flowgates or 1 Flowgates (whichever is greater), but not more than 10% of all Flowgates or 2 Flowgates (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R8 when determining firm AFC, or used additional elements, for more than 10% of all Flowgates or 2 Flowgates (whichever is greater), but not more than 15% of all Flowgates or 3 Flowgates (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R8 when determining firm AFC, or used additional elements, for more than 15% of all Flowgates or more than 3 Flowgates (whichever is greater). | [21 empty] | TSP
Inactive | MOD | MOD-030-2 | R9. | When calculating non-firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): [Time Horizon: Operations Planning] See Standard for Formula. | 2011-04-01 | 2017-03-31 | Low | The Transmission Service Provider did not use all the elements defined in R8 when determining non-firm AFC, or used additional elements, for more than zero Flowgates, but not more than 5% of all Flowgates or 1 Flowgate (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R9 when determining non-firm AFC, or used additional elements, for more than 5% of all Flowgates or 1 Flowgate (whichever is greater), but not more than 10% of all Flowgates or 2 Flowgates (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R9 when determining non-firm AFC, or used additional elements, for more than 10% of all Flowgates or 2 Flowgates (whichever is greater), but not more than 15% of all Flowgates or 3 Flowgates (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R9 when determining non-firm AFC, or used additional elements, for more than 15% of all Flowgates or more than 3 Flowgates (whichever is greater). | [21 empty] | TSP
Inactive | MOD | MOD-030-2 | R10. | Each Transmission Service Provider shall recalculate AFC, utilizing the updated models described in R3.2, R3.3, and R5, at a minimum on the following frequency, unless none of the calculated values identified in the AFC equation have changed: See Standard for Formula. | 2011-04-01 | 2017-03-31 | Medium | One or more of the following:  For Hourly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for one or more hours but not more than 15 hours, and was in excess of the 175-hour per year requirement.  For Daily, the values described in the AFC equation changed and the Transmission Service provider did not calculate for one or more calendar days but not more than 3 calendar days.  For Monthly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for seven or more calendar days, but less than 14 calendar days. | One or more of the following:  For Hourly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for more than 15 hours but not more than 20 hours, and was in excess of the 175-hour per year requirement.  For Daily, the values described in the AFC equation changed and the Transmission Service provider did not calculate for more than 3 calendar days but not more than 4 calendar days.  For Monthly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for 14 or more calendar days, but less than 21 calendar days. | One or more of the following:  For Hourly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for more than 20 hours but not more than 25 hours, and was in excess of the 175-hour per year requirement.  For Daily, the values described in the AFC equation changed and the Transmission Service provider did not calculate for more than 4 calendar days but not more than 5 calendar days.  For Monthly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for 21 or more calendar days, but less than 28 calendar days. | One or more of the following:  For Hourly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for more than 25 hours, and was in excess of the 175-hour per year requirement.  For Daily, the values described in the AFC equation changed and the Transmission Service provider did not calculate for more than 5 calendar days.  For Monthly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for 28 or more calendar days. | [21 empty] | TSP
Inactive | MOD | MOD-030-2 | R11. | When converting Flowgate AFCs to ATCs for ATC Paths, the Transmission Service Provider shall convert those values based on the following algorithm: See Standard for Formula. | 2011-04-01 | 2017-03-31 | Low | N/A | N/A | N/A | The Transmission Service Provider did not follow the procedure for converting Flowgate AFCs to ATCs described in R11. | [21 empty] | TSP
Inactive | MOD | MOD-030-3 | R1. | The Transmission Service Provider shall include in its “Available Transfer Capability Implementation Document” (ATCID): | 2017-04-01 | 2024-02-01 | Medium | The Transmission Service Provider does not include in its ATCID one or two of the sub-requirements listed under R1.2, or the sub-requirement is incomplete. | The Transmission Service Provider does not include in its ATCID three of the sub-requirements listed under R1.2, or the sub-requirement is incomplete. | The Transmission Service Provider does not include in its ATCID the information described in R1.1. OR The Transmission Service Provider does not include in its ATCID the information described in R1.2 (1.2.1, 1.2.2., 1.2.3, and 1.2.4 are missing). | The Transmission Service Provider does not include in its ATCID the information described in R1.1 and R1.2 (1.2.1, 1.2.2., 1.2.3, and 1.2.4 are missing). | [21 empty] | TSP
Inactive | MOD | MOD-030-3 | R2. | The Transmission Operator shall perform the following: | 2017-04-01 | 2024-02-01 | Medium | One or more of the following: • The Transmission Operator established its list of Flowgates less frequently than once per calendar year, but not more than three months late as described in R2.2. • The Transmission Operator established its list of Flowgates more than thirty days, but not more than sixty days, following a request to create, modify or delete a flowgate as described in R2.3. • The Transmission Operator has not updated its Flowgate TFC when notified by the Transmission Owner in more than 7 days, but it has not been more than 14 days since the notification (R2.5.1). • The Transmission Operator has not provided its Transmission Service Provider with its Flowgate TFCs within seven days (one week) of their determination, but is has not been more than 14 days (two weeks) since their determination. | One or more of the following: • The Transmission Operator did not include a Flowgate in their AFC calculations that met the criteria described in R2.1. • The Transmission Operator established its list of Flowgates more than three months late, but not more than six months late as described in R2.2. • The Transmission Operator established its list of Flowgates more than sixty days, but not more than ninety days, following a request to create, modify or delete a flowgate as described in R2.3. • The Transmission Operator has not updated its Flowgate TFCs at least once within a calendar year, and it has been not more than 15 months since the last update. • The Transmission Operator has not updated its Flowgate TFC when notified by the Transmission Owner in more than 14 days, but it has not been more than 21 days since the notification (R2.5.1). • The Transmission Operator has not provided its Transmission Service Provider with its Flowgate TFCs in more than 14 days (two weeks) of their determination, but is has not been more than 21 days (three weeks) since their determination. | One or more of the following: • The Transmission Operator did not include two to five Flowgates in their AFC calculations that met the criteria described in R2.1. • The Transmission Operator established its list of Flowgates more than six months late, but not more than nine months late as described in R2.2. • The Transmission Operator established its list of Flowgates more than ninety days, but not more than 120 days, following a request to create, modify or delete a flowgate as described in R2.3. The Transmission Operator has not updated its Flowgate TFCs at least once within a calendar year, and it has been more than 15 months but not more than 18 months since the last update. • The Transmission Operator has not updated its Flowgate TFCs when notified by the Transmission Owner in more than 21 days, but it has not been more than 28 days since the notification (R2.5.1). • The Transmission Operator has not provided its Transmission Service Provider with its Flowgate TFCs in more than 21 days (three weeks) of their determination, but is has not been more than 28 days (four weeks) since their determination. | One or more of the following: • The Transmission Operator did not include six or more Flowgates in their AFC calculations that met the criteria described in R2.1. • The Transmission Operator established its list of Flowgates more than nine months late as described in R2.2. • The Transmission Operator did not establish its list of internal Flowgates as described in R2.2. • The Transmission Operator established its list of Flowgates more than 120 days following a request to create, modify or delete a flowgate as described in R2.3. • The Transmission Operator did not establish its list of external Flowgates following a request to create, modify or delete an external flowgate as described in R2.3. • The Transmission Operator did not determine the TFC for a flowgate as described in R2.4. • The Transmission Operator has not updated its Flowgate TFCs at least once within a calendar year, and it has been more than 18 months since the last update. (R2.5). • The Transmission Operator has not updated its Flowgate TFCs when notified by the Transmission Owner in more than 28 calendar days (R2.5.1). • The Transmission Operator has not provided its Transmission Service Provider with its Flowgate TFCs in more than 28 days (4 weeks) of their determination. | [19 empty] | TOP
Inactive | MOD | MOD-030-3 | R3. | The Transmission Operator shall make available to the Transmission Service Provider a Transmission model to determine Available Flowgate Capability (AFC) that meets the following criteria: | 2017-04-01 | 2024-02-01 | Medium | One or more of the following: • The Transmission Operator used one to ten Facility Ratings that were different from those specified by a Transmission or Generator Owner in their Transmission model. • The Transmission Operator used one to ten Facility Ratings that were different from those specified by a Transmission or Generator Owner in their Transmission model. • The Transmission Operator did not update the model for per R3.3 for one or more months but not more than six weeks. | One or more of the following: • The Transmission Operator used eleven to twenty Facility Ratings that were different from those specified by a Transmission or Generator Owner in their Transmission model. • The Transmission Operator did not update the model per R3.2 for more than 2 calendar days but not more than 3 calendar days. • The Transmission Operator did not update the model for per R3.3 for more than six weeks but not more than eight weeks. | One or more of the following: • The Transmission Operator used twenty-one to thirty Facility Ratings that were different from those specified by a Transmission or Generator Owner in their Transmission model. • The Transmission Operator did not update the model per R3.2 for more than 3 calendar days but not more than 4 calendar days. • The Transmission Operator did not update the model for per R3.3 for more than eight weeks but not more than ten weeks. | One or more of the following: • The Transmission Operator did not update the model per R3.2 for more than 4 calendar days. • The Transmission Operator did not update the model for per R3.3 for more than ten weeks. • The Transmission Operator used more than thirty Facility Ratings that were different from those specified by a Transmission or Generator Owner in their Transmission model. • The Transmission operator did not include in the Transmission model detailed modeling data and topology for its own Reliability Coordinator area. • The Transmission operator did not include in the Transmission modeling data and topology for immediately adjacent and beyond Reliability Coordinator area. | [19 empty] | TOP
Inactive | MOD | MOD-030-3 | R4. | When calculating AFCs, the Transmission Service Provider shall represent the impact of Transmission Service as follows: - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. | 2017-04-01 | 2024-02-01 | Medium | The Transmission Service Provider did not represent the impact of Transmission Service as described in R4 for more than zero, but not more than 5% of all reservations; or more than zero, but not more than 1 reservation, whichever is greater. | The Transmission Service Provider did not represent the impact of Transmission Service as described in R4 for more than 5%, but not more than 10% of all reservations; or more than 1, but not more than 2 reservations, whichever is greater. | The Transmission Service Provider did not represent the impact of Transmission Service as described in R4 for more than 10%, but not more than 15% of all reservations; or more than 2, but not more than 3 reservations, whichever is greater. | The Transmission Service Provider did not represent the impact of Transmission Service as described in R4 for more than 15% of all reservations; or more than 3 reservations, whichever is greater. | [21 empty] | TSP
Inactive | MOD | MOD-030-3 | R5. | When calculating AFCs, the Transmission Service Provider shall | 2017-04-01 | 2024-02-01 | Medium | The Transmission Service Provider did not include in the AFC process one to ten expected generation or Transmission outages, additions or retirements within the scope of the model as specified in the ATCID. | The Transmission Service Provider did not include in the AFC process eleven to twenty-five expected generation and Transmission outages, additions or retirements within the scope of the model as specified in the ATCID. | The Transmission Service Provider did not include in the AFC process twenty-six to fifty expected generation and Transmission outages, additions or retirements within the scope of the model as specified in the ATCID. | One or more of the following: • The Transmission Service Provider did not use the model provided by the Transmission Operator. • The Transmission Service Provider did not include in the AFC process more than fifty expected generation and Transmission outages, additions or retirements within the scope of the model as specified in the ATCID. • The Transmission Service provider did not use AFC provided by a third party. | [21 empty] | TSP
Inactive | MOD | MOD-030-3 | R6. | When calculating the impact of ETC for firm commitments (ETCFi) for all time periods for a Flowgate, the Transmission Service Provider shall sum the following: | 2017-04-01 | 2024-02-01 | Medium | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M13 for the same period, and the absolute value difference was more than 15% of the value calculated in the measure or 15MW, whichever is greater, but not more than 25% of the value calculated in the measure or 25MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M13 for the same period, and the absolute value difference was more than 25% of the value calculated in the measure or 25MW, whichever is greater, but not more than 35% of the value calculated in the measure or 35MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M13 for the same period, and the absolute value difference was more than 35% of the value calculated in the measure or 35MW, whichever is greater, but not more than 45% of the value calculated in the measure or 45MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a firm ETC with an absolute value different than that calculated in M13 for the same period, and the absolute value difference was more than 45% of the value calculated in the measure or 45MW, whichever is greater. | [21 empty] | TSP
Inactive | MOD | MOD-030-3 | R7. | When calculating the impact of ETC for non-firm commitments (ETCNFi) for all time periods for a Flowgate the Transmission Service Provider shall sum: | 2017-04-01 | 2024-02-01 | Low | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M14 for the same period, and the absolute value difference was more than 15% of the value calculated in the measure or 15MW, whichever is greater, but not more than 25% of the value calculated in the measure or 25MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M14 for the same period, and the absolute value difference was more than 25% of the value calculated in the measure or 25MW, whichever is greater, but not more than 35% of the value calculated in the measure or 35MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M14 for the same period, and the absolute value difference was more than 35% of the value calculated in the measure or 35MW, whichever is greater, but not more than 45% of the value calculated in the measure or 45MW, whichever is greater. | For a specified period, the Transmission Service Provider calculated a non-firm ETC with an absolute value different than that calculated in M14 for the same period, and the absolute value difference was more than 45% of the value calculated in the measure or 45MW, whichever is greater. | [21 empty] | TSP
Inactive | MOD | MOD-030-3 | R8. | When calculating firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): AFCF = TFC – ETCFi – CBMi – TRMi + PostbacksFi + counterflowsFi Where: AFCF is the firm Available Flowgate Capability for the Flowgate for that period. TFC is the Total Flowgate Capability of the Flowgate. ETCFi is the sum of the impacts of existing firm Transmission commitments for the Flowgate during that period. CBMi is the impact of the Capacity Benefit Margin on the Flowgate during that period. TRM¬i is the impact of the Transmission Reliability Margin on the Flowgate during that period. PostbacksF¬i are changes to firm AFC due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsFi are adjustments to firm AFC as determined by the Transmission Service Provider and specified in their ATCID. | 2017-04-01 | 2024-02-01 | Medium | The Transmission Service Provider did not use all the elements defined in R8 when determining firm AFC, or used additional elements, for more than zero Flowgates, but not more than 5% of all Flowgates or 1 Flowgate (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R8 when determining firm AFC, or used additional elements, for more than 5% of all Flowgates or 1 Flowgates (whichever is greater), but not more than 10% of all Flowgates or 2 Flowgates (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R8 when determining firm AFC, or used additional elements, for more than 10% of all Flowgates or 2 Flowgates (whichever is greater), but not more than 15% of all Flowgates or 3 Flowgates (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R8 when determining firm AFC, or used additional elements, for more than 15% of all Flowgates or more than 3 Flowgates (whichever is greater). | [21 empty] | TSP
Inactive | MOD | MOD-030-3 | R9. | When calculating non-firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): AFCNF = TFC – ETCFi – ETCNFi – CBMSi – TRMUi + PostbacksNFi + counterflows Where: AFCNF is the non-firm Available Flowgate Capability for the Flowgate for that period. TFC is the Total Flowgate Capability of the Flowgate. ETCFi is the sum of the impacts of existing firm Transmission commitments for the Flowgate during that period. ETCNFi is the sum of the impacts of existing non-firm Transmission commitments for the Flowgate during that period. CBMSi is the impact of any schedules during that period using Capacity Benefit Margin. TRMUi is the impact on the Flowgate of the Transmission Reliability Margin that has not been released (unreleased) for sale as non-firm capacity by the Transmission Service Provider during that period. PostbacksNF¬ are changes to non-firm Available Flowgate Capability due to a change in the use of Transmission Service for that period, as defined in Business Practices. counterflowsNF are adjustments to non-firm AFC as determined by the Transmission Service Provider and specified in their ATCID. | 2017-04-01 | 2024-02-01 | Low | The Transmission Service Provider did not use all the elements defined in R8 when determining non-firm AFC, or used additional elements, for more than zero Flowgates, but not more than 5% of all Flowgates or 1 Flowgate (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R9 when determining non-firm AFC, or used additional elements, for more than 5% of all Flowgates or 1 Flowgate (whichever is greater), but not more than 10% of all Flowgates or 2 Flowgates (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R9 when determining non-firm AFC, or used additional elements, for more than 10% of all Flowgates or 2 Flowgates (whichever is greater), but not more than 15% of all Flowgates or 3 Flowgates (whichever is greater). | The Transmission Service Provider did not use all the elements defined in R9 when determining non-firm AFC, or used additional elements, for more than 15% of all Flowgates or more than 3 Flowgates (whichever is greater). | [21 empty] | TSP
Inactive | MOD | MOD-030-3 | R10. | Each Transmission Service Provider shall recalculate AFC, utilizing the updated models described in R3.2, R3.3, and R5, at a minimum on the following frequency, unless none of the calculated values identified in the AFC equation have changed: | 2017-04-01 | 2024-02-01 | Medium | One or more of the following: ? For Hourly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for one or more hours but not more than 15 hours, and was in excess of the 175-hour per year requirement. ? For Daily, the values described in the AFC equation changed and the Transmission Service provider did not calculate for one or more calendar days but not more than 3 calendar days. ? For Monthly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for seven or more calendar days, but less than 14 calendar days. | One or more of the following: ? For Hourly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for more than 15 hours but not more than 20 hours, and was in excess of the 175-hour per year requirement. ? For Daily, the values described in the AFC equation changed and the Transmission Service provider did not calculate for more than 3 calendar days but not more than 4 calendar days. ? For Monthly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for 14 or more calendar days, but less than 21 calendar days. | One or more of the following: ? For Hourly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for more than 20 hours but not more than 25 hours, and was in excess of the 175-hour per year requirement. ? For Daily, the values described in the AFC equation changed and the Transmission Service provider did not calculate for more than 4 calendar days but not more than 5 calendar days. ? For Monthly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for 21 or more calendar days, but less than 28 calendar days. | One or more of the following: ? For Hourly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for more than 25 hours, and was in excess of the 175-hour per year requirement. ? For Daily, the values described in the AFC equation changed and the Transmission Service provider did not calculate for more than 5 calendar days. ? For Monthly, the values described in the AFC equation changed and the Transmission Service provider did not calculate for 28 or more calendar days. | [21 empty] | TSP
Inactive | MOD | MOD-030-3 | R11. | When converting Flowgate AFCs to ATCs for ATC Paths, the Transmission Service Provider shall convert those values based on the following algorithm: ATC = min(P) P ={PATC1, PATC2,…PATCn} PATCn = AFCn/DFnp Where: ATC is the Available Transfer Capability. P is the set of partial Available Transfer Capabilities for all “impacted” Flowgates honored by the Transmission Service Provider; a Flowgate is considered “impacted” by a path if the Distribution Factor for that path is greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider on an OTDF Flowgate or PTDF Flowgate. PATCn is the partial Available Transfer Capability for a path relative to a Flowgate n. AFCn is the Available Flowgate Capability of a Flowgate n. DFnp is the distribution factor for Flowgate n relative to path p. | 2017-04-01 | 2024-02-01 | Low |  |  |  | The Transmission Service Provider did not follow the procedure for converting Flowgate AFCs to ATCs described in R11. | [21 empty] | TSP
Inactive | MOD | MOD-031-1 | R1. | Each Planning Coordinator or Balancing Authority that identifies a need for the collection of Total Internal Demand, Net Energy for Load, and Demand Side Management data shall develop and issue a data request to the applicable entities in their area. The data request shall include:[Please see the standard for more information] | 2016-07-01 | 2016-09-30 | Medium | N/A | N/A | N/A | The Planning Coordinator or Balancing Authority developed and issued a data request but failed to include either the entity(s) necessary to provide the data or the timetable for providing the data. |  | BA | [8 empty] | PCPA
Inactive | MOD | MOD-031-1 | R2. | Each Applicable Entity, identified in the data request, shall provide the data requested by its Planning Coordinator or Balancing Authority in accordance with the data request issued pursuant to Requirement R1. | 2016-07-01 | 2016-09-30 | Medium | The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide all of the data requested in Requirement R1 part 1.5.1 through part 1.5.5 OR The Applicable Entity, as defined in the data request developed in Requirement R1, provided the data requested in Requirement R1, but did so after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2 but prior to 6 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2. | The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide one of the requested items in Requirement R1 part 1.3.1 through part 1.3.4 OR The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide one of the requested items in Requirement R1 part 1.4.1 through part 1.4.5 OR The Applicable Entity, as defined in the data request developed in Requirement R1, provided the data requested in Requirement R1, but did so 6 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2 but prior to 11 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2. | The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide two of the requested items in Requirement R1 part 1.3.1 through part 1.3.4 OR The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide two of the requested items in Requirement R1 part 1.4.1 through part 1.4.5 OR The Applicable Entity, as defined in the data request developed in Requirement R1, provided the data requested in Requirement R1, but did so 11 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2 but prior to 15 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2. | The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide three or more of the requested items in Requirement R1 part 1.3.1 through part 1.3.4 OR The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide three or more of the requested items in Requirement R1 part 1.4.1 through part 1.4.5 OR The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide the data requested in the timetable provided pursuant to Requirement R1 prior to 16 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2. |  | BA | DP | [5 empty] | LSE |  | PCPA |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-031-1 | R3. | The Planning Coordinator or the Balancing Authority shall provide the data collected under Requirement R2 to the applicable Regional Entity within 75 days of receiving a request for such data, unless otherwise agreed upon by the parties. | 2016-07-01 | 2016-09-30 | Medium | The Planning Coordinator or Balancing Authority, in response to a request by the Regional Entity, made available the data collected under Requirement R2, but did so after 75 days from the date of request but prior to 81 days from the date of the request. | The Planning Coordinator or Balancing Authority, in response to a request by the Regional Entity, made available the data collected under Requirement R2, but did so after 80 days from the date of request but prior to 86 days from the date of the request. | The Planning Coordinator or Balancing Authority, in response to a request by the Regional Entity, made available the data collected under Requirement R2, but did so after 85 days from the date of request but prior to 91 days from the date of the request. | The Planning Coordinator or Balancing Authority, in response to a request by the Regional Entity, failed to make available the data collected under Requirement R2 prior to 91 days or more from the date of the request. |  | BA | [8 empty] | PCPA
Inactive | MOD | MOD-031-1 | R4. | Any Applicable Entity shall, in response to a written request for the data included in parts 1.3-1.5 of Requirement R1 from a Planning Coordinator, Balancing Authority, Transmission Planner or Resource Planner with a demonstrated need for such data in order to conduct reliability assessments of the Bulk Electric Sysytem, provide or otherwise make available that data to the requesting entity. This requirement does not modify an entity’s obligation pursuant to Requirement R2 to respond to data requests issued by its Planning Coordinator or Balancing Authority pursuant to Requirement R1. Unless otherwise agreed upon, the Applicable Entity: • shall provide the requested data within 45 calendar days of the written request, subject to part 4.1 of this requirement; and • shall not be required to alter the format in which it maintains or uses the data. | 2016-07-01 | 2016-09-30 | Medium | The Applicable Entity provided or otherwise made available the data to the requesting entity but did so after 45 days from the date of request but prior to 51 days from the date of the request OR The Applicable Entity that is not providing the data requested provided a written response specifying the data that is not being provided and on what basis but did so after 30 days of the written request but prior to 36 days of the written resquest. | The Applicable Entity provided or otherwise made available the data to the requesting entity but did so after 50 days from the date of request but prior to 56 days from the date of the request OR The Applicable Entity that is not providing the data requested provided a written response specifying the data that is not being provided and on what basis but did so after 35 days of the written request but prior to 41 days of the written resquest. | The Applicable Entity provided or otherwise made available the data to the requesting entity but did so after 55 days from the date of request but prior to 61 days from the date of the request OR The Applicable Entity that is not providing the data requested provided a written response specifying the data that is not being provided and on what basis but did so after 40 days of the written request but prior to 46 days of the written resquest. | The Applicable Entity failed to provide or otherwise make available the data to the requesting entity within 60 days from the date of the request OR The Applicable Entity that is not providing the data requested failed to provide a written response specifying the data that is not being provided and on what basis within 45 days of the written resquest. |  | BA | DP | [5 empty] | LSE |  | PCPA |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-031-2 | R1. | Each Planning Coordinator or Balancing Authority that identifies a need for the collection of Total Internal Demand, Net Energy for Load, and Demand Side Management data shall develop and issue a data request to the applicable entities in its area. The data request shall include: | 2016-10-01 | 2021-03-31 | Medium | N/A | N/A | N/A | The Planning Coordinator or Balancing Authority developed and issued a data request but failed to include either the entity(s) necessary to provide the data or the timetable for providing the data. |  | BA | [8 empty] | PCPA
Inactive | MOD | MOD-031-2 | R2. | Each Applicable Entity identified in a data request shall provide the data requested by its Planning Coordinator or Balancing Authority in accordance with the data request issued pursuant to Requirement R1. | 2016-10-01 | 2021-03-31 | Medium | The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide all of the data requested in Requirement R1 part 1.5.1 through part 1.5.5 OR The Applicable Entity, as defined in the data request developed in Requirement R1, provided the data requested in Requirement R1, but did so after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2 but prior to 6 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2. | The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide one of the requested items in Requirement R1 part 1.3.1 through part 1.3.4 OR The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide one of the requested items in Requirement R1 part 1.4.1 through part 1.4.5 OR The Applicable Entity, as defined in the data request developed in Requirement R1, provided the data requested in Requirement R1, but did so 6 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2 but prior to 11 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2. | The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide two of the requested items in Requirement R1 part 1.3.1 through part 1.3.4 OR The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide two of the requested items in Requirement R1 part 1.4.1 through part 1.4.5 OR The Applicable Entity, as defined in the data request developed in Requirement R1, provided the data requested in Requirement R1, but did so 11 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2 but prior to 15 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2. | The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide three or more of the requested items in Requirement R1 part 1.3.1 through part 1.3.4 OR The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide three or more of the requested items in Requirement R1 part 1.4.1 through part 1.4.5 OR The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide the data requested in the timetable provided pursuant to Requirement R1 prior to 16 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2. |  | BA | DP | [5 empty] | LSE |  | PCPA |  |  |  | RP | [5 empty] | TP
Inactive | MOD | MOD-031-2 | R3. | The Planning Coordinator or the Balancing Authority shall provide the data listed under Requirement R1 Parts 1.3 through 1.5 for their area to the applicable Regional Entity within 75 calendar days of receiving a request for such data, unless otherwise agreed upon by the parties. | 2016-10-01 | 2021-03-31 | Medium | The Planning Coordinator or Balancing Authority, in response to a request by the Regional Entity, made available the data requested, but did so after 75 days from the date of request but prior to 81 days from the date of the request. | The Planning Coordinator or Balancing Authority, in response to a request by the Regional Entity, made available the data requested, but did so after 80 days from the date of request but prior to 86 days from the date of the request. | The Planning Coordinator or Balancing Authority, in response to a request by the Regional Entity, made available the data requested, but did so after 85 days from the date of request but prior to 91 days from the date of the request. | The Planning Coordinator or Balancing Authority, in response to a request by the Regional Entity, failed to make available the data requested prior to 91 days or more from the date of the request. |  | BA | [8 empty] | PCPA
Inactive | MOD | MOD-031-2 | R4. | Any Applicable Entity shall, in response to a written request for the data included in parts 1.3-1.5 of Requirement R1 from a Planning Coordinator, Balancing Authority, Transmission Planner or Resource Planner with a demonstrated need for such data in order to conduct reliability assessments of the Bulk Electric System, provide or otherwise make available that data to the requesting entity. This requirement does not modify an entity’s obligation pursuant to Requirement R2 to respond to data requests issued by its Planning Coordinator or Balancing Authority pursuant to Requirement R1. Unless otherwise agreed upon, the Applicable Entity: • shall not be required to alter the format in which it maintains or uses the data; • shall provide the requested data within 45 calendar days of the written request, subject to part 4.1 of this requirement; unless providing the requested data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements | 2016-10-01 | 2021-03-31 | Medium | The Applicable Entity provided or otherwise made available the data to the requesting entity but did so after 45 days from the date of request but prior to 51 days from the date of the request OR The Applicable Entity that is not providing the data requested provided a written response specifying the data that is not being provided and on what basis but did so after 30 days of the written request but prior to 36 days of the written request. | The Applicable Entity provided or otherwise made available the data to the requesting entity but did so after 50 days from the date of request but prior to 56 days from the date of the request OR The Applicable Entity that is not providing the data requested provided a written response specifying the data that is not being provided and on what basis but did so after 35 days of the written request but prior to 41 days of the written request. | The Applicable Entity provided or otherwise made available the data to the requesting entity but did so after 55 days from the date of request but prior to 61 days from the date of the request OR The Applicable Entity that is not providing the data requested provided a written response specifying the data that is not being provided and on what basis but did so after 40 days of the written request but prior to 46 days of the written request. | The Applicable Entity failed to provide or otherwise make available the data to the requesting entity within 60 days from the date of the request OR The Applicable Entity that is not providing the data requested failed to provide a written response specifying the data that is not being provided and on what basis within 45 days of the written request. |  | BA | DP | [5 empty] | LSE |  | PCPA |  |  |  | RP | [5 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-031-3 | R1. | Each Planning Coordinator or Balancing Authority that identifies a need for the collection of Total Internal Demand, Net Energy for Load, and Demand Side Management data shall develop and issue a data request to the applicable entities in its area. The data request shall include: | 2021-04-01 |  | Medium | N/A | N/A | N/A | The Planning Coordinator or Balancing Authority developed and issued a data request but failed to include either the entity(s) necessary to provide the data or the timetable for providing the data. |  | BA | [8 empty] | PCPA
Mandatory Subject to Enforcement | MOD | MOD-031-3 | R2. | Each Applicable Entity identified in a data request shall provide the data requested by its Planning Coordinator or Balancing Authority in accordance with the data request issued pursuant to Requirement R1. | 2021-04-01 |  | Medium | The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide all of the data requested in Requirement R1 part 1.5.1 through part 1.5.5 OR The Applicable Entity, as defined in the data request developed in Requirement R1, provided the data requested in Requirement R1, but did so after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2 but prior to 6 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2. | The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide one of the requested items in Requirement R1 part 1.3.1 through part 1.3.4 OR The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide one of the requested items in Requirement R1 part 1.4.1 through part 1.4.5 OR The Applicable Entity, as defined in the data request developed in Requirement R1, provided the data requested in Requirement R1, but did so 6 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2 but prior to 11 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2. | The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide two of the requested items in Requirement R1 part 1.3.1 through part 1.3.4 OR The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide two of the requested items in Requirement R1 part 1.4.1 through part 1.4.5 OR The Applicable Entity, as defined in the data request developed in Requirement R1, provided the data requested in Requirement R1, but did so 11 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2 but prior to 15 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2. | The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide three or more of the requested items in Requirement R1 part 1.3.1 through part 1.3.4 OR The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide three or more of the requested items in Requirement R1 part 1.4.1 through part 1.4.5 OR The Applicable Entity, as defined in the data request developed in Requirement R1, failed to provide the data requested in the timetable provided pursuant to Requirement R1 prior to 16 days after the date indicated in the timetable provided pursuant to Requirement R1 part 1.2. |  | BA | DP | [7 empty] | PCPA |  |  |  | RP | [5 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-031-3 | R3. | The Planning Coordinator or the Balancing Authority shall provide the data listed under Requirement R1 Parts 1.3 through 1.5 for their area to the applicable Regional Entity within 75 calendar days of receiving a request for such data, unless otherwise agreed upon by the parties. | 2021-04-01 |  | Medium | The Planning Coordinator or Balancing Authority, in response to a request by the Regional Entity, made available the data requested, but did so after 75 days from the date of request but prior to 81 days from the date of the request. | The Planning Coordinator or Balancing Authority, in response to a request by the Regional Entity, made available the data requested, but did so after 80 days from the date of request but prior to 86 days from the date of the request. | The Planning Coordinator or Balancing Authority, in response to a request by the Regional Entity, made available the data requested, but did so after 85 days from the date of request but prior to 91 days from the date of the request. | The Planning Coordinator or Balancing Authority, in response to a request by the Regional Entity, failed to make available the data requested prior to 91 days or more from the date of the request. |  | BA | [8 empty] | PCPA
Mandatory Subject to Enforcement | MOD | MOD-031-3 | R4. | Any Applicable Entity shall, in response to a written request for the data included in parts 1.3-1.5 of Requirement R1 from a Planning Coordinator, Balancing Authority, Transmission Planner or Resource Planner with a demonstrated need for such data in order to conduct reliability assessments of the Bulk Electric System, provide or otherwise make available that data to the requesting entity. This requirement does not modify an entity’s obligation pursuant to Requirement R2 to respond to data requests issued by its Planning Coordinator or Balancing Authority pursuant to Requirement R1. Unless otherwise agreed upon, the Applicable Entity: • shall not be required to alter the format in which it maintains or uses the data; • shall provide the requested data within 45 calendar days of the written request, subject to part 4.1 of this requirement; unless providing the requested data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements | 2021-04-01 |  | Medium | The Applicable Entity provided or otherwise made available the data to the requesting entity but did so after 45 days from the date of request but prior to 51 days from the date of the request OR The Applicable Entity that is not providing the data requested provided a written response specifying the data that is not being provided and on what basis but did so after 30 days of the written request but prior to 36 days of the written request. | The Applicable Entity provided or otherwise made available the data to the requesting entity but did so after 50 days from the date of request but prior to 56 days from the date of the request OR The Applicable Entity that is not providing the data requested provided a written response specifying the data that is not being provided and on what basis but did so after 35 days of the written request but prior to 41 days of the written request. | The Applicable Entity provided or otherwise made available the data to the requesting entity but did so after 55 days from the date of request but prior to 61 days from the date of the request OR The Applicable Entity that is not providing the data requested provided a written response specifying the data that is not being provided and on what basis but did so after 40 days of the written request but prior to 46 days of the written request. | The Applicable Entity failed to provide or otherwise make available the data to the requesting entity within 60 days from the date of the request OR The Applicable Entity that is not providing the data requested failed to provide a written response specifying the data that is not being provided and on what basis within 45 days of the written request. |  | BA | DP | [7 empty] | PCPA |  |  |  | RP | [5 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-032-1 | R1. | Each Planning Coordinator and each of its Transmission Planners shall jointly develop steady-state, dynamics, and short circuit modeling data requirements and reporting procedures for the Planning Coordinator’s planning area that include: [Please see the standard for more information] | 2015-07-01 |  | Low | The Planning Coordinator and Transmission Planner(s) developed steady-state, dynamics, and short circuit modeling data requirements and reporting procedures, but failed to include less than or equal to 25% of the required components specified in Requirement R1. | The Planning Coordinator and Transmission Planner(s) developed steady-state, dynamics, and short circuit modeling data requirements and reporting procedures, but failed to include greater than 25% but less than or equal to 50% of the required components specified in Requirement R1. | The Planning Coordinator and Transmission Planner(s) developed steady-state, dynamics, and short circuit modeling data requirements and reporting procedures, but failed to include greater than 50% but less than or equal to 75% of the required components specified in Requirement R1. | The Planning and Transmission Planner(s) Coordinator did not develop any steady-state, dynamics, and short circuit modeling data requirements and reporting procedures required by Requirement R1; OR The Planning Coordinator and Transmission Planner(s) developed steady-state, dynamics, and short circuit modeling data requirements and reporting procedures, but failed to include greater than 75% of the required components specified in Requirement R1. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | MOD | MOD-032-1 | R2. | Each Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, and Transmission Service Provider shall provide steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s) according to the data requirements and reporting procedures developed by its Planning Coordinator and Transmission Planner in Requirement R1. For data that has not changed since the last submission, a written confirmation that the data has not changed is sufficient. | 2015-07-01 |  | Medium | The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider provided steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s), but failed to provide less than or equal to 25% of the required data specified in Attachment 1; OR The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider provided steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s), but less than or equal to 25% of the required data failed to meet data format, shareability, level of detail, or case type specifications; OR The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider failed to provide steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s) within the schedule specified by the data requirements and reporting procedures but did provide the data in less than or equal to 15 calendar days after the specified date. | The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider provided steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s), but failed to provide greater than 25% but less than or equal to 50% of the required data specified in Attachment 1;OR The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider provided steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s), but greater than 25% but less than or equal to 50% of the required data failed to meet data format, shareability, level of detail, or case type specifications; OR The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider failed to provide steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s) within the schedule specified by the data requirements and reporting procedures but did provide the data in greater than 15 but less than or equal to 30 calendar days after the specified date. | The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider provided steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s), but failed to provide greater than 50% but less than or equal to 75% of the required data specified in Attachment 1; OR The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider provided steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s), but greater than 50% but less than or equal to 75% of the required data failed to meet data format, shareability, level of detail, or case type specifications; OR The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider failed to provide steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s) within the schedule specified by the data requirements and reporting procedures but did provide the data in greater than 30 but less than or equal to 45 calendar days after the specified date. | The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider did not provide any steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s); OR The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider provided steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s), but failed to provide greater than 75% of the required data specified in Attachment 1; OR The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider provided steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s), but greater than 75% of the required data failed to meet data format, shareability, level of detail, or case type specifications; OR The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, or Transmission Service Provider failed to provide steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s) within the schedule specified by the data requirements and reporting procedures but did provide the data in greater than 45 calendar days after the specified date. |  | BA |  |  |  | GO |  |  | LSE | [5 empty] | RP |  |  |  | TO |  |  | TSP
Mandatory Subject to Enforcement | MOD | MOD-032-1 | R3. | Upon receipt of written notification from its Planning Coordinator or Transmission Planner regarding technical concerns with the data submitted under Requirement R2, including the technical basis or reason for the technical concerns, each notified Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider shall respond to the notifying Planning Coordinator or Transmission Planner as follows: [Please see the standard for more information] | 2015-07-01 |  | Low | The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider failed to provide a written response to its Transmission Planner(s) or Planning Coordinator(s) according to the specifications of Requirement R4 within 90 calendar days (or within a longer period agreed upon by the notifying Planning Coordinator or Transmission Planner), but did provide the response within 105 calendar days (or within 15 calendar days after the longer period agreed upon by the notifying Planning Coordinator or Transmission Planner). | The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider failed to provide a written response to its Transmission Planner(s) or Planning Coordinator(s) according to the specifications of Requirement R4 within 90 calendar days (or within a longer period agreed upon by the notifying Planning Coordinator or Transmission Planner), but did provide the response within greater than 105 calendar days but less than or equal to 120 calendar days (or within greater than 15 calendar days but less than or equal to 30 calendar days after the longer period agreed upon by the notifying Planning Coordinator or Transmission Planner). | The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider failed to provide a written response to its Transmission Planner(s) or Planning Coordinator(s) according to the specifications of Requirement R4 within 90 calendar days (or within a longer period agreed upon by the notifying Planning Coordinator or Transmission Planner), but did provide the response within greater than 120 calendar days but less than or equal to 135 calendar days (or within greater than 30 calendar days but less than or equal to 45 calendar days after the longer period agreed upon by the notifying Planning Coordinator or Transmission Planner). | The Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider failed to provide a written response to its Transmission Planner(s) or Planning Coordinator(s) according to the specifications of Requirement R4 within 135 calendar days (or within a longer period agreed upon by the notifying Planning Coordinator or Transmission Planner). |  | BA |  |  |  | GO |  |  | LSE | [5 empty] | RP |  |  |  | TO |  |  | TSP
Mandatory Subject to Enforcement | MOD | MOD-032-1 | R4. | Each Planning Coordinator shall make available models for its planning area reflecting data provided to it under Requirement R2 to the Electric Reliability Organization (ERO) or its designee to support creation of the Interconnection-wide case(s) that includes the Planning Coordinator’s planning area. | 2015-07-01 |  | Medium | The Planning Coordinator made available the required data to the ERO or its designee but failed to provide less than or equal to 25% of the required data in the format specified by the ERO or its designee. | The Planning Coordinator made available the required data to the ERO or its designee but failed to provide greater than 25% but less than or equal to 50% of the required data in the format specified by the ERO or its designee. | The Planning Coordinator made available the required data to the ERO or its designee but failed to provide greater than 50% but less than or equal to 75% of the required data in the format specified by the ERO or its designee. | The Planning Coordinator made available the required data to the ERO or its designee but failed to provide greater than 75% of the required data in the format specified by the ERO or its designee. | [10 empty] | PCPA
Inactive | MOD | MOD-033-1 | R1. | Each Planning Coordinator shall implement a documented data validation process that includes the following attributes:[Please see the standard for more information] | 2017-07-01 | 2021-03-31 | Medium | The Planning Coordinator documented and implemented a process to validate data but did not address one of the four required topics under Requirement R1; OR The Planning Coordinator did not perform simulation as required by part 1.1 within 24 calendar months but did perform the simulation within 28 calendar months; OR The Planning Coordinator did not perform simulation as required by part 1.2 within 24 calendar months (or the next dynamic local event in cases where there is more than 24 months between events) but did perform the simulation within 28 calendar months. | The Planning Coordinator documented and implemented a process to validate data but did not address two of the four required topics under Requirement R1; OR The Planning Coordinator did not perform simulation as required by part 1.1 within 24 calendar months but did perform the simulation in greater than 28 calendar months but less than or equal to 32 calendar months;OR The Planning Coordinator did not perform simulation as required by part 1.2 within 24 calendar months (or the next dynamic local event in cases where there is more than 24 months between events) but did perform the simulation in greater than 28 calendar months but less than or equal to 32 calendar months. | The Planning Coordinator documented and implemented a process to validate data but did not address three of the four required topics under Requirement R1; OR The Planning Coordinator did not perform simulation as required by part 1.1 within 24 calendar months but did perform the simulation in greater than 32 calendar months but less than or equal to 36 calendar months; OR The Planning Coordinator did not perform simulation as required by part 1.2 within 24 calendar months (or the next dynamic local event in cases where there is more than 24 months between events) but did perform the simulation in greater than 32 calendar months but less than or equal to 36 calendar months. | The Planning Coordinator did not have a validation process at all or did not document or implement any of the four required topics under Requirement R1; OR The Planning Coordinator did not validate its portion of the system in the power flow model as required by part 1.1 within 36 calendar months; OR The Planning Coordinator did not perform simulation as required by part 1.2 within 36 calendar months (or the next dynamic local event in cases where there is more than 24 months between events). | [10 empty] | PCPA
Inactive | MOD | MOD-033-1 | R2. | Each Reliability Coordinator and Transmission Operator shall provide actual system behavior data (or a written response that it does not have the requested data) to any Planning Coordinator performing validation under Requirement R1 within 30 calendar days of a written request, such as, but not limited to, state estimator case or other Real-time data (including disturbance data recordings) necessary for actual system response validation. | 2017-07-01 | 2021-03-31 | Low | The Reliability Coordinator or Transmission Operator did not provide requested actual system behavior data (or a written response that it does not have the requested data) to a requesting Planning Coordinator within 30 calendar days of the written request, but did provide the data (or written response that it does not have the requested data) in less than or equal to 45 calendar days. | The Reliability Coordinator or Transmission Operator did not provide requested actual system behavior data (or a written response that it does not have the requested data) to a requesting Planning Coordinator within 30 calendar days of the written request, but did provide the data (or written response that it does not have the requested data) in greater than 45 calendar days but less than or equal to 60 calendar days. | The Reliability Coordinator or Transmission Operator did not provide requested actual system behavior data (or a written response that it does not have the requested data) to a requesting Planning Coordinator within 30 calendar days of the written request, but did provide the data (or written response that it does not have the requested data) in greater than 60 calendar days but less than or equal to 75 calendar days. | The Reliability Coordinator or Transmission Operator did not provide requested actual system behavior data (or a written response that it does not have the requested data) to a requesting Planning Coordinator within 75 calendar days; OR The Reliability Coordinator or Transmission Operator provided a written response that it does not have the requested data, but actually had the data. | [12 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | MOD | MOD-033-2 | R1. | Each Planning Coordinator shall implement a documented data validation process that includes the following attributes:[Please see the standard for more information] | 2021-04-01 |  | Medium | The Planning Coordinator documented and implemented a process to validate data but did not address one of the topics under Requirement R1; OR The Planning Coordinator did not preform simulation as required by part 1.1 within 24 calendar months but did preform the simulation within 28 calendar months; OR The Planning Coordinator did not preform simulation as required by part 1.2 within 24 calendar months (or the next dynamic local event in cases where there is more than 24 months between events) but did preform the simulation within 24 calendar months. | The Planning Coordinator documented and implemented a process to validate data but did not address one of the topics under Requirement R1; OR The Planning Coordinator did not preform simulation as required by part 1.1 within 24 calendar months but did preform the simulation within 28 calendar months but less than or equal to 32 calendar months; OR The Planning Coordinator did not preform simulation as required by part 1.2 within 24 calendar months (or the next dynamic local event in cases where there is more than 24 months between events) but did preform the simulation in greater than 28 calendar months but less than or equal to 32 calendar months. | The Planning Coordinator documented and implemented a process to validate data but did not address one of the topics under Requirement R1; OR The Planning Coordinator did not preform simulation as required by part 1.1 within 24 calendar months but did preform the simulation in greater than 32 calendar months but less than or equal to 36 calendar months; OR The Planning Coordinator did not preform simulation as required by part 1.2 within 24 calendar months (or the next dynamic local event in cases where there is more than 24 months between events) but did preform the simulation in greater than 32 calendar months but less than or equal to 36 calendar months. | The Planning Coordinator did not have a validation process at all or did not document or implement any of the four required topics under Requirement R1; OR The Planning Coordinator did not validate its portion of the system in the power flow model as required by part 1.1 within 36 calendar months; OR The Planning Coordinator did not perform simulation as requred by part 1.2 within 36 calendar months (or the next dynamic local event in cases where there is more than 24 months between events). | [10 empty] | PCPA
Mandatory Subject to Enforcement | MOD | MOD-033-2 | R2. | Each Reliability Coordinator and Transmission Operator shall provide actual system behavior data (or a written response that it does not have the requested data) to any Planning Coordinator performing validation under Requirement R1 within 30 calendar days of a written request, such as, but not limited to, state estimator case or other Real-time data (including disturbance data recordings) necessary for actual system response validation. | 2021-04-01 |  | Low | The Reliaiblity Coordinator or Transmission Operator did not provide requested actual system behavior data (or writen response that it does not have the requested data) to a requesting Planning Coordinator within 30 calendar days of the written request, but did provide the data (or written repsonse that it does not have the requested data) in less than or equal to 45 calendar days. | The Reliaiblity Coordinator or Transmission Operator did not provide requested actual system behavior data (or writen response that it does not have the requested data) to a requesting Planning Coordinator within 30 calendar days of the written request, but did provide the data (or written repsonse that it does not have the requested data) in greater than 45 calendar days but less than or equal to 60 calendar days. | The Reliaiblity Coordinator or Transmission Operator did not provide requested actual system behavior data (or writen response that it does not have the requested data) to a requesting Planning Coordinator within 30 calendar days of the written request, but did provide the data (or written repsonse that it does not have the requested data) in greater than 6o calendar days but less than or equal to 75 calendar days. | The Reliaiblity Coordinator or Transmission Operator did not provide requested actual system behavior data (or writen response that it does not have the requested data) to a requesting Planning Coordinator within 75 calendar days; OR The Reliability Coordinator or Transmission Operator provided a wriiten response that it does not have the requested data, but actually had the data. | [12 empty] | RC | [6 empty] | TOP
Inactive | NUC | NUC-001-1 | R1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt |  | 2010-03-31 | Low | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-1 | R2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements1 that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. |  | 2010-03-31 | Low | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-1 | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. |  | 2010-03-31 | Medium | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-1 | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: |  | 2010-03-31 | Medium | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-1 | R5. | The Nuclear Plant Generator Operator shall operate per the Agreements developed in accordance with this standard. |  | 2010-03-31 | Medium | [10 empty] | GOP
Inactive | NUC | NUC-001-1 | R6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. |  | 2010-03-31 | Medium | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-1 | R7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design, configuration, operations, limits, protection systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. |  | 2010-03-31 | Medium | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-1 | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, protection systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. |  | 2010-03-31 | Medium | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-1 | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: |  | 2010-03-31 | Low | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2 | R1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt [Risk Factor: Lower] | 2010-04-01 | 2013-03-31 | Low | The Nuclear Plant Generator Operator did not verify receipt of the proposed NPIR's. | The Nuclear Plant Generator Operator submitted an incomplete proposed NPIR to the applicable transmission entities. | The Nuclear Plant Generator Operator did not provide the proposed NPIR's to some applicable entities. | The Nuclear Plant Generator Operator did not provide the proposed NPIR's to any applicable entities. | [6 empty] | GOP
Inactive | NUC | NUC-001-2 | R2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. [Risk Factor: Medium] | 2010-04-01 | 2013-03-31 | Medium | N/A | N/A | N/A | The Nuclear Plant Generator Operator or the applicable Transmission Entity does not have in effect one or more agreements that include NPIRs and document the implementation of the NPIRs. |  | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2 | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. [Risk Factor: Medium] | 2010-04-01 | 2013-03-31 | Medium | The applicable Transmission Entity incorporated the NPIRs into its planning analyses and identified no areas of concern but it did not communicate these results to the Nuclear Plant Generator Operator. | The applicable Transmission Entity incorporated the NPIRs into its planning analyses and identified one or more areas of concern but did not communicate these results to the Nuclear Plant Generator Operator. | The applicable Transmission Entity did not incorporate the NPIRs into its planning analyses of the electric system. | N/A |  | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2 | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] | 2010-04-01 | 2013-03-31 | High | The applicable Transmission Entity failed to incorporate one or more applicable NPIRs into their operating analyses. | The applicable Transmission Entity failed to incorporate any NPIRs into their operating analyses OR did not inform NPG operator when their ability of assess the operation of the electric system affecting the NPIRs was lost. | The applicable Transmission Entity failed to operate the system to meet the NPIRs | N/A |  | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2 | R5. | The Nuclear Plant Generator Operator shall operate per the Agreements developed in accordance with this standard. [Risk Factor: High] | 2010-04-01 | 2013-03-31 | High | The Nuclear Operator failed to operate the plant in accordance with one or more of the administrative or training elements within the agreements. | The Nuclear Operator failed to operate the plant in accordance with one or two of the technical, operations, and maintenance or communication elements within the agreements. | The Nuclear Operator failed to operate the plant in accordance with three or more of the technical, operations, and maintenance or communication elements within the agreements. | N/A | [6 empty] | GOP
Inactive | NUC | NUC-001-2 | R6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. [Risk Factor: Medium] | 2010-04-01 | 2013-03-31 | Medium | The Nuclear Operator or Transmission Entity failed to coordinate outages or maintenance activities in accordance with one or more of the administrative elements within the agreements. | The Nuclear Operator or Transmission Entity failed to provide outage or maintenance schedules to the appropriate parties as described in the agreement or on a time period consistent with the agreements. | The Nuclear Operator or Transmission Entity failed to coordinate one or more outages or maintenance activities in accordance the requirements of the agreements. | N/A |  | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2 | R7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design, configuration, operations, limits, protection systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | 2010-04-01 | 2013-03-31 | High | The Nuclear Plant Generator Operator did not inform the applicable Transmission Entities of proposed changes to nuclear plant design, configuration, operations, limits, protection systems, or capabilities that may impact the ability of the electric system | The Nuclear Plant Generator Operator did not inform the applicable Transmission Entities of actual changes to nuclear plant design, configuration, operations, limits, protection systems, or capabilities that may impact the ability of the electric system t | The Nuclear Plant Generator Operator did not inform the applicable Transmission Entities of actual changes to nuclear plant design, configuration, operations, limits, protection systems, or capabilities that directly impact the ability of the electric sys | N/A | [6 empty] | GOP
Inactive | NUC | NUC-001-2 | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, protection systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | 2010-04-01 | 2013-03-31 | High | The applicable Transmission Entities did not inform the Nuclear Plant Generator Operator of proposed changes to transmission system design, configuration, operations, limits, protection systems, or capabilities that may impact the ability of the electric | The applicable Transmission Entities did not inform the Nuclear Plant Generator Operator of actual changes to transmission system design, configuration, operations, limits, protection systems, or capabilities that may impact the ability of the electric sy | The applicable Transmission Entities did not inform the Nuclear Plant Generator Operator of actual changes to transmission system design, configuration, operations, limits, protection systems, or capabilities that directly impacts the ability of the elect | N/A |  | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2 | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] | 2010-04-01 | 2013-03-31 | Medium | The agreement identified in R2. between the Nuclear Plant Generator Operator and the applicable Transmission Entities is missing one or more sub-components of R9.1. | The agreement identified in R2. between the Nuclear Plant Generator Operator and the applicable Transmission Entities is missing from one to five of the combined sub-components in R9.2, R9.3 and R9.4. | The agreement identified in R2. between the Nuclear Plant Generator Operator and the applicable Transmission Entities is missing from six to ten of the combined sub-components in R9.2, R9.3 and R9.4. | The agreement identified in R2. between the Nuclear Plant Generator Operator and the applicable Transmission Entities is missing eleven or more of the combined sub-components in R9.2, R9.3 and R9.4. |  | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2.1 | R1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt | 2013-04-01 | 2015-12-31 | Low | [10 empty] | GOP
Inactive | NUC | NUC-001-2.1 | R2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. | 2013-04-01 | 2015-12-31 | Medium | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2.1 | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. [Risk Factor: Medium] | 2013-04-01 | 2015-12-31 | Medium | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2.1 | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] | 2013-04-01 | 2015-12-31 | Medium | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2.1 | R5. | The Nuclear Plant Generator Operator shall operate per the Agreements developed in accordance with this standard. [Risk Factor: High] | 2013-04-01 | 2015-12-31 | Medium | [10 empty] | GOP
Inactive | NUC | NUC-001-2.1 | R6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. [Risk Factor: Medium] | 2013-04-01 | 2015-12-31 | Medium | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2.1 | R7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | 2013-04-01 | 2015-12-31 | Medium | [10 empty] | GOP
Inactive | NUC | NUC-001-2.1 | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | 2013-04-01 | 2015-12-31 | High | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2.1 | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] | 2013-04-01 | 2015-12-31 | Medium | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2.1(i) | R1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt. |  | 2014-11-13 | Low | [10 empty] | GOP
Inactive | NUC | NUC-001-2.1(i) | R2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. |  | 2014-11-13 | Medium | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2.1(i) | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator |  | 2014-11-13 | Medium | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2.1(i) | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: |  | 2014-11-13 | High | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2.1(i) | R5. | The Nuclear Plant Generator Operator shall operate per the Agreements developed in accordance with this standard. |  | 2014-11-13 | High | [10 empty] | GOP
Inactive | NUC | NUC-001-2.1(i) | R6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. |  | 2014-11-13 | Medium | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2.1(i) | R7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. |  | 2014-11-13 | High | [10 empty] | GOP
Inactive | NUC | NUC-001-2.1(i) | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. |  | 2014-11-13 | High | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-2.1(i) | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: |  | 2014-11-13 | Medium | [5 empty] | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-3 | R1. | R1. The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt. | 2016-01-01 | 2021-03-31 | Medium | The Nuclear Plant Generator Operator provided the NPIRs to the applicable entities but did not verify receipt. | The Nuclear Plant Generator Operator did not provide the proposed NPIR to one of the applicable entities unless there was only one entity. | The Nuclear Plant Generator Operator did not provide the proposed NPIRs to two of the applicable entities unless there were only two entities. | The Nuclear Plant Generator Operator did not provide the proposed NPIRs to more than two of applicable entities. OR For a particular nuclear power plant, if the number of possible applicable transmission entities is equal to the number of applicable transmission entities not provided NPIRs | [6 empty] | GOP
Inactive | NUC | NUC-001-3 | R2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs (Footnote: Agreements may include mutually agreed upon procedures or protocols in effect between entities or between departments of a vertically integrated system.) | 2016-01-01 | 2021-03-31 | Medium | N/A | N/A | N/A | The Nuclear Plant Generator Operator or the applicable Transmission Entity does not have in effect one or more agreements that include mutually agreed to NPIRs and document the implementation of the NPIRs. |  | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-3 | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. | 2016-01-01 | 2021-03-31 | Medium | N/A | The responsible entity incorporated the NPIRs into its planning analyses but did not communicate the results to the Nuclear Plant Generator Operator. | N/A | The responsible entity did not incorporate the NPIRs into its planning analyses of the electric system. |  | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-3 | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: | 2016-01-01 | 2021-03-31 | High | N/A | The responsible entity did not comply with Requirement R4, Part 4.3. | The responsible entity did not comply with Requirement R4, Part R4.1. | The responsible entity did not comply with Requirement R4, Part R4.2. |  | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-3 | R5. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall operate the nuclear plant to meet the NPIRs. | 2016-01-01 | 2021-03-31 | High | N/A | N/A | N/A | The Nuclear Plant Generator Operator failed to operate per the NPIRs developed in accordance with this standard. | [6 empty] | GOP
Inactive | NUC | NUC-001-3 | R6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. | 2016-01-01 | 2021-03-31 | Medium | N/A | The Nuclear Plant Generator Operator or Transmission Entity failed to provide outage or maintenance schedules to the appropriate parties as described in the agreement or on a time period consistent with the agreements. | The Nuclear Plant Generator Operator or Transmission Entity failed to coordinate one or more outages or maintenance activities in accordance the requirements of the agreements. | N/A |  | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-3 | R7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | 2016-01-01 | 2021-03-31 | High | The Nuclear Plant Generator Operator did not inform the applicable Transmission Entities of proposed changes to nuclear plant design (e.g. protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | N/A | The Nuclear Plant Generator Operator did not inform the applicable Transmission Entities of actual changes to nuclear plant design (e.g. protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | The Nuclear Plant Generator Operator did not inform the applicable Transmission Entities of actual changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits or capabilities that directly impact the ability of the electric system to meet the NPIRs. | [6 empty] | GOP
Inactive | NUC | NUC-001-3 | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | 2016-01-01 | 2021-03-31 | High | The applicable Transmission Entities did not inform the Nuclear Plant Generator Operator of proposed changes to transmission system design, configuration (e.g. protective relay setpoints), operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | N/A | The applicable Transmission Entities did not inform the Nuclear Plant Generator Operator of actual changes to transmission system design (e.g. protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | The applicable Transmission Entities did not inform the Nuclear Plant Generator Operator of actual changes to transmission system design (e.g. protective relay setpoints), configuration, operations, limits, or capabilities that directly impacts the ability of the electric system to meet the NPIRs. |  | BA | DP |  |  |  | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | NUC | NUC-001-3 | R9. | R9. The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. • Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. • Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity. | 2016-01-01 | 2021-03-31 | Medium |  | The Agreement(s) identified in R2. between the Nuclear Plant Generator Operator and the applicable Transmission Entity failed to include up to 20% of the combined sub-components in Requirement R9 Parts 9.2, 9.3 and 9.4 applicable to that entity. | The Agreement(s) identified in R2. between the Nuclear Plant Generator Operator and the applicable Transmission Entity failed to include greater than 20%, but less than 40% of the combined sub-components in Requirement R9 Parts 9.2, 9.3 and 9.4 applicable to the entity. | The Agreement(s) identified in R2. between the Nuclear Plant Generator Operator and the applicable Transmission Entity failed to include 40% or more of the combined sub-components in Requirement R9 Parts 9.2, 9.3 and 9.4 applicable to the entity. |  | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001-4 | R1. | R1. The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt. | 2021-04-01 |  | Medium | The Nuclear Plant Generator Operator provided the NPIRs to the applicable entities but did not verify receipt. | The Nuclear Plant Generator Operator did not provide the proposed NPIR to one of the applicable entities unless there was only one entity. | The Nuclear Plant Generator Operator did not provide the proposed NPIRs to two of the applicable entities unless there were only two entities. | The Nuclear Plant Generator Operator did not provide the proposed NPIRs to more than two of applicable entities. OR For a particular nuclear power plant, if the number of possible applicable transmission entities is equal to the number of applicable transmission entities not provided NPIRs | [6 empty] | GOP
Mandatory Subject to Enforcement | NUC | NUC-001-4 | R2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs | 2021-04-01 |  | Medium | N/A | N/A | N/A | The Nuclear Plant Generator Operator or the applicable Transmission Entity does not have in effect one or more agreements that include mutually agreed to NPIRs and document the implementation of the NPIRs. |  | BA | DP |  |  | GO | GOP |  |  |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001-4 | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. | 2021-04-01 |  | Medium | N/A | The responsible entity incorporated the NPIRs into its planning analyses but did not communicate the results to the Nuclear Plant Generator Operator. | N/A | The responsible entity did not incorporate the NPIRs into its planning analyses of the electric system. |  | BA | DP |  |  | GO | GOP |  |  |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001-4 | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: | 2021-04-01 |  | High | N/A | The responsible entity did not comply with Requirement R4, Part 4.3. | The responsible entity did not comply with Requirement R4, Part R4.1. | The responsible entity did not comply with Requirement R4, Part R4.2. |  | BA | DP |  |  | GO | GOP |  |  |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001-4 | R5. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall operate the nuclear plant to meet the NPIRs. | 2021-04-01 |  | High | N/A | N/A | N/A | The Nuclear Plant Generator Operator failed to operate per the NPIRs developed in accordance with this standard. | [6 empty] | GOP
Mandatory Subject to Enforcement | NUC | NUC-001-4 | R6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. | 2021-04-01 |  | Medium | N/A | The Nuclear Plant Generator Operator or Transmission Entity failed to provide outage or maintenance schedules to the appropriate parties as described in the agreement or on a time period consistent with the agreements. | The Nuclear Plant Generator Operator or Transmission Entity failed to coordinate one or more outages or maintenance activities in accordance the requirements of the agreements. | N/A |  | BA | DP |  |  | GO | GOP |  |  |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001-4 | R7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | 2021-04-01 |  | High | The Nuclear Plant Generator Operator did not inform the applicable Transmission Entities of proposed changes to nuclear plant design (e.g. protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | N/A | The Nuclear Plant Generator Operator did not inform the applicable Transmission Entities of actual changes to nuclear plant design (e.g. protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | The Nuclear Plant Generator Operator did not inform the applicable Transmission Entities of actual changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits or capabilities that directly impact the ability of the electric system to meet the NPIRs. | [6 empty] | GOP
Mandatory Subject to Enforcement | NUC | NUC-001-4 | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | 2021-04-01 |  | High | The applicable Transmission Entities did not inform the Nuclear Plant Generator Operator of proposed changes to transmission system design, configuration (e.g. protective relay setpoints), operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | N/A | The applicable Transmission Entities did not inform the Nuclear Plant Generator Operator of actual changes to transmission system design (e.g. protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | The applicable Transmission Entities did not inform the Nuclear Plant Generator Operator of actual changes to transmission system design (e.g. protective relay setpoints), configuration, operations, limits, or capabilities that directly impacts the ability of the electric system to meet the NPIRs. |  | BA | DP |  |  |  | GOP |  |  |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Mandatory Subject to Enforcement | NUC | NUC-001-4 | R9. | R9. The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. • Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. • Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity. | 2021-04-01 |  | Medium |  | The Agreement(s) identified in R2. between the Nuclear Plant Generator Operator and the applicable Transmission Entity failed to include up to 20% of the combined sub-components in Requirement R9 Parts 9.2, 9.3 and 9.4 applicable to that entity. | The Agreement(s) identified in R2. between the Nuclear Plant Generator Operator and the applicable Transmission Entity failed to include greater than 20%, but less than 40% of the combined sub-components in Requirement R9 Parts 9.2, 9.3 and 9.4 applicable to the entity. | The Agreement(s) identified in R2. between the Nuclear Plant Generator Operator and the applicable Transmission Entity failed to include 40% or more of the combined sub-components in Requirement R9 Parts 9.2, 9.3 and 9.4 applicable to the entity. |  | BA | DP |  |  | GO | GOP |  |  |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP
Inactive | PER | PER-001-0 | R1. | Each Transmission Operator and Balancing Authority shall provide operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. | 2007-06-18 | 2009-12-09 | High | [5 empty] | BA | [17 empty] | TOP
Inactive | PER | PER-001-0.1 | R1. | Each Transmission Operator and Balancing Authority shall provide operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. | 2009-12-10 | 2012-09-12 | High | [5 empty] | BA | [17 empty] | TOP
Inactive | PER | PER-001-0.2 | R1. | Each Transmission Operator and Balancing Authority shall provide operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. | 2012-09-13 | 2017-03-31 | High | [5 empty] | BA | [17 empty] | TOP
Inactive | PER | PER-002-0 | R1. | Each Transmission Operator and Balancing Authority shall be staffed with adequately trained operating personnel. | 2007-06-18 | 2013-03-31 | High | The applicable entity did not adequately staff and train operating personnel, affecting 5% or less of its operating personnel. | The applicable entity did not adequately staff and train operating personnel, affecting between 5-10% of its operating personnel. | The applicable entity did not adequately staff and train operating personnel, affecting 10-15%, inclusive, of its operating personnel. | The applicable entity did not adequately staff and train operating personnel, affecting greater than 15% of its operating personnel. |  | BA | [17 empty] | TOP
Inactive | PER | PER-002-0 | R2. | Each Transmission Operator and Balancing Authority shall have a training program for all operating personnel that are in: | 2007-06-18 | 2013-03-31 | High | [5 empty] | BA | [17 empty] | TOP
Inactive | PER | PER-002-0 | R3. | For personnel identified in Requirement R2, the Transmission Operator and Balancing Authority shall provide a training program meeting the following criteria: | 2007-06-18 | 2013-03-31 | High | The applicable entity did not comply with one of the four required elements. | The applicable entity did not comply with two of the four required elements. | The applicable entity did not comply with three of the four required elements. | The applicable entity did not comply with any of the four required elements. |  | BA | [17 empty] | TOP
Inactive | PER | PER-002-0 | R4. | For personnel identified in Requirement R2, each Transmission Operator and Balancing Authority shall provide its operating personnel at least five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel. | 2007-06-18 | 2011-03-31 | High | The applicable entity did not provide five days per year of training and drills, as directed by the requirement, affecting 5% or less of its operating personnel. | The applicable entity did not provide five days per year of training and drills, as directed by the requirement, affecting between 5-10% of its operating personnel. | The applicable entity did not provide five days per year of training and drills, as directed by the requirement, affecting 10-15%, inclusive, of its operating personnel. | The applicable entity did not provide five days per year of training and drills, as directed by the requirement, affecting greater than 15% of its operating personnel. |  | BA | [17 empty] | TOP
Inactive | PER | PER-003-0 | R1. | Each Transmission Operator, Balancing Authority, and Reliability Coordinator shall staff all operating positions that meet both of the following criteria with personnel that are NERC-certified for the applicable functions: | 2007-06-18 | 2012-09-30 | High | [5 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | PER | PER-003-1 | R1. | Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate: Note: Non-NERC certified personnel performing any reliability-related task of a real-time operating position must be under the direct supervision of a NERC Certified System Operator stationed at that operating position; the NERC Certified System Operator at that operating position has ultimate responsibility for the performance of the reliability-related tasks. | 2012-10-01 | 2019-06-30 | High | N/A | N/A | N/A | The Reliability Coordinator failed to staff each Real-time operating position performing Reliability Coordinator reliability-related tasks with a System Operator having a valid NERC certificate as defined in Requirement R1. | [12 empty] | RC
Inactive | PER | PER-003-1 | R2. | Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates: Note: Non-NERC certified personnel performing any reliability-related task of an operating position must be under the direct supervision of a NERC Certified System Operator stationed at that operating position; the NERC Certified System Operator at that operating position has ultimate responsibility for the performance of the reliability-related tasks. | 2012-10-01 | 2019-06-30 | High | N/A | N/A | N/A | The Transmission Operator failed to staff each Real-time operating position performing Transmission Operator reliability-related tasks with a System Operator having a valid NERC certificate as defined in Requirement R2, Part 2.2. | [19 empty] | TOP
Inactive | PER | PER-003-1 | R3. | Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates: Note: Non-NERC certified personnel performing any reliability-related task of an operating position must be under the direct supervision of a NERC Certified System Operator stationed at that operating position; the NERC Certified System Operator at that operating position has ultimate responsibility for the performance of the reliability-related tasks. | 2012-10-01 | 2019-06-30 | High | N/A | N/A | N/A | The Balancing Authority failed to staff each Real-time operating position performing Balancing Authority reliability-related tasks with a System Operator having a valid NERC certificate as defined in Requirement R3, Part 3.2. |  | BA
Mandatory Subject to Enforcement | PER | PER-003-2 | R1. | Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate (Footnote: Non-NERC certified personnel performing any reliability-related task of a real-time operating position must be under the direct supervision of a NERC Certified System Operator stationed at that operating position; the NERC Certified System Operator at that operating position has ultimate responsibility for the performance of the reliability-related tasks. The NERC certificates referenced in this standard pertain to those certificates identified in the NERC System Operator Certification Program Manual. | 2019-07-01 |  | High | N/A | N/A | N/A | The Reliability Coordinator failed to staff each Real-time operating position performing Reliability Coordinator reliability-related tasks with a System Operator having a valid NERC certificate as defined in Requirement R1. | [12 empty] | RC
Mandatory Subject to Enforcement | PER | PER-003-2 | R2. | Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates. (Footnote: 1 Non-NERC certified personnel performing any reliability-related task of a real-time operating position must be under the direct supervision of a NERC Certified System Operator stationed at that operating position; the NERC Certified System Operator at that operating position has ultimate responsibility for the performance of the reliability-related tasks. The NERC certificates referenced in this standard pertain to those certificates identified in the NERC System Operator Certification Program Manual.) | 2019-07-01 |  | High | N/A | N/A | N/A | The Transmission Operator failed to staff each Real-time operating position performing Transmission Operator reliability-related tasks with a System Operator having a valid NERC certificate as defined in Requirement R2, Part 2.2. | [19 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-003-2 | R3. | Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates (Footnote: 1 Non-NERC certified personnel performing any reliability-related task of a real-time operating position must be under the direct supervision of a NERC Certified System Operator stationed at that operating position; the NERC Certified System Operator at that operating position has ultimate responsibility for the performance of the reliability-related tasks. The NERC certificates referenced in this standard pertain to those certificates identified in the NERC System Operator Certification Program Manual.) | 2019-07-01 |  | High | N/A | N/A | N/A | The Balancing Authority failed to staff each Real-time operating position performing Balancing Authority reliability-related tasks with a System Operator having a valid NERC certificate as defined in Requirement R3, Part 3.2. |  | BA
Inactive | PER | PER-004-0 | R1. | Each Reliability Coordinator shall be staffed with adequately trained and NERC-certified Reliability Coordinator operators, 24 hours per day, seven days per week. |  | 2007-01-01 | [17 empty] | RC
Inactive | PER | PER-004-0 | R2. | All Reliability Coordinator operating personnel shall each complete a minimum of five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel. |  | 2007-01-01 | [17 empty] | RC
Inactive | PER | PER-004-0 | R3. | Reliability Coordinator operating personnel shall have a comprehensive understanding of the Reliability Coordinator Area and interactions with neighboring Reliability Coordinator Areas. |  | 2007-01-01 | [17 empty] | RC
Inactive | PER | PER-004-0 | R4. | Reliability Coordinator operating personnel shall have an extensive understanding of the Balancing Authorities, Transmission Operators, and Generation Operators within the Reliability Coordinator Area, including the operating staff, operating practices and procedures, restoration priorities and objectives, outage plans, equipment capabilities, and operational restrictions. |  | 2007-01-01 | [17 empty] | RC
Inactive | PER | PER-004-0 | R5. | Reliability Coordinator operating personnel shall place particular attention on SOLs and IROLs and inter-tie facility limits. The Reliability Coordinator shall ensure protocols are in place to allow Reliability Coordinator operating personnel to have the best available information at all times. |  | 2007-01-01 | [17 empty] | RC
Inactive | PER | PER-004-1 | R1. | Each Reliability Coordinator shall be staffed with adequately trained and NERC-certified Reliability Coordinator operators, 24 hours per day, seven days per week. | 2007-06-18 | 2011-03-31 | High | N/A | N/A | N/A | The responsible entity has failed to be staffed with adequately trained and NERC-certified Reliability Coordinator operators, 24 hours per day, seven days per week. | [12 empty] | RC
Inactive | PER | PER-004-1 | R2. | All Reliability Coordinator operating personnel shall each complete a minimum of five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel. | 2007-06-18 | 2011-03-31 | High | The Reliability Coordinator's operating personnel completed at least 4 (but less than 5) days of emergency training. | The Reliability Coordinator's operating personnel completed at least 3 (but less than 4) days of emergency training. | The Reliability Coordinator's operating personnel completed at least 2 (but less than 3) days of emergency training. | The Reliability Coordinator's operating personnel completed less than 2 days of emergency training. | [12 empty] | RC
Inactive | PER | PER-004-1 | R3. | Reliability Coordinator operating personnel shall have a comprehensive understanding of the Reliability Coordinator Area and interactions with neighboring Reliability Coordinator Areas. | 2007-06-18 | 2013-03-31 | High | Reliability Coordinator personnel have a comprehensive understanding of the interactions with at least 75% and less than 100% of neighboring Reliability Coordinator areas. | Reliability Coordinator personnel have a comprehensive understanding of the interactions with 50% or more and less than 75% of neighboring Reliability Coordinator areas. | Reliability Coordinator personnel have a comprehensive understanding of the interactions with 25% or more and less than 50% of neighboring Reliability Coordinator areas. | Reliability Coordinator personnel have a comprehensive understanding of the interactions less than 25% of neighboring Reliability Coordinator areas. | [12 empty] | RC
Inactive | PER | PER-004-1 | R4. | Reliability Coordinator operating personnel shall have an extensive understanding of the Balancing Authorities, Transmission Operators, and Generation Operators within the Reliability Coordinator Area, including the operating staff, operating practices and procedures, restoration priorities and objectives, outage plans, equipment capabilities, and operational restrictions. | 2007-06-18 | 2013-03-31 | High | Reliability Coordinator operating personnel have an extensive understanding of the operations of more than 75% and less than 100% of all Balancing Authorities, Transmission Operators and Generator Operators in the Reliability Coordinator Area. | Reliability Coordinator operating personnel have an extensive understanding of the operations of more than 50% and less than 75% of all Balancing Authorities, Transmission Operators and Generator Operators in the Reliability Coordinator Area. | Reliability Coordinator operating personnel have an extensive understanding of the operations of more than 25% and less than 50% of all Balancing Authorities, Transmission Operators and Generator Operators in the Reliability Coordinator Area. | Reliability Coordinator operating personnel have an extensive understanding of the operations of less than 25% of all Balancing Authorities, Transmission Operators and Generator Operators in the Reliability Coordinator Area. | [12 empty] | RC
Inactive | PER | PER-004-1 | R5. | Reliability Coordinator operating personnel shall place particular attention on SOLs and IROLs and inter-tie facility limits. The Reliability Coordinator shall ensure protocols are in place to allow Reliability Coordinator operating personnel to have the best available information at all times. | 2007-06-18 | 2011-03-31 | High | Reliability Coordinator has failed to provide its operating personnel with less than 25% of the SOL and IROL limits and for inter-tie facility limits | Reliability Coordinator has failed to provide its operating personnel with 25% or more and less than 50% of the SOL and IROL limits and for inter-tie facility limits. | Reliability Coordinator has failed to provide its operating personnel with 50% or more and less than 75% of the SOL and IROL limits and for inter-tie facility limits. | Reliability Coordinator has failed to provide its operating personnel with 75% or more of the SOL and IROL limits and for inter-tie facility limits. | [12 empty] | RC
Inactive | PER | PER-004-2 | R1. | Each Reliability Coordinator shall be staffed with adequately trained and NERC-certified Reliability Coordinator operators, 24 hours per day, seven days per week. | 2011-04-01 | 2019-06-30 | High | N/A | N/A | N/A | The responsible entity has failed to be staffed with adequately trained and NERCcertified Reliability Coordinator operators, 24 hours per day, seven days per week. | [12 empty] | RC
Inactive | PER | PER-004-2 | R2. | Reliability Coordinator operating personnel shall place particular attention on SOLs and IROLs and inter-tie facility limits. The Reliability Coordinator shall ensure protocols are in place to allow Reliability Coordinator operating personnel to have the best available information at all times. | 2011-04-01 | 2019-06-30 | High | Reliability Coordinator operating personnel did not place particular attention on 5% or IROLs or inter-tie facility limits. | Reliability Coordinator operating personnel did not place particular attention on more than 5% up to (and including) 10% of the SOLs or IROLs or inter-tie facility limits. | Reliability Coordinator operating personnel did not place particular attention on more than 10% up to (and including) 15% of the SOLs or IROLs or inter-tie facility limits. | Reliability Coordinator operating personnel did not place particular attention on more than 15% of the SOLs or IROLs or inter-tie facility limits. OR The Reliability Coordinator did not ensure protocols are in place to allow Reliability Coordinator operating personnel to have the best available information at all times. | [12 empty] | RC
Inactive | PER | PER-005-1 | R1. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall use a systematic approach to training to establish a training program for the BES company-specific reliability-related tasks performed by its System Operators and shall implement the program. | 2013-04-01 | 2016-06-30 | Medium | N/A | The responsible entity failed to update its BES company-specific reliability-related task list to identify new or modified tasks each calendar year. (R1.1.1) OR The responsible entity failed to evaluate its training program to identify needed changes to its training program(s). (R1.4) OR An entity evaluated its training program and identified changes, but failed to implement them. (R1.4) | The responsible entity failed to design and develop learning objectives and training materials based on the BES company specific reliability related tasks. (R1.2) | The responsible entity failed to prepare a BES company-specific reliability-related task list. (R1.1) OR The responsible entity failed to deliver training based on the BES company specific reliability related tasks. (R1.3) |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | PER | PER-005-1 | R2. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall verify each of its System Operator’s capabilities to perform each assigned task identified in R1.1 at least one time. [Time Horizon: Long-term Planning] | 2013-04-01 | 2016-06-30 | High | N/A | The responsible entity failed to verify 5% or less of its System Operators’ capabilities to perform each assigned task from its list of BES company-specific reliability-related tasks. (R2) | The responsible entity failed to verify more than 5% up to (and including) 10% of its System Operators’ capabilities to perform each assigned task from its list of BES company-specific reliability-related tasks. (R2) OR The responsible entity verified its System Operator’s capabilities to perform each new or modified task more than six months but fewer than twelve months after making a modification to its BES company specific reliability-related task list. (R2.1) | The responsible entity failed to verify more than 10% of its System Operators’ capabilities to perform each assigned task from its list of BES company-specific reliability-related tasks. (R2) OR The responsible entity failed to verify its System Operator’s capabilities to perform each new or modified task within twelve months of making a modification to its BES company-specific reliability-related task list. (R2.1) |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | PER | PER-005-1 | R3. | At least every 12 months each Reliability Coordinator, Balancing Authority and Transmission Operator shall provide each of its System Operators with at least 32 hours of emergency operations training applicable to its organization that reflects emergency operations topics, which includes system restoration using drills, exercises or other training required to maintain qualified personnel. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | 2011-04-01 | 2016-06-30 | Medium | N/A | The responsible entity failed to provide at least 32 hours of emergency operations training applicable to its organization, affecting 5% or less of their System Operators. (R3) | The responsible entity failed to provide at least 32 hours of emergency operations training applicable to its organization, affecting more than 5% and up to (and including) 10% of its System Operators. (R3) | The responsible entity failed to provide at least 32 hours of emergency operations training applicable to its organization, affecting more than 10% its System Operators (R3) OR The responsible entity did not include simulation technology replicating the operational behavior of the BES in its emergency operations training. (R3.1) |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-005-2 | R1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement a training program for its System Operators as follows: | 2016-07-01 |  | Medium | None | The Reliability Coordinator, Balancing Authority, or Transmission Operator failed to review or update, if necessary, its BES company-specific Real-time reliability-related task list each calendar year. (1.1.1.) | The Reliability Coordinator, Balancing Authority, or Transmission Operator failed to use a systematic approach to develop and implement a training program. (R1) | The Reliability Coordinator, Balancing Authority, or Transmission Operator failed to create a BES company-specific Real-time reliability-related task list. (1.1.) |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-005-2 | R2. | Each Transmission Owner shall use a systematic approach to develop and implement a training program for its personnel identified in Applicability Section 4.1.4.1 of this standard as follows: | 2016-07-01 |  | Medium | None | The Transmission Owner failed to review or update, if necessary, its company-specific Real-time reliability-related task list each calendar year. (2.1.1.) | The Transmission Owner failed to use a systematic approach to develop and implement a training program. (R2) OR The Transmission Owner failed to design and develop training materials based on the BES company-specific Real-time reliability-related task lists (2.2) | The Transmission Owner failed to create a BES company-specific Real-time reliability-related task list. (2.1.) OR The Transmission Owner failed to deliver training based on the BES company-specific Real-time reliability-related task lists. (2.3) | [18 empty] | TO
Mandatory Subject to Enforcement | PER | PER-005-2 | R3. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify, at least once, the capabilities of its personnel, identified in Requirement R1 or Requirement R2, assigned to perform each of the BES company-specific Real-time reliability-related tasks identified under Requirement R1 part 1.1 or Requirement R2 part 2.1. | 2016-07-01 |  | High | None | The Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner verified the capabilities of at least 90% but less than 100% of its personnel identified in Requirements R1 or Requirement R2 to perform all of their assigned BES company-specific Real-time reliability-related tasks. (R3) | The Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner verified the capabilities of at least 70% but less than 90% of its personnel identified in Requirements R1 or Requirement R2 to perform all of their assigned BES company-specific Real-time reliability-related tasks. (R3) | The Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner verified the capabilities of less than 70% of its personnel identified in Requirements R1 or Requirement R2 to perform all of their assigned BES company-specific Real-time reliability-related tasks. (R3) |  | BA | [10 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | PER | PER-005-2 | R4. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner that (1) has operational authority or control over Facilities with established Interconnection Reliability Operating Limits (IROLs), or (2) has established protection systems or operating guides to mitigate IROL violations, shall provide its personnel identified in Requirement R1 or Requirement R2 with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES. | 2016-07-01 |  | Medium | None | None | None | The Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner that meet the criteria of Requirement R4 did not provide its personnel identified in Requirement R1 or Requirement R2 with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES. (R4) |  | BA | [10 empty] | RC | [5 empty] | TO | TOP
Mandatory Subject to Enforcement | PER | PER-005-2 | R5. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement training for its identified Operations Support Personnel on how their job function(s) impact those BES company-specific Real-time reliability-related tasks identified by the entity pursuant to Requirement R1 part 1.1. | 2016-07-01 |  | Medium | None | The Reliability Coordinator, Balancing Authority, or Transmission Operator failed to evaluate its training established in Requirement R5 each calendar year. (5.1) | The Reliability Coordinator, Balancing Authority, or Transmission Operator failed to develop training for its Operations Support Personnel. (R5) | The Reliability Coordinator, Balancing Authority, or Transmission Operator failed to implement training for its Operations Support Personnel. (R5) |  | BA | [10 empty] | RC | [6 empty] | TOP
Mandatory Subject to Enforcement | PER | PER-005-2 | R6. | Each Generator Operator shall use a systematic approach to develop and implement training to its personnel identified in Applicability Section 4.1.5.1 of this standard, on how their job function(s) impact the reliable operations of the BES during normal and emergency operations. | 2016-07-01 |  | Medium | None | The Generator Operator failed to evaluate its training established in Requirement R6 each calendar year. (6.1) | The Generator Operator failed to develop training for its personnel. (R6) | The Generator Operator failed to implement the training for its personnel identified in Requirement R6. (R6) | [6 empty] | GOP
Mandatory Subject to Enforcement | PER | PER-006-1 | R1. | Each Generator Operator shall provide training to personnel identified in Applicability section 4.1.1.1. on the operational functionality of Protection Systems and Remedial Action Schemes (RAS) that affect the output of the generating Facility(ies) it operates. | 2021-04-01 |  | Medium | The Generator Operator failed to provide training as described in Requirement R1 to the greater of: • one applicable personnel at a single Facility, or • 5% or less of the total applicable personnel of the Generator Operator. | The Generator Operator failed to provide training as described in Requirement R1 to the greater of: • two applicable personnel at a single Facility, or • more than 5% and less than or equal to 10% of the total applicable personnel of the Generator Operator. | The Generator Operator failed to provide training as described in Requirement R1 to the greater of: • three applicable personnel at a single Facility, or • more than 10% and less than or equal to 15% of the total applicable personnel of the Generator Operator. | The Generator Operator failed to provide training as described in Requirement R1 to the greater of: • five or more applicable personnel at a single Facility, or • more than 15% of the total applicable personnel of the Generator Operator. or The Generator Operator failed to provide training as described in Requirement R1 to its applicable personnel. | [6 empty] | GOP
Inactive | PRC | PRC-001-0 | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of protection system schemes applied in its area. |  | 2007-01-01 |  | NONE SPECIFIED | NONE SPECIFIED | NONE SPECIFIED | NONE SPECIFIED |  | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-0 | R2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: |  | 2007-01-01 |  | NONE SPECIFIED | NONE SPECIFIED | NONE SPECIFIED | NONE SPECIFIED | [6 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-0 | R3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows: |  | 2007-01-01 |  | NONE SPECIFIED | NONE SPECIFIED | NONE SPECIFIED | NONE SPECIFIED | [6 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-0 | R4. | Each Transmission Operator shall coordinate protection systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. |  | 2007-01-01 |  | NONE SPECIFIED | NONE SPECIFIED | NONE SPECIFIED | NONE SPECIFIED | [19 empty] | TOP
Inactive | PRC | PRC-001-0 | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the protection systems of others: |  | 2007-01-01 |  | NONE SPECIFIED | NONE SPECIFIED | NONE SPECIFIED | NONE SPECFIED | [6 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-0 | R6. | Each Transmission Operator and Balancing Authority shall monitor the status of each Special Protection System in their area, and shall notify affected Transmission Operators and Balancing Authorities of each change in status. |  | 2007-01-01 |  | NONE SPECIFIED | NONE SPECIFIED | NONE SPECIFIED | NONE SPECIFIED |  | BA | [17 empty] | TOP
Inactive | PRC | PRC-001-1 | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of protection system schemes applied in its area. | 2007-06-18 | 2013-03-31 | High |  |  | The responsible entity was familiar with the purpose of protection system schemes applied in its area but failed to be familiar with the limitations of protection system schemes applied in its area. | The responsible entity failed to be familiar with the purpose and limitations of protection system schemes applied in its area. |  | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1 | R2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: | 2007-06-18 | 2013-03-31 | High |  |  |  | The responsible entity failed to notify any reliability entity of relay or equipment failures. | [6 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1 | R3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | 2007-06-18 | 2013-03-31 | High | [10 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1 | R4. | Each Transmission Operator shall coordinate protection systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. | 2007-06-18 | 2013-03-31 | High | The Transmission Operator failed to coordinate protection systems on major transmission lines and interconnections with one of its neighboring Generator Operators, Transmission Operators, or Balancing Authorities. | The Transmission Operator failed to coordinate protection systems on major transmission lines and interconnections with two of its neighboring Generator Operators, Transmission Operators, or Balancing Authorities. | The Transmission Operator failed to coordinate protection systems on major transmission lines and interconnections with three of its neighboring Generator Operators, Transmission Operators, or Balancing Authorities. | The Transmission Operator failed to coordinate protection systems on major transmission lines and interconnections with three or more of its neighboring Generator Operators, Transmission Operators, and Balancing Authorities. | [19 empty] | TOP
Inactive | PRC | PRC-001-1 | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the protection systems of others: | 2007-06-18 | 2013-03-31 | High |  |  |  | The responsible entity failed to coordinate changes in generation, transmission, load or operating conditions that could require changes in the protection systems of others: | [6 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1 | R6. | Each Transmission Operator and Balancing Authority shall monitor the status of each Special Protection System in their area, and shall notify affected Transmission Operators and Balancing Authorities of each change in status. | 2007-06-18 | 2013-03-31 | High |  |  | Notification of a change in status of a Special Protection System was not made to the affected Transmission Operators and Balancing Authorities. | The responsible entity failed to monitor the status of each Special Protection System in its area, and did not notify affected Transmission Operators and Balancing Authorities of each change in status. |  | BA | [17 empty] | TOP
Inactive | PRC | PRC-001-1.1 | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of Protection System schemes applied in its area. | 2013-04-01 | 2015-05-28 | High | [5 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1.1 | R2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: | 2013-04-01 | 2015-05-28 | High |  |  |  | The responsible entity failed to notify any reliability entity of relay or equipment failures. | [6 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1.1 | R3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | 2013-04-01 | 2015-05-28 | High | [10 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1.1 | R4. | Each Transmission Operator shall coordinate Protection Systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. | 2013-04-01 | 2015-05-28 | High | [23 empty] | TOP
Inactive | PRC | PRC-001-1.1 | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | 2013-04-01 | 2015-05-28 | High | [10 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1.1 | R6. | Each Transmission Operator and Balancing Authority shall monitor the status of each Special Protection System in their area, and shall notify affected Transmission Operators and Balancing Authorities of each change in status. | 2013-04-01 | 2015-05-28 | High | [5 empty] | BA | [17 empty] | TOP
Inactive | PRC | PRC-001-1.1(i) | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of Protection System schemes applied in its area. | 2017-04-01 | 2015-05-28 | High | [5 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1.1(i) | R2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: | 2017-04-01 | 2015-05-28 | High | [10 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1.1(i) | R3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | 2017-04-01 | 2015-05-28 | [11 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1.1(i) | R4. | Each Transmission Operator shall coordinate Protection Systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. | 2017-04-01 | 2015-05-28 | High | [23 empty] | TOP
Inactive | PRC | PRC-001-1.1(i) | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | 2017-04-01 | 2015-05-28 | High | [10 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1.1(i) | R6. | Each Transmission Operator and Balancing Authority shall monitor the status of each Remedial Action Scheme in their area, and shall notify affected Transmission Operators and Balancing Authorities of each change in status. | 2017-04-01 | 2015-05-28 | High | [5 empty] | BA | [17 empty] | TOP
Inactive | PRC | PRC-001-1.1(ii) | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of Protection System schemes applied in its area. | 2015-05-29 | 2021-03-31 | High | [5 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1.1(ii) | R2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: | 2015-05-29 | 2017-03-31 | High | [10 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1.1(ii) | R3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | 2015-05-29 | 2021-03-31 | [11 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1.1(ii) | R4. | Each Transmission Operator shall coordinate Protection Systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. | 2015-05-29 | 2021-03-31 | High | [23 empty] | TOP
Inactive | PRC | PRC-001-1.1(ii) | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others:[See standard for additional information.] | 2015-05-29 | 2017-03-31 | High | [10 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-1.1(ii) | R6. | Each Transmission Operator and Balancing Authority shall monitor the status of each Special Protection System in their area, and shall notify affected Transmission Operators and Balancing Authorities of each change in status. | 2015-05-29 | 2017-03-31 | High | [5 empty] | BA | [17 empty] | TOP
Inactive | PRC | PRC-001-2 | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of protection system schemes applied in its area. |  | 2016-01-26 | High | N/A | N/A | The responsible entity failed to be familiar with the limitations of protection system schemes applied in its area. | The responsible entity failed to be familiar with the purpose of protection system schemes applied in its area. |  | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-2 | R2. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. |  | 2016-01-26 | High | N/A | N/A | N/A | N/A | [6 empty] | GOP | [12 empty] | TOP
Inactive | PRC | PRC-001-2 | R3. | Each Transmission Operator shall coordinate protection systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. |  | 2016-01-26 | High | The Transmission Operator failed to coordinate protection Systems on major transmission lines and interconnections with one of its neighboring Generator Operators, Transmission Operators, or Balancing Authorities. | The Transmission Operator failed to coordinate protection Systems on major transmission lines and interconnections with two of its neighboring Generator Operators, Transmission Operators, or Balancing Authorities. | The Transmission Operator failed to coordinate protection Systems on major transmission lines and interconnections with three of its neighboring Generator Operators, Transmission Operators, or Balancing Authorities. | The Transmission Operator failed to coordinate protection Systems on major transmission lines and interconnections with three or more of its neighboring Generator Operators, Transmission Operators, and Balancing Authorities. | [19 empty] | TOP
Inactive | PRC | PRC-002-0 | R1. | The Regional Reliability Organization shall develop comprehensive requirements for the installation of Disturbance monitoring equipment to ensure data is available to determine system performance and the causes of System Disturbances. The comprehensive requirements shall include all of the following: |  | 2007-01-01 | [20 empty] | RRO
Inactive | PRC | PRC-002-0 | R2. | The Regional Reliability Organization shall provide its requirements for the installation of Disturbance monitoring equipment to other Regional Reliability Organizations and NERC on request (30 calendar days). |  | 2007-01-01 | [20 empty] | RRO
Inactive | PRC | PRC-002-1 | R1. | The Regional Reliability Organization shall establish the following installation requirements for sequence of event recording: |  | 2016-06-30 | Low | [19 empty] | RRO
Inactive | PRC | PRC-002-1 | R2. | The Regional Reliability Organization shall establish the following installation requirements for fault recording: |  | 2016-06-30 | Low | [19 empty] | RRO
Inactive | PRC | PRC-002-1 | R3. | The Regional Reliability Organization shall establish the following installation requirements for dynamic Disturbance recording: |  | 2016-06-30 | Low | [19 empty] | RRO
Inactive | PRC | PRC-002-1 | R4. | The Regional Reliability Organization shall establish requirements for facility owners to report Disturbance data recorded by their DME installations. The Disturbance data reporting requirements shall include the following: |  | 2016-06-30 | Low | [19 empty] | RRO
Inactive | PRC | PRC-002-1 | R5. | The Regional Reliability Organization shall provide its requirements (and any revisions to those requirements) including those for DME installation and Disturbance data reporting to the affected Transmission Owners and Generator Owners within 30 calendar |  | 2016-06-30 | Low | [19 empty] | RRO
Inactive | PRC | PRC-002-1 | R6. | The Regional Reliability Organization shall periodically (at least every five years) review, update and approve its Regional requirements for Disturbance monitoring and reporting. |  | 2016-06-30 | Low | [19 empty] | RRO
Inactive | PRC | PRC-002-2 | R1. | Each Transmission Owner shall: | 2016-07-01 | 2024-03-31 | Low | The Transmission Owner identified the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 for more than 80 percent but less than 100 percent of the required BES buses that they own. OR The Transmission Owner evaluated the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 but was late by 30-calendar days or less. OR The Transmission Owner as directed by Requirement R1, Part 1.2 was late in notifying the other owners by 10-calendar days or less. | The Transmission Owner identified the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 for more than 70 percent but less than or equal to 80 percent of the required BES buses that they own. OR The Transmission Owner evaluated the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 but was late by greater than 30-calendar days and less than or equal to 60-calendar days. OR The Transmission Owner as directed by Requirement R1, Part 1.2 was late in notifying the other owners by greater than 10-calendar days but less than or equal to 20-calendar days. | The Transmission Owner identified the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 for more than 60 percent but less than or equal to 70 percent of the required BES buses that they own. OR The Transmission Owner evaluated the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 but was late by greater than 60-calendar days and less than or equal to 90-calendar days. OR The Transmission Owner as directed by Requirement R1, Part 1.2 was late in notifying the other owners by greater than 20-calendar days but less than or equal to 30-calendar days. | The Transmission Owner identified the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 for less than or equal to 60 percent of the required BES buses that they own. OR The Transmission Owner evaluated the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 but was late by greater than 90-calendar days. OR The Transmission Owner as directed by Requirement R1, Part 1.2 was late in notifying one or more other owners by greater than 30-calendar days. | Entities will be required to establish 50% compliance with Requirements R2-R4 and R6-R11 by January 1, 2021. See Implementation Plan for additional effective date information. | [17 empty] | TO
Inactive | PRC | PRC-002-2 | R2. | Each Transmission Owner and Generator Owner shall have SER data for circuit breaker position (open/close) for each circuit breaker it owns connected directly to the BES buses identified in Requirement R1 and associated with the BES Elements at those BES buses. | 2021-01-01 | 2024-03-31 | Low | Each Transmission Owner or Generator Owner as directed by Requirement R2 had more than 80 percent but less than 100 percent of the total SER data for circuit breaker position (open/close) for each of the circuit breakers at the BES buses identified in Requirement R1. | Each Transmission Owner or Generator Owner as directed by Requirement R2 had more than 70 percent but less than or equal to 80 percent of the total SER data for circuit breaker position (open/close) for each of the circuit breakers at the BES buses identified in Requirement R1. | Each Transmission Owner or Generator Owner as directed by Requirement R2 had more than 60 percent but less than or equal to 70 percent of the total SER data for circuit breaker position (open/close) for each of the circuit breakers at the BES buses identified in Requirement R1. | Each Transmission Owner or Generator Owner as directed by Requirement R2 for less than or equal to 60 percent of the total SER data for circuit breaker position (open/close) for each of the circuit breakers at the BES buses identified in Requirement R1 | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-002-2 | R3. | Each Transmission Owner and Generator Owner shall have FR data to determine the following electrical quantities for each triggered FR for the BES Elements it owns connected to the BES buses identified in Requirement R1: | 2021-01-01 | 2024-03-31 | Low | The Transmission Owner or Generator Owner had FR data as directed by Requirement R3, Parts 3.1 and 3.2 that covers more than 80 percent but less than 100 percent of the total set of required electrical quantities, which is the product of the total number of monitored BES Elements and the number of specified electrical quantities for each BES Element. | The Transmission Owner or Generator Owner had FR data as directed by Requirement R3, Parts 3.1 and 3.2 that covers more than 70 percent but less than or equal to 80 percent of the total set of required electrical quantities, which is the product of the total number of monitored BES Elements and the number of specified electrical quantities for each BES Element. | The Transmission Owner or Generator Owner had FR data as directed by Requirement R3, Parts 3.1 and 3.2 that covers more than 60 percent but less than or equal to 70 percent of the total set of required electrical quantities, which is the product of the total number of monitored BES Elements and the number of specified electrical quantities for each BES Element. | The Transmission Owner or Generator Owner had FR data as directed by Requirement R3, Parts 3.1 and 3.2 that covers less than or equal to 60 percent of the total set of required electrical quantities, which is the product of the total number of monitored BES Elements and the number of specified electrical quantities for each BES Element. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-002-2 | R4. | Each Transmission Owner and Generator Owner shall have FR data as specified in Requirement R3 that meets the following: | 2021-01-01 | 2024-03-31 | Low | The Transmission Owner or Generator Owner had FR data that meets more than 80 percent but less than 100 percent of the total recording properties as specified in Requirement R4. | The Transmission Owner or Generator Owner had FR data that meets more than 70 percent but less than or equal to 80 percent of the total recording properties as specified in Requirement R4. | The Transmission Owner or Generator Owner had FR data that meets more than 60 percent but less than or equal to 70 percent of the total recording properties as specified in Requirement R4. | The Transmission Owner or Generator Owner had FR data that meets less than or equal to 60 percent of the total recording properties as specified in Requirement R4. | 1/1/2021,100% Complaint by 7/1/2022 |  |  |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-002-2 | R5. | Each Responsible Entity shall: | 2016-07-01 | 2024-03-31 | Low | The Responsible Entity identified the BES Elements for which DDR data is required as directed by Requirement R5 for more than 80 percent but less than 100 percent of the required BES Elements included in Part 5.1. OR The Responsible Entity identified the BES Elements for DDR as directed by Requirement R5, Part 5.1 or Part 5.4 but was late by 30-calendar days or less. OR The Responsible Entity as directed by Requirement R5, Part 5.3 was late in notifying the owners by 10-calendar days or less. | The Responsible Entity identified the BES Elements for which DDR data is required as directed by Requirement R5 for more than 70 percent but less than or equal to 80 percent of the required BES Elements included in Part 5.1. OR The Responsible Entity identified the BES Elements for DDR as directed by Requirement R5, Part 5.1 or Part 5.4 but was late by greater than 30-calendar days and less than or equal to 60 -calendar days. | The Responsible Entity identified the BES Elements for which DDR data is required as directed by Requirement R5 for more than 60 percent but less than or equal to 70 percent of the required BES Elements included in Part 5.1. OR The Responsible Entity identified the BES Elements for DDR as directed by Requirement R5, Part 5.1 or Part 5.4 but was late by greater than 60-calendar days and less than or equal to 90-calendar days. OR The Responsible Entity as directed by Requirement R5, Part 5.3 was late in notifying the owners by greater than 20-calendar days but less than or equal to 30-calendar days. | The Responsible Entity identified the BES Elements for which DDR data is required as directed by Requirement R5 for less than or equal to 60 percent of the required BES Elements included in Part 5.1. OR The Responsible Entity identified the BES Elements for DDR as directed by Requirement R5, Part 5.1 or Part 5.4 but was late by greater than 90-calendar days. OR The Responsible Entity as directed by Requirement R5, Part 5.3 was late in notifying one or more owners by greater than 30-calendar days. OR The Responsible Entity failed to ensure a minimum DDR coverage per Part 5.2. | Entities will be required to establish 50% compliance with Requirements R2-R4 and R6-R11 by January 1, 2021. See Implementation Plan for additional effective date information. | [9 empty] | PCPA |  | RC
Inactive | PRC | PRC-002-2 | R6. | Each Transmission Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: | 2021-01-01 | 2024-03-31 | Low | The Transmission Owner had DDR data as directed by Requirement R6, Parts 6.1 through 6.4 that covered more than 80 percent but less than 100 percent of the total required electrical quantities for all applicable BES Elements. | The Transmission Owner had DDR data as directed by Requirement R6, Parts 6.1 through 6.4 for more than 70 percent but less than or equal to 80 percent of the total required electrical quantities for all applicable BES Elements. | The Transmission Owner had DDR data as directed by Requirement R6, Parts 6.1 through 6.4 for more than 60 percent but less than or equal to 70 percent of the total required electrical quantities for all applicable BES Elements. | The Transmission Owner failed to have DDR data as directed by Requirement R6, Parts 6.1 through 6.4. | [18 empty] | TO
Inactive | PRC | PRC-002-2 | R7. | Each Generator Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: | 2021-01-01 | 2024-03-31 | Low | The Generator Owner had DDR data as directed by Requirement R7, Parts 7.1 through 7.4 that covers more than 80 percent but less than 100 percent of the total required electrical quantities for all applicable BES Elements. | The Generator Owner had DDR data as directed by Requirement R7, Parts 7.1 through 7.4 for more than 70 percent but less than or equal to 80 percent of the total required electrical quantities for all applicable BES Elements. | The Generator Owner had DDR data as directed by Requirement R7, Parts 7.1 through 7.4 for more than 60 percent but less than or equal to 70 percent of the total required electrical quantities for all applicable BES Elements. | The Generator Owner failed to have DDR data as directed by Requirement R7, Parts 7.1 through 7.4. | [5 empty] | GO
Inactive | PRC | PRC-002-2 | R8. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have continuous data recording and storage. If the equipment was installed prior to the effective date of this standard and is not capable of continuous recording, triggered records must meet the following: | 2021-01-01 | 2024-03-31 | Low | The Transmission Owner or Generator Owner had continuous or non-continuous DDR data, as directed in Requirement R8, for more than 80 percent but less than 100 percent of the BES Elements they own as determined in Requirement R5. | The Transmission Owner or Generator Owner had continuous or non-continuous DDR data, as directed in Requirement R8, for more than 70 percent but less than or equal to 80 percent of the BES Elements they own as determined in Requirement R5. | The Transmission Owner or Generator Owner had continuous or non-continuous DDR data, as directed in Requirement R8, for more than 60 percent but less than or equal to 70 percent of the BES Elements they own as determined in Requirement R5. | The Transmission Owner or Generator Owner failed to have continuous or non-continuous DDR data, as directed in Requirement R8, for the BES Elements they own as determined in Requirement R5. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-002-2 | R9. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have DDR data that meet the following: | 2021-01-01 | 2024-03-31 | Low | The Transmission Owner or Generator Owner had DDR data that meets more than 80 percent but less than 100 percent of the total recording properties as specified in Requirement R9. | The Transmission Owner or Generator Owner had DDR data that meets more than 70 percent but less than or equal to 80 percent of the total recording properties as specified in Requirement R9. | The Transmission Owner or Generator Owner had DDR data that meets more than 60 percent but less than or equal to 70 percent of the total recording properties as specified in Requirement R9. | The Transmission Owner or Generator Owner had DDR data that meets less than or equal to 60 percent of the total recording properties as specified in Requirement R9. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-002-2 | R10. | Each Transmission Owner and Generator Owner shall time synchronize all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to meet the following: | 2021-01-01 | 2024-03-31 | Low | The Transmission Owner or Generator Owner had time synchronization per Requirement R10, Parts 10.1 and 10.2 for SER, FR, and DDR data for more than 90 percent but less than 100 percent of the BES buses identified in Requirement R1 and BES Elements identified in Requirement R5 as directed by Requirement R10. | The Transmission Owner or Generator Owner had time synchronization per Requirement R10, Parts 10.1 and 10.2 for SER, FR, and DDR data for more than 80 percent but less than or equal to 90 percent of the BES buses identified in Requirement R1 and BES Elements identified in Requirement R5 as directed by Requirement R10. | The Transmission Owner or Generator Owner had time synchronization per Requirement R10, Parts 10.1 and 10.2 for SER, FR, and DDR data for more than 70 percent but less than or equal to 80 percent of the BES buses identified in Requirement R1 and BES Elements identified in Requirement R5 as directed by Requirement R10. | The Transmission Owner or Generator Owner failed to have time synchronization per Requirement R10, Parts 10.1 and 10.2 for SER, FR, and DDR data for less than or equal to 70 percent of the BES buses identified in Requirement R1 and BES Elements identified in Requirement R5 as directed by Requirement R10. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-002-2 | R11. | Each Transmission Owner and Generator Owner shall provide, upon request, all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to the Responsible Entity, Regional Entity, or NERC in accordance with the following: | 2021-01-01 | 2024-03-31 | Low | The Transmission Owner or Generator Owner as directed by Requirement R11, Part 11.1 provided the requested data more than 30-calendar days but less than 40-calendar days after the request unless an extension was granted by the requesting authority. OR The Transmission Owner or Generator Owner as directed by Requirement R11 provided more than 90 percent but less than 100 percent of the requested data. OR The Transmission Owner or Generator Owner as directed by Requirement R11, Parts 11.3 through 11.5 provided more than 90 percent of the data but less than 100 percent of the data in the proper data format. | The Transmission Owner or Generator Owner as directed by Requirement R11, Part 11.1 provided the requested data more than 40-calendar days but less than or equal to 50-calendar days after the request unless an extension was granted by the requesting authority. OR The Transmission Owner or Generator Owner as directed by Requirement R11 provided more than 80 percent but less than or equal to 90 percent of the requested data. OR The Transmission Owner or Generator Owner as directed by Requirement R11, Parts 11.3 through 11.5 provided more than 80 percent of the data but less than or equal to 90 percent of the data in the proper data format. | The Transmission Owner or Generator Owner as directed by Requirement R11, Part 11.1 provided the requested data more than 50-calendar days but less than or equal to 60-calendar days after the request unless an extension was granted by the requesting authority. OR The Transmission Owner or Generator Owner as directed by Requirement R11 provided more than 70 percent but less than or equal to 80 percent of the requested data. OR The Transmission Owner or Generator Owner as directed by Requirement R11, Parts 11.3 through 11.5 provided more than 70 percent of the data but less than or equal to 80 percent of the data in the proper data format. | The Transmission Owner or Generator Owner as directed by Requirement R11, Part 11.1 failed to provide the requested data more than 60-calendar days after the request unless an extension was granted by the requesting authority. OR The Transmission Owner or Generator Owner as directed by Requirement R11 failed to provide less than or equal to 70 percent of the requested data. OR The Transmission Owner or Generator Owner as directed by Requirement R11, Parts 11.3 through 11.5 provided less than or equal to 70 percent of the data in the proper data format. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-002-2 | R12. | Each Transmission Owner and Generator Owner shall, within 90-calendar days of the discovery of a failure of the recording capability for the SER, FR or DDR data, either: • Restore the recording capability, or • Submit a Corrective Action Plan (CAP) to the Regional Entity and implement it. | 2016-10-01 | 2024-03-31 | Low | The Transmission Owner or Generator Owner as directed by Requirement R12 reported a failure and provided a Corrective Action Plan to the Regional Entity more than 90-calendar days but less than or equal to 100-calendar days after discovery of the failure. | The Transmission Owner or Generator Owner as directed by Requirement R12 reported a failure and provided a Corrective Action Plan to the Regional Entity more than 100-calendar days but less than or equal to 110-calendar days after discovery of the failure. | The Transmission Owner or Generator Owner as directed by Requirement R12 reported a failure and provided a Corrective Action Plan to the Regional Entity more than 110-calendar days but less than or equal to 120-calendar days after discovery of the failure. OR The Transmission Owner or Generator Owner as directed by Requirement R12 submitted a CAP to the Regional Entity but failed to implement it. | The Transmission Owner or Generator Owner as directed by Requirement R12 failed to report a failure and provide a Corrective Action Plan to the Regional Entity more than 120-calendar days after discovery of the failure. OR Transmission Owner or Generator Owner as directed by Requirement R12 failed to restore the recording capability and failed to submit a CAP to the Regional Entity. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-002-3 | R1. | Each Transmission Owner shall: |  | 2024-03-31 | Low | The Transmission Owner identified the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 for more than 80 percent but less than 100 percent of the required BES buses that they own. OR The Transmission Owner evaluated the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 but was late by 30- calendar days or less. OR The Transmission Owner as directed by Requirement R1, Part 1.2 was late in notifying the other owners by 10-calendar days or less. | The Transmission Owner identified the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 for more than 70 percent but less than or equal to 80 percent of the required BES buses that they own. OR The Transmission Owner evaluated the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 but was late by greater than 30-calendar days and less than or equal to 60-calendar days. OR The Transmission Owner as directed by Requirement R1, Part 1.2 was late in notifying the other owners by greater than 10-calendar days but less than or equal to 20-calendar days. | The Transmission Owner identified the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 for more than 60 percent but less than or equal to 70 percent of the required BES buses that they own. OR The Transmission Owner evaluated the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 but was late by greater than 60-calendar days and less than or equal to 90-calendar days. OR The Transmission Owner as directed by Requirement R1, Part 1.2 was late in notifying the other owners by greater than 20-calendar days but less than or equal to 30-calendar days. | The Transmission Owner identified the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 for less than or equal to 60 percent of the required BES buses that they own. OR The Transmission Owner evaluated the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 but was late by greater than 90-calendar days. OR The Transmission Owner as directed by Requirement R1, Part 1.2 was late in notifying one or more other owners by greater than 30- calendar days. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002-3 | R2. | Each Transmission Owner and Generator Owner shall have SER data for circuit breaker position (open/close) for each circuit breaker it owns connected directly to the BES buses identified in Requirement R1 and associated with the BES Elements at those BES buses. |  | 2024-03-31 | Low | Each Transmission Owner or Generator Owner as directed by Requirement R2 had more than 80 percent but less than 100 percent of the total SER data for circuit breaker position (open/close) for each of the circuit breakers at the BES buses identified in Requirement R1. | Each Transmission Owner or Generator Owner as directed by Requirement R2 had more than 70 percent but less than or equal to 80 percent of the total SER data for circuit breaker position (open/close) for each of the circuit breakers at the BES buses identified in Requirement R1. | Each Transmission Owner or Generator Owner as directed by Requirement R2 had more than 60 percent but less than or equal to 70 percent of the total SER data for circuit breaker position (open/close) for each of the circuit breakers at the BES buses identified in Requirement R1. | Each Transmission Owner or Generator Owner as directed by Requirement R2 for less than or equal to 60 percent of the total SER data for circuit breaker position (open/close) for each of the circuit breakers at the BES buses identified in Requirement R1. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002-3 | R3. | Each Transmission Owner and Generator Owner shall have FR data to determine the following electrical quantities for each triggered FR for the BES Elements it owns connected to the BES buses identified in Requirement R1: |  | 2024-03-31 | Low | The Transmission Owner or Generator Owner had FR data as directed by Requirement R3, Parts 3.1 and 3.2 that covers more than 80 percent but less than 100 percent of the total set of required electrical quantities, which is the product of the total number of monitored BES Elements and the number of specified electrical quantities for each BES Element. | The Transmission Owner or Generator Owner had FR data as directed by Requirement R3, Parts 3.1 and 3.2 that covers more than 70 percent but less than or equal to 80 percent of the total set of required electrical quantities, which is the product of the total number of monitored BES Elements and the number of specified electrical quantities for each BES Element. | The Transmission Owner or Generator Owner had FR data as directed by Requirement R3, Parts 3.1 and 3.2 that covers more than 60 percent but less than or equal to 70 percent of the total set of required electrical quantities, which is the product of the total number of monitored BES Elements and the number of specified electrical quantities for each BES Element. | The Transmission Owner or Generator Owner had FR data as directed by Requirement R3, Parts 3.1 and 3.2 that covers less than or equal to 60 percent of the total set of required electrical quantities, which is the product of the total number of monitored BES Elements and the number of specified electrical quantities for each BES Element. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002-3 | R4. | Each Transmission Owner and Generator Owner shall have FR data as specified in Requirement R3 that meets the following: |  | 2024-03-31 | Low | The Transmission Owner or Generator Owner had FR data that meets more than 80 percent but less than 100 percent of the total recording properties as specified in Requirement R4. | The Transmission Owner or Generator Owner had FR data that meets more than 70 percent but less than or equal to 80 percent of the total recording properties as specified in Requirement R4. | The Transmission Owner or Generator Owner had FR data that meets more than 60 percent but less than or equal to 70 percent of the total recording properties as specified in Requirement R4. | The Transmission Owner or Generator Owner had FR data that meets less than or equal to 60 percent of the total recording properties as specified in Requirement R4. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002-3 | R5. | Each Reliability Coordinator shall: |  | 2024-03-31 | Low | The Reliability Coordinator identified the BES Elements for which DDR data is required as directed by Requirement R5 for more than 80 percent but less than 100 percent of the required BES Elements included in Part 5.1. OR The Reliability Coordinator identified the BES Elements for DDR as directed by Requirement R5, Part 5.1 or Part 5.4 but was late by 30-calendar days or less. OR The Reliability Coordinator as directed by Requirement R5, Part 5.3 was late in notifying the owners by 10-calendar days or less. | The Reliability Coordinator identified the BES Elements for which DDR data is required as directed by Requirement R5 for more than 70 percent but less than or equal to 80 percent of the required BES Elements included in Part 5.1. OR The Reliability Coordinator identified the BES Elements for DDR as directed by Requirement R5, Part 5.1 or Part 5.4 but was late by greater than 30-calendar days and less than or equal to 60 -calendar days. OR The Reliability Coordinator as directed by Requirement R5, Part 5.3 was late in notifying the owners by greater than 10- calendar days but less than or equal to 20- calendar days. | The Reliability Coordinator identified the BES Elements for which DDR data is required as directed by Requirement R5 for more than 60 percent but less than or equal to 70 percent of the required BES Elements included in Part 5.1. OR The Reliability Coordinator identified the BES Elements for DDR as directed by Requirement R5, Part 5.1 or Part 5.4 but was late by greater than 60-calendar days and less than or equal to 90-calendar days. OR The Reliability Coordinator as directed by Requirement R5, Part 5.3 was late in notifying the owners by greater than 20- calendar days but less than or equal to 30- calendar days. | The Reliability Coordinator identified the BES Elements for which DDR data is required as directed by Requirement R5 for less than or equal to 60 percent of the required BES Elements included in Part 5.1. OR The Reliability Coordinator identified the BES Elements for DDR as directed by Requirement R5, Part 5.1 or Part 5.4 but was late by greater than 90-calendar days. OR The Reliability Coordinator as directed by Requirement R5, Part 5.3 was late in notifying one or more owners by greater than 30-calendar days. OR The Reliability Coordinator failed to ensure a minimum DDR coverage per Part 5.2. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002-3 | R6. | Each Transmission Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: |  | 2024-03-31 | Low | The Transmission Owner had DDR data as directed by Requirement R6, Parts 6.1 through 6.4 that covered more than 80 percent but less than 100 percent of the total required electrical quantities for all applicable BES Elements. | The Transmission Owner had DDR data as directed by Requirement R6, Parts 6.1 through 6.4 for more than 70 percent but less than or equal to 80 percent of the total required electrical quantities for all applicable BES Elements. | The Transmission Owner had DDR data as directed by Requirement R6, Parts 6.1 through 6.4 for more than 60 percent but less than or equal to 70 percent of the total required electrical quantities for all applicable BES Elements. | The Transmission Owner failed to have DDR data as directed by Requirement R6, Parts 6.1 through 6.4. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002-3 | R7. | Each Generator Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: |  | 2024-03-31 | Low | The Generator Owner had DDR data as directed by Requirement R7, Parts 7.1 through 7.4 that covers more than 80 percent but less than 100 percent of the total required electrical quantities for all applicable BES Elements. | The Generator Owner had DDR data as directed by Requirement R7, Parts 7.1 through 7.4 for more than 70 percent but less than or equal to 80 percent of the total required electrical quantities for all applicable BES Elements. | The Generator Owner had DDR data as directed by Requirement R7, Parts 7.1 through 7.4 for more than 60 percent but less than or equal to 70 percent of the total required electrical quantities for all applicable BES Elements. | The Generator Owner failed to have DDR data as directed by Requirement R7, Parts 7.1 through 7.4. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002-3 | R8. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have continuous data recording and storage. If the equipment was installed prior to the effective date of this standard and is not capable of continuous recording, triggered records must meet the following: |  | 2024-03-31 | Low | The Transmission Owner or Generator Owner had continuous or non-continuous DDR data, as directed in Requirement R8, for more than 80 percent but less than 100 percent of the BES Elements they own as determined in Requirement R5. | The Transmission Owner or Generator Owner had continuous or non-continuous DDR data, as directed in Requirement R8, for more than 70 percent but less than or equal to 80 percent of the BES Elements they own as determined in Requirement R5. | The Transmission Owner or Generator Owner had continuous or non-continuous DDR data, as directed in Requirement R8, for more than 60 percent but less than or equal to 70 percent of the BES Elements they own as determined in Requirement R5. | The Transmission Owner or Generator Owner failed to have continuous or non- continuous DDR data, as directed in Requirement R8, for the BES Elements they own as determined in Requirement R5. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002-3 | R9. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have DDR data that meet the following: |  | 2024-03-31 | Low | The Transmission Owner or Generator Owner had DDR data that meets more than 80 percent but less than 100 percent of the total recording properties as specified in Requirement R9. | The Transmission Owner or Generator Owner had DDR data that meets more than 70 percent but less than or equal to 80 percent of the total recording properties as specified in Requirement R9. | The Transmission Owner or Generator Owner had DDR data that meets more than 60 percent but less than or equal to 70 percent of the total recording properties as specified in Requirement R9. | The Transmission Owner or Generator Owner had DDR data that meets less than or equal to 60 percent of the total recording properties as specified in Requirement R9. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002-3 | R10. | Each Transmission Owner and Generator Owner shall time synchronize all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to meet the following: |  | 2024-03-31 | Low | The Transmission Owner or Generator Owner had time synchronization per Requirement R10, Parts 10.1 and 10.2 for SER, FR, and DDR data for more than 90 percent but less than 100 percent of the BES buses identified in Requirement R1 and BES Elements identified in Requirement R5 as directed by Requirement R10. | The Transmission Owner or Generator Owner had time synchronization per Requirement R10, Parts 10.1 and 10.2 for SER, FR, and DDR data for more than 80 percent but less than or equal to 90 percent of the BES buses identified in Requirement R1 and BES Elements identified in Requirement R5 as directed by Requirement R10. | The Transmission Owner or Generator Owner had time synchronization per Requirement R10, Parts 10.1 and 10.2 for SER, FR, and DDR data for more than 70 percent but less than or equal to 80 percent of the BES buses identified in Requirement R1 and BES Elements identified in Requirement R5 as directed by Requirement R10. | The Transmission Owner or Generator Owner failed to have time synchronization per Requirement R10, Parts 10.1 and 10.2 for SER, FR, and DDR data for less than or equal to 70 percent of the BES buses identified in Requirement R1 and BES Elements identified in Requirement R5 as directed by Requirement R10. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002-3 | R11. | Each Transmission Owner and Generator Owner shall provide, upon request, all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to the Reliability Coordinator, Regional Entity, or NERC in accordance with the following: |  | 2024-03-31 | Low | The Transmission Owner or Generator Owner as directed by Requirement R11, Part 11.1 provided the requested data more than 30-calendar days but less than 40- calendar days after the request unless an extension was granted by the requesting authority. OR The Transmission Owner or Generator Owner as directed by Requirement R11 provided more than 90 percent but less than 100 percent of the requested data. OR The Transmission Owner or Generator Owner as directed by Requirement R11, Parts 11.3 through 11.5 provided more than 90 percent of the data but less than 100 percent of the data in the proper data format. | The Transmission Owner or Generator Owner as directed by Requirement R11, Part 11.1 provided the requested data more than 40-calendar days but less than or equal to 50-calendar days after the request unless an extension was granted by the requesting authority. OR The Transmission Owner or Generator Owner as directed by Requirement R11 provided more than 80 percent but less than or equal to 90 percent of the requested data. OR The Transmission Owner or Generator Owner as directed by Requirement R11, Parts 11.3 through 11.5 provided more than 80 percent of the data but less than or equal to 90 percent of the data in the proper data format. | The Transmission Owner or Generator Owner as directed by Requirement R11, Part 11.1 provided the requested data more than 50-calendar days but less than or equal to 60-calendar days after the request unless an extension was granted by the requesting authority. OR The Transmission Owner or Generator Owner as directed by Requirement R11 provided more than 70 percent but less than or equal to 80 percent of the requested data. OR The Transmission Owner or Generator Owner as directed by Requirement R11, Parts 11.3 through 11.5 provided more than 70 percent of the data but less than or equal to 80 percent of the data in the proper data format. | The Transmission Owner or Generator Owner as directed by Requirement R11, Part 11.1 failed to provide the requested data more than 60-calendar days after the request unless an extension was granted by the requesting authority. OR The Transmission Owner or Generator Owner as directed by Requirement R11 failed to provide less than or equal to 70 percent of the requested data. OR The Transmission Owner or Generator Owner as directed by Requirement R11, Parts 11.3 through 11.5 provided less than or equal to 70 percent of the data in the proper data format. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002-3 | R12. | Each Transmission Owner and Generator Owner shall, within 90-calendar days of the discovery of a failure of the recording capability for the SER, FR or DDR data, either: · Restore the recording capability, or · Submit a Corrective Action Plan (CAP) to the Regional Entity and implement it. |  | 2024-03-31 | Low | The Transmission Owner or Generator Owner as directed by Requirement R12 reported a failure and provided a Corrective Action Plan to the Regional Entity more than 90-calendar days but less than or equal to 100-calendar days after discovery of the failure. | The Transmission Owner or Generator Owner as directed by Requirement R12 reported a failure and provided a Corrective Action Plan to the Regional Entity more than 100-calendar days but less than or equal to 110-calendar days after discovery of the failure. | The Transmission Owner or Generator Owner as directed by Requirement R12 reported a failure and provided a Corrective Action Plan to the Regional Entity more than 110-calendar days but less than or equal to 120-calendar days after discovery of the failure. OR The Transmission Owner or Generator Owner as directed by Requirement R12 submitted a CAP to the Regional Entity but failed to implement it. | The Transmission Owner or Generator Owner as directed by Requirement R12 failed to report a failure and provide a Corrective Action Plan to the Regional Entity more than 120-calendar days after discovery of the failure. OR Transmission Owner or Generator Owner as directed by Requirement R12 failed to restore the recording capability and failed to submit a CAP to the Regional Entity. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002-4 | R1. | Each Transmission Owner shall: | 2024-04-01 |  | Low | The Transmission Owner identified the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 for more than 80 percent, but less than 100 percent of the required BES buses that they own. OR The Transmission Owner evaluated the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3, but was late by 30 calendar days or less. OR The Transmission Owner as directed by Requirement R1, Part 1.2 was late in notifying the other owners that their BES Elements require SER or FR data by 10 calendar days or less. | The Transmission Owner identified the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 for more than 70 percent, but less than 80 percent of the required BES buses that they own. OR The Transmission Owner evaluated the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3, but was late by greater than 30 calendar days and less than or equal to 60 calendar days. OR The Transmission Owner as directed by Requirement R1, Part 1.2 was late in notifying the other owners that their BES Elements require SER or FR data by greater than 10 calendar days, but less than or equal to 20 calendar days. | The Transmission Owner identified the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 for more than 60 percent, but less than 70 percent of the required BES buses that they own. OR The Transmission Owner evaluated the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3, but was late by greater than 60 calendar days and less than or equal to 90 calendar days. OR The Transmission Owner as directed by Requirement R1, Part 1.2 was late in notifying the other owners that their BES Elements require SER or FR data by greater than 20 calendar days, but less than or equal to 30 calendar days. | The Transmission Owner identified the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3 for less than or equal to 60 percent of the required BES buses that they own. OR The Transmission Owner evaluated the BES buses as directed by Requirement R1, Part 1.1 or Part 1.3, but was late by greater than 90 calendar days. OR The Transmission Owner as directed by Requirement R1, Part 1.2 was late in notifying one or more other owners that their BES Elements require SER or FR data by greater than 30 calendar days. | [18 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002-4 | R2. | Each Transmission Owner and Generator Owner shall have SER data for circuit breaker position (open/close) for each circuit breaker it owns directly connected to the BES buses identified in Requirement R1 and associated with the BES Elements at those BES buses. | 2024-04-01 |  | Low | Each Transmission Owner or Generator Owner as directed by Requirement R2 had more than 80percent, but less than 100 percent of the total SER data for circuit breaker position (open/close) for each of the circuit breakers at the BES buses identified in Requirement R1. | Each Transmission Owner or Generator Owner as directed by Requirement R2 had more than 70 percent,but less than or equal to 80 percent of the total SER data for circuit breaker position (open/close) for each of the circuit breakers at the BES buses identified in Requirement R1. | Each Transmission Owner or Generator Owner as directed by Requirement R2 had more than 60 percent but less than or equal to 70 percent of the total SER data for circuit breaker position (open/close) for each of the circuit breakers at the BES buses identified in Requirement R1. | Each Transmission Owner or Generator Owner as directed by Requirement R2 for less than or equal to 60 percent of the total SER data for circuit breaker position (open/close) for each of the circuit breakers at the BES buses identified in Requirement R1. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002-4 | R3. | Each Transmission Owner and Generator Owner shall have FR data to determine the following electrical quantities for each triggered FR for the BES Elements it owns directly connected to the BES buses identified in Requirement R1: [Violation Risk Factor: | 2024-04-01 |  | Low | The Transmission Owner or Generator Owner had FR data as directed by Requirement R3, Parts 3.1 and 3.2 that covers more than 80 percent, but less than 100 percent of the total set of required electrical quantities, which is the product of the total number of monitored BES Elements and the number of specified electrical quantities for each BES Element. | The Transmission Owner or Generator Owner had FR data as directed by Requirement R3, Parts 3.1 and 3.2 that covers more than 70 percent, but less than or equal to 80 percent of the total set of required electrical quantities, which is the product of the total number of monitored BES Elements and the number of specified electrical quantities for each BES Element. | The Transmission Owner or Generator Owner had FR data as directed by Requirement R3, Parts 3.1 and 3.2 that covers more than 60 percent, but less than or equal to 70 percent of the total set of required electrical quantities, which is the product of the total number of monitored BES Elements and the number of specified electrical quantities for each BES Element. | The Transmission Owner or Generator Owner had FR data as directed by Requirement R3, Parts 3.1 and 3.2 that covers less than or equal to 60 percent of the total set of required electrical quantities, which is the product of the total number of monitored BES Elements and the number of specified electrical quantities for each BES Element. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002-4 | R4. | Each Transmission Owner and Generator Owner shall have FR data as specified in Requirement R3 that meets the following: | 2024-04-01 |  | Low | The Transmission Owner or Generator Owner had FR data that meets more than 80 percent, but less than 100 percent of the total recording properties as specified in Requirement R4. | The Transmission Owner or Generator Owner had FR data that meets more than 70 percent, but less than or equal to 80 percent of the total recording properties as specified in Requirement R4. | The Transmission Owner or Generator Owner had FR data that meets more than 60 percent, but less than or equal to 70 percent of the total recording properties as specified in Requirement R4. | The Transmission Owner or Generator Owner had FR data that meets less than or equal to 60 percent of the total recording properties as specified in Requirement R4. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002-4 | R5. | Each Reliability Coordinator shall: | 2024-04-01 |  | Low | The Reliability Coordinator identified the BES Elements for which DDR data is required as directed by Requirement R5 for more than 80 percent, but less than 100 percent of the required BES Elements included in Part 5.1. OR The Reliability Coordinator identified the BES Elements for DDR as directed by Requirement R5, Part 5.1 or Part 5.4, but was late by 30 callendar days or less. OR The Reliability Coordinator as directed by Requirement R5, Part 5.3 was late in notifying the owners that their BES Elements require DDR data by 10 calendar days or less. | The Reliability Coordinator identified the BES Elements for which DDR data is required as directed by Requirement R5 for more than 70 percent, but less than or equal to 80 percent of the required BES Elements included in Part 5.1. OR The Reliability Coordinator identified the BES Elements for DDR as directed by Requirement R5, Part 5.1 or Part 5.4, but was late by greater than 30 calendar days and less than or equal to 60 calendar days. OR The Reliability Coordinator as directed by Requirement R5, Part 5.3 was late in notifying the owners that their BES Elements require DDR data by greater than 10 calendar days, but less than or equal to 20 calendar days. | The Reliability Coordinator identified the BES Elements for which DDR data is required as directed by Requirement R5 for more than 60 percent, but less than or equal to 70 percent of the required BES Elements included in Part 5.1. OR The Reliability Coordinator identified the BES Elements for DDR as directed by Requirement R5, Part 5.1 or Part 5.4, but was late by greater than 60 calendar days and less than or equal to 90 calendar days. OR The Reliability Coordinator as directed by Requirement R5, Part 5.3 was late in notifying the owners that their BES Elements require DDR data by greater than 20 calendar days, but less than or equal to 30 calendar days. | The Reliability Coordinator identified the BES Elements for which DDR data is required as directed by Requirement R5 for less than or equal to 60 percent of the required BES Elements included in Part 5.1. OR The Reliability Coordinator identified the BES Elements for DDR as directed by Requirement R5, Part 5.1 or Part 5.4, but was late by greater than 90 calendar days. OR The Reliability Coordinator as directed by Requirement R5, Part 5.3 was late in notifying one or more owners that their BES Elements require DDR data by greater than 30 calendar days. OR The Reliability Coordinator failed to ensure a minimum DDR coverage per Part 5.2. | [12 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-002-4 | R6. | Each Transmission Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: | 2024-04-01 |  | Low | The Transmission Owner had DDR data as directed by Requirement R6, Parts 6.1 through 6.4 that covered more than 80 percent, but less than 100 percent of the total required electrical quantities for all applicable BES Elements. | The Transmission Owner had DDR data as directed by Requirement R6, Parts 6.1 through 6.4 for more than 70 percent, but less than or equal to 80 percent of the total required electrical quantities for all applicable BES Elements. | The Transmission Owner had DDR data as directed by Requirement R6, Parts 6.1 through 6.4 for more than 60 percent, but less than or equal to 70 percent of the total required electrical quantities for all applicable BES Elements. | The Transmission Owner failed to have DDR data as directed by Requirement R6, Parts 6.1 through 6.4 | [18 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002-4 | R7. | Each Generator Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: | 2024-04-01 |  | Low | The Generator Owner had DDR data as directed by Requirement R7, Parts 7.1 through 7.4 that covers more than 80 percent, but less than 100 percent of the total required electrical quantities for all applicable BES Elements. | The Generator Owner had DDR data as directed by Requirement R7, Parts 7.1 through 7.4 for more than 70 percent, but less than or equal to 80 percent of the total required electrical quantities for all applicable BES Elements. | The Generator Owner had DDR data as directed by Requirement R7, Parts 7.1 through 7.4 for more than 60 percent, but less than or equal to 70 percent of the total required electrical quantities for all applicable BES Elements. | The Generator Owner failed to have DDR data as directed by Requirement R7, Parts 7.1 through 7.4. | [5 empty] | GO
Mandatory Subject to Enforcement | PRC | PRC-002-4 | R8. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have continuous data recording and storage. If the equipment was installed prior to the effective date of the Reliability Standard PRC-002-2 2 and is not capable of continuous recording, triggered records must meet the following: | 2024-04-01 |  | Low | The Transmission Owner or Generator Owner had continuous or noncontinuous DDR data, as directed in Requirement R8, for more than 80 percent, but less than 100 percent of the BES Elements they own as determined in Requirement R5. | The Transmission Owner or Generator Owner had continuous or noncontinuous DDR data, as directed in Requirement R8, for more than 70 percent, but less than or equal to 80 percent of the BES Elements they own as determined in Requirement R5. | The Transmission Owner or Generator Owner had continuous or noncontinuous DDR data, as directed in Requirement R8, for more than 60 percent, but less than or equal to 70 percent of the BES Elements they own as determined in Requirement R5. | The Transmission Owner or Generator Owner failed to have continuous or noncontinuous DDR data, as directed in Requirement R8, for the BES Elements they own as determined in Requirement R5. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002-4 | R9. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have DDR data that meet the following: | 2024-04-01 |  | Low | The Transmission Owner or Generator Owner had DDR data that meets more than 80 percent, but less than 100 percent of the total recording properties as specified in Requirement R9. | The Transmission Owner or Generator Owner had DDR data that meets more than 70 percent, but less than or equal to 80 percent of the total recording properties as specified in Requirement R9. | The Transmission Owner or Generator Owner had DDR data that meets more than 60 percent, but less than or equal to 70 percent of the total recording properties as specified in Requirement R9. | The Transmission Owner or Generator Owner had DDR data that meets less than or equal to 60 percent of the total recording properties as specified in Requirement R9. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002-4 | R10. | Each Transmission Owner and Generator Owner shall time synchronize all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to meet the following: | 2024-04-01 |  | Low | The Transmission Owner or Generator Owner had time synchronization per Requirement R10, Parts 10.1 and 10.2 for SER, FR, and DDR data for more than 90 percent, but less than 100 percent of the BES buses identified in Requirement R1 and BES Elements identified in Requirement R5 as directed by Requirement R10. | The Transmission Owner or Generator Owner had time synchronization per Requirement R10, Parts 10.1 and 10.2 for SER, FR, and DDR data for more than 80 percent, but less than or equal to 90 percent of the BES buses identified in Requirement R1 and BES Elements identified in Requirement R5 as directed by Requirement R10. | The Transmission Owner or Generator Owner had time synchronization per Requirement R10, Parts 10.1 and 10.2 for SER, FR, and DDR data for more than 70 percent, but less than or equal to 80 percent of the BES buses identified in Requirement R1 and BES Elements identified in Requirement R5 as directed by Requirement R10. | The Transmission Owner or Generator Owner failed to have time synchronization per Requirement R10, Parts 10.1 and 10.2 for SER, FR, and DDR data for less than or equal to 70 percent of the BES buses identified in Requirement R1 and BES Elements identified in Requirement R5 as directed by Requirement R10. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002-4 | R11. | Each Transmission Owner and Generator Owner shall provide, upon request, all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to the Reliability Coordinator, Regional Entity, or NERC in accordance with the following: | 2024-04-01 |  | Low | The Transmission Owner or Generator Owner as directed by Requirement R11, Part 11.2 provided the requested data more than 30 calendar days, but less than 40 calendar days after the request, unless an extension was granted by the requesting authority. OR The Transmission Owner or Generator Owner as directed by Requirement R11 provided more than 90 percent, but less than 100 percent of the requested data. OR The Transmission Owner or Generator Owner as directed by Requirement R11, Parts 11.3 through 11.5 provided more than 90 percent of the data, but less than 100 percent of the data in the proper data format. | The Transmission Owner or Generator Owner as directed by Requirement R11, Part 11.2 provided the requested data more than 40 calendar days, but less than or equal to 50 calendar days after the request, unless an extension was granted by the requesting authority. OR The Transmission Owner or Generator Owner as directed by Requirement R11 provided more than 80 percent, but less than or equal to 90 percent of the requested data. OR The Transmission Owner or Generator Owner as directed by Requirement R11, Parts 11.3 through 11.5 provided more than 80 percent of the data, but less than or equal to 90 percent of the data in the proper data format. | The Transmission Owner or Generator Owner as directed by Requirement R11, Part 11.2 provided the requested data more than 50 calendar days, but less than or equal to 60 calendar days after the request, unless an extension was granted by the requesting authority. OR The Transmission Owner or Generator Owner as directed by Requirement R11 provided more than 70 percent, but less than or equal to 80 percent of the requested data. OR The Transmission Owner or Generator Owner as directed by Requirement R11, Parts 11.3 through 11.5 provided more than 70 percent of the data, but less than or equal to 80 percent of the data in the proper data format. | The Transmission Owner or Generator Owner as directed by Requirement R11, Part 11.2 failed to provide the requested data more than 60 calendar days after the request, unless an extension was granted by the requesting authority. OR The Transmission Owner or Generator Owner as directed by Requirement R11 failed to provide less than or equal to 70 percent of the requested data. OR The Transmission Owner or Generator Owner as directed by Requirement R11, Parts 11.3 through 11.5 provided less than or equal to 70 percent of the data in the proper data format. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002-4 | R12. | Each Transmission Owner and Generator Owner shall, within 90 calendar days of the discovery of a failure of the recording capability for the SER, FR or DDR data, either: • Restore the recording capability, or • Submit a Corrective Action Plan (CAP) to the Regional Entity and implement it. | 2024-04-01 |  | Low | The Transmission Owner or Generator Owner as directed by Requirement R12 reported a failure and provided a Corrective Action Plan to the Regional Entity more than 90 calendar days, but less than or equal to 100 calendar days after discovery of the failure. | The Transmission Owner or Generator Owner as directed by Requirement R12 reported a failure and provided a Corrective Action Plan to the Regional Entity more than 100 calendar days, but less than or equal to 110 calendar days after discovery of the failure. | The Transmission Owner or Generator Owner as directed by Requirement R12 reported a failure and provided a Corrective Action Plan to the Regional Entity more than 110 calendar days, but less than or equal to 120 calendar days after discovery of the failure. OR The Transmission Owner or Generator Owner as directed by Requirement R12 submitted a CAP to the Regional Entity but failed to implement it | The Transmission Owner or Generator Owner as directed by Requirement R12 failed to report a failure and provide a Corrective Action Plan to the Regional Entity more than 120 calendar days after discovery of the failure. OR Transmission Owner or Generator Owner as directed by Requirement R12 failed to restore the recording capability and failed to submit a CAP to the Regional Entity. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-002-4 | R13. | Each Transmission Owner and Generator Owner shall: | 2024-04-01 |  | Low | N/A | The Transmission Owner or Generator Owner had data, as applicable, for the BES buses identified during the re-evaluation per Requirement R1, Part 1.3 and was late by less than or equal to 6 months. OR The Transmission Owner or Generator Owner had data, as applicable, for the BES Elements identified during the re-evaluation per Requirement R5, Part 5.4 and was late by less than or equal to 6 months. | The Transmission Owner or Generator Owner had data, as applicable, for the BES buses identified during the re-evaluation per Requirement R1, Part 1.3 and was late by greater than 6 months but less than or equal to 12 months. OR The Transmission Owner or Generator Owner had data, as applicable, for the BES Elements identified during the re-evaluation per Requirement R5, Part 5.4 and was late by greater than 6 months but less than or equal to 12 months | The Transmission Owner or Generator Owner had data, as applicable, for the BES buses identified during the re-evaluation per Requirement R1, Part 1.3 and was late by greater than 12 months. OR The Transmission Owner or Generator Owner had data, as applicable, for the BES Elements identified during the re-evaluation per Requirement R5, Part 5.4 and was late by greater than 12 months. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-002-NPCC-01 | R1. | Each Transmission Owner and Generator Owner shall provide Sequence of Event (SOE) recording capability by installing Sequence of Event recorders or as part of another device, such as a Supervisory Control And Data Acquisition (SCADA) Remote Terminal Unit (RTU), a generator plant Digital (or Distributed) Control System (DCS) or part of Fault recording equipment. This capability shall: | 2013-10-20 | 2016-07-01 | Medium | The Transmission Owner or Generator Owner provided the Sequence of Event recording capability meeting the bulk of R1 but missed up to and including 10% of the total set, which is the product of the total number of locations in 1.1 times the total number of parameters in 1.2. | The Transmission Owner or Generator Owner provided the Sequence of Event recording capability meeting the bulk of R1 but missed more than 10% and up to and including 20% of the total set, which is the product of the total number of locations in 1.1 times the total number of parameters in 1.2. | The Transmission Owner or Generator Owner provided the Sequence of Event recording capability meeting the bulk of R1 but missed more than 20% and up to and including 30% of the total set, which is the product of the total number of locations in 1.1 times the total number of parameters in 1.2. | The Transmission Owner or Generator Owner provided the Sequence of Event recording capability meeting the bulk of R1 but missed more than 30% of the total set, which is the product of the total number of locations in 1.1 times the total number of parameters in 1.2. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-002-NPCC-01 | R2. | Each Transmission Owner shall provide Fault recording capability for the following Elements at facilities where Fault recording equipment is required to be installed as per R3: | 2013-10-20 | 2016-07-01 | Medium | The Transmission Owner provided the Fault recording capability meeting the bulk of R2 but missed up to and including 10% of the total set, which is the total number of Elements at all locations required to be installed as per R3 that meet the criteria listed in 2.1 through 2.6. | The Transmission Owner provided the Fault recording capability meeting the bulk of R2 but missed more than 10% and up to and including 20% of the total set, which is the total number of Elements at all locations required to be installed as per R3 that meet the criteria listed in 2.1 through 2.6. | The Transmission Owner provided the Fault recording capability meeting the bulk of R2 but missed more than 20% and up to and including 30% of the total set, which is the total number of Elements at all locations required to be installed as per R3 that meet the criteria listed in 2.1 through 2.6. | The Transmission Owner provided the Fault recording capability meeting the bulk of R2 but missed more than 30% of the total set, which is the total number of Elements at all locations required to be installed as per R3 that meet the criteria listed in 2.1 through 2.6. | [18 empty] | TO
Inactive | PRC | PRC-002-NPCC-01 | R3. | Each Transmission Owner shall have Fault recording capability that determines the Current Zero Time for loss of Bulk Electric System (BES) transmission Elements. | 2013-10-20 | 2016-07-01 | Medium | N/A | N/A | N/A | The Transmission Owner failed to provide fault recording capability that determines the current zero time for loss of transmission Elements. | [18 empty] | TO
Inactive | PRC | PRC-002-NPCC-01 | R4. | Each Generator Owner shall provide Fault recording capability for Generating Plants at and above 200 MVA Capacity and connected through a generator step up (GSU) transformer to a Bulk Electric System Element unless Fault recording capability is already provided by the Transmission Owner. | 2013-10-20 | 2016-07-01 | Medium | The Generator Owner failed to provide Fault recording capability at up to and including 10% of its Generating Plants at and above 200 MVA Capacity and connected to a Bulk Electric System Element if Fault recording capability for that portion of the system is inadequate. | The Generator Owner failed to provide Fault recording capability at more than 10% and up to and including 20% of its Generating Plants at and above 200 MVA Capacity and connected to a Bulk Electric System Element if Fault recording capability for that portion of the system is inadequate. | The Generator Owner failed to provide Fault recording capability at more than 20% and up to 30% of its Generating Plants at and above 200 MVA Capacity and connected to a Bulk Electric System Element if Fault recording capability for that portion of the system is inadequate. | The Generator Owner failed to provide Fault recording capability at more than 30% of its Generating Plants at and above 200 MVA Capacity and connected to a Bulk Electric System Element if Fault recording capability for that portion of the system is inadequate. | [5 empty] | GO
Inactive | PRC | PRC-002-NPCC-01 | R5. | Each Transmission Owner and Generator Owner shall record for Faults, sufficient electrical quantities for each monitored Element to determine the following: | 2013-10-20 | 2016-07-01 | Medium | The Transmission Owner or Generator Owner failed to record for the Faults up to and including 10% of the total set of parameters, which is the product of the total number of monitored Elements and the number of parameters listed in 5.1 through 5.5. | The Transmission Owner or Generator Owner failed to record for the Faults more than 10% and up to and including 20% of the total set of parameters, which is the product of the total number of monitored Elements and the number of parameters listed in 5.1 through 5.5. | The Transmission Owner or Generator Owner failed to record for the Faults more than 20% and up to and including 30% of the total set of parameters, which is the product of the total number of monitored Elements and the number of parameters listed in 5.1 through 5.5. | The Transmission Owner or Generator Owner failed to record for the Faults more than 30% of the total set of parameters, which is the product of the total number of monitored Elements and the number of parameters listed in 5.1 through 5.5. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-002-NPCC-01 | R6. | Each Transmission Owner and Generator Owner shall provide Fault recording with the following capabilities: | 2013-10-20 | 2016-07-01 | Medium | The Transmission Owner or Generator Owner failed to provide Fault recording capability for up to and including 10% of the total set of requirements, which is the product of the total number of monitored Elements and the total number of capabilities identified in 6.1through 6.2. OR Failed to document additional triggers or deviations from the settings stipulated in 6.3 through 6.4 for up to 2 locations. | The Transmission Owner or Generator Owner failed to provide Fault recording capability for more than 10% and up to and including 20% of the total set of requirements, which is the product of the total number of monitored Elements and the total number of capabilities identified in 6.1 through 6.2. OR Failed to document additional triggers or deviations from the settings stipulated in 6.3 through 6.4 for more than two (2) and up to and including five (5) locations. | The Transmission Owner or Generator Owner failed to provide Fault recording capability for more than 20% and up to and including 30% of the total set of requirements, which is the product of the total number of monitored Elements and the total number of 6.1 through 6.2. OR Failed to document additional triggers or deviations from the settings stipulated in6.3 through 6.4 for more than five (5) and up to and including ten (10) locations. | The Transmission Owner or Generator Owner failed to provide Fault recording capability for more than 30% of the total set of requirements, which is the product of the total number of monitored Elements and the total number of capabilities identified in 6.1 through 6.2. OR Failed to document additional triggers or deviations from the settings stipulated in 6.3 through 6.4 for more than ten (10) locations. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-002-NPCC-01 | R7. | Each Reliability Coordinator shall establish its area’s requirements for Dynamic Disturbance Recording (DDR) capability that: | 2013-10-20 | 2016-07-01 | Medium | The Reliability Coordinator failed to establish its area’s requirements for up to and including 10% of the required DDR coverage for its area as per 7.1and 7.2. | The Reliability Coordinator failed to establish its area’s requirements for more than 10% and up to and including 20% of the required DDR coverage for its area as per 7.1 and 7.2. | The Reliability Coordinator failed to establish its area’s requirements for more than 20% and up to and including 30% of the required DDR coverage for its area as per 7.1 and 7.2. | The Reliability Coordinator failed to establish its area’s requirements for more than 30% of the required DDR coverage for its area as per 7.1 and 7.2. | [12 empty] | RC
Inactive | PRC | PRC-002-NPCC-01 | R8. | Each Reliability Coordinator shall specify that DDRs installed, after the approval of this standard, function as continuous recorders. | 2013-10-20 | 2016-07-01 | Medium | N/A | N/A | N/A | The Reliability Coordinator failed to specify that DDRs installed function as continuous recorders. | [12 empty] | RC
Inactive | PRC | PRC-002-NPCC-01 | R9. | Each Reliability Coordinator shall specify that DDRs are installed with the following capabilities: | 2013-10-20 | 2016-07-01 | Medium | N/A | N/A | N/A | The Reliability Coordinator failed to specify that DDRs are installed without the capabilities listed in 9.1 through 9.3. | [12 empty] | RC
Inactive | PRC | PRC-002-NPCC-01 | R10. | Each Reliability Coordinator shall establish requirements such that the following quantities are monitored or derived where DDRs are installed: | 2013-10-20 | 2016-07-01 | Medium | N/A | N/A | N/A | The Reliability Coordinator failed to ensure that the quantities listed in 10.1 through 10.5 are derived where DDRs are installed. | [12 empty] | RC
Inactive | PRC | PRC-002-NPCC-01 | R11. | Each Reliability Coordinator shall document additional settings and deviations from the required trigger settings described in R9 and the required list of monitored quantities as described in R10, and report this to the Regional Entity (RE) upon request. | 2013-10-20 | 2016-07-01 | Low | The Reliability Coordinator failed to document and report to the Regional Entity upon request additional settings and deviations from the required trigger settings described in R9 and the required list of monitored quantities as described in R10 for up to two (2) facilities within the Reliability Coordinator’s area that have a DDR. | The Reliability Coordinator failed to document and report to the Regional Entity upon request additional settings and deviations from the required trigger settings described in R9 and the required list of monitored quantities as described in R10 for more than two (2) and up to five (5) facilities within the Reliability Coordinator’s area that have a DDR. | The Reliability Coordinator failed to document and report to the Regional Entity upon request additional settings and deviations from the required trigger settings described in R9 and the required list of monitored quantities as described in R10 for more than five (5) and up to ten (10) facilities within the Reliability Coordinator’s area that have a DDR. | The Reliability Coordinator failed to document and report to the Regional Entity upon request additional settings and deviations from the required trigger settings described in R9 and the required list of monitored quantities as described in R10 for more than ten (10) facilities within the Reliability Coordinator’s area that have a DDR. | [12 empty] | RC
Inactive | PRC | PRC-002-NPCC-01 | R12. | Each Reliability Coordinator shall specify its DDR requirements including the DDR setting triggers established in R9 to the Transmission Owners and Generator Owners. | 2013-10-20 | 2016-07-01 | Medium | N/A | N/A | N/A | The Reliability Coordinator failed to specify to the Transmission Owners and Generator Owners its DDR requirements including the DDR setting triggers established in R9 but missed established setting triggers. | [12 empty] | RC
Inactive | PRC | PRC-002-NPCC-01 | R13. | Each Transmission Owner and Generator Owner that receives a request from the Reliability Coordinator to install a DDR shall acquire and install the DDR in accordance with R12. Reliability Coordinators, Transmission Owners, and Generator Owners shall mutually agree on an implementation schedule. | 2013-10-20 | 2016-07-01 | Medium | The Transmission Owner or Generator Owner failed to comply with the Reliability Coordinator’s request installing the DDR in accordance with R12 for up to and including 10% of the requirement set of the Reliability Coordinator’s request to install DDRs, with the requirement set being the total number of DDRs requested times the number of setting triggers specified for each DDR. | The Transmission Owner or Generator Owner failed to comply with the Reliability Coordinator’s request installing the DDR in accordance with R12 for more than 10% and up to 20% of the requirement set requested by the Reliability Coordinator for installing DDRs, with the requirement set being the total number of DDRs requested times the number of setting triggers specified for each DDR. | The Transmission Owner or Generator Owner failed to comply with the Reliability Coordinator’s request installing the DDR in accordance with R12 for more than 20% and up to 30% of the requirement set requested by the Reliability Coordinator for installing DDRs, with the requirement set being the total number of DDRs requested times the number of setting triggers specified for each DDR. | The Transmission Owner or Generator Owner failed to comply with the Reliability Coordinator’s request installing the DDR in accordance with R12 for more than 30% of the requirement set requested by the Reliability Coordinator and installing DDRs, with the requirement set being the total number of DDRs requested times the number of setting triggers specified for each DDR OR The Reliability Coordinator, Transmission Owners, and Generator Owners failed to mutually agree on an implementation schedule. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002-NPCC-01 | R14. | Each Transmission Owner and Generator Owner shall establish a maintenance and testing program for stand alone DME (equipment whose only purpose is disturbance monitoring) that includes: [See standard for list of inclusions] | 2013-10-20 | 2016-07-01 | Medium | The Transmission Owner or Generator Owner established a maintenance and testing program for stand alone DME but provided incomplete data for any one (1) of 14.1 through 14.7. | The Transmission Owner or Generator Owner established a maintenance and testing program for stand alone DME but provided incomplete data for more than one (1) and up to and including three (3) of 14.1 through 14.7. | The Transmission Owner or Generator Owner established a maintenance and testing program for stand alone DME but provided incomplete data for more than three (3) and up to and including six (6) of 14.1 through 14.7. | The Transmission Owner or Generator Owner did not establish any maintenance and testing program for DME; OR The Transmission Owner or Generator Owner established a maintenance and testing program for DME but did not provide any data that meets all of 14.1 through 14.7. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-002-NPCC-01 | R15. | Each Reliability Coordinator, Transmission Owner and Generator Owner shall share data within 30 days upon request. Each Reliability Coordinator, Transmission Owner, and Generator Owner shall provide recorded disturbance data from DMEs within 30 days of receipt of the request in each of the following cases: | 2013-10-20 | 2016-07-01 | Low | The Reliability Coordinator, Transmission Owner or Generator Owner provided recorded disturbance data from DMEs but was late for up to and including fifteen (15) days in meeting the requests of an entity, or entities in 15.1, or 15.2. | The Reliability Coordinator, Transmission Owner or Generator Owner provided recorded disturbance data from DMEs but was late for more than fifteen (15) days but less than and including thirty (30) days in meeting the requests of an entity, or entities in 15.1 or 15.2. | The Reliability Coordinator, Transmission Owner or Generator Owner provided recorded disturbance data from DMEs but was late for more than 30 days but less than and including forty-five (45) days in meeting the requests of an entity, or entities in 15.1 or 15.2. | The Reliability Coordinator, Transmission Owner or Generator Owner provided recorded disturbance data from DMEs but was late for more than forty-five (45) days in meeting the requests of an entity, or entities in 15.1 or 15.2. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002-NPCC-01 | R16. | Each Reliability Coordinator, Transmission Owner and Generator Owner shall submit the data files conforming to the following format requirements: | 2013-10-20 | 2016-07-01 | Low | The Reliability Coordinator, Transmission Owner or Generator Owner failed to submit up to and including two (2) data files in a format that meets the applicable format requirements in 16.1 through 16.3. | The Reliability Coordinator, Transmission Owner or Generator Owner failed to submit more than two (2) and up to and including five (5) data files in a format that meets the applicable format requirements in 16.1 through 16.3. | The Reliability Coordinator, Transmission Owner or Generator Owner failed to submit more than five (5) and up to and including ten (10) data files in a format that meets the applicable format requirements in 16.1 through 16.3. | The Reliability Coordinator, Transmission Owner or Generator Owner failed to submit more than ten (10) data files in a format that meets the applicable format requirements in 16.1 through 16.3. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-002-NPCC-01 | R17. | Each Reliability Coordinator, Transmission Owner and Generator Owner shall maintain, record and provide to the Regional Entity (RE), upon request, the following data on the DMEs installed to meet this standard: | 2013-10-20 | 2016-07-01 | Low | The Reliability Coordinator, Transmission Owner or Generator Owner failed to maintain or provide to the Regional Entity , upon request up to and including two (2) of the items in 17.1 through 17.8. | The Reliability Coordinator, Transmission Owner or Generator Owner failed to maintain or provide to the Regional Entity , upon request more than two (2) and up to and including four (4) of the items in 17.1 to 17.8. | The Reliability Coordinator, Transmission Owner or Generator Owner failed to maintain or provide to the Regional Entity , upon request more than four (4) and up to and including six (6) of the items in 17.1 through 17.8. | The Reliability Coordinator, Transmission Owner or Generator Owner failed to maintain or provide to the Regional Entity , upon request more than six (6) of the items in 17.1 through 17.8. | [5 empty] | GO | [6 empty] | RC | [5 empty] | TO
Inactive | PRC | PRC-003-0 | R1. | Each Regional Reliability Organization shall have a procedure for the monitoring, review, analysis, and correction of all transmission protection system misoperations. Each Regional Reliability Organization’s procedure shall include the following elements: |  | 2006-05-01 | [20 empty] | RRO
Inactive | PRC | PRC-003-0 | R2. | Each Regional Reliability Organization shall maintain documentation of its procedure and provide it to NERC on request (within 30 calendar days). |  | 2006-05-01 | [20 empty] | RRO
Inactive | PRC | PRC-003-1 | R1. | Each Regional Reliability Organization shall establish, document and maintain its procedures for, review, analysis, reporting and mitigation of transmission and generation Protection System Misoperations. These procedures shall include the following elements: |  | 2016-06-30 | [20 empty] | RRO
Inactive | PRC | PRC-003-1 | R2. | Each Regional Reliability Organization shall maintain and periodically update documentation of its procedures for review, analysis, reporting, and mitigation of transmission and generation Protection System Misoperations. |  | 2016-06-30 | [20 empty] | RRO
Inactive | PRC | PRC-003-1 | R3. | Each Regional Reliability Organization shall distribute procedures in Requirement 1 and any changes to those procedures, to the affected Transmission Owners, Distribution Providers that own transmission Protection Systems, and Generator Owners within 30 calendar days of approval of those procedures. |  | 2016-06-30 | [20 empty] | RRO
Inactive | PRC | PRC-004-0 | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall analyze all protection system misoperations and shall take corrective actions to avoid future misoperations. |  | 2006-08-01 | [7 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-0 | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall provide to its affected Regional Reliability Organization and NERC on request (within 30 calendar days) documentation of the misoperations analyses and corrective actions according to the Regional Reliability Organization’s procedures of Reliability Standard PRC-003-0_R1. |  | 2006-08-01 | [7 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-1 | R1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Reliability Organization’s procedures developed for Reliability Standard PRC-003 Requirement 1. | 2007-06-18 | 2011-09-25 | High | Documentation of Misoperations is complete, but | Documentation of Misoperations is incomplete, and | Documentation of Misoperations is incomplete, and | Misoperations have not been analyzed |  |  | DP | [15 empty] | TO
Inactive | PRC | PRC-004-1 | R2. | The Generator Owner shall analyze its generator Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Reliability Organization’s procedures developed for PRC-003 R1. | 2007-06-18 | 2011-09-25 | High | Documentation of Misoperations is complete, but | Documentation of Misoperations is incomplete, and | Documentation of Misoperations is incomplete, and | Misoperations have not been analyzed | [5 empty] | GO
Inactive | PRC | PRC-004-1 | R3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Reliability Organization, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Reliability Organization’s procedures developed for PRC-003 R1. | 2007-06-18 | 2011-09-25 | Low | The responsible entity provided its Regional Reliability Organization with documentation of its Misoperations analyses and its Corrective Action Plans, but did not provide these according to the Regional Reliability Organization’s procedures. |  | The responsible entity provided its Regional Reliability Organization with documentation of its Misoperations analyses but did not provide its Corrective Action Plans. | The responsible entity did not provide its Regional Reliability Organization with documentation of its Misoperations analyses and did not provide its Corrective Action Plans. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-1a | R1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Reliability Organization’s procedures developed for Reliability Standard PRC-003 Requirement 1. | 2011-09-26 | 2012-03-31 | High | Documentation of Misoperations is complete, but | Documentation of Misoperations is incomplete, and | Documentation of Misoperations is incomplete, and | Misoperations have not been analyzed |  |  | DP | [15 empty] | TO
Inactive | PRC | PRC-004-1a | R2. | The Generator Owner shall analyze its generator Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Reliability Organization’s procedures developed for PRC-003 R1. | 2011-09-26 | 2012-03-31 | High | Documentation of Misoperations is complete, but | Documentation of Misoperations is incomplete, and | Documentation of Misoperations is incomplete, and | Misoperations have not been analyzed | [5 empty] | GO
Inactive | PRC | PRC-004-1a | R3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Reliability Organization, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Reliability Organization’s procedures developed for PRC-003 R1. | 2011-09-26 | 2012-03-31 | Low | The responsible entity provided its Regional Reliability Organization with documentation of its Misoperations analyses and its Corrective Action Plans, but did not provide these according to the Regional Reliability Organization’s procedures. |  | The responsible entity provided its Regional Reliability Organization with documentation of its Misoperations analyses but did not provide its Corrective Action Plans. | The responsible entity did not provide its Regional Reliability Organization with documentation of its Misoperations analyses and did not provide its Corrective Action Plans. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-2 | R1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. |  | 2011-09-25 | High | Documentation of Misoperations is complete, but documentation of Corrective Action Plans is incomplete. | Documentation of Misoperations is incomplete, and documentation of Corrective Action Plans is incomplete. | Documentation of Misoperations is incomplete, and there are no associated Corrective Action Plans. | Misoperations have not been analyzed |  |  | DP | [15 empty] | TO
Inactive | PRC | PRC-004-2 | R2. | The Generator Owner shall analyze its generator Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. |  | 2011-09-25 | High | Documentation of Misoperations is complete, but documentation of Corrective Action Plans is incomplete. | Documentation of Misoperations is incomplete, and documentation of Corrective Action Plans is incomplete. | Documentation of Misoperations is incomplete, and there are no associated Corrective Action Plans. | Misoperations have not been analyzed | [5 empty] | GO
Inactive | PRC | PRC-004-2 | R3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures. |  | 2011-09-25 | Low | The responsible entity provided its Regional Reliability Organization with documentation of its Misoperations analyses and its Corrective Action Plans, but did not provide these according to the Regional Reliability Organization’s procedures. | N/A | The responsible entity provided its Regional Reliability Organization with documentation of its Misoperations analyses but did not provide its Corrective Action Plans. | The responsible entity did not provide its Regional Reliability Organization with documentation of its Misoperations analyses and did not provide its Corrective Action Plans. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-2.1a | R1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | 2013-11-25 | 2015-05-28 | High | [6 empty] | DP | [15 empty] | TO
Inactive | PRC | PRC-004-2.1a | R2. | The Generator Owner shall analyze its generator and generator interconnection Facility Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | 2013-11-25 | 2015-05-28 | High | [9 empty] | GO
Inactive | PRC | PRC-004-2.1a | R3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures. | 2013-11-25 | 2015-05-28 | Low | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-2.1(i)a | R1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | 2015-05-29 | 2016-06-30 | [7 empty] | DP | [15 empty] | TO
Inactive | PRC | PRC-004-2.1(i)a | R2. | The Generator Owner shall analyze its generator and generator interconnection Facility Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. • For Misoperations occurring on the Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES facilities, this requirement does not apply. | 2015-05-29 | 2016-06-30 | [10 empty] | GO
Inactive | PRC | PRC-004-2.1(i)a | R3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures. • For Misoperations occurring on the Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES facilities, this requirement does not apply. | 2015-05-29 | 2016-06-30 | [7 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-2a | R1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | 2012-04-01 | 2013-11-24 | High | Documentation of Misoperations is complete, but documentation of Corrective Action Plans is incomplete. | Documentation of Misoperations is incomplete, and documentation of Corrective Action Plans is incomplete. | Documentation of Misoperations is incomplete, and there are no associated Corrective Action Plans. | Misoperations have not been analyzed |  |  | DP | [15 empty] | TO
Inactive | PRC | PRC-004-2a | R2. | The Generator Owner shall analyze its generator Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | 2012-04-01 | 2013-11-24 | High | Documentation of Misoperations is complete, but documentation of Corrective Action Plans is incomplete. | Documentation of Misoperations is incomplete, and documentation of Corrective Action Plans is incomplete. | Documentation of Misoperations is incomplete, and there are no associated Corrective Action Plans. | Misoperations have not been analyzed | [5 empty] | GO
Inactive | PRC | PRC-004-2a | R3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures. | 2012-04-01 | 2013-11-24 | Low | The responsible entity provided its Regional Reliability Organization with documentation of its Misoperations analyses and its Corrective Action Plans, but did not provide these according to the Regional Reliability Organization’s procedures. | N/A | The responsible entity provided its Regional Reliability Organization with documentation of its Misoperations analyses but did not provide its Corrective Action Plans. | The responsible entity did not provide its Regional Reliability Organization with documentation of its Misoperations analyses and did not provide its Corrective Action Plans. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-3 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: | 2016-07-01 | 2016-06-30 | Medium | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 120 calendar days and less than or equal to 150 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 150 calendar days and less than or equal to 165 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 165 calendar days and less than or equal to 180 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 180 calendar days of the BES interrupting device operation. OR The responsible entity failed to identify whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-3 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. | 2016-07-01 | 2016-06-30 | Medium | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 120 calendar days and less than or equal to 150 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 150 calendar days and less than or equal to 165 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 165 calendar days and less than or equal to 180 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 180 calendar days of the BES interrupting device operation. OR The responsible entity failed to notify one or more of the other owner(s) of the Protection System component(s) in accordance with Requirement R2. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-3 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. | 2016-07-01 | 2016-06-30 | Medium | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was less than or equal to 30 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 30 calendar days and less than or equal to 45 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 45 calendar days and less than or equal to 60 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 60 calendar days late. OR The responsible entity failed to identify whether or not a Misoperation of its Protection System component(s) occurred in accordance with Requirement R3. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-3 | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | 2016-07-01 | 2016-06-30 | Medium | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was less than or equal to one calendar quarter late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was greater than one calendar quarter and less than or equal to two calendar quarters late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was greater than two calendar quarters and less than or equal to three calendar quarters late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was more than three calendar quarters late. OR The responsible entity failed to perform investigative action(s) in accordance with Requirement R4. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-3 | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | 2016-07-01 | 2016-06-30 | Medium | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 60 calendar days and less than or equal to 70 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 60 calendar days and less than or equal to 70 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 70 calendar days and less than or equal to 80 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 70 calendar days and less than or equal to 80 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 80 calendar days and less than or equal to 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 80 calendar days and less than or equal to 90 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity failed to develop a CAP or explain in a declaration in accordance with Requirement R5. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity failed to develop an evaluation in accordance with Requirement R5. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-3 | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. | 2016-07-01 | 2016-06-30 | Medium | The responsible entity implemented, but failed to update a CAP, when actions or timetables changed, in accordance with Requirement R6. | N/A | N/A | The responsible entity failed to implement a CAP in accordance with Requirement R6. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-3(i) | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: | 2016-07-01 | 2016-06-30 | High | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 120 calendar days and less than or equal to 150 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 150 calendar days and less than or equal to 165 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 165 calendar days and less than or equal to 180 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 180 calendar days of the BES interrupting device operation. OR The responsible entity failed to identify whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-3(i) | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. | 2016-07-01 | 2016-06-30 | High | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 120 calendar days and less than or equal to 150 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 150 calendar days and less than or equal to 165 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 165 calendar days and less than or equal to 180 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 180 calendar days of the BES interrupting device operation. OR The responsible entity failed to notify one or more of the other owner(s) of the Protection System component(s) in accordance with Requirement R2. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-3(i) | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. | 2016-07-01 | 2016-06-30 | High | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was less than or equal to 30 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 30 calendar days and less than or equal to 45 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 45 calendar days and less than or equal to 60 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 60 calendar days late. OR The responsible entity failed to identify whether or not a Misoperation of its Protection System component(s) occurred in accordance with Requirement R3. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-3(i) | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | 2016-07-01 | 2016-06-30 | High | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was less than or equal to one calendar quarter late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was greater than one calendar quarter and less than or equal to two calendar quarters late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was greater than two calendar quarters and less than or equal to three calendar quarters late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was more than three calendar quarters late. OR The responsible entity failed to perform investigative action(s) in accordance with Requirement R4. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-3(i) | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | 2016-07-01 | 2016-06-30 | High | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 60 calendar days and less than or equal to 70 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 60 calendar days and less than or equal to 70 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 70 calendar days and less than or equal to 80 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 70 calendar days and less than or equal to 80 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 80 calendar days and less than or equal to 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 80 calendar days and less than or equal to 90 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity failed to develop a CAP or explain in a declaration in accordance with Requirement R5. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 90 calendar days of first identifying a cause of the Misoperation.OR The responsible entity failed to develop an evaluation in accordance with Requirement R5. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-3(i) | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. | 2016-07-01 | 2016-06-30 | High | The responsible entity implemented, but failed to update a CAP, when actions or timetables changed, in accordance with Requirement R6. | N/A | N/A | The responsible entity failed to implement a CAP in accordance with Requirement R6. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-4 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: |  | 2016-06-30 | Medium | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 120 calendar days and less than or equal to 150 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 150 calendar days and less than or equal to 165 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 165 calendar days and less than or equal to 180 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 180 calendar days of the BES interrupting device operation. OR The responsible entity failed to identify whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-4 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. |  | 2016-06-30 | Medium | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 120 calendar days and less than or equal to 150 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 150 calendar days and less than or equal to 165 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 165 calendar days and less than or equal to 180 calendar days of the BES interrupting device operation | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 180 calendar days of the BES interrupting device operation. OR The responsible entity failed to notify one or more of the other owner(s) of the Protection System component(s) in accordance with Requirement R2. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-4 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. |  | 2016-06-30 | Medium | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was less than or equal to 30 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 30 calendar days and less than or equal to 45 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 45 calendar days and less than or equal to 60 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 60 calendar days late. OR The responsible entity failed to identify whether or not a Misoperation of its Protection System component(s) occurred in accordance with Requirement R3. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-4 | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. |  | 2016-06-30 | Medium | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was less than or equal to one calendar quarter late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was greater than one calendar quarter and less than or equal to two calendar quarters late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was greater than two calendar quarters and less than or equal to three calendar quarters late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was more than three calendar quarters late. OR The responsible entity failed to perform investigative action(s) in accordance with Requirement R4. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-4 | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. |  | 2016-06-30 | Medium | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 60 calendar days and less than or equal to 70 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 60 calendar days and less than or equal to 70 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 70 calendar days and less than or equal to 80 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 70 calendar days and less than or equal to 80 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 80 calendar days and less than or equal to 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 80 calendar days and less than or equal to 90 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity failed to develop a CAP or explain in a declaration in accordance with Requirement R5. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity failed to develop an evaluation in accordance with Requirement R5. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-4 | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. |  | 2016-06-30 | Medium | The responsible entity implemented, but failed to update a CAP, when actions or timetables changed, in accordance with Requirement R6. | N/A | N/A | The responsible entity failed to implement a CAP in accordance with Requirement R6. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-4(i) | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: | 2016-07-01 | 2017-04-01 | High | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 120 calendar days and less than or equal to 150 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 150 calendar days and less than or equal to 165 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 165 calendar days and less than or equal to 180 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 180 calendar days of the BES interrupting device operation. OR The responsible entity failed to identify whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-4(i) | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. | 2016-07-01 | 2017-04-01 | High | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 120 calendar days and less than or equal to 150 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 150 calendar days and less than or equal to 165 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 165 calendar days and less than or equal to 180 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 180 calendar days of the BES interrupting device operation. OR The responsible entity failed to notify one or more of the other owner(s) of the Protection System component(s) in accordance with Requirement R2. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-4(i) | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. | 2016-07-01 | 2017-04-01 | High | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was less than or equal to 30 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 30 calendar days and less than or equal to 45 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 30 calendar days and less than or equal to 45 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 60 calendar days late. OR The responsible entity failed to identify whether or not a Misoperation of its Protection System component(s) occurred in accordance with Requirement R3. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-4(i) | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | 2016-07-01 | 2017-04-01 | High | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was less than or equal to one calendar quarter late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was greater than one calendar quarter and less than or equal to two calendar quarters late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was greater than two calendar quarters and less than or equal to three calendar quarters late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was more than three calendar quarters late. OR The responsible entity failed to perform investigative action(s) in accordance with Requirement R4. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-4(i) | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: | 2016-07-01 | 2017-04-01 | High | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 60 calendar days and less than or equal to 70 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 60 calendar days and less than or equal to 70 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 70 calendar days and less than or equal to 80 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 70 calendar days and less than or equal to 80 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 80 calendar days and less than or equal to 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 80 calendar days and less than or equal to 90 calendar days of first identifying a cause of the Misoperation. | developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity failed to develop a CAP or explain in a declaration in accordance with Requirement R5. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 90 calendar days of first identifying a cause of the Misoperation.OR The responsible entity failed to develop an evaluation in accordance with Requirement R5. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-4(i) | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. | 2016-07-01 | 2017-04-01 | High | The responsible entity implemented, but failed to update a CAP, when actions or timetables changed, in accordance with Requirement R6. | N/A | N/A | The responsible entity failed to implement a CAP in accordance with Requirement R6. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-5 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: | 2017-04-02 | 2017-04-01 | Medium | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 120 calendar days and less than or equal to 150 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 150 calendar days and less than or equal to 165 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 165 calendar days and less than or equal to 180 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 180 calendar days of the BES interrupting device operation. OR The responsible entity failed to identify whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-5 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. | 2017-04-02 | 2017-04-01 | Medium | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 120 calendar days and less than or equal to 150 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 150 calendar days and less than or equal to 165 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 165 calendar days and less than or equal to 180 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 180 calendar days of the BES interrupting device operation. OR The responsible entity failed to notify one or more of the other owner(s) of the Protection System component(s) in accordance with Requirement R2. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-5 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. | 2017-04-02 | 2017-04-01 | Medium | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was less than or equal to 30 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 30 calendar days and less than or equal to 45 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 45 calendar days and less than or equal to 60 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 60 calendar days late. OR The responsible entity failed to identify whether or not a Misoperation of its Protection System component(s) occurred in accordance with Requirement R3. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-5 | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | 2017-04-02 | 2017-04-01 | Medium | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was less than or equal to one calendar quarter late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was greater than one calendar quarter and less than or equal to two calendar quarters late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was greater than two calendar quarters and less than or equal to three calendar quarters late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was more than three calendar quarters late. OR The responsible entity failed to perform investigative action(s) in accordance with Requirement R4. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-5 | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | 2017-04-02 | 2017-04-01 | Medium | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 60 calendar days and less than or equal to 70 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 60 calendar days and less than or equal to 70 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 70 calendar days and less than or equal to 80 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 70 calendar days and less than or equal to 80 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 80 calendar days and less than or equal to 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 80 calendar days and less than or equal to 90 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity failed to develop a CAP or explain in a declaration in accordance with Requirement R5. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity failed to develop an evaluation in accordance with Requirement R5. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-5 | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. | 2017-04-02 | 2017-04-01 | Medium | The responsible entity implemented, but failed to update a CAP, when actions or timetables changed, in accordance with Requirement R6. | N/A | N/A | The responsible entity failed to implement a CAP in accordance with Requirement R6. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-5(i) | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: | 2017-04-02 | 2021-03-31 | High | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 120 calendar days and less than or equal to 150 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 150 calendar days and less than or equal to 165 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 165 calendar days and less than or equal to 180 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 165 calendar days and less than or equal to 180 calendar days of the BES interrupting device operation. OR The responsible entity failed to identify whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-5(i) | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. | 2017-04-02 | 2021-03-31 | High | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 120 calendar days and less than or equal to 150 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 150 calendar days and less than or equal to 165 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 165 calendar days and less than or equal to 180 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 180 calendar days of the BES interrupting device operation. OR The responsible entity failed to notify one or more of the other owner(s) of the Protection System component(s) in accordance with Requirement R2. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-5(i) | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. | 2017-04-02 | 2021-03-31 | High | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was less than or equal to 30 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 30 calendar days and less than or equal to 45 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 45 calendar days and less than or equal to 60 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 60 calendar days late. OR The responsible entity failed to identify whether or not a Misoperation of its Protection System component(s) occurred in accordance with Requirement R3. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-5(i) | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: • The identification of the cause(s) of the Misoperation; or • A declaration that no cause was identified. | 2017-04-02 | 2021-03-31 | High | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was less than or equal to one calendar quarter late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was greater than one calendar quarter and less than or equal to two calendar quarters late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was greater than two calendar quarters and less than or equal to three calendar quarters late. | The responsible entity performed at least one investigative action in accordance with Requirement R4, but was more than three calendar quarters late. OR The responsible entity failed to perform investigative action(s) in accordance with Requirement R4. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-5(i) | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | 2017-04-02 | 2021-03-31 | High | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 60 calendar days and less than or equal to 70 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 60 calendar days and less than or equal to 70 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 70 calendar days and less than or equal to 80 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 70 calendar days and less than or equal to 80 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 80 calendar days and less than or equal to 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 80 calendar days and less than or equal to 90 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity failed to develop a CAP or explain in accordance with Requirement R5. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity failed to develop an evaluation in accordance with Requirement R5. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-5(i) | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. | 2017-04-02 | 2021-03-31 | High | The responsible entity implemented, but failed to update a CAP, when actions or timetables changed, in accordance with Requirement R6. | N/A | N/A | The responsible entity failed to implement a CAP in accordance with Requirement R6. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004-6 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | 2021-04-01 |  | High | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 120 calendar days and less than or equal to 150 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 150 calendar days and less than or equal to 165 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 165 calendar days and less than or equal to 180 calendar days of the BES interrupting device operation. | The responsible entity identified whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1, but in more than 180 calendar days of the BES interrupting device operation. OR The responsible entity failed to identify whether its Protection System component(s) caused a Misoperation in accordance with Requirement R1. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004-6 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | 2021-04-01 |  | High | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 120 calendar days and less than or equal to 150 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 150 calendar days and less than or equal to 165 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 165 calendar days and less than or equal to 180 calendar days of the BES interrupting device operation. | The responsible entity notified the other owner(s) of the Protection System component(s) in accordance with Requirement R2, but in more than 180 calendar days of the BES interrupting device operation. OR The responsible entity failed to notify one or more of the other owner(s) of the Protection System component(s) in accordance with Requirement R2. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004-6 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | 2021-04-01 |  | High | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was less than or equal to 30 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 30 calendar days and less than or equal to 45 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 45 calendar days and less than or equal to 60 calendar days late. | The responsible entity identified whether or not its Protection System component(s) caused a Misoperation in accordance with Requirement R3, but was greater than 60 calendar days late. OR The responsible entity failed to identify whether or not a Misoperation of its Protection System component(s) occurred in accordance with Requirement R3. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004-6 | R4. | Reserved. | 2021-04-01
Mandatory Subject to Enforcement | PRC | PRC-004-6 | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: High] [Time Horizon: Operations Planning, Long-Term Planning] • Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or • Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | 2021-04-01 |  | High | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 60 calendar days and less than or equal to 70 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 60 calendar days and less than or equal to 70 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 70 calendar days and less than or equal to 80 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 70 calendar days and less than or equal to 80 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 80 calendar days and less than or equal to 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 80 calendar days and less than or equal to 90 calendar days of first identifying a cause of the Misoperation. | The responsible entity developed a CAP, or explained in a declaration in accordance with Requirement R5, but in more than 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity failed to develop a CAP or explain in a declaration in accordance with Requirement R5. OR The responsible entity developed an evaluation in accordance with Requirement R5, but in more than 90 calendar days of first identifying a cause of the Misoperation. OR The responsible entity failed to develop an evaluation in accordance with Requirement R5. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-004-6 | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: High][Time Horizon: Operations Planning, Long-Term Planning] | 2021-04-01 |  | High | The responsible entity implemented, but failed to update a CAP, when actions or timetables changed, in accordance with Requirement R6. | N/A | N/A | The responsible entity failed to implement a CAP in accordance with Requirement R6. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-004-WECC-1 | R1. | System Operators and System Protection personnel of the Transmission Owners and Generator Owners shall analyze all Protection System and RAS operations. | 2011-10-01 | 2017-03-31 | Low | [9 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-004-WECC-1 | R2. | Transmission Owners and Generator Owners shall perform the following actions for each Misoperation of the Protection System or RAS. It is not intended that Requirements R2.1 through R2.4 apply to Protection System and/or RAS actions that appear to be entirely reasonable and correct at the time of occurrence and associated system performance is fully compliant with NERC Reliability Standards. If the Transmission Owner or Generator Owner later finds the Protection System or RAS operation to be incorrect through System Protection personnel analysis, the requirements of R2.1 through R2.4 become applicable at the time the Transmission Owner or Generator Owner identifies the Misoperation: | 2011-10-01 | 2017-03-31 | [10 empty] | GO | [12 empty] | TO | TOP
Inactive | PRC | PRC-004-WECC-1 | R3. | Transmission Owners and Generation Owners shall submit Misoperation incident reports to WECC within 10 business days for the following. [Time Horizon: Operations Assessment] | 2011-10-01 | 2017-03-31 | Low | The Transmission Owner and Generator Owner did not perform the required repairs, replacement, or system operation adjustments to comply with the requirements within 20 business days but did perform the required activities within 25 business days. | The Transmission Owner and Generator Owner did not perform the required repairs, replacement, or system operation adjustment to comply with the requirements within 25 business days but did perform the required activities within 28 business days. | The Transmission Owner and Generator Owner did not perform the required repairs, replacement, or system operation adjustment to comply with the requirements within 28 business days but did perform the required activities within 30 business days. | The Transmission Owner and Generator Owner did not perform the required repairs, replacement, or system operation adjustments to comply with the requirements within 30 business days. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-004-WECC-2 | R1. | System Operators and System Protection personnel of the Transmission Owners and Generator Owners shall analyze all Protection System and RAS operations. | 2017-04-01 | 2021-01-01 | Low | System Operating personnel of the Transmission Owner or Generator Owner did not review the Protection System Operation or RAS operation within 24 hours but did review the Protection System Operation or RAS operation within six business days. | System Operating personnel of the Transmission Owner or Generator Owner did not review the Protection System operation or RAS operation within six business days. | System Protection personnel of the Transmission Owner and Generator Owner did not analyze the Protection System operation or RAS operation within 20 business days but did analyze the Protection System operation or RAS operation within 25 business days. | System Protection personnel of the Transmission Owner or Generator Owner did not analyze the Protection System operation or RAS operation within 25 business days. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-004-WECC-2 | R2. | Transmission Owners and Generator Owners shall perform the following actions for each Misoperation of the Protection System or RAS. It is not intended that Requirements R2.1 through R2.4 apply to Protection System and/or RAS actions that appear to be entirely reasonable and correct at the time of occurrence and associated system performance is fully compliant with NERC Reliability Standards. If the Transmission Owner or Generator Owner later finds the Protection System or RAS operation to be incorrect through System Protection personnel analysis, the requirements of R2.1 through R2.4 become applicable at the time the Transmission Owner or Generator Owner identifies the Misoperation: | 2017-04-01 | 2021-01-01 | High | The Transmission Owner and Generator Owner did not remove from service, repair, or implement other compliance measures for the Protection System or RAS that misoperated as required within 22 hours but did perform the requirements within 24 hours. | The Transmission Owner and Generator Owner did not remove from service, repair, or implement other compliance measures for the Protection System or RAS that misoperated as required in less than 24 hours but did perform the requirements within 28 hours. | The Transmission Owner and Generator Owner did not perform the removal from service, repair, or implement other compliance measures for the Protection System or RAS that misoperated as required in less than 28 hours but did perform the requirements within 32 hours. | The Transmission Owner and Generator Owner did not perform the removal from service, repair, or implement other compliance measures for the Protection System or RAS that misoperated as required within 32 hours. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-004-WECC-2 | R3. | Transmission Owners and Generation Owners shall submit Misoperation incident reports to WECC within 10 business days for the following. | 2017-04-01 | 2021-01-01 | Low | 3.1 The Transmission Owner and Generator Owner did not report the Misoperation and corrective actions taken or planned to comply with the requirements within 10 business days but did perform the required activities within 15 business days. 3.2 The Transmission Owner and Generator Owner did not report the completion of repair or replacement of Protection System and/or RAS that misoperated to comply with the requirements within 10 business days of the completion but did perform the required activities within 15 business days. 3.2 The Transmission Owner and Generator Owner did not report the completion of repair or replacement of Protection System and/or RAS that misoperated to comply with the requirements within 10 business days of the completion but did perform the required activities within 15 business days. | 3.1 The Transmission Owner and Generator Owner did not report the Misoperation and corrective actions taken or planned to comply with the requirements within 15 business days but did perform the required activities within 20 business days. 3.2 The Transmission Owner and Generator Owner did not report the completion of repair or replacement of Protection System and/or RAS that misoperated to comply with the requirements within 15 business days of the completion but did perform the required activities within 20 business days. | 3.1 The Transmission Owner and Generator Owner did not report the Misoperation and corrective actions taken or planned to comply with the requirements within 20 business days but did perform the required activities within 25 business days. 3.2 The Transmission Owner and Generator Owner did not report the completion of repair or replacement of Protection System and/or RAS that misoperated to comply with the requirements within 20 business days of the completion but did perform the required activities within 25 business days. | 3.1 The Transmission Owner and Generator Owner did not report the Misoperation and corrective actions taken or planned to comply with the requirements within 25 business days. 3.2 The Transmission Owner and Generator Owner did not report the completion of repair or replacement of Protection System and/or RAS that misoperated to comply with the requirements within 25 business days of the completion. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-005-0 | R1. | The Transmission Owner, Generator Owner and Distribution Provider that owns a transmission protection system shall have a transmission protection system maintenance and testing program in place. The program(s) shall include: |  | 2006-05-01 | [7 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-0 | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a transmission protection system shall provide documentation of its transmission protection system program and its implementation to the appropriate Regional Reliability Organization and NERC on request (within 30 calendar days). |  | 2006-05-01 | [7 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-1 | R1. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: | 2007-06-18 | 2011-09-25 | High |  |  | The responsible entity that owned a transmission Protection System or Generator Owner that owned a generation Protection System failed to have either a Protection System maintenance program or a Protection System testing program for Protection Systems tha | The responsible entity that owned a transmission Protection System or Generator Owner that owned a generation Protection System failed to have a Protection System maintenance program and a Protection System testing program for Protection Systems that affe |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-1 | R2. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Reliability Organization on request (within 30 calendar days). The documentation of the program implementation shall include: | 2007-06-18 | 2011-09-25 | Low | The responsible entity provided documentation of its Protection System maintenance and testing program for more than 30 but less than or equal to 40 days following a request from its Regional Reliability Organization and/or NERC. | The responsible entity provided documentation of its Protection System maintenance and testing program for more than 40 but less than or equal to 50 days following a request from its Regional Reliability Organization and/or NERC. | The responsible entity provided documentation of its Protection System maintenance and testing program for more than 50 but less than or equal to 60 days following a request from its Regional Reliability Organization and/or NERC. | The responsible entity did not provide documentation of its Protection System maintenance and testing program for more than 60 days following a request from its Regional Reliability Organization and/or NERC. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-005-1.1b | R1. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: | 2013-11-25 | 2027-03-31 | High | [6 empty] | DP | DP-UFLS |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-005-1.1b | R2. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Entity on request (within 30 calendar days). The documentation of the program implementation shall include: | 2013-11-25 | 2027-03-31 | Low | [6 empty] | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-1a | R1. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: | 2011-09-26 | 2012-03-13 | High |  |  | The responsible entity that owned a transmission Protection System or Generator Owner that owned a generation Protection System failed to have either a Protection System maintenance program or a Protection System testing program for Protection Systems tha | The responsible entity that owned a transmission Protection System or Generator Owner that owned a generation Protection System failed to have a Protection System maintenance program and a Protection System testing program for Protection Systems that affe |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-1a | R2. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Reliability Organization on request (within 30 calendar days). The documentation of the program implementation shall include: | 2011-09-26 | 2012-03-13 | Low | The responsible entity provided documentation of its Protection System maintenance and testing program for more than 30 but less than or equal to 40 days following a request from its Regional Reliability Organization and/or NERC. | The responsible entity provided documentation of its Protection System maintenance and testing program for more than 40 but less than or equal to 50 days following a request from its Regional Reliability Organization and/or NERC. | The responsible entity provided documentation of its Protection System maintenance and testing program for more than 50 but less than or equal to 60 days following a request from its Regional Reliability Organization and/or NERC. | The responsible entity did not provide documentation of its Protection System maintenance and testing program for more than 60 days following a request from its Regional Reliability Organization and/or NERC. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-1b | R1. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: | 2012-03-14 | 2013-11-24 | High | [6 empty] | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-1b | R2. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Reliability Organization on request (within 30 calendar days). The documentation of the program implementation shall include: | 2012-03-14 | 2013-11-24 | Low | [6 empty] | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-2 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems identified in Section 4.2. | 2015-04-01 | 2015-05-28 | Medium | The responsible entity’s PSMP failed to specify whether one Component Type is being addressed by time-based maintenance, or a combination of both. (Part 1.1) | The responsible entity’s PSMP failed to specify whether two Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1) | The responsible entity’s PSMP failed to include the applicable monitoring attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. (Part 1.2). | The responsible entity failed to establish a PSMP. OR The responsible entity failed to specify whether three or more Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1) OR The responsible entity’s PSMP failed to include applicable station batteries in a time-based program. (Part 1.1) |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-2 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | 2015-04-01 | 2015-05-28 | Medium | The responsible entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within three years. | N/A | The responsible entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within four years. | The responsible entity uses performance-based maintenance intervals in its PSMP but: 1) Failed to establish the technical justification described within Requirement R2 for the initial use of the performance-based PSMP OR 2) Failed to reduce Countable Events to no more than 4% within five years OR 3) Maintained a Segment with less than 60 Components OR 4) Failed to: • Annually update the list of Components, OR • Annually perform maintenance on the greater of 5% of the segment population or 3 Components, OR • Annually analyze the program activities and results for each Segment. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-2 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes timebased maintenance program(s) shall maintain its Protection System Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | 2015-04-01 | 2015-05-28 | High | For Protection System Components included within a time-based maintenance program, the responsible entity failed to maintain 5% or less of the total Components included within a specific Protection System Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | For Protection System Components included within a time-based maintenance program, the responsible entity failed to maintain more than 5% but 10% or less of the total Components included within a specific Protection System Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | For Protection System Components included within a time-based maintenance program, the responsible entity failed to maintain more than 10% but 15% or less of the total Components included within a specific Protection System Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | For Protection System Components included within a time-based maintenance program, the responsible entity failed to maintain more than 15% of the total Components included within a specific Protection System Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-2 | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System Components that are included within the performance-based program(s). | 2015-04-01 | 2015-05-28 | High | For Protection System Components included within a performance-based maintenance program, the responsible entity failed to maintain 5% or less of the annual scheduled maintenance for a specific Protection System Component Type in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | For Protection System Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 5% but 10% or less of the annual scheduled maintenance for a specific Protection System Component Type in accordance with their performance-based PSMP. | For Protection System Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 10% but 15% or less of the annual scheduled maintenance for a specific Protection System Component Type in accordance with their performance-based PSMP. | For Protection System Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 15% of the annual scheduled maintenance for a specific Protection System Component Type in accordance with their performance-based PSMP. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-2 | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | 2015-04-01 | 2015-05-28 | Medium | The responsible entity failed to undertake efforts to correct 5 or fewer identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 5, but less than or equal to 10 identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 10, but less than or equal to 15 identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 15 identified Unresolved Maintenance Issues. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-2(i) | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems identified in Section 4.2. The PSMP shall: | 2015-05-29 | 2016-12-31 | Medium | The responsible entity’s PSMP failed to specify whether one Component Type is being addressed by time- based or performance-based maintenance, or a combination of both. (Part 1.1) | The responsible entity’s PSMP failed to specify whether two Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1) | The responsible entity’s PSMP failed to include the applicable monitoring attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. (Part 1.2). | The responsible entity failed to establish a PSMP. OR The responsible entity failed to specify whether three or more Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1). OR The responsible entity’s PSMP failed to include applicable station batteries in a time-based program. (Part 1.1) |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-2(i) | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | 2015-05-29 | 2016-12-31 | Medium | The responsible entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within three years. | N/A | The responsible entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within four years. | The responsible entity uses performance-based maintenance intervals in its PSMP but: 1) Failed to establish the technical justification described within Requirement R2 for the initial use of the performance-based PSMP OR 2) Failed to reduce Countable Events to no more than 4% within five years OR 3) Maintained a Segment with less than 60 Components OR 4) Failed to: • Annually update the list of Components, OR • Annually perform maintenance on the greater of 5% of the segment population or 3 Components, OR • Annually analyze the program activities and results for each Segment. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-2(i) | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | 2015-05-29 | 2016-12-31 | High | For Protection System Components included within a time-based maintenance program, the responsible entity failed to maintain 5% or less of the total Components included within a specific Protection System Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | For Protection System Components included within a time-based maintenance program, the responsible entity failed to maintain more than 5% but 10% or less of the total Components included within a specific Protection System Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | For Protection System Components included within a time-based maintenance program, the responsible entity failed to maintain more than 10% but 15% or less of the total Components included within a specific Protection System Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | For Protection System Components included within a time-based maintenance program, the responsible entity failed to maintain more than 15% of the total Components included within a specific Protection System Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-2(i) | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System Components that are included within the performance-based program(s). | 2015-05-29 | 2016-12-31 | High | For Protection System Components included within a performance-based maintenance program, the responsible entity failed to maintain 5% or less of the annual scheduled maintenance for a specific Protection System Component Type in accordance with their performance- based PSMP. | For Protection System Components included within a performance- based maintenance program, the responsible entity failed to maintain more than 5% but 10% or less of the annual scheduled maintenance for a specific Protection System Component Type in accordance with their performance-based PSMP. | For Protection System Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 10% but 15% or less of the annual scheduled maintenance for a specific Protection System Component Type in accordance with their performance-based PSMP. | For Protection System Components included within a performance- based maintenance program, the responsible entity failed to maintain more than 15% of the annual scheduled maintenance for a specific Protection System Component Type in accordance with their performance-based PSMP. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-2(i) | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | 2015-05-29 | 2016-12-31 | Medium | The responsible entity failed to undertake efforts to correct 5 or fewer identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 5, but less than or equal to 10 identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 10, but less than or equal to 15 identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 15 identified Unresolved Maintenance Issues. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-2(ii) | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems identified in Section 4.2. The PSMP shall: | 2017-04-01 | 2015-12-31 | Medium | The responsible entity’s PSMP failed to specify whether one Component Type is being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1) | The responsible entity’s PSMP failed to specify whether two Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1) | The responsible entity’s PSMP failed to include the applicable monitoring attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. (Part 1.2). | The responsible entity failed to establish a PSMP. OR The responsible entity failed to specify whether three or more Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1). OR The responsible entity’s PSMP failed to include applicable station batteries in a time-based program. (Part 1.1) |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-2(ii) | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | 2017-04-01 | 2015-12-31 | Medium | The responsible entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within three years. | N/A | The responsible entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within four years. | The responsible entity uses performance-based maintenance intervals in its PSMP but: 1) Failed to establish the technical justification described within Requirement R2 for the initial use of the performance-based PSMP OR 2) Failed to reduce Countable Events to no more than 4% within five years OR 3) Maintained a Segment with less than 60 Components OR 4) Failed to: • Annually update the list of Components, OR • Annually perform maintenance on the greater of 5% of the segment population or 3 Components, OR • Annually analyze the program activities and results for each Segment. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-2(ii) | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | 2017-04-01 | 2015-12-31 | High | For Protection System Components included within a time-based maintenance program, the responsible entity failed to maintain 5% or less of the total Components included within a specific Protection System Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | For Protection System Components included within a time-based maintenance program, the responsible entity failed to maintain more than 5% but 10% or less of the total Components included within a specific Protection System Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | For Protection System Components included within a time-based maintenance program, the responsible entity failed to maintain more than 10% but 15% or less of the total Components included within a specific Protection System Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | For Protection System Components included within a time-based maintenance program, the responsible entity failed to maintain more than 15% of the total Components included within a specific Protection System Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-2(ii) | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System Components that are included within the performance-based program(s). | 2017-04-01 | 2015-12-31 | High | For Protection System Components included within a performance-based maintenance program, the responsible entity failed to maintain 5% or less of the annual scheduled maintenance for a specific Protection System Component Type in accordance with their performance-based PSMP. | For Protection System Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 5% but 10% or less of the annual scheduled maintenance for a specific Protection System Component Type in accordance with their performance-based PSMP. | For Protection System Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 10% but 15% or less of the annual scheduled maintenance for a specific Protection System Component Type in accordance with their performance-based PSMP. | For Protection System Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 15% of the annual scheduled maintenance for a specific Protection System Component Type in accordance with their performance-based PSMP. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-2(ii) | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | 2017-04-01 | 2015-12-31 | Medium | The responsible entity failed to undertake efforts to correct 5 or fewer identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 5, but less than or equal to 10 identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 10, but less than or equal to 15 identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 15 identified Unresolved Maintenance Issues. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-3 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems and Automatic Reclosing identified in Facilities Section 4.2. |  | 2015-12-31 | Medium | The responsible entity’s PSMP failed to specify whether one Component Type is being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1) | The responsible entity’s PSMP failed to specify whether two Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1) | The responsible entity’s PSMP failed to specify whether three Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1). OR The responsible entity’s PSMP failed to include the applicable monitoring attributes applied to each Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Tables 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Components. (Part 1.2). | The responsible entity failed to establish a PSMP. OR The responsible entity’s PSMP failed to specify whether four or more Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1). |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-3 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. |  | 2015-12-31 | Medium | The responsible entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within three years. | N/A | The responsible entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within four years. | The responsible entity uses performance-based maintenance intervals in its PSMP but: 1) Failed to establish the technical justification described within Requirement R2 for the initial use of the performance-based PSMP OR 2) Failed to reduce Countable Events to no more than 4% within five years OR 3) Maintained a Segment with less than 60 Components OR 4) Failed to: • Annually update the list of Components, OR • Annually perform maintenance on the greater of 5% of the Segment population or 3 Components, OR • Annually analyze the program activities and results for each Segment. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-3 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System and Automatic Reclosing Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. |  | 2015-12-31 | High | For Components included within a time-based maintenance program, the responsible entity failed to maintain 5% or less of the total Components included within a specific Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Tables 4-1 through 4-2. | For Components included within a time-based maintenance program, the responsible entity failed to maintain more than 5% but 10% or less of the total Components included within a specific Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Tables 4-1 through 4-2. | For Components included within a time-based maintenance program, the responsible entity failed to maintain more than 10% but 15% or less of the total Components included within a specific Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Tables 4-1 through 4-2. | For Components included within a time-based maintenance program, the responsible entity failed to maintain more than 15% of the total Components included within a specific Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Tables 4-1 through 4-2. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-3 | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System and Automatic Reclosing Components that are included within the performance-based program(s). |  | 2015-12-31 | High | For Components included within a performance-based maintenance program, the responsible entity failed to maintain 5% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 5% but 10% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 10% but 15% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 15% of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-3 | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. |  | 2015-12-31 | Medium | The responsible entity failed to undertake efforts to correct 5 or fewer identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 5, but less than or equal to 10 identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 10, but less than or equal to 15 identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 15 identified Unresolved Maintenance Issues. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-3(i) | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems and Automatic Reclosing identified in Facilities Section 4.2. |  | 2015-12-31 | Medium | The responsible entity’s PSMP failed to specify whether one Component Type is being addressed by timebased or performance-based maintenance, or a combination of both. (Part 1.1) | The responsible entity’s PSMP failed to specify whether two Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1) | The responsible entity’s PSMP failed to specify whether three Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1). OR The responsible entity’s PSMP failed to include the applicable monitoring attributes applied to each Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Tables 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Components. (Part 1.2). | The responsible entity failed to establish a PSMP. OR The responsible entity’s PSMP failed to specify whether four or more Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1). OR The responsible entity’s PSMP failed to include applicable station batteries in a time-based program. (Part 1.1) |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-3(i) | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. |  | 2015-12-31 | Medium | The responsible entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within three years. | N/A | The responsible entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within four years. | The responsible entity uses performance-based maintenance intervals in its PSMP but: 1) Failed to establish the technical justification described within Requirement R2 for the initial use of the performance-based PSMP OR 2) Failed to reduce Countable Events to no more than 4% within five years OR 3) Maintained a Segment with less than 60 Components OR 4) Failed to: • Annually update the list of Components, OR • Annually perform maintenance on the greater of 5% of the Segment population or 3 Components, OR • Annually analyze the program activities and results for each Segment. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-3(i) | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System and Automatic Reclosing Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. |  | 2015-12-31 | High | For Components included within a time-based maintenance program, the responsible entity failed to maintain 5% or less of the total Components included within a specific Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Tables 4-1 through 4-2. | For Components included within a time-based maintenance program, the responsible entity failed to maintain more than 5% but 10% or less of the total Components included within a specific Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Tables 4-1 through 4-2. | For Components included within a time-based maintenance program, the responsible entity failed to maintain more than 10% but 15% or less of the total Components included within a specific Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Tables 4-1 through 4-2. | For Components included within a time-based maintenance program, the responsible entity failed to maintain more than 15% of the total Components included within a specific Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Tables 4-1 through 4-2. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-3(i) | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System and Automatic Reclosing Components that are included within the performance-based program(s). |  | 2015-12-31 | High | For Components included within a performance-based maintenance program, the responsible entity failed to maintain 5% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 5% but 10% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 10% but 15% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 15% of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-3(i) | R5. | R5. Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. |  | 2015-12-31 | Medium | The responsible entity failed to undertake efforts to correct 5 or fewer identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 5, but less than or equal to 10 identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 10, but less than or equal to 15 identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 15 identified Unresolved Maintenance Issues |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-3(ii) | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems and Automatic Reclosing identified in Facilities Section 4.2. | 2017-04-01 | 2015-12-31 | Medium | The responsible entity’s PSMP failed to specify whether one Component Type is being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1) | The responsible entity’s PSMP failed to specify whether two Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1) | The responsible entity’s PSMP failed to specify whether three Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1). OR The responsible entity’s PSMP failed to include the applicable monitoring attributes applied to each Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Tables 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Components. (Part 1.2). | The responsible entity failed to establish a PSMP. OR The responsible entity’s PSMP failed to specify whether four or more Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1). OR The responsible entity’s PSMP failed to include applicable station batteries in a time-based program. (Part 1.1) |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-3(ii) | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | 2017-04-01 | 2015-12-31 | Medium | The responsible entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within three years. | N/A | The responsible entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within four years. | The responsible entity uses performance-based maintenance intervals in its PSMP but: 1) Failed to establish the technical justification described within Requirement R2 for the initial use of the preformance-based PSMP OR 2) Failed to reduce Countable Events to no more than 4% within five years OR 3) Maintained a Segment with less than 60 Components OR 4) Failed to: • Annually update the list of Components, • Annually perform maintenance on the greater of 5% of the Segment population or 3 Components, OR • Annually analyze the program activities and results for each Segment. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-3(ii) | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System and Automatic Reclosing Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. | 2017-04-01 | 2015-12-31 | High | For Components included within a time-based maintenance program, the responsible entity failed to maintain 5% or less of the total Components included within a specific Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Tables 4-1 through 4-2. | For Components included within a time-based maintenance program, the responsible entity failed to maintain more than 5% but 10% or less of the total Components included within a specific Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Tab e 3, and Tables 4-1 through 4-2. | For Components included within a time-based maintenance program, the responsible entity failed to maintain more than 10% but 15% or less of the total Components included within a specific Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Tables 4-1 through 4-2. | For Components included within a time-based maintenance program, the responsible entity failed to maintain more than 15% of the total Components included within a specific Component Type, in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3,and Tables 4-1 through 4-2. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-3(ii) | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System and Automatic Reclosing Components that are included within the performance-based program(s). | 2017-04-01 | 2015-12-31 | High | For Components included within a performance-based maintenance program, the responsible entity failed to maintain 5% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 5% but 10% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 10% but 15% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the responsible entity failed to maintain more than 15% of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-3(ii) | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | 2017-04-01 | 2015-12-31 | Medium | The responsible entity failed to undertake efforts to correct 5 or fewer identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 5, but less than or equal to 10 identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 10, but less than or equal to 15 identified Unresolved Maintenance Issues. | The responsible entity failed to undertake efforts to correct greater than 15 identified Unresolved Maintenance Issues. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-4 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. |  | 2015-12-31 | Medium | The entity’s PSMP failed to specify whether one Component Type is being addressed by time-based or performance-based maintenance, or a combination of both (Part 1.1). | The entity’s PSMP failed to specify whether two Component Types are being addressed by time-based or performance-based maintenance, or a combination of both (Part 1.1). | The entity’s PSMP failed to specify whether three Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1). OR The entity’s PSMP failed to include the applicable monitoring attributes applied to each Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Tables 4-1 through 4-2, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Components (Part 1.2). | The entity failed to establish a PSMP. OR The entity’s PSMP failed to specify whether four or more Component Types are being addressed by time-based or performance-based maintenance, or a combination of both (Part 1.1). OR The entity’s PSMP failed to include applicable station batteries in a time-based program (Part 1.1). |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-4 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. |  | 2015-12-31 | Medium | The entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within three years. | N/A | The entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within four years. | The entity uses performance-based maintenance intervals in its PSMP but: 1) Failed to establish the technical justification described within Requirement R2 for the initial use of the performance-based PSMP OR 2) Failed to reduce Countable Events to no more than 4% within five years OR 3) Maintained a Segment with less than 60 Components OR 4) Failed to: • Annually update the list of Components, OR • Annually perform maintenance on the greater of 5% of the Segment population or 3 Components, OR • Annually analyze the program activities and results for each Segment. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-4 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5. |  | 2015-12-31 | High | For Components included within a time-based maintenance program, the entity failed to maintain 5% or less of the total Components included within a specific Component Type in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Tables 4-1 through 4-2, and Table 5. | For Components included within a time-based maintenance program, the entity failed to maintain more than 5% but 10% or less of the total Components included within a specific Component Type in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Tables 4-1 through 4-2, and Table 5. | For Components included within a time-based maintenance program, the entity failed to maintain more than 10% but 15% or less of the total Components included within a specific Component Type in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Tables 4-1 through 4-2, and Table 5. | For Components included within a time-based maintenance program, the entity failed to maintain more than 15% of the total Components included within a specific Component Type in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Tables 4-1 through 4-2, and Table 5. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-4 | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performance-based program(s). |  | 2015-12-31 | High | For Components included within a performance-based maintenance program, the entity failed to maintain 5% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the entity failed to maintain more than 5% but 10% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the entity failed to maintain more than 10% but 15% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the entity failed to maintain more than 15% of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-4 | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. |  | 2015-12-31 | Medium | The entity failed to undertake efforts to correct 5 or fewer identified Unresolved Maintenance Issues. | The entity failed to undertake efforts to correct greater than 5 but less than or equal to 10 identified Unresolved Maintenance Issues. | The entity failed to undertake efforts to correct greater than 10 but less than or equal to 15 identified Unresolved Maintenance Issues. | The entity failed to undertake efforts to correct greater than 15 identified Unresolved Maintenance Issues. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-5 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. |  | 2015-12-31 | Medium | The entity’s PSMP failed to specify whether one Component Type is being addressed by time-based or performance-based maintenance, or a combination of both (Part 1.1). | The entity’s PSMP failed to specify whether two Component Types are being addressed by time-based or performance-based maintenance, or a combination of both (Part 1.1). | The entity’s PSMP failed to specify whether three Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1). OR The entity’s PSMP failed to include the applicable monitoring attributes applied to each Component Type consistent with the maintenance intervals specified in Tables 1‐1 through 1‐5, Table 2, Table 3, Tables 4‐1 through 4‐2, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Components (Part 1.2). | The entity failed to establish a PSMP. OR The entity’s PSMP failed to specify whether four or more Component Types are being addressed by time-based or performance-based maintenance, or a combination of both (Part 1.1). OR The entity’s PSMP failed to include applicable station batteries in a time‐based program (Part 1.1). |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-5 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. |  | 2015-12-31 | Medium | The entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within three years. | N/A | The entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within four years. | The entity uses performance‐based maintenance intervals in its PSMP but: 1) Failed to establish the technical justification described within Requirement R2 for the initial use of the performance‐based PSMP OR 2) Failed to reduce Countable Events to no more than 4% within five years OR 3) Maintained a Segment with less than 60 Components OR 4) Failed to: • Annually update the list of Components, OR • Annually perform maintenance on the greater of 5% of the Segment population or 3 Components, OR • Annually analyze the program activities and results for each Segment. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-5 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time-based based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5. |  | 2015-12-31 | High | For Components included within a time-based maintenance program, the entity failed to maintain 5% or less of the total Components included within a specific Component Type in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1‐1 through 1‐5, Table 2, Table 3, Tables 4‐1 through 4‐2, and Table 5. | For Components included within a time-based maintenance program, the entity failed to maintain more than 5% but 10% or less of the total Components included within a specific Component Type in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1‐1 through 1‐5, Table 2, Table 3, Tables 4‐1 through 4‐2, and Table 5. | For Components included within a time-based maintenance program, the entity failed to maintain more than 10% but 15% or less of the total Components included within a specific Component Type in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1‐1 through 1‐5, Table 2, Table 3, Tables 4‐1 through 4‐2, and Table 5. | For Components included within a time-based maintenance program, the entity failed to maintain more than 15% of the total Components included within a specific Component Type in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1‐1 through 1‐5, Table 2, Table 3, Tables 4‐1 through 4‐2, and Table 5. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-5 | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performance-based program(s). |  | 2015-12-31 | High | For Components included within a performance-based maintenance program, the entity failed to maintain 5% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the entity failed to maintain more than 5% but 10% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the entity failed to maintain more than 10% but 15% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the entity failed to maintain more than 15% of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-005-5 | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. |  | 2015-12-31 | Medium | The entity failed to undertake efforts to correct 5 or fewer identified Unresolved Maintenance Issues. | The entity failed to undertake efforts to correct greater than 5 but less than or equal to 10 identified Unresolved Maintenance Issues. | The entity failed to undertake efforts to correct greater than 10 but less than or equal to 15 identified Unresolved Maintenance Issues. | The entity failed to undertake efforts to correct greater than 15 identified Unresolved Maintenance Issues. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-005-6 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. | 2016-01-01 |  | Medium | The entity’s PSMP failed to specify whether one Component Type is being addressed by time-based or performance-based maintenance, or a combination of both (Part 1.1). | The entity’s PSMP failed to specify whether two Component Types are being addressed by time-based or performance-based maintenance, or a combination of both (Part 1.1). | The entity’s PSMP failed to specify whether three Component Types are being addressed by time-based or performance-based maintenance, or a combination of both. (Part 1.1). OR The entity’s PSMP failed to include the applicable monitoring attributes applied to each Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Tables 4-1 through 4-3, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Components (Part 1.2). | The entity failed to establish a PSMP. OR The entity’s PSMP failed to specify whether four or more Component Types are being addressed by time-based or performance-based maintenance, or a combination of both (Part 1.1). OR The entity’s PSMP failed to include applicable station batteries in a time-based program (Part 1.1). |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-005-6 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | 2016-01-01 |  | Medium | The entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within three years. | N/A | The entity uses performance-based maintenance intervals in its PSMP but failed to reduce Countable Events to no more than 4% within four years. | The entity uses performance-based maintenance intervals in its PSMP but: 1) Failed to establish the technical justification described within Requirement R2 for the initial use of the performance-based PSMP OR 2) Failed to reduce Countable Events to no more than 4% within five years OR 3) Maintained a Segment with less than 60 Components OR 4) Failed to: • Annually update the list of Components, OR • Annually perform maintenance on the greater of 5% of the Segment population or 3 Components, OR • Annually analyze the program activities and results for each Segment. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-005-6 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5. | 2016-01-01 |  | High | For Components included within a time-based maintenance program, the entity failed to maintain 5% or less of the total Components included within a specific Component Type in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Tables 4-1 through 4-3, and Table 5. | For Components included within a time-based maintenance program, the entity failed to maintain more than 5% but 10% or less of the total Components included within a specific Component Type in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Tables 4-1 through 4-3, and Table 5. | For Components included within a time-based maintenance program, the entity failed to maintain more than 10% but 15% or less of the total Components included within a specific Component Type in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Tables 4-1 through 4-3, and Table 5. | For Components included within a time-based maintenance program, the entity failed to maintain more than 15% of the total Components included within a specific Component Type in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Tables 4-1 through 4-3, and Table 5. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-005-6 | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performance-based program(s). | 2016-01-01 |  | High | For Components included within a performance-based maintenance program, the entity failed to maintain 5% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the entity failed to maintain more than 5% but 10% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the entity failed to maintain more than 10% but 15% or less of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. | For Components included within a performance-based maintenance program, the entity failed to maintain more than 15% of the annual scheduled maintenance for a specific Component Type in accordance with their performance-based PSMP. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-005-6 | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | 2016-01-01 |  | Medium | The entity failed to undertake efforts to correct 5 or fewer identified Unresolved Maintenance Issues. | The entity failed to undertake efforts to correct greater than 5 but less than or equal to 10 identified Unresolved Maintenance Issues. | The entity failed to undertake efforts to correct greater than 10 but less than or equal to 15 identified Unresolved Maintenance Issues. | The entity failed to undertake efforts to correct greater than 15 identified Unresolved Maintenance Issues. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-006-0 | R1. | Each Regional Reliability Organization shall develop, coordinate, and document an UFLS program, which shall include the following: |  | 2013-09-30 | High | [19 empty] | RRO
Inactive | PRC | PRC-006-0 | R2. | The Regional Reliability Organization shall provide documentation of its UFLS program and its database information to NERC on request (within 30 calendar days). |  | 2013-09-30 | Low | [19 empty] | RRO
Inactive | PRC | PRC-006-0 | R3. | The Regional Reliability Organization shall provide documentation of the assessment of its UFLS program to NERC on request (within 30 calendar days). |  | 2013-09-30 | Low | [19 empty] | RRO
Inactive | PRC | PRC-006-1 | E.B.1. | Each Planning Coordinator shall participate in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that develops and documents criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES) that may form islands. | 2013-10-01 | 2015-09-30 | Medium | N/A | The Planning Coordinator participated in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria but failed to include the consideration of historical events, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas, that may form islands OR The Planning Coordinator participated in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria but failed to include the consideration of system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas, that may form islands | The Planning Coordinator participated in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria but failed to include the consideration of historical events and system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas, that may form islands | The Planning Coordinator failed to participate in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas that may form islands | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | E.B.2. | Each Planning Coordinator shall identify one or more islands from the regional review (per E.B.1) to serve as a basis for designing a region-wide coordinated UFLS program including: [See standard for additional information.] | 2013-10-01 | 2015-09-30 | Medium | N/A | N/A | The Planning Coordinator identified an island(s) from the regional review to serve as a basis for designing its UFLS program but failed to include one (1) of the parts as specified in Requirement E.B.2, Parts E.B.2.1 or E.B.2.2 | The Planning Coordinator identified an island(s) from the regional review to serve as a basis for designing its UFLS program but failed to include all of the parts as specified in Requirement E.B.2, Parts E.B.2.1 or E.B.2.2 OR The Planning Coordinator failed to identify any island(s) from the regional review to serve as a basis for designing its UFLS program. | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | E.B.3. | Each Planning Coordinator shall adopt a UFLS program, coordinated across the WECC Regional Entity area, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | 2013-10-01 | 2015-09-30 | High | N/A | The Planning Coordinator adopted a UFLS program, coordinated across the WECC Regional Entity area that included notification of and a schedule for implementation by UFLS entities within its area, but failed to meet one (1) of the performance characteristic in Requirement E.B.3, Parts E.B.3.1, E.B.3.2, or E.B.3.3 in simulations of underfrequency conditions | The Planning Coordinator adopted a UFLS program, coordinated across the WECC Regional Entity area that included notification of and a schedule for implementation by UFLS entities within its area, but failed to meet two (2) of the performance characteristic in Requirement E.B.3, Parts E.B.3.1, E.B.3.2, or E.B.3.3 in simulations of underfrequency conditions | The Planning Coordinator adopted a UFLS program, coordinated across the WECC Regional Entity area that included notification of and a schedule for implementation by UFLS entities within its area, but failed to meet all the performance characteristic in Requirement E.B.3, Parts E.B.3.1, E.B.3.2, and E.B.3.3 in simulations of underfrequency conditions OR The Planning Coordinator failed to adopt a UFLS program, coordinated across the WECC Regional Entity area, including notification of and a schedule for implementation by UFLS entities within its area. | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | R1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. | 2013-10-01 | 2015-09-30 | Medium | N/A | The Planning Coordinator developed and documented criteria but failed to include the consideration of historical events, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. OR The Planning Coordinator developed and documented criteria but failed to include the consideration of system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas, that may form islands. | The Planning Coordinator developed and documented criteria but failed to include the consideration of historical events and system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas, that may form islands. | The Planning Coordinator failed to develop and document criteria to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas, that may form islands. | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | R2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: | 2013-10-01 | 2015-09-30 | Medium | N/A | The Planning Coordinator identified an island(s) to serve as a basis for designing its UFLS program but failed to include one (1) of the Parts as specified in Requirement R2, Parts 2.1, 2.2, or 2.3. | The Planning Coordinator identified an island(s) to serve as a basis for designing its UFLS program but failed to include two (2) of the Parts as specified in Requirement R2, Parts 2.1, 2.2, or 2.3. | The Planning Coordinator identified an island(s) to serve as a basis for designing its UFLS program but failed to include all of the Parts as specified in Requirement R2, Parts 2.1, 2.2, or 2.3. OR The Planning Coordinator failed to identify any island(s) to serve as a basis for designing its UFLS program. | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | 2013-10-01 | 2015-09-30 | High | N/A | The Planning Coordinator developed a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area where imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s)., but failed to meet one (1) of the performance characteristic in Requirement R3, Parts 3.1, 3.2, or 3.3 in simulations of underfrequency conditions. | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area where imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s)., but failed to meet two (2) of the performance characteristic in Requirement R3, Parts 3.1, 3.2, or 3.3 in simulations of underfrequency conditions. | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area where imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s).,but failed to meet all the performance characteristic in Requirement R3, Parts 3.1, 3.2, and 3.3 in simulations of underfrequency conditions. OR The Planning Coordinator failed to develop a UFLS program including notification of and a schedule for implementation by UFLS entities within its area | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | R4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: | 2013-10-01 | 2015-09-30 | High | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 for each island identified in Requirement R2 but the simulation failed to include one (1) of the items as specified in Requirement R4, Parts 4.1 through 4.7. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 for each island identified in Requirement R2 but the simulation failed to include two (2) of the items as specified in Requirement R4, Parts 4.1 through 4.7. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 for each island identified in Requirement R2 but the simulation failed to include three (3) of the items as specified in Requirement R4, Parts 4.1 through 4.7. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 but simulation failed to include four (4) or more of the items as specified in Requirement R4, Parts 4.1 through 4.7. OR The Planning Coordinator failed to conduct and document a UFLS assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2 | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | R5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | 2013-10-01 | 2015-09-30 | Medium | N/A | N/A | N/A | The Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, failed to coordinate its UFLS program design through one of the manners described in Requirement R5. | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | R6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | 2013-10-01 | 2015-09-30 | Low | N/A | N/A | N/A | The Planning Coordinator failed to maintain a UFLS database for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | R7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | 2013-10-01 | 2015-09-30 | Low | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 30 calendar days and up to and including 40 calendar days following the request. | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 40 calendar days but less than and including 50 calendar days following the request. | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 50 calendar days but less than and including 60 calendar days following the request. | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 60 calendar days following the request. OR The Planning Coordinator failed to provide its UFLS database to other Planning Coordinators. | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | 2013-10-01 | 2015-09-30 | Low | The UFLS entity provided data to its Planning Coordinator(s) less than or equal to 10 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | The UFLS entity provided data to its Planning Coordinator(s) more than 10 calendar days but less than or equal to 15 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. OR The UFLS entity provided data to its Planning Coordinator(s) but the data was not according to the format specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | The UFLS entity provided data to its Planning Coordinator(s) more than 15 calendar days but less than or equal to 20 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | The UFLS entity provided data to its Planning Coordinator(s) more than 20 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. OR The UFLS entity failed to provide data to its Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. |  |  | DP | [15 empty] | TO
Inactive | PRC | PRC-006-1 | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for application determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | 2013-10-01 | 2015-09-30 | High | The UFLS entity provided less than 100% but more than (and including) 95% of automatic tripping of Load in accordance with the UFLS program design and schedule for application determined by the Planning Coordinator(s) area in which it owns assets. | The UFLS entity provided less than 95% but more than (and including) 90% of automatic tripping of Load in accordance with the UFLS program design and schedule for application determined by the Planning Coordinator(s) area in which it owns assets. | The UFLS entity provided less than 90% but more than (and including) 85% of automatic tripping of Load in accordance with the UFLS program design and schedule for application determined by the Planning Coordinator(s) area in which it owns assets. | The UFLS entity provided less than 85% of automatic tripping of Load in accordance with the UFLS program design and schedule for application determined by the Planning Coordinator(s) area in which it owns assets. |  |  | DP | [15 empty] | TO
Inactive | PRC | PRC-006-1 | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for application determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | 2013-10-01 | 2015-09-30 | High | The Transmission Owner provided less than 100% but more than (and including) 95% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for application determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission | The Transmission Owner provided less than 95% but more than (and including) 90% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for application determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission | The Transmission Owner provided less than 90% but more than (and including) 85% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for application determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission | The Transmission Owner provided less than 85% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for application determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission | [18 empty] | TO
Inactive | PRC | PRC-006-1 | R11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: | 2013-10-01 | 2015-09-30 | Medium | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than one year but less than or equal to 13 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than 13 months but less than or equal to 14 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than 14 months but less than or equal to 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event within one year of event actuation but failed to evaluate one (1) of the Parts as specified in Requirement R11, Parts11.1 or 11.2. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, failed to conduct and document an assessment of the event and evaluate the Parts as specified in Requirement R11, Parts 11.1 and 11.2. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event within one year of event actuation but failed to evaluate all of the Parts as specified in Requirement R11, Parts 11.1 and 11.2. | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | R12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | 2013-10-01 | 2015-09-30 | Medium | N/A | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, conducted and documented a UFLS design assessment to consider the identified deficiencies greater than two years but less than or equal to 25 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, conducted and documented a UFLS design assessment to consider the identified deficiencies greater than 25 months but less than or equal to 26 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, conducted and documented a UFLS design assessment to consider the identified deficiencies greater than 26 months of event actuation. OR The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, failed to conduct and document a UFLS design assessment to consider the identified deficiencies. | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | R13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | 2013-10-01 | 2015-09-30 | Medium | N/A | N/A | N/A | The Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, failed to coordinate its UFLS event assessment with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event in one of the manners described in Requirement R13 | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | R14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following: | 2013-10-01 | 2015-09-30 | Low | N/A | N/A | N/A | The Planning Coordinator failed to respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes were made or reasons why changes were not made to the items in Parts 14.1 through 14.3. | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | E.A.4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement E.A.3 for each island identified in Requirement R2. The simulation shall model each of the following; | 2013-10-01 | 2015-09-30 | High | N/A | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement E.A.3 but simulation failed to include one (1) of the items as specified in Parts E.A.4.1, E.A.4.2 or E.A.4.3. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement E3 but simulation failed to include two (2) of the items as specified in Parts E.A.4.1, E.A.4.2 or E.A.4.3. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement E3 but simulation failed to include all of the items as specified in Parts E.A.4.1, E.A.4.2 and E.A.4.3. OR The Planning Coordinator failed to conduct and document a UFLS assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement E.A.3 | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | E.A.3. | Each Planning Coordinator shall develop a UFLS program, including a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance | 2013-10-01 | 2015-09-30 | High | N/A | The Planning Coordinator developed a UFLS program, including a schedule for implementation by UFLS entities within its area, but failed to meet one (1) of the performance characteristic in Parts E.A.3.1, E.A.3.2, or E.A.3.3 in simulations of underfrequency conditions | The Planning Coordinator developed a UFLS program including a schedule for implementation by UFLS entities within its area, but failed to meet two (2) of the performance characteristic in Parts E.A.3.1, E.A.3.2, or E.A.3.3 in simulations of underfrequency conditions | The Planning Coordinator developed a UFLS program including a schedule for implementation by UFLS entities within its area, but failed to meet all the performance characteristic in Parts E.A.3.1, E.A.3.2, and E.A.3.3 in simulations of underfrequency conditions OR The Planning Coordinator failed to develop a UFLS program. | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | E.B.4. | Each Planning Coordinator shall participate in and document a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement E.B.3 for each island identified in Requirement E.B.2. The simulation shall model each of the following: | 2013-10-01 | 2015-09-30 | High | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement E.B.3 for each island identified in Requirement E.B.2 but the simulation failed to include one (1) of the items as specified in Requirement E.B.4, Parts E.B.4.1 through E.B.4.7. | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement E.B.3 for each island identified in Requirement E.B.2 but the simulation failed to include two (2) of the items as specified in Requirement E.B.4, Parts E.B.4.1 through E.B.4.7. | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement E.B.3 for each island identified in Requirement E.B.2 but the simulation failed to include three (3) of the items as specified in Requirement E.B.4, Parts E.B.4.1 through E.B.4.7. | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement E.B.3 for each island identified in Requirement E.B.2 but the simulation failed to include four (4) or more of the items as specified in Requirement E.B.4, Parts E.B.4.1 through E.B.4.7. OR The Planning Coordinator failed to participate in and document a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement E.B.3 for each island identified in Requirement E.B.2 | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | E.B.11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall participate in and document a coordinated event assessment with all affected Planning Coordinators to conduct and document an assessment of the event within one year of event actuation to evaluate: | 2013-10-01 | 2015-09-30 | Medium | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement E.B.11, Parts E.B.11.1 and E.B.11.2 within a time greater than one year but less than or equal to 13 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement E.B.11, Parts E.B.11.1 and E.B.11.2 within a time greater than 13 months but less than or equal to 14 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement E.B.11, Parts E.B.11.1 and E.B.11.2 within a time greater than 14 months but less than or equal to 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event within one year of event actuation but failed to evaluate one (1) of the parts as specified in Requirement E.B.11, Parts E.B.11.1 or E.B.11.2. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement E.B.11, Parts E.B.11.1 and E.B.11.2 within a time greater than 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, failed to participate in and document a coordinated event assessment with all Planning Coordinators whose areas or portion of whose areas were also included in the same island event and evaluate the parts as specified in Requirement E.B.11, Parts E.B.11.1 and E.B.11.2. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event within one year of event actuation but failed to evaluate all of the parts as specified in Requirement E.B.11, Parts E.B.11.1 and E.B.11.2. | [10 empty] | PCPA
Inactive | PRC | PRC-006-1 | E.B.12. | Each Planning Coordinator, in whose islanding event assessment (per E.B.11) UFLS program deficiencies are identified, shall participate in and document a coordinated UFLS design assessment of the UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies within two years of event actuation. | 2013-10-01 | 2015-09-30 | Medium | N/A | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement E.B.11, participated in and documented a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies in greater than two years but less than or equal to 25 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement E.B.11, participated in and documented a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies in greater than 25 months but less than or equal to 26 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement E.B.11, participated in and documented a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies in greater than 26 months of event actuation. OR The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement E.B.11, failed to participate in and document a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies | [10 empty] | PCPA
Inactive | PRC | PRC-006-2 | D.B.1. | Each Planning Coordinator shall participate in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that develops and documents criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES) that may form islands. | 2015-10-01 | 2017-09-30 | Medium | N/A | The Planning Coordinator participated in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria but failed to include the consideration of historical events, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas, that may form islands OR The Planning Coordinator participated in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria but failed to include the consideration of system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas, that may form islands | The Planning Coordinator participated in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria but failed to include the consideration of historical events and system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas, that may form islands | The Planning Coordinator failed to participate in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas that may form islands | [10 empty] | PCPA
Inactive | PRC | PRC-006-2 | D.B.2. | Each Planning Coordinator shall identify one or more islands from the regional review (per D.B.1) to serve as a basis for designing a region-wide coordinated UFLS program including: | 2015-10-01 | 2017-09-30 | Medium | N/A | N/A | The Planning Coordinator identified an island(s) from the regional review to serve as a basis for designing its UFLS program but failed to include one (1) of the parts as specified in Requirement D.B.2, Parts D.B.2.1 or D.B.2.2 | The Planning Coordinator identified an island(s) from the regional review to serve as a basis for designing its UFLS program but failed to include all of the parts as specified in Requirement D.B.2, Parts D.B.2.1 or D.B.2.2 OR The Planning Coordinator failed to identify any island(s) from the regional review to serve as a basis for designing its UFLS program. | [10 empty] | PCPA
Inactive | PRC | PRC-006-2 | D.B.3. | Each Planning Coordinator shall adopt a UFLS program, coordinated across the WECC Regional Entity area, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | 2015-10-01 | 2017-09-30 | High | N/A | The Planning Coordinator adopted a UFLS program, coordinated across the WECC Regional Entity area that included notification of and a schedule for implementation by UFLS entities within its area, but failed to meet one (1) of the performance characteristic in Requirement D.B.3, Parts D.B.3.1, D.B.3.2, or D.B.3.3 in simulations of underfrequency conditions | The Planning Coordinator adopted a UFLS program, coordinated across the WECC Regional Entity area that included notification of and a schedule for implementation by UFLS entities within its area, but failed to meet two (2) of the performance characteristic in Requirement D.B.3, Parts D.B.3.1, D.B.3.2, or D.B.3.3 in simulations of underfrequency conditions | The Planning Coordinator adopted a UFLS program, coordinated across the WECC Regional Entity area that included notification of and a schedule for implementation by UFLS entities within its area, but failed to meet all the performance characteristic in Requirement D.B.3, Parts D.B.3.1, D.B.3.2, and D.B.3.3 in simulations of underfrequency conditions OR The Planning Coordinator failed to adopt a UFLS program, coordinated across the WECC Regional Entity area, including notification of and a schedule for implementation by UFLS entities within its area. | [10 empty] | PCPA
Inactive | PRC | PRC-006-2 | D.B.4. | Each Planning Coordinator shall participate in and document a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2. The simulation shall model each of the following: | 2015-10-01 | 2017-09-30 | High | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include one (1) of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include two (2) of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include three (3) of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include four (4) or more of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. OR The Planning Coordinator failed to participate in and document a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 | [10 empty] | PCPA
Inactive | PRC | PRC-006-2 | D.B.11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall participate in and document a coordinated event assessment with all affected Planning Coordinators to conduct and document an assessment of the event within one year of event actuation to evaluate: | 2015-10-01 | 2017-09-30 | Medium | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than one year but less than or equal to 13 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than 13 months but less than or equal to 14 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than 14 months but less than or equal to 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event within one year of event actuation but failed to evaluate one (1) of the parts as specified in Requirement D.B.11, Parts D.B.11.1 or D.B.11.2. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, failed to participate in and document a coordinated event assessment with all Planning Coordinators whose areas or portion of whose areas were also included in the same island event and evaluate the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event within one year of event actuation but failed to evaluate all of the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2. | [10 empty] | PCPA
Inactive | PRC | PRC-006-2 | D.B.12. | Each Planning Coordinator, in whose islanding event assessment (per D.B.11) UFLS program deficiencies are identified, shall participate in and document a coordinated UFLS design assessment of the UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies within two years of event actuation. | 2015-10-01 | 2017-09-30 | Medium | N/A | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, participated in and documented a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies in greater than two years but less than or equal to 25 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, participated in and documented a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies in greater than 25 months but less than or equal to 26 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, participated in and documented a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies in greater than 26 months of event actuation. OR The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, failed to participate in and document a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies | [10 empty] | PCPA
Inactive | PRC | PRC-006-2 | R1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. | 2015-10-01 | 2017-09-30 | Medium | N/A | The Planning Coordinator developed and documented criteria but failed to include the consideration of historical events, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. OR The Planning Coordinator developed and documented criteria but failed to include the consideration of system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas, that may form islands. | The Planning Coordinator developed and documented criteria but failed to include the consideration of historical events and system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas, that may form islands. | The Planning Coordinator failed to develop and document criteria to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas, that may form islands. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-2 | R2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: [See Standard for additional information.] | 2015-10-01 | 2017-09-30 | Medium | N/A | The Planning Coordinator identified an island(s) to serve as a basis for designing its UFLS program but failed to include one (1) of the Parts as specified in Requirement R2, Parts 2.1, 2.2, or 2.3. | The Planning Coordinator identified an island(s) to serve as a basis for designing its UFLS program but failed to include two (2) of the Parts as specified in Requirement R2, Parts 2.1, 2.2, or 2.3. | The Planning Coordinator identified an island(s) to serve as a basis for designing its UFLS program but failed to include all of the Parts as specified in Requirement R2, Parts 2.1, 2.2, or 2.3. OR The Planning Coordinator failed to identify any island(s) to serve as a basis for designing its UFLS program. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-2 | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | 2015-10-01 | 2017-09-30 | High | N/A | The Planning Coordinator developed a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area where imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s)., but failed to meet one (1) of the performance characteristic in Requirement R3, Parts 3.1, 3.2, or 3.3 in simulations of underfrequency conditions. | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area where imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s), but failed to meet two (2) of the performance characteristic in Requirement R3, Parts 3.1, 3.2, or 3.3 in simulations of underfrequency conditions. | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area where imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s), but failed to meet all the performance characteristic in Requirement R3, Parts 3.1, 3.2, and 3.3 in simulations of underfrequency conditions. OR The Planning Coordinator failed to develop a UFLS program including notification of and a schedule for implementation by UFLS entities within its area. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-2 | R4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: | 2015-10-01 | 2017-09-30 | High | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 for each island identified in Requirement R2 but the simulation failed to include one (1) of the items as specified in Requirement R4, Parts 4.1 through 4.7. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 for each island identified in Requirement R2 but the simulation failed to include two (2) of the items as specified in Requirement R4, Parts 4.1 through 4.7. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 for each island identified in Requirement R2 but the simulation failed to include three (3) of the items as specified in Requirement R4, Parts 4.1 through 4.7. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 but simulation failed to include four (4) or more of the items as specified in Requirement R4, Parts 4.1 through 4.7. OR The Planning Coordinator failed to conduct and document a UFLS assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2 |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-2 | R5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | 2015-10-01 | 2017-09-30 | High | N/A | N/A | N/A | The Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, failed to coordinate its UFLS program design through one of the manners described in Requirement R5. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-2 | R6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | 2015-10-01 | 2017-09-30 | Low | N/A | N/A | N/A | The Planning Coordinator failed to maintain a UFLS database for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-2 | R7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | 2015-10-01 | 2017-09-30 | Low | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 30 calendar days and up to and including 40 calendar days following the request. | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 40 calendar days but less than and including 50 calendar days following the request. | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 50 calendar days but less than and including 60 calendar days following the request. | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 60 calendar days following the request. OR The Planning Coordinator failed to provide its UFLS database to other Planning Coordinators. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-2 | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | 2015-10-01 | 2017-09-30 | Low | The UFLS entity provided data to its Planning Coordinator(s) less than or equal to 10 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | The UFLS entity provided data to its Planning Coordinator(s) more than 10 calendar days but less than or equal to 15 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. OR The UFLS entity provided data to its Planning Coordinator(s) but the data was not according to the format specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | The UFLS entity provided data to its Planning Coordinator(s) more than 15 calendar days but less than or equal to 20 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | The UFLS entity provided data to its Planning Coordinator(s) more than 20 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. OR The UFLS entity failed to provide data to its Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-2 | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | 2015-10-01 | 2017-09-30 | High | The UFLS entity provided less than 100% but more than (and including) 95% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. | The UFLS entity provided less than 95% but more than (and including) 90% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. | The UFLS entity provided less than 90% but more than (and including) 85% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. | The UFLS entity provided less than 85% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-2 | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | 2015-10-01 | 2017-09-30 | High | The Transmission Owner provided less than 100% but more than (and including) 95% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | The Transmission Owner provided less than 95% but more than (and including) 90% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | The Transmission Owner provided less than 90% but more than (and including) 85% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | The Transmission Owner provided less than 85% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. |  |  |  | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-2 | R11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: | 2015-10-01 | 2017-09-30 | Medium | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than one year but less than or equal to 13 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than 13 months but less than or equal to 14 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than 14 months but less than or equal to 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event within one year of event actuation but failed to evaluate one (1) of the Parts as specified in Requirement R11, Parts11.1 or 11.2. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, failed to conduct and document an assessment of the event and evaluate the Parts as specified in Requirement R11, Parts 11.1 and 11.2. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event within one year of event actuation but failed to evaluate all of the Parts as specified in Requirement R11, Parts 11.1 and 11.2. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-2 | R12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | 2015-10-01 | 2017-09-30 | Medium | N/A | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, conducted and documented a UFLS design assessment to consider the identified deficiencies greater than two years but less than or equal to 25 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, conducted and documented a UFLS design assessment to consider the identified deficiencies greater than 25 months but less than or equal to 26 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, conducted and documented a UFLS design assessment to consider the identified deficiencies greater than 26 months of event actuation. OR The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, failed to conduct and document a UFLS design assessment to consider the identified deficiencies. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-2 | R13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | 2015-10-01 | 2017-09-30 | Medium | N/A | N/A | N/A | The Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, failed to coordinate its UFLS event assessment with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event in one of the manners described in Requirement R13 |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-2 | R14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following | 2015-10-01 | 2017-09-30 | Low | N/A | N/A | N/A | The Planning Coordinator failed to respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes were made or reasons why changes were not made to the items in Parts 14.1 through 14.3. |  |  | DP | DP-UFLS | [6 empty] | PCPA | [7 empty] | TO
Inactive | PRC | PRC-006-2 | R15. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. | 2015-10-01 | 2017-09-30 | High | N/A | The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, and developed a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, but exceeded the permissible time frame for development by a period of up to 1 month. | The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, and developed a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, but exceeded the permissible time frame for development by a period greater than 1 month but not more than 2 months. | The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, but failed to develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. OR The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, and developed a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, but exceeded the permissible time frame for development by a period greater than 2 months. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-3 | D.B.1. | Each Planning Coordinator shall participate in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that develops and documents criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES) that may form islands. | 2017-10-01 | 2021-03-31 | Medium | N/A | The Planning Coordinator participated in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria but failed to include the consideration of historical events, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas, that may form islands OR The Planning Coordinator participated in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria but failed to include the consideration of system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas, that may form islands | The Planning Coordinator participated in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria but failed to include the consideration of historical events and system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas, that may form islands | The Planning Coordinator failed to participate in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas that may form islands | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | D.B.2. | Each Planning Coordinator shall identify one or more islands from the regional review (per D.B.1) to serve as a basis for designing a region-wide coordinated UFLS program including: | 2017-10-01 | 2021-03-31 | Medium | N/A | N/A | The Planning Coordinator identified an island(s) from the regional review to serve as a basis for designing its UFLS program but failed to include one (1) of the parts as specified in Requirement D.B.2, Parts D.B.2.1 or D.B.2.2 | The Planning Coordinator identified an island(s) from the regional review to serve as a basis for designing its UFLS program but failed to include all of the parts as specified in Requirement D.B.2, Parts D.B.2.1 or D.B.2.2 OR The Planning Coordinator failed to identify any island(s) from the regional review to serve as a basis for designing its UFLS program. | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | D.B.3. | Each Planning Coordinator shall adopt a UFLS program, coordinated across the WECC Regional Entity area, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | 2017-10-01 | 2021-03-31 | High | N/A | The Planning Coordinator adopted a UFLS program, coordinated across the WECC Regional Entity area that included notification of and a schedule for implementation by UFLS entities within its area, but failed to meet one (1) of the performance characteristic in Requirement D.B.3, Parts D.B.3.1, D.B.3.2, or D.B.3.3 in simulations of underfrequency conditions | The Planning Coordinator adopted a UFLS program, coordinated across the WECC Regional Entity area that included notification of and a schedule for implementation by UFLS entities within its area, but failed to meet two (2) of the performance characteristic in Requirement D.B.3, Parts D.B.3.1, D.B.3.2, or D.B.3.3 in simulations of underfrequency conditions | The Planning Coordinator adopted a UFLS program, coordinated across the WECC Regional Entity area that included notification of and a schedule for implementation by UFLS entities within its area, but failed to meet all the performance characteristic in Requirement D.B.3, Parts D.B.3.1, D.B.3.2, and D.B.3.3 in simulations of underfrequency conditions OR The Planning Coordinator failed to adopt a UFLS program, coordinated across the WECC Regional Entity area, including notification of and a schedule for implementation by UFLS entities within its area. | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | D.B.4. | Each Planning Coordinator shall participate in and document a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2. The simulation shall model each of the following: | 2017-10-01 | 2021-03-31 | High | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include one (1) of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include two (2) of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include three (3) of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include four (4) or more of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. OR The Planning Coordinator failed to participate in and document a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | D.B.11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall participate in and document a coordinated event assessment with all affected Planning Coordinators to conduct and document an assessment of the event within one year of event actuation to evaluate: | 2017-10-01 | 2021-03-31 | Medium | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than one year but less than or equal to 13 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than 13 months but less than or equal to 14 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than 14 months but less than or equal to 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event within one year of event actuation but failed to evaluate one (1) of the parts as specified in Requirement D.B.11, Parts D.B.11.1 or D.B.11.2. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, failed to participate in and document a coordinated event assessment with all Planning Coordinators whose areas or portion of whose areas were also included in the same island event and evaluate the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event within one year of event actuation but failed to evaluate all of the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2. | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | D.B.12. | Each Planning Coordinator, in whose islanding event assessment (per D.B.11) UFLS program deficiencies are identified, shall participate in and document a coordinated UFLS design assessment of the UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies within two years of event actuation. | 2017-10-01 | 2021-03-31 | Medium | N/A | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, participated in and documented a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies in greater than two years but less than or equal to 25 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, participated in and documented a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies in greater than 25 months but less than or equal to 26 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, participated in and documented a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies in greater than 26 months of event actuation. OR The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, failed to participate in and document a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | R1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. | 2017-10-01 | 2021-03-31 | Medium | N/A | The Planning Coordinator developed and documented criteria but failed to include the consideration of historical events, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. OR The Planning Coordinator developed and documented criteria but failed to include the consideration of system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas, that may form islands. | The Planning Coordinator developed and documented criteria but failed to include the consideration of historical events and system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas, that may form islands. | The Planning Coordinator failed to develop and document criteria to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas, that may form islands. | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | R2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: | 2017-10-01 | 2021-03-31 | Medium | N/A | The Planning Coordinator identified an island(s) to serve as a basis for designing its UFLS program but failed to include one (1) of the Parts as specified in Requirement R2, Parts 2.1, 2.2, or 2.3. | The Planning Coordinator identified an island(s) to serve as a basis for designing its UFLS program but failed to include two (2) of the Parts as specified in Requirement R2, Parts 2.1, 2.2, or 2.3. | The Planning Coordinator identified an island(s) to serve as a basis for designing its UFLS program but failed to include all of the Parts as specified in Requirement R2, Parts 2.1, 2.2, or 2.3. OR The Planning Coordinator failed to identify any island(s) to serve as a basis for designing its UFLS program. | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | 2017-10-01 | 2021-03-31 | High | N/A | The Planning Coordinator developed a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area where imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s)., but failed to meet one (1) of the performance characteristic in Requirement R3, Parts 3.1, 3.2, or 3.3 in simulations of underfrequency conditions. | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area where imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s)., but failed to meet two (2) of the performance characteristic in Requirement R3, Parts 3.1, 3.2, or 3.3 in simulations of underfrequency conditions. | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area where imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s).,but failed to meet all the performance characteristic in Requirement R3, Parts 3.1, 3.2, and 3.3 in simulations of underfrequency conditions. OR The Planning Coordinator failed to develop a UFLS program including notification of and a schedule for implementation by UFLS entities within its area | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | R4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: | 2017-10-01 | 2021-03-31 | High | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 for each island identified in Requirement R2 but the simulation failed to include one (1) of the items as specified in Requirement R4, Parts 4.1 through 4.7. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 for each island identified in Requirement R2 but the simulation failed to include two (2) of the items as specified in Requirement R4, Parts 4.1 through 4.7. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 for each island identified in Requirement R2 but the simulation failed to include three (3) of the items as specified in Requirement R4, Parts 4.1 through 4.7. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 but simulation failed to include four (4) or more of the items as specified in Requirement R4, Parts 4.1 through 4.7. OR The Planning Coordinator failed to conduct and document a UFLS assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2 | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | R5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | 2017-10-01 | 2021-03-31 | High | N/A | N/A | N/A | The Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, failed to coordinate its UFLS program design through one of the manners described in Requirement R5. | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | R6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | 2017-10-01 | 2021-03-31 | Low | N/A | N/A | N/A | The Planning Coordinator failed to maintain a UFLS database for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | R7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | 2017-10-01 | 2021-03-31 | Low | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 30 calendar days and up to and including 40 calendar days following the request. | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 40 calendar days but less than and including 50 calendar days following the request. | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 50 calendar days but less than and including 60 calendar days following the request. | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 60 calendar days following the request. OR The Planning Coordinator failed to provide its UFLS database to other Planning Coordinators. | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | 2017-10-01 | 2021-03-31 | Low | The UFLS entity provided data to its Planning Coordinator(s) less than or equal to 10 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | The UFLS entity provided data to its Planning Coordinator(s) more than 10 calendar days but less than or equal to 15 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. OR The UFLS entity provided data to its Planning Coordinator(s) but the data was not according to the format specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | The UFLS entity provided data to its Planning Coordinator(s) more than 15 calendar days but less than or equal to 20 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | The UFLS entity provided data to its Planning Coordinator(s) more than 20 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. OR The UFLS entity failed to provide data to its Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-3 | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | 2017-10-01 | 2021-03-31 | High | The UFLS entity provided less than 100% but more than (and including) 95% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. | The UFLS entity provided less than 95% but more than (and including) 90% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. | The UFLS entity provided less than 90% but more than (and including) 85% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. | The UFLS entity provided less than 85% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-3 | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | 2017-10-01 | 2021-03-31 | High | The Transmission Owner provided less than 100% but more than (and including) 95% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | The Transmission Owner provided less than 95% but more than (and including) 90% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | The Transmission Owner provided less than 90% but more than (and including) 85% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | The Transmission Owner provided less than 85% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | [18 empty] | TO
Inactive | PRC | PRC-006-3 | R11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: | 2017-10-01 | 2021-03-31 | Medium | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than one year but less than or equal to 13 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than 13 months but less than or equal to 14 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than 14 months but less than or equal to 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event within one year of event actuation but failed to evaluate one (1) of the Parts as specified in Requirement R11, Parts11.1 or 11.2. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, failed to conduct and document an assessment of the event and evaluate the Parts as specified in Requirement R11, Parts 11.1 and 11.2. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event within one year of event actuation but failed to evaluate all of the Parts as specified in Requirement R11, Parts 11.1 and 11.2. | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | R12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | 2017-10-01 | 2021-03-31 | Medium | N/A | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, conducted and documented a UFLS design assessment to consider the identified deficiencies greater than two years but less than or equal to 25 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, conducted and documented a UFLS design assessment to consider the identified deficiencies greater than 25 months but less than or equal to 26 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, conducted and documented a UFLS design assessment to consider the identified deficiencies greater than 26 months of event actuation. OR The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, failed to conduct and document a UFLS design assessment to consider the identified deficiencies. | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | R13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | 2017-10-01 | 2021-03-31 | Medium | N/A | N/A | N/A | The Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, failed to coordinate its UFLS event assessment with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event in one of the manners described in Requirement R13 | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | R14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following | 2017-10-01 | 2021-03-31 | Low | N/A | N/A | N/A | The Planning Coordinator failed to respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes were made or reasons why changes were not made to the items in Parts 14.1 through 14.3. | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | R15. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. | 2017-10-01 | 2021-03-31 | High | N/A | The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, and developed a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, but exceeded the permissible time frame for development by a period of up to 1 month. | The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, and developed a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, but exceeded the permissible time frame for development by a period greater than 1 month but not more than 2 months. | The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, but failed to develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. OR The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, and developed a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, but exceeded the permissible time frame for development by a period greater than 2 months. | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | D.A.3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from each of these extreme events: • Loss of the entire capability of a generating station. • Loss of all transmission circuits emanating from a generating station, switching station, substation or dc terminal. • Loss of all transmission circuits on a common right-of-way. • Three-phase fault with failure of a circuit breaker to operate and correct operation of a breaker failure protection system and its associated breakers. • Three-phase fault on a circuit breaker, with normal fault clearing. • The operation or partial operation of a RAS for an event or condition for which it was not intended to operate. | 2017-10-01 | 2021-03-31 | High | N/A | The Planning Coordinator developed a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, but failed to meet one (1) of the performance characteristic in Parts D.A.3.1, D.A.3.2, or D.A.3.3 in simulations of underfrequency conditions | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area, but failed to meet two (2) of the performance characteristic in Parts D.A.3.1, D.A.3.2, or D.A.3.3 in simulations of underfrequency conditions | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area, but failed to meet all the performance characteristic in Parts D.A.3.1, D.A.3.2, and D.A.3.3 in simulations of underfrequency conditions OR The Planning Coordinator failed to develop a UFLS program including notification of and a schedule for implementation by UFLS entities within its area. | [10 empty] | PCPA
Inactive | PRC | PRC-006-3 | D.A.4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.A.3 for each island identified in Requirement R2. The simulation shall model each of the following; | 2017-10-01 | 2021-03-31 | High | N/A | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement D.A.3 but the simulation failed to include one (1) of the items as specified in Parts D.A.4.1, D.A.4.2 or D.A.4.3. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement D.A.3 but the simulation failed to include two (2) of the items as specified in Parts D.A.4.1, D.A.4.2 or D.A.4.3. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement D.A.3 but the simulation failed to include all of the items as specified in Parts D.A.4.1, D.A.4.2 and D.A.4.3. OR The Planning Coordinator failed to conduct and document a UFLS assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.A.3 | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | D.B.1. | Each Planning Coordinator shall participate in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that develops and documents criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES) that may form islands. |  | 2021-03-31 | Medium | N/A | The Planning Coordinator participated in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria but failed to include the consideration of historical events, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas, that may form islands OR The Planning Coordinator participated in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria but failed to include the consideration of system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas, that may form islands | The Planning Coordinator participated in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria but failed to include the consideration of historical events and system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas, that may form islands | The Planning Coordinator failed to participate in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas that may form islands | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | D.B.2. | Each Planning Coordinator shall identify one or more islands from the regional review (per D.B.1) to serve as a basis for designing a region-wide coordinated UFLS program including: |  | 2021-03-31 | Medium | N/A | N/A | The Planning Coordinator identified an island(s) from the regional review to serve as a basis for designing its UFLS program but failed to include one (1) of the parts as specified in Requirement D.B.2, Parts D.B.2.1 or D.B.2.2 | The Planning Coordinator identified an island(s) from the regional review to serve as a basis for designing its UFLS program but failed to include all of the parts as specified in Requirement D.B.2, Parts D.B.2.1 or D.B.2.2 OR The Planning Coordinator failed to identify any island(s) from the regional review to serve as a basis for designing its UFLS program. | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | D.B.3. | Each Planning Coordinator shall adopt a UFLS program, coordinated across the WECC Regional Entity area, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). |  | 2021-03-31 | High | N/A | The Planning Coordinator adopted a UFLS program, coordinated across the WECC Regional Entity area that included notification of and a schedule for implementation by UFLS entities within its area, but failed to meet one (1) of the performance characteristic in Requirement D.B.3, Parts D.B.3.1, D.B.3.2, or D.B.3.3 in simulations of underfrequency conditions | The Planning Coordinator adopted a UFLS program, coordinated across the WECC Regional Entity area that included notification of and a schedule for implementation by UFLS entities within its area, but failed to meet two (2) of the performance characteristic in Requirement D.B.3, Parts D.B.3.1, D.B.3.2, or D.B.3.3 in simulations of underfrequency conditions | The Planning Coordinator adopted a UFLS program, coordinated across the WECC Regional Entity area that included notification of and a schedule for implementation by UFLS entities within its area, but failed to meet all the performance characteristic in Requirement D.B.3, Parts D.B.3.1, D.B.3.2, and D.B.3.3 in simulations of underfrequency conditions OR The Planning Coordinator failed to adopt a UFLS program, coordinated across the WECC Regional Entity area, including notification of and a schedule for implementation by UFLS entities within its area. | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | D.B.4. | Each Planning Coordinator shall participate in and document a coordinated UFLS design assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2. The simulation shall model each of the following: |  | 2021-03-31 | High | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include one (1) of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include two (2) of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include three (3) of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include four (4) or more of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. OR The Planning Coordinator failed to participate in and document a coordinated UFLS assessment with the other Planning Coordinators in the WECC Regional Entity area at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | D.B.11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall participate in and document a coordinated event assessment with all affected Planning Coordinators to conduct and document an assessment of the event within one year of event actuation to evaluate: |  | 2021-03-31 | Medium | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than one year but less than or equal to 13 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than 13 months but less than or equal to 14 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than 14 months but less than or equal to 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event within one year of event actuation but failed to evaluate one (1) of the parts as specified in Requirement D.B.11, Parts D.B.11.1 or D.B.11.2. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, failed to participate in and document a coordinated event assessment with all Planning Coordinators whose areas or portion of whose areas were also included in the same island event and evaluate the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event within one year of event actuation but failed to evaluate all of the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2. | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | D.B.12. | Each Planning Coordinator, in whose islanding event assessment (per D.B.11) UFLS program deficiencies are identified, shall participate in and document a coordinated UFLS design assessment of the UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies within two years of event actuation. |  | 2021-03-31 | Medium | N/A | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, participated in and documented a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies in greater than two years but less than or equal to 25 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, participated in and documented a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies in greater than 25 months but less than or equal to 26 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, participated in and documented a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies in greater than 26 months of event actuation. OR The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, failed to participate in and document a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators in the WECC Regional Entity area to consider the identified deficiencies | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | R1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. |  | 2021-03-31 | Medium | N/A | The Planning Coordinator developed and documented criteria but failed to include the consideration of historical events, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. OR The Planning Coordinator developed and documented criteria but failed to include the consideration of system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas, that may form islands. | The Planning Coordinator developed and documented criteria but failed to include the consideration of historical events and system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas, that may form islands. | The Planning Coordinator failed to develop and document criteria to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas, that may form islands. | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | R2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: |  | 2021-03-31 | Medium | N/A | The Planning Coordinator identified an island(s) to serve as a basis for designing its UFLS program but failed to include one (1) of the Parts as specified in Requirement R2, Parts 2.1, 2.2, or 2.3. | The Planning Coordinator identified an island(s) to serve as a basis for designing its UFLS program but failed to include two (2) of the Parts as specified in Requirement R2, Parts 2.1, 2.2, or 2.3. | The Planning Coordinator identified an island(s) to serve as a basis for designing its UFLS program but failed to include all of the Parts as specified in Requirement R2, Parts 2.1, 2.2, or 2.3. OR The Planning Coordinator failed to identify any island(s) to serve as a basis for designing its UFLS program. | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). |  | 2021-03-31 | High | N/A | The Planning Coordinator developed a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area where imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s)., but failed to meet one (1) of the performance characteristic in Requirement R3, Parts 3.1, 3.2, or 3.3 in simulations of underfrequency conditions. | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area where imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s)., but failed to meet two (2) of the performance characteristic in Requirement R3, Parts 3.1, 3.2, or 3.3 in simulations of underfrequency conditions. | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area where imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s).,but failed to meet all the performance characteristic in Requirement R3, Parts 3.1, 3.2, and 3.3 in simulations of underfrequency conditions. OR The Planning Coordinator failed to develop a UFLS program including notification of and a schedule for implementation by UFLS entities within its area | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | R4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: |  | 2021-03-31 | High | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 for each island identified in Requirement R2 but the simulation failed to include one (1) of the items as specified in Requirement R4, Parts 4.1 through 4.7. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 for each island identified in Requirement R2 but the simulation failed to include two (2) of the items as specified in Requirement R4, Parts 4.1 through 4.7. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 for each island identified in Requirement R2 but the simulation failed to include three (3) of the items as specified in Requirement R4, Parts 4.1 through 4.7. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 but simulation failed to include four (4) or more of the items as specified in Requirement R4, Parts 4.1 through 4.7. OR The Planning Coordinator failed to conduct and document a UFLS assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2 | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | R5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: [VRF: High][Time Horizon: Long-term Planning] • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. |  | 2021-03-31 | High | N/A | N/A | N/A | The Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, failed to coordinate its UFLS program design through one of the manners described in Requirement R5. | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | R6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. |  | 2021-03-31 | Low | N/A | N/A | N/A | The Planning Coordinator failed to maintain a UFLS database for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | R7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. |  | 2021-03-31 | Low | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 30 calendar days and up to and including 40 calendar days following the request. | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 40 calendar days but less than and including 50 calendar days following the request. | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 50 calendar days but less than and including 60 calendar days following the request. | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 60 calendar days following the request. OR The Planning Coordinator failed to provide its UFLS database to other Planning Coordinators. | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. |  | 2021-03-31 | Low | The UFLS entity provided data to its Planning Coordinator(s) less than or equal to 10 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | The UFLS entity provided data to its Planning Coordinator(s) more than 10 calendar days but less than or equal to 15 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. OR The UFLS entity provided data to its Planning Coordinator(s) but the data was not according to the format specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | The UFLS entity provided data to its Planning Coordinator(s) more than 15 calendar days but less than or equal to 20 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | The UFLS entity provided data to its Planning Coordinator(s) more than 20 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. OR The UFLS entity failed to provide data to its Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. |  | 2021-03-31 | High | The UFLS entity provided less than 100% but more than (and including) 95% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. | The UFLS entity provided less than 95% but more than (and including) 90% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. | The UFLS entity provided less than 90% but more than (and including) 85% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. | The UFLS entity provided less than 85% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. |  | 2021-03-31 | High | The Transmission Owner provided less than 100% but more than (and including) 95% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | The Transmission Owner provided less than 95% but more than (and including) 90% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | The Transmission Owner provided less than 90% but more than (and including) 85% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | The Transmission Owner provided less than 85% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | [18 empty] | TO
Inactive | PRC | PRC-006-4 | R11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: |  | 2021-03-31 | Medium | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than one year but less than or equal to 13 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than 13 months but less than or equal to 14 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than 14 months but less than or equal to 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event within one year of event actuation but failed to evaluate one (1) of the Parts as specified in Requirement R11, Parts11.1 or 11.2. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, failed to conduct and document an assessment of the event and evaluate the Parts as specified in Requirement R11, Parts 11.1 and 11.2. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event within one year of event actuation but failed to evaluate all of the Parts as specified in Requirement R11, Parts 11.1 and 11.2. | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | R12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. |  | 2021-03-31 | Medium | N/A | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, conducted and documented a UFLS design assessment to consider the identified deficiencies greater than two years but less than or equal to 25 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, conducted and documented a UFLS design assessment to consider the identified deficiencies greater than 25 months but less than or equal to 26 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, conducted and documented a UFLS design assessment to consider the identified deficiencies greater than 26 months of event actuation. OR The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, failed to conduct and document a UFLS design assessment to consider the identified deficiencies. | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | R13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. |  | 2021-03-31 | Medium | N/A | N/A | N/A | The Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, failed to coordinate its UFLS event assessment with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event in one of the manners described in Requirement R13 | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | R14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following |  | 2021-03-31 | Low | N/A | N/A | N/A | The Planning Coordinator failed to respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes were made or reasons why changes were not made to the items in Parts 14.1 through 14.3. | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | R15. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. |  | 2021-03-31 | High |  | The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, and developed a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, but exceeded the permissible time frame for development by a period of up to 1 month. | The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, and developed a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, but exceeded the permissible time frame for development by a period greater than 1 month but not more than 2 months. | The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, but failed to develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. OR The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, and developed a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, but exceeded the permissible time frame for development by a period greater than 2 months. | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | D.A.3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from each of these extreme events: • Loss of the entire capability of a generating station. • Loss of all transmission circuits emanating from a generating station, switching station, substation or dc terminal. • Loss of all transmission circuits on a common right-of-way. • Three-phase fault with failure of a circuit breaker to operate and correct operation of a breaker failure protection system and its associated breakers. • Three-phase fault on a circuit breaker, with normal fault clearing. • The operation or partial operation of a RAS for an event or condition for which it was not intended to operate. |  | 2021-03-31 | High | N/A | The Planning Coordinator developed a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, but failed to meet one (1) of the performance characteristic in Parts D.A.3.1, D.A.3.2, or D.A.3.3 in simulations of underfrequency conditions | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area, but failed to meet two (2) of the performance characteristic in Parts D.A.3.1, D.A.3.2, or D.A.3.3 in simulations of underfrequency conditions | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area, but failed to meet all the performance characteristic in Parts D.A.3.1, D.A.3.2, and D.A.3.3 in simulations of underfrequency conditions OR The Planning Coordinator failed to develop a UFLS program including notification of and a schedule for implementation by UFLS entities within its area. | [10 empty] | PCPA
Inactive | PRC | PRC-006-4 | D.A.4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.A.3 for each island identified in Requirement R2. The simulation shall model each of the following; |  | 2021-03-31 | High | N/A | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement D.A.3 but the simulation failed to include one (1) of the items as specified in Parts D.A.4.1, D.A.4.2 or D.A.4.3. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement D.A.3 but the simulation failed to include two (2) of the items as specified in Parts D.A.4.1, D.A.4.2 or D.A.4.3. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement D.A.3 but the simulation failed to include all of the items as specified in Parts D.A.4.1, D.A.4.2 and D.A.4.3. OR The Planning Coordinator failed to conduct and document a UFLS assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.A.3 | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | D.B.1. | Each Planning Coordinator shall participate in a joint regional review with the other Planning Coordinators that develops and documents criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES) that may form islands. | 2021-04-01 |  | Medium | N/A | The Planning Coordinator participated in a joint regional review with the other Planning Coordinators that developed and documented criteria but failed to include the consideration of historical events, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas, that may form islands OR The Planning Coordinator participated in a joint regional review with the other Planning Coordinators that developed and documented criteria but failed to include the consideration of system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas, that may form islands | The Planning Coordinator participated in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria but failed to include the consideration of historical events and system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas, that may form islands | The Planning Coordinator failed to participate in a joint regional review with the other Planning Coordinators in the WECC Regional Entity area that developed and documented criteria to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas that may form islands | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | D.B.2. | Each Planning Coordinator shall identify one or more islands from the regional review (per D.B.1) to serve as a basis for designing a Western Interconnection-wide coordinated UFLS program including: | 2021-04-01 |  | Medium | N/A | N/A | The Planning Coordinator identified an island(s) from the regional review to serve as a basis for designing its UFLS program but failed to include one (1) of the parts as specified in Requirement D.B.2, Parts D.B.2.1 or D.B.2.2 | The Planning Coordinator identified an island(s) from the regional review to serve as a basis for designing its UFLS program but failed to include all of the parts as specified in Requirement D.B.2, Parts D.B.2.1 or D.B.2.2 OR The Planning Coordinator failed to identify any island(s) from the regional review to serve as a basis for designing its UFLS program. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | D.B.3. | Each Planning Coordinator shall adopt a UFLS program, coordinated across the Western Interconnection, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | 2021-04-01 |  | High | N/A | The Planning Coordinator adopted a UFLS program, coordinated across the Western Interconnection that included notification of and a schedule for implementation by UFLS entities within its area, but failed to meet one (1) of the performance characteristic in Requirement D.B.3, Parts D.B.3.1, D.B.3.2, or D.B.3.3 in simulations of underfrequency conditions | The Planning Coordinator adopted a UFLS program, coordinated across the Western Interconnection that included notification of and a schedule for implementation by UFLS entities within its area, but failed to meet two (2) of the performance characteristic in Requirement D.B.3, Parts D.B.3.1, D.B.3.2, or D.B.3.3 in simulations of underfrequency conditions | The Planning Coordinator adopted a UFLS program, coordinated across the Western Interconnection that included notification of and a schedule for implementation by UFLS entities within its area, but failed to meet all the performance characteristic in Requirement D.B.3, Parts D.B.3.1, D.B.3.2, and D.B.3.3 in simulations of underfrequency conditions OR The Planning Coordinator failed to adopt a UFLS program, coordinated across the Western Interconnection , including notification of and a schedule for implementation by UFLS entities within its area. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | D.B.4. | Each Planning Coordinator shall participate in and document a coordinated UFLS design assessment with the other Planning Coordinators in the Western Interconnection at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2. The simulation shall model each of the following: | 2021-04-01 |  | High | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators across the Western Interconnection at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include one (1) of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators across the Western Interconnection at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include two (2) of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators across the Western Interconnection at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include three (3) of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. | The Planning Coordinator participated in and documented a coordinated UFLS assessment with the other Planning Coordinators across the Western Interconnection at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 but the simulation failed to include four (4) or more of the items as specified in Requirement D.B.4, Parts D.B.4.1 through D.B.4.7. OR The Planning Coordinator failed to participate in and document a coordinated UFLS assessment with the other Planning Coordinators across the Western Interconnection at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.B.3 for each island identified in Requirement D.B.2 | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | D.B.11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall participate in and document a coordinated event assessment with all affected Planning Coordinators to conduct and document an assessment of the event within one year of event actuation to evaluate:[VRF: Medium][Time Horizon: Operations Assessment] | 2021-04-01 |  | Medium | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than one year but less than or equal to 13 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than 13 months but less than or equal to 14 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than 14 months but less than or equal to 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event within one year of event actuation but failed to evaluate one (1) of the parts as specified in Requirement D.B.11, Parts D.B.11.1 or D.B.11.2. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event and evaluated the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2 within a time greater than 15 months of actuation.OR The Planning Coordinator, in whose area an islanding event resulting in system frequency The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, participated in and documented a coordinated event assessment with all Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event within one year of event actuation but failed to evaluate all of the parts as specified in Requirement D.B.11, Parts D.B.11.1 and D.B.11.2. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | D.B.12. | Each Planning Coordinator, in whose islanding event assessment (per D.B.11) UFLS program deficiencies are identified, shall participate in and document a coordinated UFLS design assessment of the UFLS program with all other Planning Coordinators in the Western Interconnection to consider the identified deficiencies within two years of event actuation. [VRF: Medium][Time Horizon: Operations Assessment] | 2021-04-01 |  | Medium | N/A | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, participated in and documented a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators across the Western Interconnection to consider the identified deficiencies in greater than two years but less than or equal to 25 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, participated in and documented a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators across the Western Interconnection to consider the identified deficiencies in greater than 25 months but less than or equal to 26 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, participated in and documented a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators across the Western Interconnection to consider the identified deficiencies in greater than 26 months of event actuation. OR The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement D.B.11, failed to participate in and document a coordinated UFLS design assessment of the coordinated UFLS program with the other Planning Coordinators across the Western Interconnection to consider the identified deficiencies | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | R1. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. | 2021-04-01 |  | Medium | N/A | The Planning Coordinator developed and documented criteria but failed to include the consideration of historical events, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. OR The Planning Coordinator developed and documented criteria but failed to include the consideration of system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas, that may form islands. | The Planning Coordinator developed and documented criteria but failed to include the consideration of historical events and system studies, to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas, that may form islands. | The Planning Coordinator failed to develop and document criteria to select portions of the BES, including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas, that may form islands. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | R2. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: | 2021-04-01 |  | Medium | N/A | The Planning Coordinator identified an island(s) to serve as a basis for designing its UFLS program but failed to include one (1) of the Parts as specified in Requirement R2, Parts 2.1, 2.2, or 2.3. | The Planning Coordinator identified an island(s) to serve as a basis for designing its UFLS program but failed to include two (2) of the Parts as specified in Requirement R2, Parts 2.1, 2.2, or 2.3. | The Planning Coordinator identified an island(s) to serve as a basis for designing its UFLS program but failed to include all of the Parts as specified in Requirement R2, Parts 2.1, 2.2, or 2.3. OR The Planning Coordinator failed to identify any island(s) to serve as a basis for designing its UFLS program. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | R3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). | 2021-04-01 |  | High | N/A | The Planning Coordinator developed a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area where imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s)., but failed to meet one (1) of the performance characteristic in Requirement R3, Parts 3.1, 3.2, or 3.3 in simulations of underfrequency conditions. | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area where imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s)., but failed to meet two (2) of the performance characteristic in Requirement R3, Parts 3.1, 3.2, or 3.3 in simulations of underfrequency conditions. | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area where imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s).,but failed to meet all the performance characteristic in Requirement R3, Parts 3.1, 3.2, and 3.3 in simulations of underfrequency conditions. OR The Planning Coordinator failed to develop a UFLS program including notification of and a schedule for implementation by UFLS entities within its area | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | R4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: | 2021-04-01 |  | High | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 for each island identified in Requirement R2 but the simulation failed to include one (1) of the items as specified in Requirement R4, Parts 4.1 through 4.7. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 for each island identified in Requirement R2 but the simulation failed to include two (2) of the items as specified in Requirement R4, Parts 4.1 through 4.7. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 for each island identified in Requirement R2 but the simulation failed to include three (3) of the items as specified in Requirement R4, Parts 4.1 through 4.7. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement R3 but simulation failed to include four (4) or more of the items as specified in Requirement R4, Parts 4.1 through 4.7. OR The Planning Coordinator failed to conduct and document a UFLS assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2 | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | R5. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | 2021-04-01 |  | High | N/A | N/A | N/A | The Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, failed to coordinate its UFLS program design through one of the manners described in Requirement R5. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | R6. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | 2021-04-01 |  | Low | N/A | N/A | N/A | The Planning Coordinator failed to maintain a UFLS database for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | R7. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | 2021-04-01 |  | Low | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 30 calendar days and up to and including 40 calendar days following the request. | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 40 calendar days but less than and including 50 calendar days following the request. | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 50 calendar days but less than and including 60 calendar days following the request. | The Planning Coordinator provided its UFLS database to other Planning Coordinators more than 60 calendar days following the request. OR The Planning Coordinator failed to provide its UFLS database to other Planning Coordinators. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | 2021-04-01 |  | Low | The UFLS entity provided data to its Planning Coordinator(s) less than or equal to 10 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | The UFLS entity provided data to its Planning Coordinator(s) more than 10 calendar days but less than or equal to 15 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. OR The UFLS entity provided data to its Planning Coordinator(s) but the data was not according to the format specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | The UFLS entity provided data to its Planning Coordinator(s) more than 15 calendar days but less than or equal to 20 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | The UFLS entity provided data to its Planning Coordinator(s) more than 20 calendar days following the schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. OR The UFLS entity failed to provide data to its Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. |  |  | DP | DP-UFLS | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006-5 | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. [VRF: High][Time Horizon: Long-term Planning] | 2021-04-01 |  | High | The UFLS entity provided less than 100% but more than (and including) 95% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. | The UFLS entity provided less than 95% but more than (and including) 90% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. | The UFLS entity provided less than 90% but more than (and including) 85% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. | The UFLS entity provided less than 85% of automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) area in which it owns assets. |  |  | DP | DP-UFLS | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006-5 | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. [VRF: High][Time Horizon: Long-term Planning] | 2021-04-01 |  | High | The Transmission Owner provided less than 100% but more than (and including) 95% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | The Transmission Owner provided less than 95% but more than (and including) 90% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | The Transmission Owner provided less than 90% but more than (and including) 85% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | The Transmission Owner provided less than 85% automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | [18 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006-5 | R11. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: | 2021-04-01 |  | Medium | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than one year but less than or equal to 13 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than 13 months but less than or equal to 14 months of actuation. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than 14 months but less than or equal to 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event within one year of event actuation but failed to evaluate one (1) of the Parts as specified in Requirement R11, Parts11.1 or 11.2. | The Planning Coordinator, in whose area a BES islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event and evaluated the parts as specified in Requirement R11, Parts 11.1 and 11.2 within a time greater than 15 months of actuation. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, failed to conduct and document an assessment of the event and evaluate the Parts as specified in Requirement R11, Parts 11.1 and 11.2. OR The Planning Coordinator, in whose area an islanding event resulting in system frequency excursions below the initializing set points of the UFLS program, conducted and documented an assessment of the event within one year of event actuation but failed to evaluate all of the Parts as specified in Requirement R11, Parts 11.1 and 11.2. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | R12. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | 2021-04-01 |  | Medium | N/A | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, conducted and documented a UFLS design assessment to consider the identified deficiencies greater than two years but less than or equal to 25 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, conducted and documented a UFLS design assessment to consider the identified deficiencies greater than 25 months but less than or equal to 26 months of event actuation. | The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, conducted and documented a UFLS design assessment to consider the identified deficiencies greater than 26 months of event actuation. OR The Planning Coordinator, in which UFLS program deficiencies were identified per Requirement R11, failed to conduct and document a UFLS design assessment to consider the identified deficiencies. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | R13. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | 2021-04-01 |  | Medium | N/A | N/A | N/A | The Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, failed to coordinate its UFLS event assessment with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event in one of the manners described in Requirement R13 | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | R14. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following | 2021-04-01 |  | Low | N/A | N/A | N/A | The Planning Coordinator failed to respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes were made or reasons why changes were not made to the items in Parts 14.1 through 14.3. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | R15. | Each Planning Coordinator that conducts a UFLS design assessment under Requirement R4, R5, or R12 and determines that the UFLS program does not meet the performance characteristics in Requirement R3, shall develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. | 2021-04-01 |  | High | N/A | The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, and developed a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, but exceeded the permissible time frame for development by a period of up to 1 month. | The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, and developed a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, but exceeded the permissible time frame for development by a period greater than 1 month but not more than 2 months. | The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, but failed to develop a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area. OR The Planning Coordinator determined, through a UFLS design assessment performed under Requirement R4, R5, or R12, that the UFLS program did not meet the performance characteristics in Requirement R3, and developed a Corrective Action Plan and a schedule for implementation by the UFLS entities within its area, but exceeded the permissible time frame for development by a period greater than 2 months. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | D.A.3. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from each of these extreme events: • Loss of the entire capability of a generating station. • Loss of all transmission circuits emanating from a generating station, switching station, substation or dc terminal. • Loss of all transmission circuits on a common right-of-way. • Three-phase fault with failure of a circuit breaker to operate and correct operation of a breaker failure protection system and its associated breakers. • Three-phase fault on a circuit breaker, with normal fault clearing. • The operation or partial operation of a RAS for an event or condition for which it was not intended to operate. | 2021-04-01 |  | High | N/A | The Planning Coordinator developed a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, but failed to meet one (1) of the performance characteristic in Parts D.A.3.1, D.A.3.2, or D.A.3.3 in simulations of underfrequency conditions | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area, but failed to meet two (2) of the performance characteristic in Parts D.A.3.1, D.A.3.2, or D.A.3.3 in simulations of underfrequency conditions | The Planning Coordinator developed a UFLS program including notification of and a schedule for implementation by UFLS entities within its area, but failed to meet all the performance characteristic in Parts D.A.3.1, D.A.3.2, and D.A.3.3 in simulations of underfrequency conditions OR The Planning Coordinator failed to develop a UFLS program including notification of and a schedule for implementation by UFLS entities within its area. |  |  | DP | DP-UFLS | [6 empty] | PCPA | [7 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006-5 | D.A.4. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.A.3 for each island identified in Requirement R2. The simulation shall model each of the following; | 2021-04-01 |  | High | N/A | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement D.A.3 but the simulation failed to include one (1) of the items as specified in Parts D.A.4.1, D.A.4.2 or D.A.4.3. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement D.A.3 but the simulation failed to include two (2) of the items as specified in Parts D.A.4.1, D.A.4.2 or D.A.4.3. | The Planning Coordinator conducted and documented a UFLS assessment at least once every five years that determined through dynamic simulation whether the UFLS program design met the performance characteristics in Requirement D.A.3 but the simulation failed to include all of the items as specified in Parts D.A.4.1, D.A.4.2 and D.A.4.3. OR The Planning Coordinator failed to conduct and document a UFLS assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement D.A.3 | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-5 | D.B.5. | Reserved. | 2021-04-01
Mandatory Subject to Enforcement | PRC | PRC-006-5 | D.B.6. | Reserved. | 2021-04-01
Mandatory Subject to Enforcement | PRC | PRC-006-5 | D.B.7. | Reserved | 2021-04-01
Mandatory Subject to Enforcement | PRC | PRC-006-5 | D.B.8. | Reserved. | 2021-04-01
Mandatory Subject to Enforcement | PRC | PRC-006-5 | D.B.9. | Reserved. | 2021-04-01
Mandatory Subject to Enforcement | PRC | PRC-006-5 | D.B.10. | Reserved | 2021-04-01
Inactive | PRC | PRC-006-NPCC-1 | R1. | Each Planning Coordinator shall establish requirements for entities aggregating their UFLS programs for each anticipated island and requirements for compensatory load shedding based on islanding criteria (required by the NERC PRC Standard on UFLS). | 2016-01-01 | 2020-03-31 | Medium | N/A | N/A | Planning Coordinator did not establish requirements for entities aggregating their UFLS programs. or Did not establish requirements for compensatory load shedding. | Planning Coordinator did not establish requirements for entities aggregating their UFLS programs and did not establish requirements for compensatory load shedding. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-NPCC-1 | R2. | Each Planning Coordinator shall, within 30 days of completion of its system studies required by the NERC PRC Standard on UFLS, identify to the Regional Entity the generation facilities within its Planning Coordinator Area necessary to support the UFLS program performance characteristics. | 2016-01-01 | 2020-03-31 | Medium | The Planning Coordinator identified the generation facilities within its Planning Coordinator Area necessary to support the UFLS program, but did so more than 30 days but less than 41 days after completion of the system studies. | The Planning Coordinator identified the generation facilities within its Planning Coordinator Area necessary to support the UFLS program, but did so more than 40 days but less than 51 days after completion of the system studies. | The Planning Coordinator identified the generation facilities within its Planning Coordinator Area necessary to support the UFLS program, but did so more than 50 days but less than 61 days after completion of the system studies. | The Planning Coordinator identified the generation facilities within its Planning Coordinator Area necessary to support the UFLS program, but did so more than 60 days after completion of the system studies. Or The Planning Coordinator did not identify the generation facilities within its Planning Coordinator Area necessary to support the UFLS program. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-NPCC-1 | R3. | Each Planning Coordinator shall provide to the Transmission Owner, Distribution Provider, and Generator Owner within 30 days upon written request the requirements for entities aggregating the UFLS programs and requirements for compensatory load shedding program derived from each Planning Coordinator’s system studies as determined by Requirement R1. | 2016-01-01 | 2020-03-31 | Low | The Planning Coordinator provided the requested information, but did so more than 30 days but less than 41 days to the requesting entity. | The Planning Coordinator provided the requested information, but did so more than 40 days but less than 51 days to the requesting entity. | The Planning Coordinator provided the requested information, but did so more than 50 days but less than 61 days to the requesting entity. | The Planning Coordinator provided the requested information, but did so more than 60 days after the request. Or The Planning Coordinator failed to provide the requested information. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-NPCC-1 | R4. | Each Distribution Provider and Transmission Owner in the Eastern Interconnection portion of NPCC shall implement an automatic UFLS program reflecting normal operating conditions excluding outages for its Facilities based on frequency thresholds, total nominal operating time and amounts specified in Attachment C, Tables 1 through 3, or shall collectively implement by mutual agreement with one or more Distribution Providers and Transmission Owners within the same island identified in Requirement R1 and acting as a single entity, provide an aggregated automatic UFLS program that sheds their coincident peak aggregated net Load, based on frequency thresholds, total nominal operating time and amounts specified in Attachment C, Tables 1 through 3. | 2016-01-01 | 2020-03-31 | High | N/A | N/A | N/A | The Distribution Provider or Transmission Owner failed to implement an automatic UFLS program reflecting normal operating conditions excluding outages, for its Facilities or collectively implemented by mutual agreement with one or more Distribution Providers and Transmission Owners within the same island identified in Requirement R1, an aggregated automatic UFLS program that sheds Load based on frequency thresholds, total nominal operating time, and amounts specified in the appropriate included tables. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-NPCC-1 | R5. | Each Distribution Provider or Transmission Owner that must arm its load to trip on underfrequency in order to meet its requirements as specified and by doing so exceeds the tolerances and/or deviates from the number of stages and frequency set points of the UFLS program as specified in the tables contained in Requirement R4 above, as applicable depending on its total peak net Load shall: | 2016-01-01 | 2020-03-31 | High | N/A | The Distribution Provider or Transmission Owner armed its load to trip on underfrequency in order to meet its minimum obligations and by doing so exceeded the tolerances and/or deviated from the number of stages and frequency set points of the UFLS program as specified in the tables contained in Attachment C, as applicable depending on their total peak net Load, but did not inform the Planning Coordinator of the need to exceed the stated tolerances of UFLS Table 2 or Table 3, and in the case of Table 2 only, the need to deviate from providing two stages of UFLS. | The Distribution Provider or Transmission Owner armed its load to trip on underfrequency in order to meet its minimum obligations and by doing so exceeded the tolerances and/or deviated from the number of stages and frequency set points of the UFLS program as specified in the tables contained in Attachment C, as applicable depending on their total peak net Load, but did not provide the Planning Coordinator with an analysis demonstrating that no alternative load shedding solution is available that would allow the Distribution Provider or Transmission Owner to comply with the appropriate table. | The Distribution Provider or Transmission Owner did not arm its load to trip on underfrequency in order to meet its minimum obligations and in doing so exceeded the tolerances and/or deviated from the number of stages and frequency set points of the UFLS program as specified in the tables contained in Attachment C, as applicable depending on their total peak net Load. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-NPCC-1 | R6. | Each Distribution Provider and Transmission Owner in the Québec Interconnection portion of NPCC shall implement an automatic UFLS program for its Facilities based on the frequency thresholds, slopes, total nominal operating time and amounts specified in Attachment C, Table 4 or shall collectively implement by mutual agreement with one or more Distribution Providers and Transmission Owners within the same island, identified in Requirement R1, an aggregated automatic UFLS program that sheds Load based on the frequency thresholds, slopes, total nominal operating time and amounts specified in Attachment C, Table 4. | 2016-01-01 | 2020-03-31 | High | N/A | N/A | N/A | The Distribution Provider or Transmission Owner in the Québec Interconnection portion of NPCC did not implement an automatic UFLS program for its Facilities based on the frequency thresholds, slopes, total nominal operating time and amounts specified in Attachment C, Table 4 or did not collectively implement by mutual agreement with one or more Distribution Providers and Transmission Owners within the same island, identified in Requirement R1, an aggregated automatic UFLS program that sheds Load based on the frequency thresholds, slopes, total nominal operating time and amounts specified in Attachment C, Table 4. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-NPCC-1 | R7. | Each Distribution Provider and Transmission Owner shall set each underfrequency relay that is part of its region’s UFLS program with the following minimum time delay: | 2016-01-01 | 2020-03-31 | High | N/A | N/A | N/A | The Distribution Provider or Transmission Owner failed to set an underfrequency relay that is part of its region’s UFLS program as specified in Requirement R7. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-NPCC-1 | R8. | Each Planning Coordinator shall develop and review once per calendar year settings for inhibit thresholds (such as but not limited to voltage, current and time) to be utilized within its region's UFLS program. | 2015-07-01 | 2020-03-31 | Medium | N/A | N/A | The Planning Coordinator developed inhibit thresholds as specified in Requirement R8 but did not perform the review once per calendar year. | The Planning Coordinator did not develop inhibit thresholds as specified in Requirement R8. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-NPCC-1 | R9. | Each Planning Coordinator shall provide each Transmission Owner and Distribution Provider within its Planning Coordinator area the applicable inhibit thresholds within 30 days of the initial determination of those inhibit thresholds and within 30 days of any changes to those thresholds. | 2015-07-01 | 2020-03-31 | Medium | The Planning Coordinator provided to a Transmission Owner or Distribution Provider within its Planning Coordinator area the applicable inhibit thresholds more than 30 days but less than 41 days of the initial determination or any subsequent change to the inhibit thresholds. | The Planning Coordinator provided to a Transmission Owner or Distribution Provider within its Planning Coordinator area the applicable inhibit thresholds more than 40 days but less than 51 days of the initial determination or any subsequent change to the inhibit thresholds. | The Planning Coordinator provided to a Transmission Owner or Distribution Provider within its Planning Coordinator area the applicable inhibit thresholds more than 50 days but less than 61 days of the initial determination or any subsequent change to the inhibit thresholds. | The Planning Coordinator provided to a Transmission Owner or Distribution Provider within its Planning Coordinator area the applicable inhibit thresholds more than 60 days after the initial determination or any subsequent change to the inhibit thresholds OR The Planning Coordinator did not provide to a Transmission Owner or Distribution Provider within its Planning Coordinator area the applicable inhibit thresholds. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-NPCC-1 | R10. | Each Distribution Provider and Transmission Owner shall implement the inhibit threshold settings based on the notification provided by the Planning Coordinator in accordance with Requirement R9. | 2015-07-01 | 2020-03-31 | High | N/A | N/A | N/A | The Distribution Provider or Transmission Owner did not implement the inhibit threshold based on the notification provided by the Planning Coordinator in accordance with Requirement R9. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-NPCC-1 | R11. | Each Distribution Provider and Transmission Owner shall develop and submit an implementation plan within 90 days of the request from the Planning Coordinator for approval by the Planning Coordinator in accordance with R9. | 2015-07-01 | 2020-03-31 | Low | The Distribution Provider or Transmission Owner developed and submitted its implementation plan more than 90 days but less than 101 days after the request from the Planning Coordinator. | The Distribution Provider or Transmission Owner developed and submitted its implementation plan more than 100 days but less than 111 days after the request from the Planning Coordinator. | The Distribution Provider or Transmission Owner developed and submitted its implementation plan more than 110 days but less than 121 days after the request from the Planning Coordinator. | The Distribution Provider or Transmission Owner developed and submitted its implementation plan more than 120 days after the request from the Planning Coordinator. Or The Distribution Provider or Transmission Owner did not develop its implementation plan. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-NPCC-1 | R12. | Each Transmission Owner and Distribution Provider shall annually provide documentation, with no more than 15 months between updates, to its Planning Coordinator of the actual net Load that would have been shed by the UFLS relays at each UFLS stage coincident with their integrated hourly peak net Load during the previous year, as determined by measuring actual metered Load through the switches that would be opened by the UFLS relays. | 2015-07-01 | 2020-03-31 | Low | N/A | N/A | N/A | The Transmission Owner or Distribution Provider did not provide documentation to its Planning Coordinator of actual net load data or updates to the data that would be shed by the UFLS relays, as determined by measuring actual metered load through the switches that would be opened by the UFLS relays, that were armed to shed at each UFLS stage coincident with their integrated hourly peak during the previous year |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-NPCC-1 | R13. | Each Generator Owner shall set each generator underfrequency trip relay, if so equipped, below the appropriate generator underfrequency trip protection settings threshold curve in Figure 1, except as otherwise exempted in Requirements R16 and R19. | 2015-07-01 | 2020-03-31 | High | N/A | N/A | N/A | The Generator Owner did not set each generator underfrequency trip relay, if so equipped, below the appropriate generator underfrequency trip protection settings threshold curve in Figure 1, except as otherwise exempted. |  |  |  | DP-UFLS |  | GO
Inactive | PRC | PRC-006-NPCC-1 | R14. | Each Generator Owner shall transmit the generator underfrequency trip setting and time delay to its Planning Coordinator within 45 days of the Planning Coordinator’s request. | 2015-07-01 | 2020-03-31 | High | The Generator Owner transmitted the generator underfrequency trip setting and time delay to its Planning Coordinator more than 45 days and less than 56 days of the Planning Coordinator’s request. | The Generator Owner transmitted the generator underfrequency trip setting and time delay to its Planning Coordinator more than 55 days and less than 66 days of the Planning Coordinator’s request. | The Generator Owner transmitted the generator underfrequency trip setting and time delay to its Planning Coordinator more than 65 days and less than 76 days of the Planning Coordinator’s request. | The Generator Owner transmitted the generator underfrequency trip setting and time delay to its Planning Coordinator more than 75days after the Planning Coordinator’s request. Or The Generator Owner did not transmit the generator underfrequency trip setting and time delay to its Planning Coordinator. |  |  |  | DP-UFLS |  | GO
Inactive | PRC | PRC-006-NPCC-1 | R15. | Each Generator Owner with a new generating unit, scheduled to be in service on or after the effective date of this Standard, or an existing generator increasing its net capability by greater than 10% shall: | 2015-07-01 | 2020-03-31 | High | N/A | N/A | The Generator Owner did not fulfill the obligation of Requirement R15; Part 15.1 OR did not fulfill the obligation of Requirement R15, Part 15.2. | The Generator Owner did not fulfill the obligation of Requirement R15, Part 15.1 and did not fulfill the obligation of Requirement R15, Part 15.2. |  |  |  | DP-UFLS |  | GO
Inactive | PRC | PRC-006-NPCC-1 | R16. | Each Generator Owner of existing non-nuclear units in service prior to the effective date of this standard that have underfrequency protections set to trip above the appropriate curve in Figure 1 shall: | 2015-07-01 | 2020-03-31 | High | N/A | The Generator Owner did not fulfill the obligation of Requirement R16, Part 16.2. | The Generator Owner did not fulfill the obligation of Requirement R16; Part 16.1 OR did not fulfill the obligation of Requirement R16, Part 16.3. | The Generator Owner did not fulfill the obligation of Requirement R16, Part 16.1 and did not fulfill the obligation of Requirement R16, Part 16.3. |  |  |  | DP-UFLS |  | GO
Inactive | PRC | PRC-006-NPCC-1 | R17. | Each Planning Coordinator in Ontario, Quebec and the Maritime provinces shall apply the criteria described in Attachment A to determine the compensatory load shedding that is required in Requirement R16.3 for generating units in its respective NPCC area. | 2015-07-01 | 2020-03-31 | High | N/A | N/A | N/A | The Planning Coordinator did not apply the methodology described in Attachment A to determine the compensatory load shedding that is required. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-NPCC-1 | R18. | Each Generator Owner, Distribution Provider or Transmission Owner within the Planning Coordinator area of ISO-NE or the New York ISO shall apply the criteria described in Attachment B to determine the compensatory load shedding that is required in Requirement R16.3 for generating units in its respective NPCC area. | 2015-07-01 | 2020-03-31 | High | N/A | N/A | N/A | The Generator Owner, Distribution Provider, or Transmission Owner did not apply the methodology described in Attachment B to determine the compensatory load shedding that is required. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-006-NPCC-1 | R19. | Each Generator Owner of existing nuclear generating plants with units that have underfrequency relay threshold settings above the Eastern Interconnection generator tripping curve in Figure 1, based on their licensing design basis, shall: | 2015-07-01 | 2020-03-31 | High | N/A | The Generator Owner did not fulfill the obligation of Requirement R19, Part 19.3. | The Generator Owner did not fulfill the obligation of Requirement R19; Part 19.1 OR did not fulfill the obligation of Requirement R19, Part 19.2. | The Generator Owner did not fulfill the obligation of Requirement R19, Part 19.1 and did not fulfill the obligation of Requirement R19, Part 19.2. |  |  |  | DP-UFLS |  | GO
Inactive | PRC | PRC-006-NPCC-1 | R20. | The Planning Coordinator shall update its UFLS program database as specified by the NERC PRC Standard on UFLS. This database shall include the following information: | 2015-07-01 | 2020-03-31 | Low | The Planning Coordinator did not have data in its database for one of the parameters listed in Requirement 20, Parts 20.1 through 20.5. | The Planning Coordinator did not have data in its database for two of the parameters listed in Requirement 20, Parts 20.1 through 20.5. | The Planning Coordinator did not have data in its database for three of the parameters listed in Requirement 20, Parts 20.1 through 20.5. | The Planning Coordinator did not have data in its database for four or more of the parameters listed in Requirement 20, Parts 20.1 through 20.5. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-NPCC-1 | R21. | Each Planning Coordinator shall notify each Distribution Provider, Transmission Owner, and Generator Owner within its Planning Coordinator area of changes to load distribution needed to satisfy UFLS program performance characteristics as specified by the NERC PRC Standard on UFLS. | 2015-07-01 | 2020-03-31 | High | N/A | N/A | N/A | The Planning Coordinator did not notify a Distribution Provider, Transmission Owner, or Generator Owner within its Planning Coordinator area of changes to load distribution needed to satisfy UFLS program requirements. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-NPCC-1 | R22. | Each Distribution Provider, Transmission Owner and Generator Owner shall implement the load distribution changes based on the notification provided by the Planning Coordinator in accordance with Requirement R21. | 2015-07-01 | 2020-03-31 | High | N/A | N/A | N/A | The Distribution Provider, Transmission Owner, or Generator Owner did not implement the load distribution changes based on the notification provided by the Planning Coordinator. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Inactive | PRC | PRC-006-NPCC-1 | R23. | Each Distribution Provider, Transmission Owner and Generator Owner shall develop and submit an implementation plan within 90 days of the request from the Planning Coordinator for approval by the Planning Coordinator in accordance with Requirement R21. | 2015-07-01 | 2020-03-31 | Low | The Distribution Provider. Transmission Owner or Generator Owner developed and submitted its implementation plan more than 90 days but less than 101 days after the request from the Planning Coordinator. | The Distribution Provider. Transmission Owner or Generator Owner developed and submitted its implementation plan more than 100 days but less than 111 days after the request from the Planning Coordinator. | The Distribution Provider. Transmission Owner or Generator Owner developed and submitted its implementation plan more than 110 days but less than 121 days after the request from the Planning Coordinator. | The Distribution Provider. Transmission Owner or Generator Owner developed and submitted its implementation plan more than 120 days after the request from the Planning Coordinator. Or The Distribution Provider. Transmission Owner or Generator Owner did not develop its implementation plan. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R1. | Each Planning Coordinator in the Eastern Interconnection portion of NPCC shall design an UFLS program, pertaining to islands wholly within the NPCC Region, having performance characteristics that prevents the frequency from remaining below 59.5 Hz for more than 30 seconds in accordance with Figure 1. | 2020-02-18 |  | High | N/A | N/A | N/A | The Planning Coordinator failed to design an UFLS program having performance characteristics that prevent frequency from remaining below 59.5 Hz in accordance with Figure 1. |  |  |  | DP-UFLS | [6 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R2. | Each Planning Coordinator shall provide UFLS island boundaries, as identified per the NERC continent-wide PRC-006 Standard on UFLS, to Distribution Providers, Generator Owners, and Transmission Owners within 30 calendar days of receipt of a request. | 2020-02-18 |  | Low | The Planning Coordinator provided its UFLS island boundaries, as identified per the NERC continent-wide PRC-006 Standard on UFLS but did so more than 30 calendar days and up to and including 40 days following a request. | The Planning Coordinator provided its UFLS island boundaries, as identified per the NERC continent-wide PRC-006 Standard on UFLS but did so more than 40 calendar days but less than and including 50 days following a request. | The Planning Coordinator provided its UFLS island boundaries, as identified per the NERC continent-wide PRC-006 Standard on UFLS but did so more than 50 calendar days but less than and including 60 days following a request. | The Planning Coordinator failed to provide its UFLS island boundaries, as identified per the NERC continent-wide PRC-006 Standard on UFLS. within 60 calendar days following a request. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R3. | Each Distribution Provider and Transmission Owner in the Eastern Interconnection portion of NPCC shall implement an automatic UFLS program, reflecting normal operating conditions, excluding outages. The automatic UFLS program shall be implemented on an island basis for each identified island per the NERC continent-wide PRC-006 Standard on UFLS as follows: • The UFLS program shall be implemented by each Distribution Provider and Transmission Owner according to the frequency thresholds, nominal operating times, and load shedding amounts specified in Attachment C, Tables 1-3; or • The UFLS program shall be implemented collectively by multiple Distribution Providers or Transmission Owners, as long as they reside in the same UFLS island identified by the Planning Coordinator per Requirement R2. These multiple Distribution Providers or Transmission Owners, via mutual agreement, shall act as a single entity to provide an aggregated automatic UFLS program that sheds their coincident peak aggregated net Load according to the frequency thresholds, total nominal operating time, and load shedding amounts specified in Attachment C, Tables 1-3. | 2021-04-01 |  | High | The Distribution Provider or Transmission Owner failed to apply appropriate settings on 20% or less of the relays identified as included in the UFLS program, or amount of load tripped is within 10% deviation from the required amount of Load required to be shed at each stage | The Distribution Provider or Transmission Owner failed to apply appropriate settings on 20%-40% of the relays identified as included in the UFLS program, or amount of load tripped is within 20% deviation from the required amount of Load required to be shed at each stage | The Distribution Provider or Transmission Owner failed to apply appropriate settings on 40%-60% of the relays identified as included in the UFLS program, or amount of load tripped is within 30% deviation from the required amount of Load required to be shed at each stage. | The Distribution Provider or Transmission Owner failed to apply appropriate settings on > 60% of the relays identified as included in the UFLS program, or amount of load tripped has a > 30% deviation from the required amount of Load required to be shed at each stage |  |  | DP | DP-UFLS | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R4. | Each Distribution Provider or Transmission Owner in the Eastern Interconnection portion of NPCC that does not meet the UFLS program parameters specified in Attachment C, Table 1-3, and each Distribution Provider or Transmission Owner in the Quebec Interconnection that does not meet the UFLS program parameters specified by its Planning Coordinator shall: • Within 30 calendar days of determining that it does not meet the specified parameters, notify its Planning Coordinator that it does not meet the UFLS program parameters; and • Within the following 180 calendar days from notification of the Planning Coordinator, (1) develop a Corrective Action Plan and a schedule for implementation that is mutually agreed upon with its Planning Coordinator or (2) provide its Planning Coordinator with a technical study that demonstrates that the deviations from the program parameters will not result in failure of UFLS performance criteria being met for any island. The technical study must be acceptable to the Planning Coordinator prior to implementing deviations from program parameters and shall demonstrate coordination with UFLS programs of all entities residing within the same island(s) identified by the Planning Coordinator in Requirement R2. The technical study shall also demonstrate coordination with other UFLS programs of adjoining Planning Coordinators, or (3) provide its Planning Coordinator with an analysis demonstrating that no alternative load shedding solution is available that would allow the Distribution Provider or Transmission Owner to comply with UFLS Attachment C Table 2 or Attachment C Table 3. | 2020-02-18 |  | High | The Distribution Provider or Transmission Owner that cannot meet the tolerances and/or number of stages and frequency set points specified in the UFLS Program fulfilled its obligations for Requirement R5, Parts %.1 through Part 5.4 but exceeded the permissible time frame for one or more of the 4 items by a period of up to 10 calendar days but less than or equal to 20 calendar days. | The Distribution Provider or Transmission Owner that cannot meet the tolerances and/or number of stages and frequency set points specified in the UFLS Program fulfilled its obligations for Requirement R5, Parts %.1 through Part 5.4 but exceeded the permissible time frame for one or more of the 4 items within a time greater than 20 calendar days but less than or equal to 30 calendar days. | The Distribution Provider or Transmission Owner that cannot meet the tolerances and/or number of stages and frequency set points specified in the UFLS Program fulfilled its obligations but exceeded the permissible time frame for one or more of the 4 items within a time greater than 30 calendar days but less than or equal to 60 calendar days. | The Distribution Provider or Transmission Owner that cannot meet the tolerances and/or number of stages and frequency set points specified in the UFLS Program failed to meet all of items in Requirement 5 within 60 calendar days of permissible time for each item. |  |  | DP | DP-UFLS | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R5. | Each Planning Coordinator shall develop and review settings for inhibit thresholds at least once per five calendar years (such as, but not limited to, voltage, current and time) to be utilized within its region’s UFLS program. | 2020-02-18 |  | Medium | The Planning Coordinator developed or reviewed settings for inhibit thresholds at least once per five calendar years, for less than 100% but more than (and including) 95% of relays within its region’s UFLS program. | The Planning Coordinator developed or reviewed settings for inhibit thresholds at least once per five calendar years, for less than 95% but more than (and including) 90% of relays within its region’s UFLS program. | The Planning Coordinator developed or reviewed settings for inhibit thresholds at least once per five calendar years, for less than 90% but more than (and including) 85% of relays within its region’s UFLS program. | The Planning Coordinator developed or reviewed settings for inhibit thresholds at least once per five calendar years, for less than 85% of relays within its region’s UFLS program. |  |  |  | DP-UFLS | [6 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R6. | Each Planning Coordinator shall provide each Transmission Owner and Distribution Provider within its Planning Coordinator area the applicable inhibit thresholds within 30 calendar days of any changes. | 2020-02-18 |  | Low | The Planning Coordinator provided to a Transmission Owner or Distribution Provider within its Planning Coordinator area the applicable inhibit thresholds more than 30 calendar days and up to and including 40 calendar days of any changes. | The Planning Coordinator provided to a Transmission Owner or Distribution Provider within its Planning Coordinator area the applicable inhibit thresholds more than 40 calendar days but less than and including 50 calendar days of any changes. | The Planning Coordinator provided to a Transmission Owner or Distribution Provider within its Planning Coordinator area the applicable inhibit thresholds more than 50 calendar days but less than and including 60 calendar days of any changes. | The Planning Coordinator failed to provide to a Transmission Owner or Distribution Provider within its Planning Coordinator area the applicable inhibit thresholds within 60 calendar days after any changes | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R7. | Each Distribution Provider and Transmission Owner that receives a notification pursuant to Requirement R6 shall develop and submit an implementation plan with respect to inhibit thresholds for approval by the Planning Coordinator within 90 calendar days of the request from the Planning Coordinator. | 2020-02-18 |  | Low | The Distribution Provider or Transmission Owner developed and submitted its implementation plan more than 90 calendar days and up to and including 100 calendar days following the request. | The Distribution Provider or Transmission Owner developed and submitted its implementation plan more than 100 calendar days and up to and including 110 calendar days following the request. | The Distribution Provider or Transmission Owner developed and submitted its implementation plan more than 110 calendar days and up to and including 120 calendar days following the request. | The Distribution Provider or Transmission Owner failed to develop and submit its implementation plan within 120 days following the request. |  |  | DP | DP-UFLS | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R8. | Each Distribution Provider and Transmission Owner shall implement the inhibit thresholds provided by the Planning Coordinator in accordance with Requirement R6 and based on the Planning Coordinator approved implementation plan in accordance with R7. | 2020-02-18 |  | High | Implemented the inhibit threshold settings provided by the Planning Coordinator in accordance with the Planning Coordinator approved implementation plan for less than 100% but more than (and including) 95% of UFLS relays. | The Distribution Provider or Transmission Owner implemented the inhibit threshold settings provided by the Planning Coordinator in accordance with the Planning Coordinator approved implementation plan for less than 95% but more than (and including) 90% of UFLS relays. | The Distribution Provider or Transmission Owner implemented the inhibit threshold settings provided by the Planning Coordinator in accordance with the Planning Coordinator approved implementation plan for less than 90% but more than (and including) 85% of UFLS relays. | The Distribution Provider or Transmission Owner implemented the inhibit threshold settings provided by the Planning Coordinator in accordance with the Planning Coordinator approved implementation plan for less than 85% of UFLS relays. |  |  | DP | DP-UFLS | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R9. | Each Transmission Owner and Distribution Provider shall annually provide documentation, with no more than 15 calendar months between updates, to its Planning Coordinator of the actual net Load that would have been shed by the UFLS relays at each UFLS stage. The actual net Load shall be coincident with the entity’s integrated hourly peak net Load during the previous year, as determined by measuring or calculating Load through the switches that would disconnect load if triggered by the UFLS relays. If measured data is unavailable then calculated data may be used. | 2020-02-18 |  | Low | The Distribution Provider or Transmission Owner provided to its Planning Coordinator documentation of the actual net Load that would have been shed by the UFLS relays at each UFLS stage as described in Requirement R11 more than 15 calendar months but less than (and including) 16 calendar months since last update. | The Distribution Provider or Transmission Owner provided to its Planning Coordinator documentation of the actual net Load that would have been shed by the UFLS relays at each UFLS stage as described in Requirement R11 more than 16 calendar months but less than (and including)17 calendar months since last update. | The Distribution Provider or Transmission Owner provided to its Planning Coordinator documentation of the actual net Load that would have been shed by the UFLS relays at each UFLS stage as described in Requirement R11 more than 17 calendar months but less than (and including)18 calendar months since last update. | The Distribution Provider or Transmission Owner failed to provide to its Planning Coordinator documentation of the actual net Load that would have been shed by the UFLS relays at each UFLS stage as described in Requirement R11 within 18 calendar months since last update. |  |  | DP | DP-UFLS | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R10. | Each Generator Owner shall set each generator underfrequency trip relay, if so equipped, on or below the appropriate generator underfrequency trip protection setting threshold curve in Figure 2, except as otherwise exempted in Requirements R13 and R16. | 2020-02-18 |  | High | N/A | N/A | N/A | The Generator Owner did not set each generator underfrequency trip relay, if so equipped, on or below the appropriate generator underfrequency trip protection settings threshold curve in Figure 2, except as otherwise exempted. | [5 empty] | GO
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R11. | Each Generator Owner shall transmit the generator underfrequency trip setting and time delay within 45 calendar days of the Planning Coordinator’s request. | 2020-02-18 |  | Low | The Generator Owner transmitted the generator underfrequency trip setting and time delay more than 45calendar days and less than (and including) 55 calendar days of the Planning Coordinator’s request. | The Generator Owner transmitted the generator underfrequency trip setting and time delay more than 55 calendar days and less than (and including) 65 calendar days of the Planning Coordinator’s request. | The Generator Owner transmitted the generator underfrequency trip setting and time delay more than 65 calendar days and less than (and including) 75 calendar days of the Planning Coordinator’s request. | The Generator Owner failed to transmit the generator underfrequency trip setting and time delay within 75 calendar days of the Planning Coordinator’s request. | [5 empty] | GO
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R12. | Each Generator Owner with a new generating unit, or an existing generator increasing its net capability by greater than 10% shall: | 2020-02-18 |  | Medium | N/A | N/A | The Generator Owner with a new generating unit, or an existing generator increasing its net capability by greater than 10%: Did not fulfill the obligation of Requirement R12; Part 12.1 OR Did not fulfill the obligation of Requirement R12, Part 12.2. | The Generator Owner with a new generating unit, or an existing generator increasing its net capability by greater than 10%, did not fulfill the obligations of Requirement R12, Part 12.1 and Part 12.2. | [5 empty] | GO
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R13. | For existing non-nuclear units in service prior to July 1, 2015, that have underfrequency protections set to trip above the appropriate curve in Figure 2: | 2020-02-18 |  | High | N/A | The Generator Owner failed to transmit the existing underfrequency settings and any changes to the underfrequency settings along with the technical basis for the settings to the Planning Coordinatoras specified in Requirement R13, Part 13.2. | The Generator Owner failed to set the underfrequency protection to operate at the lowest frequency allowed by the plant design and licensing limitations a specified in Requirement 13, Part 13.1 | The Planning Coordinator in Ontario, Québec and the Maritime Provinces or the Generator Owner within the ISO-NE and in NYISO Planning Coordinator areas failed to arrange for compensatory load shedding as specified in Requirement R13, Part 13.3. | [5 empty] | GO |  |  |  |  | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R14. | Each Planning Coordinator in Ontario, Quebec and the Maritime provinces shall apply the criteria described in Attachment A to determine the compensatory load shedding that is required in Requirement R13.3 for generating units in its respective NPCC area. | 2020-02-18 |  | High | N/A | N/A | N/A | The Planning Coordinator did not apply the criteria described in Attachment A to determine the compensatory load shedding that is required. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R15. | Each Generator Owner, Distribution Provider or Transmission Owner within the ISO-NE Planning Coordinator area and in NYISO Planning Coordinator Area shall apply the criteria described in Attachment B to determine the compensatory load shedding that is required in Requirement R13.4 for generating units in its respective NPCC area. | 2020-02-18 |  | High | N/A | N/A | N/A | The Generator Owner, Distribution Provider, or Transmission Owner did not apply the criteria described in Attachment B to determine the compensatory load shedding that is required. |  |  | DP | DP-UFLS |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006-NPCC-2 | R16. | Each Generator Owner of existing nuclear generating plants with units that have underfrequency relay threshold settings above the Eastern Interconnection generator tripping curve in Figure 2 based on their licensing design shall: | 2020-02-18 |  | High | N/A | The Generator Owner failed to transmit the initial frequency trip setting and any changes to the setting and the technical basis for the settings to the Planning Coordinator as specified in Requirement R16, Part 16.3. | The Generator Owner: Failed to set the underfrequency protection as specified in Requirement R16; Part 16.1 OR Failed to set the frequency trip setting upper tolerance as specified in Requirement R16, Part 16.2. | The Generator Owner did not fulfill the obligations of Requirement R16, Part 16.1 and Part 16.2. | [5 empty] | GO
Inactive | PRC | PRC-006-SERC-01 | R1. | Each Planning Coordinator shall include its SERC subregion as an identified island in the criteria (required by the NERC PRC standard on UFLS) for selecting portions of the BPS that may form islands. | 2014-04-01 | 2017-12-31 | Medium | N/A | N/A | N/A | The Planning Coordinator did not have evidence that its criteria included selection of its SERC subregion(s) as an island, with or without adjusted boundaries. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-SERC-01 | R2. | Each Planning Coordinator shall select or develop an automatic UFLS scheme (percent of load to be shed, frequency set points, and time delays) for implementation by UFLS entities within its area that meets the following minimum requirements: | 2014-04-01 | 2017-12-31 | Medium | The Planning Coordinator's scheme did not meet one of the UFLS system design requirements identified in 2.2 through 2.6 | The Planning Coordinator's scheme did not meet two of the UFLS system design requirements identified in 2.2 through 2.6. | The Planning Coordinator's scheme did not meet three of the UFLS system design requirements identified in 2.2 through 2.6. | The Planning Coordinator's scheme did not meet 2.1 OR Four or more of the UFLS system design requirements identified in 2.2 through 2.6. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-SERC-01 | R3. | Each Planning Coordinator, when performing design assessments specified in the NERC PRC standard on UFLS, shall conduct simulations of its UFLS scheme for an imbalance between load and generation of 13%, 22%, and 25% for all identified island(s) where such imbalance equals [(load minus actual generation output) / load]. | 2014-10-01 | 2017-12-31 | High | N/A | The Planning Coordinator failed to conduct one of the required simulations of its UFLS scheme. | N/A | The Planning Coordinator failed to conduct two of the required simulations of its UFLS scheme. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-SERC-01 | R4. | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall implement the UFLS scheme developed by their Planning Coordinator. UFLS entities may implement the UFLS scheme developed by the Planning Coordinator by coordinating with other UFLS entities. The UFLS scheme shall meet the following requirements on May 1 of each calendar year. | 2015-10-01 | 2017-12-31 | Medium | The UFLS entity’s implemented UFLS scheme had one load shedding step outside the range specified in 4. 2. | The UFLS entity’s implemented UFLS scheme had two load shedding steps outside the range specified in 4. 2. | The UFLS entity’s implemented UFLS scheme had three or more load shedding steps outside the range specified in 4.2. OR The UFLS entity's implemented UFLS scheme had a total load outside the range specified in 4.3. | The UFLS entity’s implemented UFLS scheme had three or more load shedding steps outside the range specified in 4.2. AND The UFLS entity's implemented UFLS scheme had a total load outside the range specified in 4.3. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-SERC-01 | R5. | Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall implement the UFLS scheme developed by their Planning Coordinator, but shall not be required to have more than one UFLS step. UFLS entities may implement the UFLS scheme developed by the Planning Coordinator by coordinating with other UFLS entities. The UFLS scheme shall meet the following requirements on May 1 of each calendar year. | 2015-10-01 | 2017-12-31 | Medium | N/A | N/A | N/A | The UFLS entity's implemented UFLS scheme had a total load outside the range specified in 5.2. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-SERC-01 | R6. | Each UFLS entity shall implement changes to the UFLS scheme which involve frequency settings, relay time delays, or changes to the percentage of load in the scheme within 18 months of notification by the Planning Coordinator. | 2015-10-01 | 2017-12-31 | Medium | The UFLS entity implemented required scheme changes but made them 1 to 30 days after the scheduled date. | The UFLS entity implemented required scheme changes but made them 31 to 40 days after the scheduled date. | The UFLS entity implemented required scheme changes but made them 41 to 50 days after the scheduled date. | The UFLS entity implemented required scheme changes but made them more than 50 days after the scheduled date OR The UFLS entity failed to implement the required scheme changes. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-SERC-01 | R7. | Each Planning Coordinator shall provide the following information to SERC according to the schedule specified by SERC. | 2014-04-01 | 2017-12-31 | Low | The Planning Coordinator provided the data required in R7 to SERC 1 to 10 days after the scheduled submittal date. | The Planning Coordinator provided the data required in R7 to SERC 11 to 20 days after the scheduled submittal date. OR The Planning Coordinator did not provide to SERC one piece of information listed in R7. | The Planning Coordinator provided the data required in R7 to SERC 21 to 30 days after the scheduled submittal date. OR The Planning Coordinator did not provide to SERC two pieces of information listed in R7. | The Planning Coordinator provided the data required in R7 to SERC more than 30 days after the scheduled submittal date. OR The Planning Coordinator did not provide to SERC any of the information listed in R7. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-SERC-01 | R8. | Each Generator Owner shall provide the following information within 30 days of a request by SERC to facilitate post-event analysis of frequency disturbances. | 2014-04-01 | 2017-12-31 | Low | The Generator Owner provided the data required in R8 to SERC 1 to 10 days after the requested submittal date. | The Generator Owner provided the data required in R8 to SERC 11 to 20 days after the requested submittal date. OR The Generator Owner did not provide to SERC one piece of information listed in R8. | The Generator Owner provided the data required in R8 to SERC 21 to 30 days after the requested submittal date. OR The Generator Owner did not provide to SERC two pieces of information listed in R8. | The Generator Owner provided the data required in R8 to SERC more than 30 days after the requested submittal date. OR The Generator Owner did not provide to SERC any of the information listed in R8. |  |  |  | DP-UFLS |  | GO
Inactive | PRC | PRC-006-SERC-02 | R1. | Each Planning Coordinator shall include its SERC subregion as an identified island in the criteria (required by the NERC PRC standard on UFLS) for selecting portions of the BPS that may form islands. | 2018-01-01 | 2022-03-31 | Medium | N/A | N/A | N/A | The Planning Coordinator did not have evidence that its criteria included selection of its SERC subregion(s) as an island, with or without adjusted boundaries. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-SERC-02 | R2. | Each Planning Coordinator shall select or develop an automatic UFLS scheme (percent of load to be shed, frequency set points, and time delays) for implementation by UFLS entities within its area that meets the following minimum requirements: | 2018-01-01 | 2022-03-31 | Medium | The Planning Coordinator's scheme did not meet one of the UFLS system design requirements identified in 2.2 through 2.6 | The Planning Coordinator's scheme did not meet two of the UFLS system design requirements identified in 2.2 through 2.6. | The Planning Coordinator's scheme did not meet three of the UFLS system design requirements identified in 2.2 through 2.6. | The Planning Coordinator's scheme did not meet 2.1 OR Four or more of the UFLS system design requirements identified in 2.2 through 2.6. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-SERC-02 | R3. | Each Planning Coordinator, when performing design assessments specified in the NERC PRC standard on UFLS, shall conduct simulations of its UFLS scheme for an imbalance between load and generation of 13%, 22%, and 25% for all identified island(s) where such imbalance equals [(load minus actual generation output) / load]. | 2018-01-01 | 2022-03-31 | High | N/A | The Planning Coordinator failed to conduct one of the required simulations of its UFLS scheme. | N/A | The Planning Coordinator failed to conduct two of the required simulations of its UFLS scheme. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-SERC-02 | R4. | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall implement the UFLS scheme developed by their Planning Coordinator. UFLS entities may implement the UFLS scheme developed by the Planning Coordinator by coordinating with other UFLS entities. The UFLS scheme shall meet the following requirements on May 1 of each calendar year. | 2018-01-01 | 2022-03-31 | Medium | The UFLS entity’s implemented UFLS scheme had one load shedding step outside the range specified in 4.2. | The UFLS entity’s implemented UFLS scheme had two load shedding steps outside the range specified in 4.2. | The UFLS entity’s implemented UFLS scheme had three or more load shedding steps outside the range specified in 4.2. OR The UFLS entity's implemented UFLS scheme had a total load outside the range specified in 4.3. | The UFLS entity’s implemented UFLS scheme had three or more load shedding steps outside the range specified in 4.2. AND The UFLS entity's implemented UFLS scheme had a total load outside the range specified in 4.3. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-SERC-02 | R5. | Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall implement the UFLS scheme developed by their Planning Coordinator, but shall not be required to have more than one UFLS step. UFLS entities may implement the UFLS scheme developed by the Planning Coordinator by coordinating with other UFLS entities. The UFLS scheme shall meet the following requirements on May 1 of each calendar year. | 2018-01-01 | 2022-03-31 | Medium | N/A | N/A | N/A | The UFLS entity's implemented UFLS scheme had a total load outside the range specified in 5.2. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-SERC-02 | R6. | Each UFLS entity shall implement changes to the UFLS scheme which involve frequency settings, relay time delays, changes to the percentage of load in the scheme, or changes to the peak season selected in R2.1 within 18 months of notification by the Planning Coordinator. | 2018-01-01 | 2022-03-31 | High | The UFLS entity implemented required scheme changes but made them 1 to 30 days after the scheduled date. | The UFLS entity implemented required scheme changes but made them 31 to 40 days after the scheduled date. | The UFLS entity implemented required scheme changes but made them 41 to 50 days after the scheduled date. | The UFLS entity implemented required scheme changes but made them more than 50 days after the scheduled date OR The UFLS entity failed to implement the required scheme changes. |  |  | DP | DP-UFLS | [14 empty] | TO
Inactive | PRC | PRC-006-SERC-02 | R7. | Each Planning Coordinator shall provide the following information to SERC according to the schedule specified by SERC. | 2018-01-01 | 2022-03-31 | Low | The Planning Coordinator provided the data required in R7 to SERC 1 to 10 days after the scheduled submittal date. | The Planning Coordinator provided the data required in R7 to SERC 11 to 20 days after the scheduled submittal date. OR The Planning Coordinator did not provide to SERC one piece of information listed in R7. | The Planning Coordinator provided the data required in R7 to SERC 21 to 30 days after the scheduled submittal date. OR The Planning Coordinator did not provide to SERC two pieces of information listed in R7. | The Planning Coordinator provided the data required in R7 to SERC more than 30 days after the scheduled submittal date. OR The Planning Coordinator did not provide to SERC any of the information listed in R7. |  |  |  | DP-UFLS | [6 empty] | PCPA
Inactive | PRC | PRC-006-SERC-02 | R8. | Each Generator Owner shall provide the following information within 30 days of a request by SERC to facilitate post-event analysis of frequency disturbances. | 2018-01-01 | 2022-03-31 | Low | The Generator Owner provided the data required in R8 to SERC 1 to 10 days after the requested submittal date. | The Generator Owner provided the data required in R8 to SERC 11 to 20 days after the requested submittal date. OR The Generator Owner did not provide to SERC one piece of information listed in R8. | The Generator Owner provided the data required in R8 to SERC 21 to 30 days after the requested submittal date. OR The Generator Owner did not provide to SERC two pieces of information listed in R8. | The Generator Owner provided the data required in R8 to SERC more than 30 days after the requested submittal date. OR The Generator Owner did not provide to SERC any of the information listed in R8. |  |  |  | DP-UFLS |  | GO
Mandatory Subject to Enforcement | PRC | PRC-006-SERC-03 | R2. | Each Planning Coordinator shall select or develop an automatic UFLS scheme (percent of load to be shed, frequency set points, and time delays) for implementation by UFLS entities within its area that meets the following minimum requirements: | 2022-04-01 |  | Medium | The Planning Coordinator's scheme did not meet one of the UFLS system design requirements identified in 2.2 through 2.6 | The Planning Coordinator's scheme did not meet two of the UFLS system design requirements identified in 2.2 through 2.6. | The Planning Coordinator's scheme did not meet three of the UFLS system design requirements identified in 2.2 through 2.6. | The Planning Coordinator's scheme did not meet 2.1 OR Four or more of the UFLS system design requirements identified in 2.2 through 2.6. |  |  |  | DP-UFLS | [6 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-SERC-03 | R3. | Each Planning Coordinator, when performing design assessments specified in the NERC PRC standard on UFLS, shall conduct simulations of its UFLS scheme for an imbalance between load and generation of 13%, 22%, and 25% for all identified island(s) where such imbalance equals [(load minus actual generation output) / load]. | 2022-04-01 |  | High | N/A | The Planning Coordinator failed to conduct one of the required simulations of its UFLS scheme. | N/A | The Planning Coordinator failed to conduct two of the required simulations of its UFLS scheme. |  |  |  | DP-UFLS | [6 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-006-SERC-03 | R4. | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall implement the UFLS scheme developed by their Planning Coordinator. UFLS entities may implement the UFLS scheme developed by the Planning Coordinator by coordinating with other UFLS entities. The UFLS scheme shall meet the following requirements on May 1 of each calendar year. | 2022-04-01 |  | Medium | The UFLS entity’s implemented UFLS scheme had one load shedding step outside the range specified in 4.2. | The UFLS entity’s implemented UFLS scheme had two load shedding steps outside the range specified in 4.2. | The UFLS entity’s implemented UFLS scheme had three or more load shedding steps outside the range specified in 4.2. OR The UFLS entity's implemented UFLS scheme had a total load outside the range specified in 4.3. | The UFLS entity’s implemented UFLS scheme had three or more load shedding steps outside the range specified in 4.2. AND The UFLS entity's implemented UFLS scheme had a total load outside the range specified in 4.3. |  |  | DP | DP-UFLS | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006-SERC-03 | R5. | Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall implement the UFLS scheme developed by their Planning Coordinator, but shall not be required to have more than one UFLS step. UFLS entities may implement the UFLS scheme developed by the Planning Coordinator by coordinating with other UFLS entities. The UFLS scheme shall meet the following requirements on May 1 of each calendar year. | 2022-04-01 |  | Medium | N/A | N/A | N/A | The UFLS entity's implemented UFLS scheme had a total load outside the range specified in 5.2. |  |  |  | DP-UFLS
Mandatory Subject to Enforcement | PRC | PRC-006-SERC-03 | R6. | Each UFLS entity shall implement changes to the UFLS scheme which involve frequency settings, relay time delays, changes to the percentage of load in the scheme, or changes to the peak season selected in R2.1 within 18 months of notification by the Planning Coordinator. | 2022-04-01 |  | High | The UFLS entity implemented required scheme changes but made them 1 to 30 days after the scheduled date. | The UFLS entity implemented required scheme changes but made them 31 to 40 days after the scheduled date. | The UFLS entity implemented required scheme changes but made them 41 to 50 days after the scheduled date. | The UFLS entity implemented required scheme changes but made them more than 50 days after the scheduled date OR The UFLS entity failed to implement the required scheme changes. |  |  | DP | DP-UFLS | [14 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-006-SERC-03 | R8. | Each Generator Owner shall provide the following information within 30 days of a request by SERC or Planning Coordinator to facilitate post-event analysis of frequency disturbances. | 2022-04-01 |  | Low | The Generator Owner provided the data required in R8 to SERC or Planning Coordinator 1 to 10 days after the requested submittal date. | The Generator Owner provided the data required in R8 to SERC or Planning Coordinator 11 to 20 days after the requested submittal date. OR The Generator Owner did not provide to SERC or Planning Coordinator one piece of information listed in R8. | The Generator Owner provided the data required in R8 to SERC or Planning Coordinator 21 to 30 days after the requested submittal date. OR The Generator Owner did not provide to SERC or Planning Coordinator two pieces of information listed in R8. | The Generator Owner provided the data required in R8 to SERC or Planning Coordinator more than 30 days after the requested submittal date. OR The Generator Owner did not provide to SERC or Planning Coordinator any of the information listed in R8. |  |  |  | DP-UFLS |  | GO
Inactive | PRC | PRC-006-SPP-01 | R1. | Each UFLS entity that has a total forecasted peak Load greater than or equal to 100 MW shall develop and implement an automatic UFLS program that meets the following requirements: (please see the standard for the sub-requirements) |  | 2013-11-07 | High | N/A | UFLS entity developed a program, but failed to meet any one (1) of the following 5 requirements: Part 1.1 (Step1-3) | UFLS entity developed a program, but failed to meet any two (2) of the following 5 requirements: Part 1.1 (Step1-3) | UFLS entity developed a program, but failed to meet three (3) or more of the following 5 requirements: Part 1.1 (Step1-3) Failed to develop a UFLS program |  |  | DP | [15 empty] | TO
Inactive | PRC | PRC-006-SPP-01 | R2. | Each UFLS entity that has a total forecasted peak Load less than 100 MW shall develop and implement an automatic UFLS program that meets the following requirements: (please see the standard for the sub-requirements) |  | 2013-11-07 | Medium | UFLS entity developed a program, but failed to meet one (1) of the requirements in Parts 2.1 through 2.4 | UFLS entity developed a program, but failed to meet two (2) of the requirements in Parts 2.1 through 2.4 | UFLS entity developed a program, but failed to meet three (3) of the requirements in parts 2.1 through 2.4 | UFLS entity developed a program, but failed to meet all four (4) of the requirements in Parts 2.1 through 2.4 |  |  | DP | [15 empty] | TO
Inactive | PRC | PRC-006-SPP-01 | R3. | Each UFLS entity electing to use underfrequency islanding schemes shall design those islanding schemes to operate after all 3 steps of UFLS have been exhausted and the frequency continues to fall to 58.5 Hz or below. For islanding schemes designed to operate at or between 58.5 Hz and 58.0 Hz, the minimum time delay shall be 2 seconds. For islanding schemes designed to operate below 58.0 Hz, no time delay is required. |  | 2013-11-07 | Low | N/A | N/A | N/A | UFLS entity, electing to use underfrequency islanding schemes, failed to develop an islanding scheme per the requirement |  |  | DP | [15 empty] | TO
Inactive | PRC | PRC-006-SPP-01 | R4. | The Planning Coordinator shall perform and document a UFLS technical assessment within one year after the occurrence of any of the following situations: • Performance characteristic changes to PRC-006 or the SPP UFLS standard. • Changes to the boundaries of a specified island are identified. |  | 2013-11-07 | Medium | The Planning Coordinator performed a technical assessment within five years and three months or within one year and three months after one of the situations listed in R4 | The Planning Coordinator performed a technical assessment within five years and six months or within one year and six months after one of the situations listed in R4 | The Planning Coordinator performed a technical assessment within five years and nine months or within one year and nine months after one of the situations listed in R4 | The Planning Coordinator performed a technical assessment within six years or within two years after one of the situations listed in R4 OR The Planning Coordinator failed to perform a technical assessment | [10 empty] | PCPA
Inactive | PRC | PRC-006-SPP-01 | R5. | Each UFLS entity shall maintain and submit the following UFLS data based on the forecasted peak Load to the Planning Coordinator within (30) calendar days upon request from the Planning Coordinator: (please see standard for the sub-requirements) |  | 2013-11-07 | Low | UFLS entity provided required data more than 30 calendar days and up to and including 45 calendar days following the request | UFLS entity provided required data more than 45 calendar days and up to and including 60 calendar days following the request OR UFLS entity did not provide one piece of information listed in R5 (e.g., 5.1.) | UFLS entity provided required data more than 60 calendar days and up to and including 75 calendar days following the request OR UFLS entity did not provide two pieces of information listed in R5 (e.g., 5.1. and 5.2.) | UFLS entity provided required data more than 75 calendar days following the request OR UFLS entity did not provide required data after the request was made OR UFLS entity did not provide three or more pieces of information listed in R5 (e.g., 5.1. and 5. |  |  | DP | [15 empty] | TO
Inactive | PRC | PRC-006-SPP-01 | R6. | Each Generator Owner shall maintain and submit the following data to the Planning Coordinator within (30) calendar days upon request from the Planning Coordinator: (please see the standard for the sub-requirements) |  | 2013-11-07 | Low | Generator Owner provided required data more than 30 calendar days and up to and including 45 calendar days following the request | Generator Owner provided required data more than 45 calendar days and up to and including 60 calendar days following the request OR Generator Owner did not provide one piece of information listed in R6 (e.g., 6.1.) | Generator Owner provided required data more than 60 calendar days and up to and including 75 calendar days following the request OR Generator Owner did not provide two pieces of information listed in R6 (e.g., 6.1. and 6.2.) | Generator Owner provided required data more than 75 calendar days following the request OR Generator Owner did not provide required data after the request was made OR Generator Owner did not provide three or more pieces of information listed in R6 (e.g., 6.1. and 6.2. and 6.3.) | [5 empty] | GO
Inactive | PRC | PRC-006-SPP-01 | R7. | Each Generator Owner shall verify that their generating unit(s) will not trip above the Generator underfrequency curve in Attachment 1 and will not trip below the Generator overfrequency curve in Attachment 2 as a result of the unit(s) frequency protective relay settings. |  | 2013-11-07 | Medium | N/A | N/A | The Generator Owner did not provide technical evidence to the Planning Coordinator demonstrating that the unit cannot operate within the specified frequency range without causing equipment damage or violating manufacturer’s published equipment ratings for their generating units with operating characteristics that limit the unit’s ability to perform in accordance with R7. | The Generator Owner did not verify that their generating unit(s) will not trip above the Generator underfrequency curve in Attachment 1 and will not trip below the Generator overfrequency curve in Attachment 2 due to the generator unit frequency protective relay settings. | [5 empty] | GO
Inactive | PRC | PRC-006-SPP-01 | R8. | The Planning Coordinator shall determine if the Generator Owner has provided technical evidence demonstrating that the unit cannot operate within the specified frequency range without causing equipment damage or violating manufacturer’s published equipment ratings. |  | 2013-11-07 | Medium | N/A | N/A | The Planning Coordinator determined that the UFLS program was degraded in accordance with R8.1, but did not notify the Generator Owner or the UFLS entity of the Load that they were required to shed. | The Planning Coordinator did not determine if the UFLS program performance was degraded due to the removal of any generation identified in accordance with R7.1 and verified in accordance with R8. | [10 empty] | PCPA
Inactive | PRC | PRC-006-SPP-01 | R9. | The Generator Owner or other UFLS entity(s) shall implement supplementary shedding of Load required by the Planning Coordinator in accordance with R8.1.1. |  | 2013-11-07 | Medium | N/A | N/A | N/A | The Generator Owner or other UFLS entity did not implement supplementary shedding of Load required by the Planning Coordinator in accordance with R8.1.1. | [5 empty] | GO
Inactive | PRC | PRC-007-0 | R1. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall ensure that its UFLS program is consistent with its Regional Reliability Organization’s UFLS program requirements. | 2007-06-18 | 2013-09-30 | Medium | [6 empty] | DP | [15 empty] | TO
Inactive | PRC | PRC-007-0 | R2. | The Transmission Owner, Transmission Operator, Distribution Provider, and Load-Serving Entity that owns or operates a UFLS program (as required by its Regional Reliability Organization) shall provide, and annually update, its underfrequency data as necessary for its Regional Reliability Organization to maintain and update a UFLS program database. | 2007-06-18 | 2013-09-30 | Low | The responsible entity has demonstrated the reporting of information but failed to satisfy one database reporting requirements. | The responsible entity has demonstrated the reporting of information but failed to satisfy two database reporting requirements. | The responsible entity has demonstrated the reporting of information but failed to satisfy at three database reporting requirements. | The responsible entity has demonstrated the reporting of information but failed to satisfy four or more database reporting requirements or has not provided the information. |  |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-007-0 | R3. | The Transmission Owner and Distribution Provider that owns a UFLS program (as required by its Regional Reliability Organization) shall provide its documentation of that UFLS program to its Regional Reliability Organization on request (30 calendar days). | 2007-06-18 | 2013-09-30 | Low | The responsible entity has provided the documentation in more than 30 calendar days but less than 40 calendar days. | The responsible entity has provided the documentation in more than 39 calendar days but less than 50 calendar days. | The responsible entity has provided the documentation in more than 49 calendar days but less than 60 calendar days. | The responsible entity has not provided the documentation within 60 calendar days. |  |  | DP | [15 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-008-0 | R1. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall have a UFLS equipment maintenance and testing program in place. This UFLS equipment maintenance and testing program shall include UFLS equipment identification, the schedule for UFLS equipment testing, and the schedule for UFLS equipment maintenance. | 2007-06-18 | 2027-03-31 | Medium | [6 empty] | DP | [15 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-008-0 | R2. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall implement its UFLS equipment maintenance and testing program and shall provide UFLS maintenance and testing program results results to its Regional Reliability Organization and NERC on request (within 30 calendar days). | 2007-06-18 | 2027-03-31 | Medium | [6 empty] | DP | [15 empty] | TO
Inactive | PRC | PRC-009-0 | R1. | The Transmission Owner, Transmission Operator, Load-Serving Entity, and Distribution Provider that owns or operates a UFLS program (as required by its Regional Reliability Organization) shall analyze and document its UFLS program performance in accordance with its Regional Reliability Organization’s UFLS program. The analysis shall address the performance of UFLS equipment and program effectiveness following system events resulting in system frequency excursions below the initializing set points of the UFLS program. The analysis shall include, but not be limited to: | 2007-06-18 | 2013-09-30 | Medium | [6 empty] | DP | [5 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-009-0 | R2. | The Transmission Owner, Transmission Operator, Load-Serving Entity, and Distribution Provider that owns or operates a UFLS program (as required by its Regional Reliability Organization) shall provide documentation of the analysis of the UFLS program to its Regional Reliability Organization and NERC on request 90 calendar days after the system event. | 2007-06-18 | 2013-09-30 | Low | [6 empty] | DP | [5 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-010-0 | R1. | The Load-Serving Entity, Transmission Owner, Transmission Operator, and Distribution Provider that owns or operates a UVLS program shall periodically (at least every five years or as required by changes in system conditions) conduct and document an assessment of the effectiveness of the UVLS program. This assessment shall be conducted with the associated Transmission Planner(s) and Planning Authority(ies). | 2007-06-18 | 2017-03-31 | Medium | [6 empty] | DP | [5 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-010-0 | R2. | The Load-Serving Entity, Transmission Owner, Transmission Operator, and Distribution Provider that owns or operates a UVLS program shall provide documentation of its current UVLS program assessment to its Regional Reliability Organization and NERC on request (30 calendar days). | 2007-06-18 | 2014-01-21 | Low | [6 empty] | DP | [5 empty] | LSE | [9 empty] | TO | TOP
Inactive | PRC | PRC-010-1 | R1. | Each Planning Coordinator or Transmission Planner that is developing a UVLS Program shall evaluate its effectiveness and subsequently provide the UVLS Program’s specifications and implementation schedule to the UVLS entities responsible for implementing the UVLS Program. The evaluation shall include, but is not limited to, studies and analyses that show: | 2017-04-01 | 2017-04-01 | High | N/A | N/A | N/A | The applicable entity that developed the UVLS Program failed to evaluate the program’s effectiveness and subsequently provide the UVLS Program’s specifications and implementation schedule to UVLS entities in accordance with Requirement R1, including the items specified in Parts 1.1 and 1.2. | [10 empty] | PCPA | [9 empty] | TP
Inactive | PRC | PRC-010-1 | R2. | Each UVLS entity shall adhere to the UVLS Program specifications and implementation schedule determined by its Planning Coordinator or Transmission Planner associated with UVLS Program development per Requirement R1 or with any Corrective Action Plans per Requirement R5. | 2017-04-01 | 2017-04-01 | High | N/A | N/A | The applicable entity failed to adhere to the UVLS Program specifications in accordance with Requirement R2. OR The applicable entity failed to adhere to the implementation schedule in accordance with Requirement R2. | The applicable entity failed to adhere to the UVLS Program specifications and implementation schedule in accordance with Requirement R2. |  |  | DP | [15 empty] | TO
Inactive | PRC | PRC-010-1 | R3. | Each Planning Coordinator or Transmission Planner shall perform a comprehensive assessment to evaluate the effectiveness of each of its UVLS Programs at least once every 60 calendar months. Each assessment shall include, but is not limited to, studies and analyses that evaluate whether: | 2017-04-01 | 2017-04-01 | Medium | N/A | N/A | N/A | The applicable entity failed to perform an assessment at least once during the 60 calendar months in accordance with Requirement R3, including the items specified in Parts 3.1 and 3.2. | [10 empty] | PCPA | [9 empty] | TP
Inactive | PRC | PRC-010-1 | R4. | Each Planning Coordinator or Transmission Planner shall, within 12 calendar months of an event that resulted in a voltage excursion for which its UVLS Program was designed to operate, perform an assessment to evaluate whether its UVLS Program resolved the undervoltage issues associated with the event. | 2017-04-01 | 2017-04-01 | Medium | The applicable entity performed an assessment in accordance with Requirement R4 within a time period greater than 12 calendar months but less than or equal to 13 calendar months after an applicable event. | The applicable entity performed an assessment in accordance with Requirement R4 within a time period greater than 13 calendar months but less than or equal to 14 calendar months after an applicable event. | The applicable entity performed an assessment in accordance with Requirement R4 within a time period greater than 14 calendar months but less than or equal to 15 calendar months after an applicable event. | The applicable entity performed an assessment in accordance with Requirement R4 within a time period greater than 15 calendar months after an applicable event. OR The applicable entity failed to perform an assessment in accordance with Requirement R4. | [10 empty] | PCPA | [9 empty] | TP
Inactive | PRC | PRC-010-1 | R5. | Each Planning Coordinator or Transmission Planner that identifies deficiencies in its UVLS Program during an assessment performed in either Requirement R3 or R4 shall develop a Corrective Action Plan to address the deficiencies and subsequently provide the Corrective Action Plan, including an implementation schedule, to UVLS entities within three calendar months of completing the assessment. | 2017-04-01 | 2017-04-01 | Medium | The applicable entity developed a Corrective Action Plan and provided it to UVLS entities in accordance with Requirement R5 but was late by less than or equal to 15 calendar days. | The applicable entity developed a Corrective Action Plan and provided it to UVLS entities in accordance with Requirement R5 but was late by more than 15 calendar days but less than or equal to 30 calendar days. | The applicable entity developed a Corrective Action Plan and provided it to UVLS entities in accordance with Requirement R5 but was late by more than 30 calendar days but less than or equal to 45 calendar days. | The applicable entity developed a Corrective Action Plan and provided it to UVLS entities in accordance with Requirement R5 but was late by more than 30 calendar days but less than or equal to 45 calendar days. OR The responsible entity failed to develop a Corrective Action Plan or provide it to UVLS entities in accordance with Requirement R5. | [10 empty] | PCPA | [9 empty] | TP
Inactive | PRC | PRC-010-1 | R6. | Each Planning Coordinator that has a UVLS Program in its area shall update a database containing data necessary to model the UVLS Program(s) in its area for use in event analyses and assessments of the UVLS Program at least once each calendar year. | 2017-04-01 | 2017-04-01 | Low | The applicable entity updated the database in accordance with Requirement R6 but was late by less than or equal to 30 calendar days. | The applicable entity updated the database in accordance with Requirement R6 but was late by more than 30 calendar days but less than or equal to 60 calendar days. | The applicable entity updated the database in accordance with Requirement R6 but was late by more than 60 calendar days but less than or equal to 90 calendar days. | The applicable entity updated the database in accordance with Requirement R6 but was late by more than 90 calendar days. OR The applicable entity failed to update the database in accordance with Requirement R6. | [10 empty] | PCPA
Inactive | PRC | PRC-010-1 | R7. | Each UVLS entity shall provide data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of a UVLS Program database. | 2017-04-01 | 2017-04-01 | Low | The applicable entity provided data in accordance with Requirement R7 but was late by less than or equal to 30 calendar days per the specified schedule. OR The applicable entity provided data in accordance with Requirement R7 but the data was not provided according to the specified format. | The applicable entity provided data in accordance with Requirement R7 but was late by more than 30 calendar days but less than or equal to 60 calendar days per the specified schedule. | The applicable entity provided data in accordance with Requirement R7 but was late by more than 60 calendar days but less than or equal to 90 calendar days per the specified schedule. | The applicable entity provided data in accordance with Requirement R7 but was late by more than 60 calendar days but less than or equal to 90 calendar days per the specified schedule. OR The applicable entity failed to provide data in accordance with Requirement R7. |  |  | DP | [15 empty] | TO
Inactive | PRC | PRC-010-1 | R8. | Each Planning Coordinator that has a UVLS Program in its area shall provide its UVLS Program database to other Planning Coordinators and Transmission Planners within its Interconnection, and other functional entities with a reliability need, within 30 calendar days of a written request. | 2017-04-01 | 2017-04-01 | Low | The applicable entity provided its UVLS Program database in accordance with Requirement R8 but was late by less than or equal to 15 calendar days. | The applicable entity provided its UVLS Program database in accordance with Requirement R8 but was late by more than 15 calendar days but less than or equal to 30 calendar days. | The applicable entity provided its UVLS Program database in accordance with Requirement R8 but was late by more than 30 calendar days but less than or equal to 45 calendar days. | The applicable entity provided its UVLS Program database in accordance with Requirement R8 but was late by more than 45 calendar days. OR The applicable entity failed to provide its UVLS Program database in accordance with Requirement R8. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-010-2 | R1. | Each Planning Coordinator or Transmission Planner that is developing a UVLS Program shall evaluate its effectiveness and subsequently provide the UVLS Program’s specifications and implementation schedule to the UVLS entities responsible for implementing the UVLS Program. The evaluation shall include, but is not limited to, studies and analyses that show: | 2017-04-02 |  | High | N/A | N/A | N/A | The applicable entity that developed the UVLS Program failed to evaluate the program’s effectiveness and subsequently provide the UVLS Program’s specifications and implementation schedule to UVLS entities in accordance with Requirement R1, including the items specified in Parts 1.1 and 1.2. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | PRC | PRC-010-2 | R2. | Each UVLS entity shall adhere to the UVLS Program specifications and implementation schedule determined by its Planning Coordinator or Transmission Planner associated with UVLS Program development per Requirement R1 or with any Corrective Action Plans per Requirement R5. | 2017-04-02 |  | High | N/A | N/A | The applicable entity failed to adhere to the UVLS Program specifications in accordance with Requirement R2. Or The applicable entity failed to adhere to the implementation schedule in accordance with Requirement R2. | The applicable entity failed to adhere to the UVLS Program specifications and implementation schedule in accordance with Requirement R2. |  |  | DP | [15 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-010-2 | R3. | Each Planning Coordinator or Transmission Planner shall perform a comprehensive assessment to evaluate the effectiveness of each of its UVLS Programs at least once every 60 calendar months. Each assessment shall include, but is not limited to, studies and analyses that evaluate whether: | 2017-04-02 |  | Medium | N/A | N/A | N/A | The applicable entity failed to perform an assessment at least once during the 60 calendar months in accordance with Requirement R3, including the items specified in Parts 3.1 and 3.2. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | PRC | PRC-010-2 | R4. | Each Planning Coordinator or Transmission Planner shall, within 12 calendar months of an event that resulted in a voltage excursion for which its UVLS Program was designed to operate, perform an assessment to evaluate: | 2017-04-02 |  | Medium | The applicable entity performed an assessment in accordance with Requirement R4 within a time period greater than 12 calendar months but less than or equal to 13 calendar months after an applicable event. | The applicable entity performed an assessment in accordance with Requirement R4 within a time period greater than 13 calendar months but less than or equal to 14 calendar months after an applicable event. | The applicable entity performed an assessment in accordance with Requirement R4 within a time period greater than 14 calendar months but less than or equal to 15 calendar months after an applicable event. | The applicable entity performed an assessment in accordance with Requirement R4 within a time period greater than 15 calendar months after an applicable event. OR The applicable entity failed to perform an assessment in accordance with Requirement R4. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | PRC | PRC-010-2 | R5. | Each Planning Coordinator or Transmission Planner that identifies deficiencies during an assessment performed in either Requirement R3 or R4 shall develop a Corrective Action Plan to address the deficiencies and subsequently provide the Corrective Action Plan, including an implementation schedule, to UVLS entities within three calendar months of completing the assessment. | 2017-04-02 |  | Medium | The applicable entity developed a Corrective Action Plan and provided it to UVLS entities in accordance with Requirement R5 but was late by less than or equal to 15 calendar days. | The applicable entity developed a Corrective Action Plan and provided it to UVLS entities in accordance with Requirement R5 but was late by more than 15 calendar days but less than or equal to 30 calendar days. | The applicable entity developed a Corrective Action Plan and provided it to UVLS entities in accordance with Requirement R5 but was late by more than 30 calendar days but less than or equal to 45 calendar days. | The applicable entity developed a Corrective Action Plan and provided it to UVLS entities in accordance with Requirement R5 but was late by more than 45 calendar days. OR The responsible entity failed to develop a Corrective Action Plan or provide it to UVLS entities in accordance with Requirement R5. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | PRC | PRC-010-2 | R6. | Each Planning Coordinator that has a UVLS Program in its area shall update a database containing data necessary to model the UVLS Program(s) in its area for use in event analyses and assessments of the UVLS Program at least once each calendar year. | 2017-04-02 |  | Low | The applicable entity updated the database in accordance with Requirement R6 but was late by less than or equal to 30 calendar days. | The applicable entity updated the database in accordance with Requirement R6 but was late by more than 30 calendar days but less than or equal to 60 calendar days. | The applicable entity updated the database in accordance with Requirement R6 but was late by more than 60 calendar days but less than or equal to 90 calendar days. | The applicable entity updated the database in accordance with Requirement R6 but was late by more than 90 calendar days. OR The applicable entity failed to update the database in accordance with Requirement R6. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-010-2 | R7. | Each UVLS entity shall provide data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of a UVLS Program database. | 2017-04-02 |  | Low | The applicable entity provided data in accordance with Requirement R7 but was late by less than or equal to 30 calendar days per the specified schedule. OR The applicable entity provided data in accordance with Requirement R7 but the data was not provided according to the specified format. | The applicable entity provided data in accordance with Requirement R7 but was late by more than 30 calendar days but less than or equal to 60 calendar days per the specified schedule. | The applicable entity provided data in accordance with Requirement R7 but was late by more than 60 calendar days but less than or equal to 90 calendar days per the specified schedule. | The applicable entity provided data in accordance with Requirement R7 but was late by more than 90 calendar days per the specified schedule. ORThe applicable entity failed to provide data in accordance with Requirement R7. |  |  | DP | [15 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-010-2 | R8. | Each Planning Coordinator that has a UVLS Program in its area shall provide its UVLS Program database to other Planning Coordinators and Transmission Planners within its Interconnection, and other functional entities with a reliability need, within 30 calendar days of a written request. | 2017-04-02 |  | Low | The applicable entity provided its UVLS Program database in accordance with Requirement R8 but was late by less than or equal to 15 calendar days. | The applicable entity provided its UVLS Program database in accordance with Requirement R8 but was late by more than 15 calendar days but less than or equal to 30 calendar days. | The applicable entity provided its UVLS Program database in accordance with Requirement R8 but was late by more than 30 calendar days but less than or equal to 45 calendar days. | The applicable entity provided its UVLS Program database in accordance with Requirement R8 but was late by more than 45 calendar days. OR The applicable entity failed to provide its UVLS Program database in accordance with Requirement R8. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-011-0 | R1. | The Transmission Owner and Distribution Provider that owns a UVLS system shall have a UVLS equipment maintenance and testing program in place. This program shall include: | 2007-06-18 | 2027-03-31 | Medium | [6 empty] | DP | [15 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-011-0 | R2. | The Transmission Owner and Distribution Provider that owns a UVLS system shall provide documentation of its UVLS equipment maintenance and testing program and the implementation of that UVLS equipment maintenance and testing program to its Regional Reliability Organization and NERC on request (within 30 calendar days). | 2007-06-18 | 2027-03-31 | Low | [6 empty] | DP | [15 empty] | TO
Inactive | PRC | PRC-012-0 | R1. | Each Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Providers that uses or is planning to use an SPS shall have a documented Regional Reliability Organization SPS review procedure to ensure that SPSs comply with Regional criteria and NERC Reliability Standards. The Regional SPS review procedure shall include: |  | 2017-03-31 | Medium | [19 empty] | RRO
Inactive | PRC | PRC-012-0 | R2. | The Regional Reliability Organization shall provide affected Regional Reliability Organizations and NERC with documentation of its SPS review procedure on request (within 30 calendar days). |  | 2017-03-31 | Low | [19 empty] | RRO
Inactive | PRC | PRC-012-1 | R1. | Each Regional Reliability Organization with a Transmission Owner, Generator Owner, or Distribution Providers that uses or is planning to use a RAS shall have a documented Regional Reliability Organization RAS review procedure to ensure that RAS comply with Regional criteria and NERC Reliability Standards. The Regional RAS review procedure shall include: |  | 2020-12-31 | Medium | [19 empty] | RRO
Inactive | PRC | PRC-012-1 | R2. | The Regional Reliability Organization shall provide affected Regional Reliability Organizations and NERC with documentation of its RAS review procedure on request (within 30 calendar days). |  | 2020-12-31 | Low | [19 empty] | RRO
Mandatory Subject to Enforcement | PRC | PRC-012-2 | R1. | Prior to placing a new or functionally modified RAS in service or retiring an existing RAS, each RAS-entity shall provide the information identified in Attachment 1 for review to the Reliability Coordinator(s) where the RAS is located. | 2021-01-01 |  | Medium | N/A | N/A | N/A | The RAS-entity failed to provide the information identified in Attachment 1 to each Reliability Coordinator prior to placing a new or functionally modified RAS in service or retiring an existing RAS in accordance with Requirement R1. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012-2 | R2. | Each Reliability Coordinator that receives Attachment 1 information pursuant to Requirement R1 shall, within four full calendar months of receipt or on a mutually agreed upon schedule, perform a review of the RAS in accordance with Attachment 2, and provide written feedback to each RAS-entity. | 2021-01-01 |  | Medium | The reviewing Reliability Coordinator performed the review and provided the written feedback in accordance with Requirement R2, but was late by less than or equal to 30 full calendar days. | The reviewing Reliability Coordinator performed the review and provided the written feedback in accordance with Requirement R2, but was late by more than 30 full calendar days but less than or equal to 60 full calendar days. | The reviewing Reliability Coordinator performed the review and provided the written feedback in accordance with Requirement R2, but was late by more than 60 full calendar days but less than or equal to 90 full calendar days. | The reviewing Reliability Coordinator performed the review and provided the written feedback in accordance with Requirement R2, but was late by more than 90 full calendar days. OR The reviewing Reliability Coordinator failed to perform the review or provide feedback in accordance with Requirement R2. | [12 empty] | RC
Mandatory Subject to Enforcement | PRC | PRC-012-2 | R3. | Prior to placing a new or functionally modified RAS in service or retiring an existing RAS, each RAS-entity that receives feedback from the reviewing Reliability Coordinator(s) identifying reliability issue(s) shall resolve each issue to obtain approval of the RAS from each reviewing Reliability Coordinator. | 2021-01-01 |  | Medium | N/A | N/A | N/A | The RAS-entity failed to resolve identified reliability issue(s) to obtain approval from each reviewing Reliability Coordinator prior to placing a new or functionally modified RAS in service or retiring an existing RAS in accordance with Requirement R3. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012-2 | R4. | Each Planning Coordinator, at least once every five full calendar years, shall: | 2021-01-01 |  | Medium | The Planning Coordinator performed the evaluation in accordance with Requirement R4, but was late by less than or equal to 30 full calendar days. | The Planning Coordinator performed the evaluation in accordance with Requirement R4, but was late by more than 30 full calendar days but less than or equal to 60 full calendar days. | The Planning Coordinator performed the evaluation in accordance with Requirement R4, but was late by more than 60 full calendar days but less than or equal to 90 full calendar days. OR The Planning Coordinator performed the evaluation in accordance with Requirement R4, but failed to evaluate one of the Parts 4.1.1 through 4.1.5. | The Planning Coordinator performed the evaluation in accordance with Requirement R4, but was late by more than 90 full calendar days. OR The Planning Coordinator performed the evaluation in accordance with Requirement R4, but failed to evaluate two or more of the Parts 4.1.1 through 4.1.5. OR The Planning Coordinator performed the evaluation in accordance with Requirement R4, but failed to provide the results to one or more of the receiving entities listed in Part 4.2. OR The Planning Coordinator failed to perform the evaluation in accordance with Requirement R4. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-012-2 | R5. | Each RAS-entity, within 120 full calendar days of a RAS operation or a failure of its RAS to operate when expected, or on a mutually agreed upon schedule with its reviewing Reliability Coordinator(s), shall: | 2021-01-01 |  | Medium | The RAS-entity performed the analysis in accordance with Requirement R5, but was late by less than or equal to 10 full calendar days. | The RAS-entity performed the analysis in accordance with Requirement R5, but was late by more than 10 full calendar days but less than or equal to 20 full calendar days. | The RAS-entity performed the analysis in accordance with Requirement R5, but was late by more than 20 full calendar days but less than or equal to 30 full calendar days. OR The RAS-entity performed the analysis in accordance with Requirement R5, but failed to address one of the Parts 5.1.1 through 5.1.4. | The RAS-entity performed the analysis in accordance with Requirement R5, but was late by more than 30 full calendar days. OR The RAS-entity performed the analysis in accordance with Requirement R5, but failed to address two or more of the Parts 5.1.1 through 5.1.4. OR The RAS-entity performed the analysis in accordance with Requirement R5, but failed to provide the results (Part 5.2) to one or more of the reviewing Reliability Coordinator(s). OR The RAS-entity failed to perform the analysis in accordance with Requirement R5. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012-2 | R6. | Each RAS-entity shall participate in developing a Corrective Action Plan (CAP) and submit the CAP to its reviewing Reliability Coordinator(s) within six full calendar months of: • Being notified of a deficiency in its RAS pursuant to Requirement R4, or • Notifying the Reliability Coordinator of a deficiency pursuant to Requirement R5, Part 5.2, or • Identifying a deficiency in its RAS pursuant to Requirement R8. | 2021-01-01 |  | Medium | The RAS-entity developed a Corrective Action Plan and submitted it to its reviewing Reliability Coordinator(s) in accordance with Requirement R6, but was late by less than or equal to 10 full calendar days. | The RAS-entity developed a Corrective Action Plan and submitted it to its reviewing Reliability Coordinator(s) in accordance with Requirement R6, but was late by more than 10 full calendar days but less than or equal to 20 full calendar days. | The RAS-entity developed a Corrective Action Plan and submitted it to its reviewing Reliability Coordinator(s) in accordance with Requirement R6, but was late by more than 20 full calendar days but less than or equal to 30 full calendar days. | The RAS-entity developed a Corrective Action Plan and submitted it to its reviewing Reliability Coordinator(s) in accordance with Requirement R6, but was late by more than 30 full calendar days. OR The RAS-entity developed a Corrective Action Plan but failed to submit it to one or more of its reviewing Reliability Coordinator(s) in accordance with Requirement R6. OR The RAS-entity failed to develop a Corrective Action Plan in accordance with Requirement R6. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012-2 | R7. | Each RAS-entity shall, for each of its CAPs developed pursuant to Requirement R6: | 2021-01-01 |  | Medium | The RAS-entity implemented a CAP in accordance with Requirement R7, Part 7.1, but failed to update the CAP (Part 7.2) if actions or timetables changed, or failed to notify (Part 7.3) each of the reviewing Reliability Coordinator(s) of the updated CAP or completion of the CAP. | N/A | N/A | The RAS-entity failed to implement a CAP in accordance with Requirement R7, Part 7.1. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012-2 | R8. | Each RAS-entity shall participate in performing a functional test of each of its RAS to verify the overall RAS performance and the proper operation of non-Protection System components: • At least once every six full calendar years for all RAS not designated as limited impact, or • At least once every twelve full calendar years for all RAS designated as limited impact | 2021-01-01 |  | High | The RAS-entity performed the functional test for a RAS as specified in Requirement R8, but was late by less than or equal to 30 full calendar days. | The RAS-entity performed the functional test for a RAS as specified in Requirement R8, but was late by more than 30 full calendar days but less than or equal to 60 full calendar days. | The RAS-entity performed the functional test for a RAS as specified in Requirement R8, but was late by more than 60 full calendar days but less than or equal to 90 full calendar days. | The RAS-entity performed the functional test for a RAS as specified in Requirement R8, but was late by more than 90 full calendar days. OR The RAS-entity failed to perform the functional test for a RAS as specified in Requirement R8. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-012-2 | R9. | Each Reliability Coordinator shall update a RAS database containing, at a minimum, the information in Attachment 3 at least once every twelve full calendar months. | 2021-01-01 |  | Low | The Reliability Coordinator updated the RAS database in accordance with Requirement R9, but was late by less than or equal to 30 full calendar days. | The Reliability Coordinator updated the RAS database in accordance with Requirement R9, but was late by more than 30 full calendar days but less than or equal to 60 full calendar days. | The Reliability Coordinator updated the RAS database in accordance with Requirement R9, but was late by more than 60 full calendar days but less than or equal to 90 full calendar days. | The Reliability Coordinator updated the RAS database in accordance with Requirement R9 but was late by more than 90 full calendar days. OR The Reliability Coordinator failed to update the RAS database in accordance with Requirement R9. | [12 empty] | RC
Inactive | PRC | PRC-013-0 | R1. | The Regional Reliability Organization that has a Transmission Owner, Generator Owner, or Distribution Provider with an SPS installed shall maintain an SPS database. The database shall include the following types of information: |  | 2017-03-31 | Low | [19 empty] | RRO
Inactive | PRC | PRC-013-0 | R2. | The Regional Reliability Organization shall provide to affected Regional Reliability Organization(s) and NERC documentation of its database or the information therein on request (within 30 calendar days). |  | 2017-03-31 | Low | [19 empty] | RRO
Inactive | PRC | PRC-013-1 | R1. | The Regional Reliability Organization that has a Transmission Owner, Generator Owner, or Distribution Provider with a RAS installed shall maintain a RAS database. The database shall include the following types of information: |  | 2020-12-31 | Low | [19 empty] | RRO
Inactive | PRC | PRC-013-1 | R2. | The Regional Reliability Organization shall provide to affected Regional Reliability Organization(s) and NERC documentation of its database or the information therein on request (within 30 calendar days). |  | 2020-12-31 | Low | [19 empty] | RRO
Inactive | PRC | PRC-014-0 | R1. | The Regional Reliability Organization shall assess the operation, coordination, and effectiveness of all SPSs installed in its Region at least once every five years for compliance with NERC Reliability Standards and Regional criteria. |  | 2017-03-31 | Medium | [19 empty] | RRO
Inactive | PRC | PRC-014-0 | R2. | The Regional Reliability Organization shall provide either a summary report or a detailed report of its assessment of the operation, coordination, and effectiveness of all SPSs installed in its Region to affected Regional Reliability Organizations or NERC on request (within 30 calendar days). |  | 2017-03-31 | Low | [19 empty] | RRO
Inactive | PRC | PRC-014-0 | R3. | The documentation of the Regional Reliability Organization’s SPS assessment shall include the following elements: |  | 2017-03-31 | Low | [19 empty] | RRO
Inactive | PRC | PRC-014-1 | R1. | The Regional Reliability Organization shall assess the operation, coordination, and effectiveness of all RAS installed in its Region at least once every five years for compliance with NERC Reliability Standards and Regional criteria. |  | 2020-12-31 | Medium | [19 empty] | RRO
Inactive | PRC | PRC-014-1 | R2. | The Regional Reliability Organization shall provide either a summary report or a detailed report of its assessment of the operation, coordination, and effectiveness of all RAS installed in its Region to affected Regional Reliability Organizations or NERC on request (within 30 calendar days). |  | 2020-12-31 | Low | [19 empty] | RRO
Inactive | PRC | PRC-014-1 | R3. | The documentation of the Regional Reliability Organization’s RAS assessment shall include the following elements: |  | 2020-12-31 | Low | [19 empty] | RRO
Inactive | PRC | PRC-015-0 | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall maintain a list of and provide data for existing and proposed SPSs as specified in Reliability Standard PRC-013-0_R1. | 2007-06-18 | 2017-03-31 | Medium | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-015-0 | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it reviewed new or functionally modified SPSs in accordance with the Regional Reliability Organization’s procedures as defined in Reliability Standard PRC-012-0_R1 prior to being placed in service. | 2007-06-18 | 2017-03-31 | Medium | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-015-0 | R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of SPS data and the results of Studies that show compliance of new or functionally modified SPSs with NERC Reliability Standards and Regional Reliability Organization criteria to affected Regional Reliability Organizations and NERC on request (within 30 calendar days). | 2007-06-18 | 2017-03-31 | Low | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-015-1 | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall maintain a list of and provide data for existing and proposed RAS as specified in Reliability Standard PRC-013-1 R1. | 2017-04-01 | 2020-12-31 | Medium | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-015-1 | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it reviewed new or functionally modified RAS in accordance with the Regional Reliability Organization’s procedures as defined in Reliability Standard PRC-012-1_R1 prior to being placed in service. | 2017-04-01 | 2020-12-31 | Medium | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-015-1 | R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall provide documentation of RAS data and the results of Studies that show compliance of new or functionally modified RAS with NERC Reliability Standards and Regional Reliability Organization criteria to affected Regional Reliability Organizations and NERC on request (within 30 calendar days). | 2017-04-01 | 2020-12-31 | Low | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-016-0 | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall analyze its SPS operations and maintain a record of all misoperations in accordance with the Regional SPS review procedure specified in Reliability Standard PRC-012-0_R1. | 2007-06-18 | 2009-05-12 | Medium | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-016-0 | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall take corrective actions to avoid future misoperations. | 2007-06-18 | 2009-05-12 | Medium | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-016-0 | R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the misoperation analyses and the corrective action plans to its Regional Reliability Organization and NERC on request (within 90 calendar days). | 2007-06-18 | 2009-05-12 | Low | The responsible entity provided documentation of its SPS misoperation analyses and the corrective action plans more than 90 but less than or equal to 120 days following a request from its Regional Reliability Organization and/or NERC. | The responsible entity provided documentation of its SPS misoperation analyses and the corrective action plans more than 120 but less than or equal to 150 days following a request from its Regional Reliability Organization and/or NERC. | The responsible entity provided documentation of its SPS misoperation analyses and the corrective action plans more than 150 but less than or equal to 180 days following a request from its Regional Reliability Organization and/or NERC. | The responsible entity provided documentation of its SPS misoperation analyses and the corrective action plans more than 180 days following a request from its Regional Reliability Organization and/or NERC. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-016-0.1 | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall analyze its SPS operations and maintain a record of all misoperations in accordance with the Regional SPS review procedure specified in Reliability Standard PRC-012-0_R1. | 2009-05-13 | 2017-03-31 | Medium | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-016-0.1 | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall take corrective actions to avoid future misoperations. | 2009-05-13 | 2017-03-31 | Medium | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-016-0.1 | R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the misoperation analyses and the corrective action plans to its Regional Reliability Organization and NERC on request (within 90 calendar days). | 2009-05-13 | 2017-03-31 | Low | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-016-1 | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall analyze its RAS operations and maintain a record of all misoperations in accordance with the Regional RAS review procedure specified in Reliability Standard PRC-012-1_R1. | 2017-04-01 | 2020-12-31 | Medium | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-016-1 | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall take corrective actions to avoid future misoperations. | 2017-04-01 | 2020-12-31 | Medium | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-016-1 | R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall provide documentation of the misoperation analyses and the corrective action plans to its Regional Reliability Organization and NERC on request (within 90 calendar days). | 2017-04-01 | 2020-12-31 | Low | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-017-0 | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place. The program(s) shall include: | 2007-06-18 | 2017-03-31 | High | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-017-0 | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). | 2007-06-18 | 2017-03-31 | Low | [6 empty] | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-017-1 | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place. The program(s) shall include: | 2017-04-01 | 2027-03-31 | High | [6 empty] | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-017-1 | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall provide documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). | 2017-04-01 | 2027-03-31 | Low | [6 empty] | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-018-1 | R1. | Each Transmission Owner and Generator Owner required to install DMEs by its Regional Reliability Organization (reliability standard PRC-002 Requirements 1-3) shall have DMEs installed that meet the following requirements: | 2007-06-18 | 2022-06-30 | Low | [9 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-018-1 | R2. | The Transmission Owner and Generator Owner shall each install DMEs in accordance with its Regional Reliability Organization’s installation requirements (reliability standard PRC-002 Requirements 1 through 3). | 2007-06-18 | 2022-06-30 | Low | [9 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-018-1 | R3. | The Transmission Owner and Generator Owner shall each maintain, and report to its Regional Reliability Organization on request, the following data on the DMEs installed to meet that region’s installation requirements (reliability standard PRC-002 Requirements1.1, 2.1 and 3.1): | 2007-06-18 | 2022-06-30 | Low | [9 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-018-1 | R4. | The Transmission Owner and Generator Owner shall each provide Disturbance data (recorded by DMEs) in accordance with its Regional Reliability Organization’s requirements (reliability standard PRC-002 Requirement 4). | 2007-06-18 | 2022-06-30 | Low | [9 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-018-1 | R5. | The Transmission Owner and Generator Owner shall each archive all data recorded by DMEs for Regional Reliability Organization-identified events for at least three years. | 2007-06-18 | 2022-06-30 | Low | [9 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-018-1 | R6. | Each Transmission Owner and Generator Owner that is required by its Regional Reliability Organization to have DMEs shall have a maintenance and testing program for those DMEs that includes: | 2007-06-18 | 2022-06-30 | Low | [9 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-019-1 | R1. | At a maximum of every five calendar years, each Generator Owner and Transmission Owner with applicable Facilities shall coordinate the voltage regulating system controls, (including in-service limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. | 2016-07-01 | 2016-06-30 | Medium | The Generator Owner or Transmission Owner coordinated equipment capabilities, limiters, and protection specified in Requirement R1 more than 5 calendar years but less than or equal to 5 calendar years plus 4 months after the previous coordination. | The Generator Owner or Transmission Owner coordinated equipment capabilities, limiters, and protection specified in Requirement R1 more than 5 calendar years plus 4 months but less than or equal to 5 calendar years plus 8 months after the previous coordination. | The Generator Owner or Transmission Owner coordinated equipment capabilities, limiters, and protection specified in Requirement R1 more than 5 calendar years plus 8 months but less than or equal to 5 calendar years plus 12 months after the previous coordination. | The Generator Owner or Transmission Owner failed to coordinate equipment capabilities, limiters, and protection specified in Requirement R1 within 5 calendar years plus 12 months after the previous coordination. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-019-1 | R2. | Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, each Generator Owner and Transmission Owner with applicable Facilities shall perform the coordination as described in Requirement R1. These possible systems, equipment or settings changes include, but are not limited to the following • Voltage regulating settings or equipment changes; • Protection System settings or component changes; • Generating or synchronous condenser equipment capability changes; or • Generator or synchronous condenser step-up transformer changes. | 2016-07-01 | 2016-06-30 | Medium | The Generator Owner or Transmission Owner coordinated equipment capabilities, limiters, and protection specified in Requirement R1 more than 90 calendar days but less than or equal to 100 calendar days following the identification or implementation of a change in equipment or settings that affected the coordination. | The Generator Owner or Transmission Owner coordinated equipment capabilities, limiters, and protection specified in Requirement R1 more than 100 calendar days but less than or equal to 110 calendar days following the identification or implementation of a change in equipment or settings that affected the coordination. | The Generator Owner or Transmission Owner coordinated equipment capabilities, limiters, and protection specified in Requirement R1 more than 110 calendar days but less than or equal to 120 calendar days following the identification or implementation of a change in equipment or settings that affected the coordination. | The Generator Owner or Transmission Owner failed to coordinate equipment capabilities, limiters, and protection specified in Requirement R1 within 120 calendar days following the identification or implementation of a change in equipment or settings that affected the coordination. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-019-2 | R1. | At a maximum of every five calendar years, each Generator Owner and Transmission Owner with applicable Facilities shall coordinate the voltage regulating system controls, (including in-service limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. (Footnote: Limiters or protection functions that are installed and activated on the generator or synchronous condenser.) | 2016-07-01 |  | Medium | The Generator Owner or Transmission Owner coordinated equipment capabilities, limiters, and protection specified in Requirement R1 more than 5 calendar years but less than or equal to 5 calendar years plus 4 months after the previous coordination. | The Generator Owner or Transmission Owner coordinated equipment capabilities, limiters, and protection specified in Requirement R1 more than 5 calendar years plus 4 months but less than or equal to 5 calendar years plus 8 months after the previous coordination. | The Generator Owner or Transmission Owner coordinated equipment capabilities, limiters, and protection specified in Requirement R1 more than 5 calendar years plus 8 months but less than or equal to 5 calendar years plus 12 months after the previous coordination. | The Generator Owner or Transmission Owner failed to coordinate equipment capabilities, limiters, and protection specified in Requirement R1 within 5 calendar years plus 12 months after the previous coordination. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-019-2 | R2. | Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, each Generator Owner and Transmission Owner with applicable Facilities shall perform the coordination as described in Requirement R1. These possible systems, equipment or settings changes include, but are not limited to the following: • Voltage regulating settings or equipment changes; • Protection System settings or component changes; • Generating or synchronous condenser equipment capability changes; or • Generator or synchronous condenser step-up transformer changes. | 2016-07-01 |  | Medium | The Generator Owner or Transmission Owner coordinated equipment capabilities, limiters, and protection specified in Requirement R1 more than 90 calendar days but less than or equal to 100 calendar days following the identification or implementation of a change in equipment or settings that affected the coordination. | The Generator Owner or Transmission Owner coordinated equipment capabilities, limiters, and protection specified in Requirement R1 more than 100 calendar days but less than or equal to 110 calendar days following the identification or implementation of a change in equipment or settings that affected the coordination. | The Generator Owner or Transmission Owner coordinated equipment capabilities, limiters, and protection specified in Requirement R1 more than 110 calendar days but less than or equal to 120 calendar days following the identification or implementation of a change in equipment or settings that affected the coordination. | The Generator Owner or Transmission Owner failed to coordinate equipment capabilities, limiters, and protection specified in Requirement R1 within 120 calendar days following the identification or implementation of a change in equipment or settings that affected the coordination. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-020-1 | R1. | The Regional Reliability Organization shall establish, maintain and annually update a database for UVLS programs implemented by entities within the region to mitigate the risk of voltage collapse or voltage instability in the BES. This database shall include the following items: |  | 2017-03-31 | [20 empty] | RRO
Inactive | PRC | PRC-020-1 | R2. | The Regional Reliability Organization shall provide the information in its UVLS database to the Planning Authority, the Transmission Planner, or other Regional Reliability Organizations and to NERC within 30 calendar days of a request. |  | 2017-03-31 | [20 empty] | RRO
Inactive | PRC | PRC-020-2 | R1. | The Regional Reliability Organization shall establish, maintain and annually update a database for UVLS programs implemented by entities within the region to mitigate the risk of voltage collapse or voltage instability in the BES. This database shall include the following items: |  | 2014-11-13
Inactive | PRC | PRC-020-2 | R2. | The Regional Reliability Organization shall provide the information in its UVLS database to the Planning Authority, the Transmission Planner, or other Regional Reliability Organizations and to NERC within 30 calendar days of a request. |  | 2014-11-13
Inactive | PRC | PRC-021-1 | R1. | Each Transmission Owner and Distribution Provider that owns a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall annually update its UVLS data to support the Regional UVLS program database. The following data shall be provided to the Regional Reliability Organization for each installed UVLS system: | 2007-06-18 | 2017-03-31 | Low | [6 empty] | DP | [15 empty] | TO
Inactive | PRC | PRC-021-1 | R2. | Each Transmission Owner and Distribution Provider that owns a UVLS program shall provide its UVLS program data to the Regional Reliability Organization within 30 calendar days of a request. | 2007-06-18 | 2017-03-31 | Low | [6 empty] | DP | [15 empty] | TO
Inactive | PRC | PRC-021-2 | R1. | Each Transmission Owner and Distribution Provider that owns a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall annually update its UVLS data to support the Regional UVLS program database. The following data shall be provided to the Regional Reliability Organization for each installed UVLS system: |  | 2014-11-13 | [7 empty] | DP | [15 empty] | TO
Inactive | PRC | PRC-021-2 | R2. | Each Transmission Owner and Distribution Provider that owns a UVLS program shall provide its UVLS program data to the Regional Reliability Organization within 30 calendar days of a request. |  | 2014-11-13 | [7 empty] | DP | [15 empty] | TO
Inactive | PRC | PRC-022-1 | R1. | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall analyze and document all UVLS operations and Misoperations. The analysis shall include: | 2007-06-18 | 2017-03-31 | Medium | [6 empty] | DP | [5 empty] | LSE | [10 empty] | TOP
Inactive | PRC | PRC-022-1 | R2. | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program shall provide documentation of its analysis of UVLS program performance to its Regional Reliability Organization within 90 calendar days of a request. | 2007-06-18 | 2014-01-21 | Low | [6 empty] | DP | [5 empty] | LSE | [10 empty] | TOP
Inactive | PRC | PRC-023-1 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (R1.1 through R1.13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the Bulk Electric System for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees: | 2010-07-01 | 2012-06-30 | High | N/A | Evidence that relay settings comply with criteria in R1.1 though 1.13 exists, but evidence is incomplete or incorrect for one or more of the subrequirements. | N/A | Relay settings do not comply with any of the sub requirements R1.1 through R1.13 OR Evidence does not exist to support that relay settings comply with one of the criteria in subrequirements R1.1 through R1.13. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-1 | R2. | The Transmission Owner, Generator Owner, or Distribution Provider that uses a circuit capability with the practical limitations described in R1.6, R1.7, R1.8, R1.9, R1.12, or R1.13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. | 2010-07-01 | 2012-06-30 | Medium | Criteria described in R1.6, R1.7. R1.8. R1.9, R1.12, or R.13 was used but evidence does not exist that agreement was obtained in accordance with R2. | N/A | N/A | N/A |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-1 | R3. | The Planning Coordinator shall determine which of the facilities (transmission lines operated at 100 kV to 200 kV and transformers with low voltage terminals connected at 100 kV to 200 kV) in its Planning Coordinator Area are critical to the reliability of the Bulk Electric System to identify the facilities from 100 kV to 200 kV that must meet Requirement 1 to prevent potential cascade tripping that may occur when protective relay settings limit transmission loadability. | 2011-11-17 | 2012-06-30 | Medium | N/A | Provided the list of facilities critical to the reliability of the Bulk Electric System to the appropriate Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers between 31 days and 45 days after the list was established or updated. | Provided the list of facilities critical to the reliability of the Bulk Electric System to the appropriate Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers between 46 days and 60 days after list was established or updated. | Does not have a process in place to determine facilities that are critical to the reliability of the Bulk Electric System. OR Does not maintain a current list of facilities critical to the reliability of the Bulk Electric System, OR Did not provide the list of facilities critical to the reliability of the Bulk Electric System to the appropriate Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers, or provided the list more than 60 days after the list was established or updated. | [10 empty] | PCPA
Inactive | PRC | PRC-023-2 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. 1. Set transmission line relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes). 2. Set transmission line relays so they do not operate at or below 115% of the highest seasonal 15-minute Facility Rating of a circuit (expressed in amperes). 3. Set transmission line relays so they do not operate at or below 115% of the maximum theoretical power transfer capability (using a 90-degree angle between the sending-end and receiving-end voltages and either reactance or complex impedance) of the circuit (expressed in amperes) using one of the following to perform the power transfer calculation: • An infinite source (zero source impedance) with a 1.00 per unit bus voltage at each end of the line. • An impedance at each end of the line, which reflects the actual system source impedance with a 1.05 per unit voltage behind each source impedance. 4. Set transmission line relays on series compensated transmission lines so they do not operate at or below the maximum power transfer capability of the line, determined as the greater of: • 115% of the highest emergency rating of the series capacitor. • 115% of the maximum power transfer capability of the circuit (expressed in amperes), calculated in accordance with Requirement R1, criterion 3, using the full line inductive reactance. 5. Set transmission line relays on weak source systems so they do not operate at or below 170% of the maximum end-of-line three-phase fault magnitude (expressed in amperes). 6. Set transmission line relays applied on transmission lines connected to generation stations remote to load so they do not operate at or below 230% of the aggregated generation nameplate capability. 7. Set transmission line relays applied at the load center terminal, remote from generation stations, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration. 8. Set transmission line relays applied on the bulk system-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the system to the load under any system configuration. 9. Set transmission line relays applied on the load-end of transmission lines that serve load remote to the bulk system so they do not operate at or below 115% of the maximum current flow from the load to the system under any system configuration. 10. Set transformer fault protection relays and transmission line relays on transmission lines terminated only with a transformer so that the relays do not operate at or below the greater of: • 150% of the applicable maximum transformer nameplate rating (expressed in amperes), including the forced cooled ratings corresponding to all installed supplemental cooling equipment. • 115% of the highest operator established emergency transformer rating 10.1 Set load responsive transformer fault protection relays, if used, such that the protection settings do not expose the transformer to a fault level and duration that exceeds the transformer’s mechanical withstand capability . 11. For transformer overload protection relays that do not comply with the loadability component of Requirement R1, criterion 10 set the relays according to one of the following: • Set the relays to allow the transformer to be operated at an overload level of at least 150% of the maximum applicable nameplate rating, or 115% of the highest operator established emergency transformer rating, whichever is greater, for at least 15 minutes to provide time for the operator to take controlled action to relieve the overload. • Install supervision for the relays using either a top oil or simulated winding hot spot temperature element set no less than 100° C for the top oil temperature or no less than 140° C for the winding hot spot temperature . 12. When the desired transmission line capability is limited by the requirement to adequately protect the transmission line, set the transmission line distance relays to a maximum of 125% of the apparent impedance (at the impedance angle of the transmission line) subject to the following constraints: a. Set the maximum torque angle (MTA) to 90 degrees or the highest supported by the manufacturer. b. Evaluate the relay loadability in amperes at the relay trip point at 0.85 per unit voltage and a power factor angle of 30 degrees. c. Include a relay setting component of 87% of the current calculated in Requirement R1, criterion 12 in the Facility Rating determination for the circuit. 13. Where other situations present practical limitations on circuit capability, set the phase protection relays so they do not operate at or below 115% of such limitations. | 2012-07-01 | 2014-09-30 | High | N/A | N/A | N/A | The responsible entity did not use any one of the following criteria (Requirement R1 criterion 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the Bulk Electric System for all fault conditions. OR The responsible entity did not evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-2 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. | 2012-07-01 | 2014-09-30 | High | N/A | N/A | N/A | The responsible entity failed to ensure that its out-of-step blocking elements allowed tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-2 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 6, 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. | 2012-07-01 | 2014-09-30 | Medium | N/A | N/A | N/A | The responsible entity that uses a circuit capability with the practical limitations described in Requirement R1 criterion 6, 7, 8, 9, 12, or 13 did not use the calculated circuit capability as the Facility Rating of the circuit. OR The responsible entity did not obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-2 | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. | 2013-01-01 | 2014-09-30 | Low | N/A | N/A | N/A | The responsible entity did not provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits that have transmission line relays set according to the criteria established in Requirement R1 criterion 2 at least once each calendar year, with no more than 15 months between reports. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-2 | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. | 2013-01-01 | 2014-09-30 | Low | N/A | N/A | N/A | The responsible entity did not provide its Regional Entity, with an updated list of circuits that have transmission line relays set according to the criteria established in Requirement R1 criterion 12 at least once each calendar year, with no more than 15 months between reports |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-2 | R6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: | 2014-01-01 | 2014-09-30 | High | N/A | The Planning Coordinator used the criteria established within Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met parts 6.1 and 6.2, but more than 15 months and less than 24 months lapsed between assessments. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 and 6.2 but failed to include the calendar year in which any criterion in Attachment B first applies. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 and 6.2 but provided the list of circuits to the Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area between 31 days and 45 days after the list was established or updated. (part 6.2) | The Planning Coordinator used the criteria established within Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met parts 6.1 and 6.2, but 24 months or more lapsed between assessments. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 and 6.2 but provided the list of circuits to the Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area between 46 days and 60 days after list was established or updated. (part 6.2) | The Planning Coordinator failed to use the criteria established within Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard. OR The Planning Coordinator used the criteria established within Attachment B, at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard but failed to meet parts 6.1 and 6.2. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard but failed to maintain the list of circuits determined according to the process described in Requirement R6. (part 6.1) OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 but failed to provide the list of circuits to the Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area or provided the list more than 60 days after the list was established or updated. (part 6.2) OR The Planning Coordinator failed to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard. | [10 empty] | PCPA
Inactive | PRC | PRC-023-3 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. Criteria:1. Set transmission line relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes).2. Set transmission line relays so they do not operate at or below 115% of the highest seasonal 15-minute Facility Rating of a circuit (expressed in amperes).3. Set transmission line relays so they do not operate at or below 115% of the maximum theoretical power transfer capability (using a 90-degree angle between the sending-end and receiving-end voltages and either reactance or complex impedance) of the circuit (expressed in amperes) using one of the following to perform the power transfer calculation:• An infinite source (zero source impedance) with a 1.00 per unit bus voltage at each end of the line.• An impedance at each end of the line, which reflects the actual system source impedance with a 1.05 per unit voltage behind each source impedance.4. Set transmission line relays on series compensated transmission lines so they do not operate at or below the maximum power transfer capability of the line, determined as the greater of:• 115% of the highest emergency rating of the series capacitor.• 115% of the maximum power transfer capability of the circuit (expressed in amperes), calculated in accordance with Requirement R1, criterion 3, using the full line inductive reactance.5. Set transmission line relays on weak source systems so they do not operate at or below 170% of the maximum end-of-line three-phase fault magnitude (expressed in amperes).6. Not used.7. Set transmission line relays applied at the load center terminal, remote from generation stations, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration.8. Set transmission line relays applied on the bulk system-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the system to the load under any system configuration.9. Set transmission line relays applied on the load-end of transmission lines that serve load remote to the bulk system so they do not operate at or below 115% of the maximum current flow from the load to the system under any system configuration.10. Set transformer fault protection relays and transmission line relays on transmission lines terminated only with a transformer so that the relays do not operate at or below the greater of:• 150% of the applicable maximum transformer nameplate rating (expressed in amperes), including the forced cooled ratings corresponding to all installed supplemental cooling equipment.• 115% of the highest operator established emergency transformer rating.10.1 Set load-responsive transformer fault protection relays, if used, such that the protection settings do not expose the transformer to a fault level and duration that exceeds the transformer’s mechanical withstand capability .11. For transformer overload protection relays that do not comply with the loadability component of Requirement R1, criterion 10 set the relays according to one of the following: • Set the relays to allow the transformer to be operated at an overload level of at least 150% of the maximum applicable nameplate rating, or 115% of the highest operator established emergency transformer rating, whichever is greater, for at least 15 minutes to provide time for the operator to take controlled action to relieve the overload.• Install supervision for the relays using either a top oil or simulated winding hot spot temperature element set no less than 100° C for the top oil temperature or no less than 140° C for the winding hot spot temperature .12. When the desired transmission line capability is limited by the requirement to adequately protect the transmission line, set the transmission line distance relays to a maximum of 125% of the apparent impedance (at the impedance angle of the transmission line) subject to the following constraints:a. Set the maximum torque angle (MTA) to 90 degrees or the highest supported by the manufacturer.b. Evaluate the relay loadability in amperes at the relay trip point at 0.85 per unit voltage and a power factor angle of 30 degrees.c. Include a relay setting component of 87% of the current calculated in Requirement R1, criterion 12 in the Facility Rating determination for the circuit.13. Where other situations present practical limitations on circuit capability, set the phase protection relays so they do not operate at or below 115% of such limitations. | 2014-10-01 | 2017-03-31 | High | N/A | N/A | N/A | The responsible entity did not use any one of the following criteria (Requirement R1 criterion 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. OR The responsible entity did not evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-3 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. | 2014-10-01 | 2017-03-31 | High | N/A | N/A | N/A | The responsible entity failed to ensure that its out-of-step blocking elements allowed tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-3 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. | 2014-10-01 | 2017-03-31 | Medium | N/A | N/A | N/A | The responsible entity that uses a circuit capability with the practical limitations described in Requirement R1 criterion 7, 8, 9, 12, or 13 did not use the calculated circuit capability as the Facility Rating of the circuit. OR The responsible entity did not obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-3 | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. | 2014-10-01 | 2017-03-31 | Low | N/A | N/A | N/A | The responsible entity did not provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits that have transmission line relays set according to the criteria established in Requirement R1 criterion 2 at least once each calendar year, with no more than 15 months between reports. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-3 | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. | 2014-10-01 | 2017-03-31 | Low | N/A | N/A | N/A | The responsible entity did not provide its Regional Entity, with an updated list of circuits that have transmission line relays set according to the criteria established in Requirement R1 criterion 12 at least once each calendar year, with no more than 15 months between reports. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-3 | R6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-3, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: | 2014-10-01 | 2017-03-31 | High | N/A | The Planning Coordinator used the criteria established within Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met parts 6.1 and 6.2, but more than 15 months and less than 24 months lapsed between assessments. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 and 6.2 but failed to include the calendar year in which any criterion in Attachment B first applies. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 and 6.2 but provided the list of circuits to the Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area between 31 days and 45 days after the list was established or updated. (part 6.2) | The Planning Coordinator used the criteria established within Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met parts 6.1 and 6.2, but 24 months or more lapsed between assessments. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 and 6.2 but provided the list of circuits to the Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area between 46 days and 60 days after list was established or updated. (part 6.2) | The Planning Coordinator failed to use the criteria established within Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard. OR The Planning Coordinator used the criteria established within Attachment B, at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard but failed to meet parts 6.1 and 6.2. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard but failed to maintain the list of circuits determined according to the process described in Requirement R6. (part 6.1) OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 but failed to provide the list of circuits to the Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area or provided the list more than 60 days after the list was established or updated. (part 6.2) OR The Planning Coordinator failed to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard. | [10 empty] | PCPA
Inactive | PRC | PRC-023-4 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. Criteria: 1. Set transmission line relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes). 2. Set transmission line relays so they do not operate at or below 115% of the highest seasonal 15-minute Facility Rating of a circuit (expressed in amperes). 3. Set transmission line relays so they do not operate at or below 115% of the maximum theoretical power transfer capability (using a 90-degree angle between the sending-end and receiving-end voltages and either reactance or complex impedance) of the circuit (expressed in amperes) using one of the following to perform the power transfer calculation: • An infinite source (zero source impedance) with a 1.00 per unit bus voltage at each end of the line. • An impedance at each end of the line, which reflects the actual system source impedance with a 1.05 per unit voltage behind each source impedance. 4. Set transmission line relays on series compensated transmission lines so they do not operate at or below the maximum power transfer capability of the line, determined as the greater of: • 115% of the highest emergency rating of the series capacitor. • 115% of the maximum power transfer capability of the circuit (expressed in amperes), calculated in accordance with Requirement R1, criterion 3, using the full line inductive reactance. 5. Set transmission line relays on weak source systems so they do not operate at or below 170% of the maximum end-of-line three-phase fault magnitude (expressed in amperes). 6. Not used. 7. Set transmission line relays applied at the load center terminal, remote from generation stations, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration. 8. Set transmission line relays applied on the bulk system-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the system to the load under any system configuration. 9. Set transmission line relays applied on the load-end of transmission lines that serve load remote to the bulk system so they do not operate at or below 115% of the maximum current flow from the load to the system under any system configuration. 10. Set transformer fault protection relays and transmission line relays on transmission lines terminated only with a transformer so that the relays do not operate at or below the greater of: • 150% of the applicable maximum transformer nameplate rating (expressed in amperes), including the forced cooled ratings corresponding to all installed supplemental cooling equipment. • 115% of the highest operator established emergency transformer rating. 10.1 Set load-responsive transformer fault protection relays, if used, such that the protection settings do not expose the transformer to a fault level and duration that exceeds the transformer’s mechanical withstand capability . 11. For transformer overload protection relays that do not comply with the loadability component of Requirement R1, criterion 10 set the relays according to one of the following: • Set the relays to allow the transformer to be operated at an overload level of at least 150% of the maximum applicable nameplate rating, or 115% of the highest operator established emergency transformer rating, whichever is greater, for at least 15 minutes to provide time for the operator to take controlled action to relieve the overload. • Install supervision for the relays using either a top oil or simulated winding hot spot temperature element set no less than 100° C for the top oil temperature or no less than 140° C for the winding hot spot temperature . 12. When the desired transmission line capability is limited by the requirement to adequately protect the transmission line, set the transmission line distance relays to a maximum of 125% of the apparent impedance (at the impedance angle of the transmission line) subject to the following constraints: a. Set the maximum torque angle (MTA) to 90 degrees or the highest supported by the manufacturer. b. Evaluate the relay loadability in amperes at the relay trip point at 0.85 per unit voltage and a power factor angle of 30 degrees. c. Include a relay setting component of 87% of the current calculated in Requirement R1, criterion 12 in the Facility Rating determination for the circuit. 13. Where other situations present practical limitations on circuit capability, set the phase protection relays so they do not operate at or below 115% of such limitations. (Footnote: When a 15-minute rating has been calculated and published for use in real-time operations, the 15-minute rating can be used to establish the loadability requirement for the protective relays. As illustrated by the “dotted line” in IEEE C57.109-1993 - IEEE Guide for Liquid-Immersed Transformer Through-Fault-Current Duration, Clause 4.4, Figure 4. IEEE standard C57.91, Tables 7 and 8, specify that transformers are to be designed to withstand a winding hot spot temperature of 180 degrees C, and Annex A cautions that bubble formation may occur above 140 degrees C. | 2017-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The responsible entity did not use any one of the following criteria (Requirement R1 criterion 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. OR The responsible entity did not evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-4 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. | 2017-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The responsible entity failed to ensure that its out-of-step blocking elements allowed tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-4 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. | 2017-04-01 | 2024-03-31 | Medium | N/A | N/A | N/A | The responsible entity that uses a circuit capability with the practical limitations described in Requirement R1 criterion 7, 8, 9, 12, or 13 did not use the calculated circuit capability as the Facility Rating of the circuit. OR The responsible entity did not obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-4 | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. | 2017-04-01 | 2024-03-31 | Low | N/A | N/A | N/A | The responsible entity did not provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits that have transmission line relays set according to the criteria established in Requirement R1 criterion 2 at least once each calendar year, with no more than 15 months between reports. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-4 | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. | 2017-04-01 | 2024-03-31 | Low | N/A | N/A | N/A | The responsible entity did not provide its Regional Entity, with an updated list of circuits that have transmission line relays set according to the criteria established in Requirement R1 criterion 12 at least once each calendar year, with no more than 15 months between reports. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-023-4 | R6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: | 2017-04-01 | 2024-03-31 | High | N/A | The Planning Coordinator used the criteria established within Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met parts 6.1 and 6.2, but more than 15 months and less than 24 months lapsed between assessments. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 and 6.2 but failed to include the calendar year in which any criterion in Attachment B first applies. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 and 6.2 but provided the list of circuits to the Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area between 31 days and 45 days after the list was established or updated. (part 6.2) | The Planning Coordinator used the criteria established within Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met parts 6.1 and 6.2, but 24 months or more lapsed between assessments. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 and 6.2 but provided the list of circuits to the Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area between 46 days and 60 days after list was established or updated. (part 6.2) | The Planning Coordinator failed to use the criteria established within Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard. OR The Planning Coordinator used the criteria established within Attachment B, at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard but failed to meet parts 6.1 and 6.2. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard but failed to maintain the list of circuits determined according to the process described in Requirement R6. (part 6.1) OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 but failed to provide the list of circuits to the Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area or provided the list more than 60 days after the list was established or updated. (part 6.2) OR The Planning Coordinator failed to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard. |  |  | DP |  |  | GO |  |  |  |  | PCPA |  | RC | [5 empty] | TO
Pending Inactive | PRC | PRC-023-5 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. Criteria: 1. Set transmission line relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes). 2. Set transmission line relays so they do not operate at or below 115% of the highest seasonal 15-minute Facility Rating1 of a circuit (expressed in amperes). Note: When a 15-minute rating has been calculated and published for use in real-time operations, the 15-minute rating can be used to establish the loadability requirement for the protective relays. 3. Set transmission line relays so they do not operate at or below 115% of the maximum theoretical power transfer capability (using a 90-degree angle between the sending-end and receiving-end voltages and either reactance or complex impedance) of the circuit (expressed in amperes) using one of the following to perform the power transfer calculation: · An infinite source (zero source impedance) with a 1.00 per unit bus voltage at each end of the line. · An impedance at each end of the line, which reflects the actual system source impedance with a 1.05 per unit voltage behind each source impedance. 4. Set transmission line relays on series compensated transmission lines so they do not operate at or below the maximum power transfer capability of the line, determined as the greater of: · 115% of the highest emergency rating of the series capacitor. · 115% of the maximum power transfer capability of the circuit (expressed in amperes), calculated in accordance with Requirement R1, criterion 3, using the full line inductive reactance. 5. Set transmission line relays on weak source systems so they do not operate at or below 170% of the maximum end-of-line three-phase fault magnitude (expressed in amperes). 6. Not used. 7. Set transmission line relays applied at the load center terminal, remote from generation stations, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration. 8. Set transmission line relays applied on the bulk system-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the system to the load under any system configuration. 9. Set transmission line relays applied on the load-end of transmission lines that serve load remote to the bulk system so they do not operate at or below 115% of the maximum current flow from the load to the system under any system configuration. 10. Set transformer fault protection relays and transmission line relays on transmission lines terminated only with a transformer so that the relays do not operate at or below the greater of: · 150% of the applicable maximum transformer nameplate rating (expressed in amperes), including the forced cooled ratings corresponding to all installed supplemental cooling equipment. · 115% of the highest operator established emergency transformer rating. 10.1 Set load-responsive transformer fault protection relays, if used, such that the protection settings do not expose the transformer to a fault level and duration that exceeds the transformer’s mechanical withstand capability. 11. For transformer overload protection relays that do not comply with the loadability component of Requirement R1, criterion 10 set the relays according to one of the following: · Set the relays to allow the transformer to be operated at an overload level of at least 150% of the maximum applicable nameplate rating, or 115% of the highest operator established emergency transformer rating, whichever is greater, for at least 15 minutes to provide time for the operator to take controlled action to relieve the overload. · Install supervision for the relays using either a top oil or simulated winding hot spot temperature element set no less than 100° C for the top oil temperature or no less than 140° C for the winding hot spot temperature3. 12. When the desired transmission line capability is limited by the requirement to adequately protect the transmission line, set the transmission line distance relays to a maximum of 125% of the apparent impedance (at the impedance angle of the transmission line) subject to the following constraints: a. Set the maximum torque angle (MTA) to 90 degrees or the highest supported by the manufacturer. b. Evaluate the relay loadability in amperes at the relay trip point at 0.85 per unit voltage and a power factor angle of 30 degrees. c. Include a relay setting component of 87% of the current calculated in Requirement R1, criterion 12 in the Facility Rating determination for the circuit. 13. Where other situations present practical limitations on circuit capability, set the phase protection relays so they do not operate at or below 115% of such limitations. Note: As illustrated by the “dotted line” in IEEE C57.109-1993 - IEEE Guide for Liquid-Immersed Transformer Through-Fault-Current Duration, Clause 4.4, Figure 4. IEEE standard C57.91, Tables 7 and 8, specify that transformers are to be designed to withstand a winding hot spot temperature of 180 degrees C, and Annex A cautions that bubble formation may occur above 140 degrees C. | 2024-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The responsible entity did not use any one of the following criteria (Requirement R1 criterion 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. OR The responsible entity did not evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. |  |  | DP |  |  | GO | [12 empty] | TO
Pending Inactive | PRC | PRC-023-5 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. | 2024-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The responsible entity failed to ensure that its out-of-step blocking elements allowed tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. |  |  | DP |  |  | GO | [12 empty] | TO
Pending Inactive | PRC | PRC-023-5 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. | 2024-04-01 | 2024-03-31 | Medium | N/A | N/A | N/A | The responsible entity that uses a circuit capability with the practical limitations described in Requirement R1 criterion 7, 8, 9, 12, or 13 did not use the calculated circuit capability as the Facility Rating of the circuit. OR The responsible entity did not obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. |  |  | DP |  |  | GO | [12 empty] | TO
Pending Inactive | PRC | PRC-023-5 | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. | 2024-04-01 | 2024-03-31 | Low | N/A | N/A | N/A | The responsible entity did not provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits that have transmission line relays set according to the criteria established in Requirement R1 criterion 2 at least once each calendar year, with no more than 15 months between reports. |  |  | DP |  |  | GO | [12 empty] | TO
Pending Inactive | PRC | PRC-023-5 | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. | 2024-04-01 | 2024-03-31 | Low | N/A | N/A | N/A | The responsible entity did not provide its Regional Entity, with an updated list of circuits that have transmission line relays set according to the criteria established in Requirement R1 criterion 12 at least once each calendar year, with no more than 15 months between reports. |  |  | DP |  |  | GO | [12 empty] | TO
Pending Inactive | PRC | PRC-023-5 | R6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023-5, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: | 2024-04-01 | 2024-03-31 | High | N/A | The Planning Coordinator used the criteria established within Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met parts 6.1 and 6.2, but more than 15 months and less than 24 months lapsed between assessments. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 and 6.2 but failed to include the calendar year in which any criterion in Attachment B first applies. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 and 6.2 but provided the list of circuits to the Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area between 31 days and 45 days after the list was established or updated. (part 6.2) | The Planning Coordinator used the criteria established within Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met parts 6.1 and 6.2, but 24 months or more lapsed between assessments. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 and 6.2 but provided the list of circuits to the Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area between 46 days and 60 days after list was established or updated. (part 6.2) | The Planning Coordinator failed to use the criteria established within Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard. OR The Planning Coordinator used the criteria established within Attachment B, at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard but failed to meet parts 6.1 and 6.2. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard but failed to maintain the list of circuits determined according to the process described in Requirement R6. (part 6.1) OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 but failed to provide the list of circuits to the Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area or provided the list more than 60 days after the list was established or updated. (part 6.2) OR The Planning Coordinator failed to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard. | [10 empty] | PCPA
Mandatory Subject to Enforcement | PRC | PRC-023-6 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees | 2024-04-01 |  | High | N/A | N/A | N/A | The responsible entity did not use any one of the following criteria (Requirement R1 criterion 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. OR The responsible entity did not evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-023-6 | R2. | Reserved. | 2024-04-01 |  |  | N/A | N/A | N/A | Reserved. | R2.-Retired as of 4/1/2024-Not Subject to Enforcement
Mandatory Subject to Enforcement | PRC | PRC-023-6 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. | 2024-04-01 |  | Medium | N/A | N/A | N/A | The responsible entity that uses a circuit capability with the practical limitations described in Requirement R1 criterion 7, 8, 9, 12, or 13 did not use the calculated circuit capability as the Facility Rating of the circuit. OR The responsible entity did not obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-023-6 | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. | 2024-04-01 |  | Low | N/A | N/A | N/A | The responsible entity did not provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits that have transmission line relays set according to the criteria established in Requirement R1 criterion 2 at least once each calendar year, with no more than 15 months between reports. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-023-6 | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability | 2024-04-01 |  | Low | N/A | N/A | N/A | The responsible entity did not provide its Regional Entity, with an updated list of circuits that have transmission line relays set according to the criteria established in Requirement R1 criterion 12 at least once each calendar year, with no more than 15 months between reports, |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-023-6 | R6. | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in PRC-023- 6, Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: | 2024-04-01 |  | High | N/A | The Planning Coordinator used the criteria established within Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met parts 6.1 and 6.2, but more than 15 months and less than 24months lapsed between assessments. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 and 6.2 but failed to include the calendar year in which any criterion in Attachment B first applies. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 and 6.2 but provided the list of circuits to the Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area between 31 days and 45 days after the list was established or updated.(part 6.2) | The Planning Coordinator used the criteria established within Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met parts 6.1 and 6.2, but 24 months or more lapsed between assessments. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 and 6.2 but provided the list of circuits to the Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area between 46 days and 60 days after list was established or updated. (part 6.2) | The Planning Coordinator failed to use the criteria established within Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard. OR The Planning Coordinator used the criteria established within Attachment B, at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard but failed to meet parts 6.1 and 6.2. OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard but failed to maintain the list of circuits determined according to the process described in Requirement R6. (part 6.1) OR The Planning Coordinator used the criteria established within Attachment B at least once each calendar year, with no more than 15 months between assessments to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard and met 6.1 but failed to provide the list of circuits to the Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area or provided the list more than 60 days after the list was established or updated. (part 6.2) OR The Planning Coordinator failed to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard. |  |  | DP |  |  | GO |  |  |  |  | PCPA | [7 empty] | TO
Inactive | PRC | PRC-024-1 | R1. | Each Generator Owner that has generator frequency protective relaying activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1, subject to the following exceptions: • Generating unit(s) may trip if the protective functions (such as out-of-step functions or loss-of-field functions) operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 1 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | 2016-07-01 | 2016-06-30 | Medium | N/A | N/A | N/A | The Generator Owner that has frequency protection activated to trip a generating unit, failed to set its generator frequency protective relaying so that it does not trip within the criteria listed in Requirement R1 unless there is a documented and communicated regulatory or equipment limitation per Requirement R3. | [5 empty] | GO
Inactive | PRC | PRC-024-1 | R2. | Each Generator Owner that has generator voltage protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection ) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2. If the Transmission Planner allows less stringent voltage relay settings than those required to meet PRC-024 Attachment 2, then the Generator Owner shall set its protective relaying within the voltage recovery characteristics of a location-specific Transmission Planner’s study. Requirement R2 is subject to the following exceptions: • Generating unit(s) may trip in accordance with a Special Protection System (SPS) or Remedial Action Scheme (RAS). • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip by action of protective functions (such as out-of-step functions or loss-of-field functions) that operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 2 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | 2016-07-01 | 2016-06-30 | Medium | N/A | N/A | N/A | The Generator Owner with voltage protective relaying activated to trip a generating unit, failed to set its voltage protective relaying so that it does not trip as a result of a voltage excursion at the point of interconnection, caused by an event external to the plant per the criteria specified in Requirement R2 unless there is a documented and communicated regulatory or equipment limitation per Requirement R3. | [5 empty] | GO
Inactive | PRC | PRC-024-1 | R3. | Each Generator Owner shall document each known regulatory or equipment limitation that prevents an applicable generating unit with generator frequency or voltage protective relays from meeting the relay setting criteria in Requirements R1 or R2 including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. | 2016-07-01 | 2016-06-30 | Low | The Generator Owner documented the known non-protection system equipment limitation that prevented it from meeting the criteria in Requirement R1 or R2 and communicated the documented limitation to its Planning Coordinator and Transmission Planner more than 30 calendar days but less than or equal to 60 calendar days of identifying the limitation. | The Generator Owner documented the known non-protection system equipment limitation that prevented it from meeting the criteria in Requirement R1 or R2 and communicated the documented limitation to its Planning Coordinator and Transmission Planner more than 60 calendar days but less than or equal to 90 calendar days of identifying the limitation. | The Generator Owner documented the known non-protection system equipment limitation that prevented it from meeting the criteria in Requirement R1 or R2 and communicated the documented limitation to its Planning Coordinator and Transmission Planner more than 90 calendar days but less than or equal to 120 calendar days of identifying the limitation. | The Generator Owner failed to document any known non-protection system equipment limitation that prevented it from meeting the criteria in Requirement R1 or R2. OR The Generator Owner failed to communicate the documented limitation to its Planning Coordinator and Transmission Planner within 120 calendar days of identifying the limitation. | [5 empty] | GO
Inactive | PRC | PRC-024-1 | R4. | Each Generator Owner shall provide its applicable generator protection trip settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated unit within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested trip settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of relay setting changes is not required. | 2016-07-01 | 2016-06-30 | Low | The Generator Owner provided its generator protection trip settings more than 60 calendar days but less than or equal to 90 calendar days of any change to those trip settings. OR The Generator Owner provided trip settings more than 60 calendar days but less than or equal to 90 calendar days of a written request. | The Generator Owner provided its generator protection trip settings more than 90 calendar days but less than or equal to 120 calendar days of any change to those trip settings. OR The Generator Owner provided trip settings more than 90 calendar days but less than or equal to 120 calendar days of a request. | The Generator Owner provided its generator protection trip settings more than 120 calendar days but less than or equal to 150 calendar days of any change to those trip settings. OR The Generator Owner provided trip settings more than 120 calendar days but less than or equal to 150 calendar days of a written request. | The Generator Owner failed to provide its generator protection trip settings within 150 calendar days of any change to those trip settings. OR The Generator Owner failed to provide trip settings within 150 calendar days of a written request. | [5 empty] | GO
Mandatory Subject to Enforcement | PRC | PRC-024-2 | R1. | Each Generator Owner that has generator frequency protective relaying activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1, subject to the following exceptions: • Generating unit(s) may trip if the protective functions (such as out-of-step functions or loss-of-field functions) operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 1 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. Footnote: Each Generator Owner is not required to have frequency or voltage protective relaying (including but not limited to frequency and voltage protective functions for discrete relays, volts per hertz relays evaluated at nominal frequency, multi-function protective devices or protective functions within control systems that directly trip or provide tripping signals to the generator based on frequency or voltage inputs) installed or activated on its unit. | 2016-07-01 |  | Medium | N/A | N/A | N/A | The Generator Owner that has frequency protection activated to trip a generating unit, failed to set its generator frequency protective relaying so that it does not trip within the criteria listed in Requirement R1 unless there is a documented and communicated regulatory or equipment limitation per Requirement R3. | [5 empty] | GO
Mandatory Subject to Enforcement | PRC | PRC-024-2 | R2. | Each Generator Owner that has generator voltage protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection ) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2. If the Transmission Planner allows less stringent voltage relay settings than those required to meet PRC-024 Attachment 2, then the Generator Owner shall set its protective relaying within the voltage recovery characteristics of a location-specific Transmission Planner’s study. Requirement R2 is subject to the following exceptions: • Generating unit(s) may trip in accordance with a Special Protection System (SPS) or Remedial Action Scheme (RAS). • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip by action of protective functions (such as out-of-step functions or loss-of-field functions) that operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 2 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. (Footnote: Each Generator Owner is not required to have frequency or voltage protective relaying (including but not limited to frequency and voltage protective functions for discrete relays, volts per hertz relays evaluated at nominal frequency, multi-function protective devices or protective functions within control systems that directly trip or provide tripping signals to the generator based on frequency or voltage inputs) installed or activated on its unit. For frequency protective relays associated with dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition, this requirement applies to frequency protective relays applied on the individual generating unit of the dispersed power producing resources, as well as frequency protective relays applied on equipment from the individual generating unit of the dispersed power producing resource up to the point of interconnection. For the purposes of this standard, point of interconnection means the transmission (high voltage) side of the generator step-up or collector transformer. For voltage protective relays associated with dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition, this requirement applies to voltage protective relays applied on the individual generating unit of the dispersed power producing resources, as well as voltage protective relays applied on equipment from the individual generating unit of the dispersed power producing resource up to the point of interconnection. | 2016-07-01 |  | Medium | N/A | N/A | N/A | The Generator Owner with voltage protective relaying activated to trip a generating unit, failed to set its voltage protective relaying so that it does not trip as a result of a voltage excursion at the point of interconnection, caused by an event external to the plant per the criteria specified in Requirement R2 unless there is a documented and communicated regulatory or equipment limitation per Requirement R3. | [5 empty] | GO
Mandatory Subject to Enforcement | PRC | PRC-024-2 | R3. | Each Generator Owner shall document each known regulatory or equipment limitation that prevents an applicable generating unit with generator frequency or voltage protective relays from meeting the relay setting criteria in Requirements R1 or R2 including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. (Footnote: Excludes limitations that are caused by the setting capability of the generator frequency and voltage protective relays themselves but does not exclude limitations originating in the equipment that they protect.) | 2016-07-01 |  | Low | The Generator Owner documented the known non-protection system equipment limitation that prevented it from meeting the criteria in Requirement R1 or R2 and communicated the documented limitation to its Planning Coordinator and Transmission Planner more than 30 calendar days but less than or equal to 60 calendar days of identifying the limitation. | The Generator Owner documented the known non-protection system equipment limitation that prevented it from meeting the criteria in Requirement R1 or R2 and communicated the documented limitation to its Planning Coordinator and Transmission Planner more than 60 calendar days but less than or equal to 90 calendar days of identifying the limitation. | The Generator Owner documented the known non-protection system equipment limitation that prevented it from meeting the criteria in Requirement R1 or R2 and communicated the documented limitation to its Planning Coordinator and Transmission Planner more than 90 calendar days but less than or equal to 120 calendar days of identifying the limitation. | The Generator Owner failed to document any known non-protection system equipment limitation that prevented it from meeting the criteria in Requirement R1 or R2. OR The Generator Owner failed to communicate the documented limitation to its Planning Coordinator and Transmission Planner within 120 calendar days of identifying the limitation. | [5 empty] | GO
Mandatory Subject to Enforcement | PRC | PRC-024-2 | R4. | Each Generator Owner shall provide its applicable generator protection trip settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated unit within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested trip settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of relay setting changes is not required. | 2016-07-01 |  | Low | The Generator Owner provided its generator protection trip settings more than 60 calendar days but less than or equal to 90 calendar days of any change to those trip settings. OR The Generator Owner provided trip settings more than 60 calendar days but less than or equal to 90 calendar days of a written request. | The Generator Owner provided its generator protection trip settings more than 90 calendar days but less than or equal to 120 calendar days of any change to those trip settings. OR The Generator Owner provided trip settings more than 90 calendar days but less than or equal to 120 calendar days of a written request. | The Generator Owner provided its generator protection trip settings more than 120 calendar days but less than or equal to 150 calendar days of any change to those trip settings. OR The Generator Owner provided trip settings more than 120 calendar days but less than or equal to 150 calendar days of a written request. | The Generator Owner failed to provide its generator protection trip settings within 150 calendar days of any change to those trip settings. OR The Generator Owner failed to provide trip settings within 150 calendar days of a written request. | [5 empty] | GO
Mandatory Subject to Enforcement | PRC | PRC-024-3 | R1. | Each Generator Owner shall set its applicable frequency protection in accordance with PRC-024 Attachment 1 such that the applicable protection does not cause the generating resource to trip or cease injecting current within the “no trip zone” during a frequency excursion with the following exceptions: • Applicable frequency protection may be set to trip or cease injecting current within a portion of the “no trip zone” for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | 2022-10-01 |  | Medium | N/A | N/A | N/A | The Generator Owner failed to set its applicable frequency protection so that it does not trip or cease injecting current according to Requirement R1. | [5 empty] | GO
Mandatory Subject to Enforcement | PRC | PRC-024-3 | R2. | Each Generator Owner shall set its applicable voltage protection5 in accordance with PRC-024 Attachment 2, such that the applicable protection does not cause the generating resource to trip or cease injecting current within the “no trip zone” during a voltage excursion at the high side of the GSU or MPT, subject to the following exceptions: • If the Transmission Planner allows less stringent voltage protection settings than those required to meet PRC-024 Attachment 2, then the Generator Owner may set its protection within the voltage recovery characteristics of a location-specific Transmission Planner’s study. • Applicable voltage protection may be set to trip or cease injecting current during a voltage excursion within a portion of the “no trip zone” for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | 2022-10-01 |  | Medium | N/A | N/A | N/A | The Generator Owner failed to set its applicable voltage protection so that it does not trip or cease injecting current according to Requirement R2. | [5 empty] | GO
Mandatory Subject to Enforcement | PRC | PRC-024-3 | R3. | Each Generator Owner shall document each known regulatory or equipment limitation that prevents an applicable generating resource(s) with frequency or voltage protection from meeting the protection setting criteria in Requirements R1 or R2, including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. | 2022-10-01 |  | Low | The Generator Owner documented the known non-protection system equipment limitation that prevented it from meeting the criteria in Requirement R1 or R2 and communicated the documented limitation to its Planning Coordinator and Transmission Planner more than 30 calendar days but less than or equal to 60 calendar days of identifying the limitation. | The Generator Owner documented the known non-protection system equipment limitation that prevented it from meeting the criteria in Requirement R1 or R2 and communicated the documented limitation to its Planning Coordinator and Transmission Planner more than 60 calendar days but less than or equal to 90 calendar days of identifying the limitation. | The Generator Owner documented the known non-protection system equipment limitation that prevented it from meeting the criteria in Requirement R1 or R2 and communicated the documented limitation to its Planning Coordinator and Transmission Planner more than 90 calendar days but less than or equal to 120 calendar days of identifying the limitation. | The Generator Owner failed to document any known non-protection system equipment limitation that prevented it from meeting the criteria in Requirement R1 or R2. OR The Generator Owner failed to document any known non-protection system equipment limitation that prevented it from meeting the criteria in Requirement R1 or R2. | [5 empty] | GO
Mandatory Subject to Enforcement | PRC | PRC-024-3 | R4. | Each Generator Owner shall provide its applicable protection settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated generating resource(s) within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of protection setting changes is not required. | 2020-07-09 |  | Low | The Generator Owner provided its protection settings more than 60 calendar days but less than or equal to 90 calendar days of any change to those settings. OR The Generator Owner provided protection settings more than 60 calendar days but less than or equal to 90 calendar days of a written request. | The Generator Owner provided its protection settings more than 90 calendar days but less than or equal to 120 calendar days of any change to those settings. OR The Generator Owner provided protection settings more than 90 calendar days but less than or equal to 120 calendar days of a written request. | The Generator Owner provided its protection settings more than 120 calendar days but less than or equal to 150 calendar days of any change to those settings. OR The Generator Owner provided protection settings more than 120 calendar days but less than or equal to 150 calendar days of a written request. | The Generator Owner failed to provide its protection settings within 150 calendar days of any change to those settings. OR The Generator Owner failed to provide protection settings within 150 calendar days of a written request. | [5 empty] | GO
Filed and Pending Regulatory Approval | PRC | PRC-024-3 | D.A.2. | Each Generator Owner and Transmission Owner shall set its applicable voltage protection5 in accordance with PRC-024 Attachment 2a, such that the applicable protection does not cause the generating resource to trip or cease injecting current during a voltage excursion within the “no trip zone” at the high side of the GSU or MPT, subject to the following exceptions: • For newly designated strategic power plants, applicable protections must comply with the high voltage durations for such plants within 48 calendar months of the notification made pursuant to Requirement D.A.5. During this transition period, voltage protections must at least comply with the high voltage durations for “all power plants”. • The generating resource(s) are permitted to be set to trip or to cease injecting current during a voltage excursion bounded by the “no trip zone” of PRC-024 Attachment 2a for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. • If the Transmission Planner allows less stringent voltage protection settings than those required to meet PRC-024 Attachment 2a, then the Generator Owner or Transmission Owner may set its protection within the voltage recovery characteristics of a location-specific Transmission Planner’s study. • Inverter-based resources voltage protection settings may be set to cease injecting current momentarily during a voltage excursion at the high side of the MPT, bounded by the “no trip zone” of PRC-024 Attachment 2a, under the following conditions: o After a minimum delay of 0.022 s, when the positive-sequence voltage exceeds 1.25 per unit (p.u.) Normal operation must resume once the voltage drops back below 1.25 p.u at the high side of the MPT. o After a minimum delay of 0.022 s, when the phase-to-ground root mean square (RMS) voltages exceeds 1.4 p.u., as measured at generator terminals, on one or multiple phases. Normal operation must resume once the positive-sequence voltage drops back below the 1.25 p.u. at the high side of the MPT. |  |  | Medium | N/A | N/A | N/A | The Generator Owner or Transmission Owner failed to set its applicable voltage protection so that it does not trip or cease injecting current in accordance with Requirement D.A.2. OR The Generator Owner or Transmission Owner set its applicable voltage protection in accordance with Requirement D.A.2 but, for strategic power plants, failed to do so within 48 months of notification. | [5 empty] | GO | [12 empty] | TO
Filed and Pending Regulatory Approval | PRC | PRC-024-3 | D.A.5. | Each Planning Coordinator shall designate, at least once every five calendar years, the strategic power plants that must comply with Attachment 2a and notify, within 30 calendar days of its designation, each Generator Owner or Transmission Owner that owns facilities in the strategic power plants. |  |  | Medium | N/A | The Planning Coordinator designated strategic power plants at least once every five calendar years but notified each Generator Owner or Transmission Owner that owns facilities in the strategic power plants between 31 days and 45 days after its designation. | The Planning Coordinator designated strategic power plants at least once every five calendar years but notified each Generator Owner or Transmission Owner that owns facilities in the strategic power plants between 46 days and 60 days after its designation. | The Planning Coordinator failed to designate, at least once every five years, the strategic power plants that must comply with Attachment 2a. OR The Planning Coordinator failed to notify, each Generator Owner or Transmission Owner that owns facilities in the strategic power plants or notified them more than 60 days after the its designation. | [10 empty] | PCPA
Inactive | PRC | PRC-025-1 | R1. | Each Generator Owner, Transmission Owner, and Distribution Provider shall apply settings that are in accordance with PRC-025-1 – Attachment 1: Relay Settings, on each load-responsive protective relay while maintaining reliable fault protection. | 2014-10-01 | 2018-06-30 | High | N/A | N/A | N/A | The Generator Owner, Transmission Owner, and Distribution Provider did not apply settings in accordance with PRC-025-1 – Attachment 1: Relay Settings, on an applied load-responsive protective relay. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-025-2 | R1. | Each Generator Owner, Transmission Owner, and Distribution Provider shall apply settings that are in accordance with PRC-025-2 – Attachment 1: Relay Settings, on each load-responsive protective relay while maintaining reliable fault protection. | 2018-07-01 |  | High | N/A | N/A | N/A | The Generator Owner, Transmission Owner, and Distribution Provider did not apply settings in accordance with PRC-025-2 – Attachment 1: Relay Settings, on an applied load-responsive protective relay. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-026-1 | R1. | Each Planning Coordinator shall, at least once each calendar year, provide notification of each generator, transformer, and transmission line BES Element in its area that meets one or more of the following criteria, if any, to the respective Generator Owner and Transmission Owner: Criteria: 1. Generator(s) where an angular stability constraint exists that is addressed by a System Operating Limit (SOL) or a Remedial Action Scheme (RAS) and those Elements terminating at the Transmission station associated with the generator(s). 2. An Element that is monitored as part of an SOL identified by the Planning Coordinator’s methodology based on an angular stability constraint. 3. An Element that forms the boundary of an island in the most recent underfrequency load shedding (UFLS) design assessment based on application of the Planning Coordinator’s criteria for identifying islands, only if the island is formed by tripping the Element due to angular instability. 4. An Element identified in the most recent annual Planning Assessment where relay tripping occurs due to a stable or unstable power swing during a simulated disturbance. (Footnote: NERC Reliability Standard FAC-014-2 – Establish and Communicate System Operating Limits, Requirement R3. An example of an unstable power swing is provided in the Guidelines and Technical Basis section, “Justification for Including Unstable Power Swings in the Requirements section of the Guidelines and Technical Basis.”) | 2018-01-01 | 2024-03-31 | Medium | The Planning Coordinator provided notification of the BES Element(s) in accordance with Requirement R1, but was less than or equal to 30 calendar days late. | The Planning Coordinator provided notification of the BES Element(s) in accordance with Requirement R1, but was more than 30 calendar days and less than or equal to 60 calendar days late. | The Planning Coordinator provided notification of the BES Element(s) in accordance with Requirement R1, but was more than 60 calendar days and less than or equal to 90 calendar days late. | The Planning Coordinator provided notification of the BES Element(s) in accordance with Requirement R1, but was more than 90 calendar days late. OR The Planning Coordinator failed to provide notification of the BES Element(s) in accordance with Requirement R1. | [5 empty] | GO |  |  |  |  | PCPA | [7 empty] | TO
Inactive | PRC | PRC-026-1 | R2. | Each Generator Owner and Transmission Owner shall: | 2020-01-01 | 2024-03-31 | High | The Generator Owner or Transmission Owner evaluated its load-responsive protective relay(s) in accordance with Requirement R2, but was less than or equal to 30 calendar days late. | The Generator Owner or Transmission Owner evaluated its load-responsive protective relay(s) in accordance with Requirement R2, but was more than 30 calendar days and less than or equal to 60 calendar days late. | The Generator Owner or Transmission Owner evaluated its load-responsive protective relay(s) in accordance with Requirement R2, but was more than 60 calendar days and less than or equal to 90 calendar days late. | The Generator Owner or Transmission Owner evaluated its load-responsive protective relay(s) in accordance with Requirement R2, but was more than 90 calendar days late. OR The Generator Owner or Transmission Owner failed to evaluate its load-responsive protective relay(s) in accordance with Requirement R2. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-026-1 | R3. | Each Generator Owner and Transmission Owner shall, within six full calendar months of determining a load-responsive protective relay does not meet the PRC-026-1 – Attachment B criteria pursuant to Requirement R2, develop a Corrective Action Plan (CAP) to meet one of the following: • The Protection System meets the PRC-026-1 – Attachment B criteria, while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element); or • The Protection System is excluded under the PRC-026-1 – Attachment A criteria (e.g., modifying the Protection System so that relay functions are supervised by power swing blocking or using relay systems that are immune to power swings), while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element). | 2020-01-01 | 2024-03-31 | Medium | The Generator Owner or Transmission Owner developed a Corrective Action Plan (CAP) in accordance with Requirement R3, but in more than six calendar months and less than or equal to seven calendar months. | The Generator Owner or Transmission Owner developed a Corrective Action Plan (CAP) in accordance with Requirement R3, but in more than seven calendar months and less than or equal to eight calendar months. | The Generator Owner or Transmission Owner developed a Corrective Action Plan (CAP) in accordance with Requirement R3, but in more than eight calendar months and less than or equal to nine calendar months. | The Generator Owner or Transmission Owner developed a Corrective Action Plan (CAP) in accordance with Requirement R3, but in more than nine calendar months. OR The Generator Owner or Transmission Owner failed to develop a CAP in accordance with Requirement R3. | [5 empty] | GO | [12 empty] | TO
Inactive | PRC | PRC-026-1 | R4. | Each Generator Owner and Transmission Owner shall implement each CAP developed pursuant to Requirement R3 and update each CAP if actions or timetables change until all actions are complete. | 2020-01-01 | 2024-03-31 | Medium | The Generator Owner or Transmission Owner implemented a Corrective Action Plan (CAP), but failed to update a CAP when actions or timetables changed, in accordance with Requirement R4. | N/A | N/A | The Generator Owner or Transmission Owner failed to implement a Corrective Action Plan (CAP) in accordance with Requirement R4. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-026-2 | R1. | Each Planning Coordinator shall, at least once each calendar year, provide notification of each generator, transformer, and transmission line BES Element in its area that meets one or more of the following criteria, if any, to the respective Generator Owner and Transmission Owner: Criteria: 1. Generator(s) where an angular stability constraint, identified in Planning Assessments of the Near-Term Transmission Planning Horizon for a planning event, that is addressed by limiting the output of a generator or a Remedial Action Scheme (RAS), and those Elements terminating at the Transmission station associated with the generator(s). 2. Elements associated with angular instability identified in Planning Assessments of the Near-Term Transmission Planning Horizon for a planning event.. 3. An Element that forms the boundary of an island in the most recent underfrequency load shedding (UFLS) design assessment based on application of the Planning Coordinator’s criteria for identifying islands, only if the island is formed by tripping the Element due to angular instability. 4. An Element identified in the most recent annual Planning Assessment of the Near-Term Transmission Planning Horizon where relay tripping occurs due to a stable or unstable1 power swing during a simulated disturbance for a planning event. | 2024-04-01 |  | Medium | The Planning Coordinator provided notification of the BES Element(s) in accordance with Requirement R1, but was less than or equal to 30 calendar days late. | The Planning Coordinator provided notification of the BES Element(s) in accordance with Requirement R1, but was more than 30 calendar days and less than or equal to 60 calendar days late. | The Planning Coordinator provided notification of the BES Element(s) in accordance with Requirement R1, but was more than 60 calendar days and less than or equal to 90 calendar days late. | The Planning Coordinator provided notification of the BES Element(s) in accordance with Requirement R1, but was more than 90 calendar days late. OR The Planning Coordinator failed to provide notification of the BES Element(s) in accordance with Requirement R1. | [5 empty] | GO |  |  |  |  | PCPA | [7 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-026-2 | R2. | Each Generator Owner and Transmission Owner shall: | 2024-04-01 |  | High | The Generator Owner or Transmission Owner evaluated its load-responsive protective relay(s) in accordance with Requirement R2, but was less than or equal to 30 calendar days late. | The Generator Owner or Transmission Owner evaluated its load-responsive protective relay(s) in accordance with Requirement R2, but was more than 30 calendar days and less than or equal to 60 calendar days late. | The Generator Owner or Transmission Owner evaluated its load-responsive protective relay(s) in accordance with Requirement R2, but was more than 60 calendar days and less than or equal to 90 calendar days late. | The Generator Owner or Transmission Owner evaluated its load-responsive protective relay(s) in accordance with Requirement R2, but was more than 90 calendar days late. OR The Generator Owner or Transmission Owner failed to evaluate its load- responsive protective relay(s) in accordance with Requirement R2. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-026-2 | R3. | Each Generator Owner and Transmission Owner shall, within six full calendar months of determining a load-responsive protective relay does not meet the PRC-026-2 – Attachment B criteria pursuant to Requirement R2, develop a Corrective Action Plan (CAP) to meet one of the following: · The Protection System meets the PRC-026-2 – Attachment B criteria, while maintaining dependable fault detection and dependable out-of-step tripping (if out- of-step tripping is applied at the terminal of the BES Element); or · The Protection System is excluded under the PRC-026-2 – Attachment A criteria (e.g., modifying the Protection System so that relay functions are supervised by power swing blocking or using relay systems that are immune to power swings), while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element). | 2024-04-01 |  | Medium | The Generator Owner or Transmission Owner developed a Corrective Action Plan (CAP) in accordance with Requirement R3, but in more than six calendar months and less than or equal to seven calendar months. | The Generator Owner or Transmission Owner developed a Corrective Action Plan (CAP) in accordance with Requirement R3, but in more than seven calendar months and less than or equal to eight calendar months. | The Generator Owner or Transmission Owner developed a Corrective Action Plan (CAP) in accordance with Requirement R3, but in more than eight calendar months and less than or equal to nine calendar months. | The Generator Owner or Transmission Owner developed a Corrective Action Plan (CAP) in accordance with Requirement R3, but in more than nine calendar months. OR The Generator Owner or Transmission Owner failed to develop a CAP in accordance with Requirement R3. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-026-2 | R4. | Each Generator Owner and Transmission Owner shall implement each CAP developed pursuant to Requirement R3 and update each CAP if actions or timetables change until all actions are complete. | 2024-04-01 |  | Medium | The Generator Owner or Transmission Owner implemented a Corrective Action Plan (CAP), but failed to update a CAP when actions or timetables changed, in accordance with Requirement R4. | N/A | N/A | The Generator Owner or Transmission Owner failed to implement a Corrective Action Plan (CAP) in accordance with Requirement R4. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-027-1 | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a process for developing new and revised Protection System settings for BES Elements, such that the Protection Systems operate in the intended sequence during Faults. The process shall include: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | 2021-04-01 |  | Medium | N/A | The responsible entity established a process in accordance with Requirement R1, but failed to include Requirement R1, Part 1.1 or Part 1.2. | The responsible entity established a process in accordance with Requirement R1, but failed to include Requirement R1, Part 1.1 and Part 1.2. | The responsible entity established a process in accordance with Requirement R1, but failed to include Requirement R1, Part 1.3. OR The responsible entity failed to establish any process in accordance with Requirement R1 |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-027-1 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall, for each BES Element with Protection System functions identified in Attachment A: • Option 1: Perform a Protection System Coordination Study in a time interval not to exceed six-calendar years; or • Option 2: Compare present Fault current values to an established Fault current baseline and perform a Protection System Coordination Study when the comparison identifies a 15 percent or greater deviation in Fault current values (either three phase or phase to ground) at a bus to which the BES Element is connected, all in a time interval not to exceed six-calendar years; or, • Option 3: Use a combination of the above. | 2021-04-01 |  | Medium | The responsible entity performed a Protection System Coordination Study for each BES Element, in accordance with Requirement R2, Option 1, Option 2, or Option 3 but was late by less than or equal to 30 calendar days. | The responsible entity performed a Protection System Coordination Study for each BES Element, in accordance with Requirement R2, Option 1, Option 2, or Option 3, but was late by more than 30 calendar days but less than or equal to 60 calendar days. | The responsible entity performed a Protection System Coordination Study for each BES Element, in accordance with Requirement R2, Option 1, Option 2, or Option 3, but was late by more than 60 calendar days but less than or equal to 90 calendar days. | The responsible entity performed a Protection System Coordination Study for each BES Element, in accordance with Requirement R2, Option 1, Option 2, or Option 3, but was late by more than 90 calendar days. OR The responsible entity failed to perform Option 2, or Option 3, in accordance with Requirement R2. |  |  | DP |  |  | GO | [12 empty] | TO
Mandatory Subject to Enforcement | PRC | PRC-027-1 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider shall utilize its process established in Requirement R1 to develop new and revised Protection System settings for BES Elements. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | 2021-04-01 |  | Medium | N/A | N/A | N/A | The responsible entity failed to utilize the process established in accordance with Requirement R1. |  |  | DP |  |  | GO | [12 empty] | TO
Inactive | PRC | PRC-STD-001-1 | WR1. | Each Transmission Operator or Transmission Owner identified in Section 4.1 must submit documentation that an officer of the organization certifies that: a. All protective relay applications are appropriate for the Bulk Power Transmission Paths (“BPTP”) identified in Attachment A – Table 2 of this Standard pursuant to applicable WECC Standards and NERC Standards; b. The BPTP protective relay settings and logic are appropriate pursuant to applicable WECC Standards and NERC Standards; c. Since the last certification or for the last three years all network changes in the path, at the terminals of the path, or in nearby facilities that affect operation of the path have been considered in the protective relay application and settings; d. All relay operations since the last certification or during the last three-year period have been analyzed for correctness and appropriate corrective action taken pursuant to applicable WECC Standards and NERC Standards; e. Up-to-date relay information has been provided to the on-shift operating personnel and the appropriate Reliability Coordinator. Note: If a path operator cannot submit certification on behalf of the multiple owners of a path for Protective Relay Application and Settings because the authority for certification resides with one or more path owners, then the path owner(s) shall submit the certification. The path operator shall notify the path owner(s) and WECC in writing that the path owner(s) is (are) to submit the certification. (Source: WECC Criterion) | 2007-06-18 | 2011-09-30 | [23 empty] | TO | TOP
Inactive | PRC | PRC-STD-003-1 | WR1. | Owners of protective relays and Remedial Action Schemes (RAS) applied to path elements of selected WECC major transmission path facilities (listed in Attachment A - Table 2) and RAS (listed in Attachment B - Table 3) must take the following action for each known or probable relay misoperation: a. If functionally equivalent protective relaying or RAS remains in service to ensure bulk transmission system reliability; the relay or RAS that misoperated is to be removed from service for repair or modification within 22 hours of the relay or RAS misoperation. The relay or RAS shall be replaced, repaired, or modified such that the incorrect operation will not be repeated. b. If functionally equivalent protective relaying or RAS does not remain in service that will ensure bulk transmission system reliability, and the relay or RAS that misoperated cannot be repaired and placed back in service within 22 hours, the associated transmission path facility must be removed from service. The remaining path facilities, if any, must be de-rated to a reliable operating level. c. If the relay or RAS misoperates and there is some protection but not entirely functionally equivalent, the relay or RAS must be repaired or removed from service within 22 hours. The associated transmission may remain in service; however, system operation must fully comply with WECC and NERC operating standards. This may require an adjustment of operating levels. d. Protective relays or RAS removed from service must be repaired or replaced with functionally equivalent protective relays or RAS within 20 Business Days of removal, or the system shall be operated at levels that meet WECC Standards and NERC Standards or the associated transmission path elements shall be removed from service. It is not intended that the above requirements apply to system protection and/or RAS actions that appear to be entirely reasonable and correct at the time of occurrence and associated system performance is fully compliant with WECC and NERC standards, and the protective relaying or RAS operation is later found to be incorrect. In such cases, upon determination of the incorrect operation, the requirements of (a) through (d) above will become applicable at the time the incorrect operation is identified. (Source: WECC Criterion) | 2007-06-18 | 2011-09-30 | [23 empty] | TO | TOP
Inactive | PRC | PRC-STD-005-1 | WR1. | All bulk power transmission elements (i.e. lines, stations and rights of way) included as part of the transmission facilities (or required to maintain transfer capability) impacting each of the transmission paths listed in Attachment A - WECC Table 2 shall be inspected and maintained in accordance with this criterion, taking into consideration diverse environmental and climatic conditions, terrain, equipment, maintenance philosophies, and design practices. a. General This Transmission Maintenance Standard requires each Responsible Entity identified in Section A.4.1 to develop and implement a Transmission Maintenance and Inspection Plan (TMIP) detailing the Responsible Entity’s inspection and maintenance activities applicable to the transmission facilities comprising each of the transmission paths identified in Attachment A – Table 2. b. Standard Requirements (i) TMIP To comply with this Standard, each Responsible Entity identified in Section A4.1 must develop and implement a TMIP. • Because maintenance and inspection practices vary, it is the intent of this Transmission Maintenance Standard to allow flexibility in inspection and maintenance practices while still requiring a description of certain specific inspection and maintenance practices. (a) TMIP Contents The TMIP may be performance-based, time-based, conditional¬based, or a combination of all three as may be appropriate. The TMIP shall: · Identify the facilities for which it is covering by listing the names of each transmission path and the quantities of each equipment component, such as; circuit breaker, relay scheme, transmission line; · Include the scheduled interval (e.g., every two years) for any time-based maintenance activities and a description of conditions that will initiate any condition or performance-based activities; · Describe the maintenance, testing and inspection methods for each activity or component listed under Transmission Line Maintenance and Station Maintenance; · Provide any checklists or forms, or reports used for maintenance activities; · Provide criteria to be used to assess the condition of a transmission facility or component; · Specify condition assessment criteria and the requisite response to each condition as may be appropriate for each specific type of component or feature of the transmission facilities; · Include specific details regarding Transmission Line and Station Maintenance practices as per subsections (1) and (2) below. (1) Transmission Line Maintenance Details The TMIP shall, at a minimum, describe the Responsible Entity’s practices for the following transmission line maintenance activities: · Patrol/Inspection; · Contamination Control (Insulator Washing) (2) Station Maintenance Details The TMIP shall describe the Responsible Entity’s maintenance practices for the following station equipment: · Circuit Breakers · Power Transformers (including phase-shifting transformers) · Regulators · Protective Relay Systems and associated Communication Equipment · RAS Systems and associated Communication Equipment · Reactive Devices (including, but not limited to, Shunt Capacitors, Series Capacitors, Synchronous Condensers, Shunt Reactors, and Tertiary Reactors) Maintenance Record Keeping M1. Each Responsible Entity identified in Section A.4.1 must retain all pertinent maintenance and inspection records that support the TMIP according to the following guidelines: · The Responsible Entity shall maintain records of all maintenance and inspection activities for at least five years. · Each Responsible Entity’s maintenance and inspection records shall identify, at a minimum: o The person(s) responsible for performing the work or inspection; o The date(s) the work or inspection was performed; o The transmission facility on which the work was performed, and o A description of the inspection or maintenance performed. The Transmission Owner or Operator shall maintain (and make available on request) records for maintenance or inspection pertaining to the items listed in subsections (a) and (b) below. (a) Transmission Line Maintenance Records · Patrol/Inspection · Contamination Control (Insulator Washing) (b) Station Maintenance Records · Circuit Breakers · Power Transformers · Regulators · Protective Relay Systems and associated Communication Equipment · RAS Systems and associated Communication Equipment · Reactive Devices c. Compliance Measures This section defines the items that will be reviewed by WECC Staff to monitor and measure each Responsible Entity’s compliance with this Standard, and the compliance levels that will be assessed in the review process. (i) TMIP Certification Each Responsible Entity identified in Section A.4.1 shall annually certify to WECC Staff that it has developed, documented, and implemented a TMIP. (ii) WECC Staff Review WECC Staff will assess performance in the three broad areas described in Paragraph 8 of the Certification Form. These areas are: (1) Development and documentation of the TMIP; (2) Performing maintenance in accordance with the TMIP; (3) Maintaining maintenance records as required by this Standard. (iii) Review Triggers The WECC Staff will conduct a review of the Responsible Entity’s TMIP, maintenance and inspection practices and maintenance records when triggered as described below. (a) Disturbance Report. If a WECC Disturbance Report identifies that transmission maintenance and inspection activities were a substantial contributing factor in the disturbance, WECC Staff may request a review of the Responsible Entity. (b) Recommendation by CMWG team. If in its tri-annual review, the CMWG review team notes areas in transmission availability or maintenance that warrant further review, they may recommend a review by the WECC Staff. (c) Incomplete Annual Certification. If the Responsible Entity identified in Section A.4.1 fails to certify one or more categories of paragraph 8 of the Certification Plan, WECC Staff may request a review of the Responsible Entity. (d) Random Audit. The WECC Staff shall randomly select two or three Responsible Entities each year for review. When a review is requested, the Responsible Entity shall make its TMIP and all maintenance records for the facilities that are part of RMS available to the WECC Staff for review within 30 calendar days from the request date. | 2007-06-18 | 2011-06-30 | [23 empty] | TO | TOP
Inactive | TOP | TOP-001-0 | R1. | Each Transmission Operator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its area and shall exercise specific authority to alleviate operating emergencies. |  | 2007-01-01 | [24 empty] | TOP
Inactive | TOP | TOP-001-0 | R2. | Each Transmission Operator shall take immediate actions to alleviate operating emergencies including curtailing transmission service or energy schedules, operating equipment (e.g., generators, phase shifters, breakers), shedding firm load, etc. |  | 2007-01-01 | [24 empty] | TOP
Inactive | TOP | TOP-001-0 | R3. | Each Transmission Operator, Balancing Authority, and Generator Operator shall comply with reliability directives issued by the Reliability Coordinator, and each Balancing Authority and Generator Operator shall comply with reliability directives issued by the Transmission Operator, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances the Transmission Operator, Balancing Authority or Generator Operator shall immediately inform the Reliability Coordinator or Transmission Operator of the inability to perform the directive so that the Reliability Coordinator or Transmission Operator can implement alternate remedial actions. |  | 2007-01-01 | [6 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-0 | R4. | Each Distribution Provider and Load Serving Entity shall comply with all reliability directives issued by the Transmission Operator, including shedding firm load, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances, the Distribution Provider or Load Serving Entity shall immediately inform the Transmission Operator of the inability to perform the directive so that the Transmission Operator can implement alternate remedial actions. |  | 2007-01-01 | [7 empty] | DP | [5 empty] | LSE
Inactive | TOP | TOP-001-0 | R5. | Each Transmission Operator shall inform its Reliability Coordinator and any other potentially affected Transmission Operators of real time or anticipated emergency conditions, and take actions to avoid, when possible, or mitigate the emergency. |  | 2007-01-01 | [24 empty] | TOP
Inactive | TOP | TOP-001-0 | R6. | Each Transmission Operator, Balancing Authority, and Generator Operator shall render all available emergency assistance to others as requested, provided that the requesting entity has implemented its comparable emergency procedures, unless such actions would violate safety, equipment, or regulatory or statutory requirements. |  | 2007-01-01 | [6 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-0 | R7. | Each Transmission Operator and Generator Operator shall not remove Bulk Electric System facilities from service if removing those facilities would burden neighboring systems unless: |  | 2007-01-01 | [24 empty] | TOP
Inactive | TOP | TOP-001-0 | R8. | During a system emergency, the Balancing Authority and Transmission Operator shall immediately take action to restore the Real and Reactive Power Balance. If the Balancing Authority or Transmission Operator is unable to restore Real and Reactive Power Balance it shall request emergency assistance from the Reliability Coordinator. If corrective action or emergency assistance is not adequate to mitigate the Real and Reactive Power Balance, then the Reliability Coordinator, Balancing Authority, and Transmission Operator shall implement firm load shedding. |  | 2007-01-01 | [24 empty] | TOP
Inactive | TOP | TOP-001-1 | R1. | Each Transmission Operator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its area and shall exercise specific authority to alleviate operating emergencies. | 2007-06-18 | 2011-11-20 | High | [23 empty] | TOP
Inactive | TOP | TOP-001-1 | R2. | Each Transmission Operator shall take immediate actions to alleviate operating emergencies including curtailing transmission service or energy schedules, operating equipment (e.g., generators, phase shifters, breakers), shedding firm load, etc. | 2007-06-18 | 2011-11-20 | High | [23 empty] | TOP
Inactive | TOP | TOP-001-1 | R3. | Each Transmission Operator, Balancing Authority, and Generator Operator shall comply with reliability directives issued by the Reliability Coordinator, and each Balancing Authority and Generator Operator shall comply with reliability directives issued by the Transmission Operator, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances the Transmission Operator, Balancing Authority, or Generator Operator shall immediately inform the Reliability Coordinator or Transmission Operator of the inability to perform the directive so that the Reliability Coordinator or Transmission Operator can implement alternate remedial actions. | 2007-06-18 | 2011-11-20 | High | [5 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-1 | R4. | Each Distribution Provider and Load-Serving Entity shall comply with all reliability directives issued by the Transmission Operator, including shedding firm load, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances, the Distribution Provider or Load-Serving Entity shall immediately inform the Transmission Operator of the inability to perform the directive so that the Transmission Operator can implement alternate remedial actions. | 2007-06-18 | 2011-11-20 | High | [6 empty] | DP | [5 empty] | LSE
Inactive | TOP | TOP-001-1 | R5. | Each Transmission Operator shall inform its Reliability Coordinator and any other potentially affected Transmission Operators of real-time or anticipated emergency conditions, and take actions to avoid, when possible, or mitigate the emergency. | 2007-06-18 | 2011-11-20 | High | [23 empty] | TOP
Inactive | TOP | TOP-001-1 | R6. | Each Transmission Operator, Balancing Authority, and Generator Operator shall render all available emergency assistance to others as requested, provided that the requesting entity has implemented its comparable emergency procedures, unless such actions would violate safety, equipment, or regulatory or statutory requirements. | 2007-06-18 | 2011-11-20 | High | [5 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-1 | R7. | Each Transmission Operator and Generator Operator shall not remove Bulk Electric System facilities from service if removing those facilities would burden neighboring systems unless: | 2007-06-18 | 2011-11-20 | High | [10 empty] | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-1 | R8. | During a system emergency, the Balancing Authority and Transmission Operator shall immediately take action to restore the Real and Reactive Power Balance. If the Balancing Authority or Transmission Operator is unable to restore Real and Reactive Power Balance it shall request emergency assistance from the Reliability Coordinator. If corrective action or emergency assistance is not adequate to mitigate the Real and Reactive Power Balance, then the Reliability Coordinator, Balancing Authority, and Transmission Operator shall implement firm load shedding. | 2007-06-18 | 2011-11-20 | High | [5 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-001-1a | R1. | Each Transmission Operator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its area and shall exercise specific authority to alleviate operating emergencies. | 2011-11-21 | 2017-03-31 | High | [23 empty] | TOP
Inactive | TOP | TOP-001-1a | R2. | Each Transmission Operator shall take immediate actions to alleviate operating emergencies including curtailing transmission service or energy schedules, operating equipment (e.g., generators, phase shifters, breakers), shedding firm load, etc. | 2011-11-21 | 2017-03-31 | High | [23 empty] | TOP
Inactive | TOP | TOP-001-1a | R3. | Each Transmission Operator, Balancing Authority, and Generator Operator shall comply with reliability directives issued by the Reliability Coordinator, and each Balancing Authority and Generator Operator shall comply with reliability directives issued by the Transmission Operator, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances the Transmission Operator, Balancing Authority, or Generator Operator shall immediately inform the Reliability Coordinator or Transmission Operator of the inability to perform the directive so that the Reliability Coordinator or Transmission Operator can implement alternate remedial actions. | 2011-11-21 | 2017-03-31 | High | [5 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-1a | R4. | Each Distribution Provider and Load-Serving Entity shall comply with all reliability directives issued by the Transmission Operator, including shedding firm load, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances, the Distribution Provider or Load-Serving Entity shall immediately inform the Transmission Operator of the inability to perform the directive so that the Transmission Operator can implement alternate remedial actions. | 2011-11-21 | 2017-03-31 | High | [6 empty] | DP | [5 empty] | LSE
Inactive | TOP | TOP-001-1a | R5. | Each Transmission Operator shall inform its Reliability Coordinator and any other potentially affected Transmission Operators of real-time or anticipated emergency conditions, and take actions to avoid, when possible, or mitigate the emergency. | 2011-11-21 | 2017-03-31 | High | [23 empty] | TOP
Inactive | TOP | TOP-001-1a | R6. | Each Transmission Operator, Balancing Authority, and Generator Operator shall render all available emergency assistance to others as requested, provided that the requesting entity has implemented its comparable emergency procedures, unless such actions would violate safety, equipment, or regulatory or statutory requirements. | 2011-11-21 | 2017-03-31 | High | [5 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-1a | R7. | Each Transmission Operator and Generator Operator shall not remove Bulk Electric System facilities from service if removing those facilities would burden neighboring systems unless: | 2011-11-21 | 2017-03-31 | High | [10 empty] | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-1a | R8. | During a system emergency, the Balancing Authority and Transmission Operator shall immediately take action to restore the Real and Reactive Power Balance. If the Balancing Authority or Transmission Operator is unable to restore Real and Reactive Power Balance it shall request emergency assistance from the Reliability Coordinator. If corrective action or emergency assistance is not adequate to mitigate the Real and Reactive Power Balance, then the Reliability Coordinator, Balancing Authority, and Transmission Operator shall implement firm load shedding. | 2011-11-21 | 2017-03-31 | High | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-001-2 | R1. | Each Balancing Authority, Generator Operator, Distribution Provider, and Load-Serving Entity shall comply with each Reliability Directive issued and identified as such by its Transmission Operator(s), unless such action would violate safety, equipment, regulatory, or statutory requirements. |  | 2016-01-26 | High | N/A | N/A | N/A | The responsible entity did not comply with an identified Reliability Directive issued by the Transmission Operator, and such action would not have violated safety, equipment, regulatory, or statutory requirements. |  | BA | DP |  |  |  | GOP |  | LSE
Inactive | TOP | TOP-001-2 | R2. | Each Balancing Authority, Generator Operator, Distribution Provider, and Load-Serving Entity shall inform its Transmission Operator of its inability to perform an identified Reliability Directive issued by that Transmission Operator. |  | 2016-01-26 | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to perform an identified Reliability Directive issued by that Transmission Operator. |  | BA | DP |  |  |  | GOP |  | LSE
Inactive | TOP | TOP-001-2 | R3. | Each Transmission Operator shall inform its Reliability Coordinator and Transmission Operator(s) that are known or expected to be affected by each actual and anticipated Emergency based on its assessment of its Operational Planning Analysis. |  | 2016-01-26 | High | The Transmission Operator did not inform one other Transmission Operator, or 5% or less of the affected Transmission Operators, whichever is less, that are known or expected to be affected by an actual or anticipated Emergency based on its assessment of its Operational Planning Analysis. | The Transmission Operator did not inform two other Transmission Operators, or more than 5% and less than or equal to 10% of the affected Transmission Operators, whichever is less, that are known or expected to be affected by an actual or anticipated Emergency based on its assessment of its Operational Planning Analysis. | The Transmission Operator did not inform three other Transmission Operators, or more than 10% and less than or equal to 15% of the affected Transmission Operators, whichever is less, that are known or expected to be affected by an actual or anticipated Emergency based on its assessment of its Operational Planning Analysis. | The Transmission Operator did not inform its Reliability Coordinator of an actual Emergency or an anticipated Emergency condition based on its assessment of its Operational Planning Analysis. OR The Transmission Operator did not inform four or more other Transmission Operators, or more than 15% of the affected Transmission Operators, whichever is less, that are known or expected to be affected by an actual or anticipated Emergency based on its assessment of its Operational Planning Analysis. | [19 empty] | TOP
Inactive | TOP | TOP-001-2 | R4. | Each Transmission Operator shall render emergency assistance to other Transmission Operators, as requested and available, provided that the requesting entity has implemented its comparable emergency procedures, unless such actions would violate safety, equipment, regulatory, or statutory requirements. |  | 2016-01-26 | High | N/A | N/A | N/A | The Transmission Operator did not render emergency assistance to other Transmission Operators, as requested and available, when the requesting entity had implemented its comparable emergency procedures, and such actions would not have violated safety, equipment, regulatory, or statutory requirements. | [19 empty] | TOP
Inactive | TOP | TOP-001-2 | R5. | Each Transmission Operator shall inform its Reliability Coordinator and other Transmission Operators of its operations known or expected to result in an Adverse Reliability Impact on those respective Transmission Operator Areas unless conditions do not permit such communications. Examples of such operations are relay or equipment failures, and changes in generation, Transmission, or Load. |  | 2016-01-26 | High | The Transmission Operator did not inform one other Transmission Operator, or 5% or less of the affected Transmission Operators, whichever is less, of its operations known or expected to result in an Adverse Reliability Impact on respective Transmission Operator Areas when conditions did permit such communications. | The Transmission Operator did not inform two other Transmission Operators, or more than 5% and less than or equal to 10% of the affected Transmission Operators, whichever is less, of its operations known or expected to result in an Adverse Reliability Impact on respective Transmission Operator Areas when conditions did permit such communications. | The Transmission Operator did not inform three other Transmission Operators, or more than 10% and less than or equal to 15% of the affected Transmission Operators, whichever is less, of its operations known or expected to result in an Adverse Reliability Impact on respective Transmission Operator Areas when conditions did permit such communications. | The Transmission Operator did not inform its Reliability Coordinator of its operations known or expected to result in an Adverse Reliability Impact on those respective Transmission Operator Areas when conditions did permit such communications. OR The Transmission Operator did not inform four or more other Transmission Operators, or more than 15% of the affected Transmission Operators, whichever is less, of its operations known or expected to result in an Adverse Reliability Impact on those respective Transmission Operator Areas when conditions did permit such communications. | [19 empty] | TOP
Inactive | TOP | TOP-001-2 | R6. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and negatively impacted interconnected NERC registered entities of planned outages of telemetering equipment, control equipment and associated communication channels between the affected entities. |  | 2016-01-26 | Medium | The responsible entity did not notify one negatively-impacted interconnected NERC-registered entity, or 5% or less of the negatively impacted NERC registered entities, whichever is less, of a planned outage of telemetering equipment, control equipment, and associated communication channels between the affected entities. | The responsible entity did not notify two negatively-impacted interconnected NERC-registered entities, or more than 5% and less than or equal to 10% of the negatively impacted NERC registered entities, whichever is less, of a planned outage of telemetering equipment, control equipment, and associated communication channels between the affected entities. | The responsible entity did not notify three negatively-impacted interconnected NERC-registered entities, or more than 10% and less than or equal to 15% of the negatively impacted NERC registered entities, whichever is less, of a planned outage of telemetering equipment, control equipment and associated communication channels between the affected entities | The responsible entity did not notify its Reliability Coordinator of a planned outage of telemetering equipment, control equipment, and associated communication channels. OR, The responsible entity did not notify four or more negatively-impacted interconnected NERC-registered entities, or more than 15% of the negatively impacted NERC registered entities, whichever is less, of a planned outage of telemetering and control equipment and associated communication channels between the affected entities. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-001-2 | R7. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. |  | 2016-01-26 | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | [19 empty] | TOP
Inactive | TOP | TOP-001-2 | R8. | Each Transmission Operator shall inform its Reliability Coordinator of each SOL which, while not an IROL, has been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area based on its assessment of its Operational Planning Analysis. |  | 2016-01-26 | Medium | The Transmission Operator did not inform its Reliability Coordinator of one SOL, or 5% or less of the SOLs, whichever is less, which, while not an IROL, has been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area based on its assessment of its Operational Planning Analysis. | The Transmission Operator did not inform its Reliability Coordinator of two SOLs, or more than 5% and less than or equal to 10% of the SOLs whichever is less, which, while not IROLs, have been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area based on its assessment of its Operational Planning Analysis. | The Transmission Operator did not inform its Reliability Coordinator of three SOLs, or more than 10% and less than or equal to 15% of the Sols whichever is less, which, while not IROLs, have been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area based on its assessment of its Operational Planning Analysis. | The Transmission Operator did not inform its Reliability Coordinator of four or more SOLs, or more than 15% of the SOLs whichever is less, which, while not IROLs, have been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area based on its assessment of its Operational Planning Analysis. | [19 empty] | TOP
Inactive | TOP | TOP-001-2 | R9. | Each Transmission Operator shall not operate outside any System Operating Limit (SOL) identified in Requirement R8 for a continuous duration that would cause a violation of the Facility Rating or Stability criteria upon which it is based. |  | 2016-01-26 | Medium | N/A | N/A | N/A | The Transmission Operator exceeded a System Operating Limit (SOL), as identified in Requirement R8, for a continuous duration that would cause a violation of the Facility Rating or Stability criteria upon which it is based. | [19 empty] | TOP
Inactive | TOP | TOP-001-2 | R10. | Each Transmission Operator shall inform its Reliability Coordinator of its actions to return the system to within limits when an IROL, or an SOL identified in Requirement R8, has been exceeded. |  | 2016-01-26 | Medium | N/A | N/A | N/A | The Transmission Operator did not inform its Reliability Coordinator of actions being taken to return the system to within limits when an IROL, or an SOL identified in Requirement R8, had been exceeded. | [19 empty] | TOP
Inactive | TOP | TOP-001-2 | R11. | Each Transmission Operator shall act or direct others to act, to mitigate both the magnitude and duration of exceeding an IROL within the IROL’s Tv, or of an SOL identified in Requirement R8. |  | 2016-01-26 | High | N/A | N/A | N/A | The Transmission Operator did not act, or direct others to act, to mitigate both the magnitude and duration of exceeding an IROL within the IROL’s Tv, or of an SOL identified in Requirement R8. | [19 empty] | TOP
Inactive | TOP | TOP-001-3 | R1. | Each Transmission Operator shall act to address the reliability of its Transmission Operator Area via direct actions or by issuing Operating Instructions. | 2017-04-01 | 2018-06-30 | High | N/A | N/A | N/A | The Transmission Operator failed to act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | [19 empty] | TOP
Inactive | TOP | TOP-001-3 | R2. | Each Balancing Authority shall act to address the reliability of its Balancing Authority Area via direct actions or by issuing Operating Instructions. | 2017-04-01 | 2018-06-30 | High | N/A | N/A | N/A | The Balancing Authority failed to act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. |  | BA
Inactive | TOP | TOP-001-3 | R3. | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | 2017-04-01 | 2018-06-30 | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Transmission Operator, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. |  | BA | DP |  |  |  | GOP
Inactive | TOP | TOP-001-3 | R4. | Each Balancing Authority, Generator Operator, and Distribution Providershall inform its Transmission Operator of its inability to perform an Operating Instruction issued by its Transmission Operator. | 2017-04-01 | 2018-06-30 | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. |  | BA | DP |  |  |  | GOP
Inactive | TOP | TOP-001-3 | R5. | Each Transmission Operator, Generator Operator and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | 2017-04-01 | 2018-06-30 | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Balancing Authority, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. |  |  | DP |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-3 | R6. | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to perform an Operating Instruction issued by that Balancing Authority. | 2017-04-01 | 2018-06-30 | High | N/A | N/A | N/A | The responsible entity did not inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. |  |  | DP |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-3 | R7. | Each Transmission Operator shall assist other Transmission Operators, if requested and able, provided that the requesting entity has implemented its Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | 2017-04-01 | 2018-06-30 | High | N/A | N/A | N/A | The Transmission Operator did not provide comparable assistance to other Transmission Operators within its Reliability Coordinator Area, when requested and able, and the requesting entity had implemented its Emergency procedures, and such actions could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | [19 empty] | TOP
Inactive | TOP | TOP-001-3 | R8. | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. | 2017-04-01 | 2018-06-30 | High | The Transmission Operator did not inform one known impacted Transmission Operator or 5% or less of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform one known impacted Balancing Authorities or 5% or less of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform two known impacted Transmission Operators or more than 5% and less than or equal to 10% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform two known impacted Balancing Authorities or more than 5% and less than or equal to 10% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform three known impacted Transmission Operators or more than 10% and less than or equal to 15% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform three known impacted Balancing Authorities or more than 10% and less than or equal to 15% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform its Reliability Coordinator of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Transmission Operators or more than 15% of the known impacted Transmission Operators of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Balancing Authorities or more than 15% of the known impacted Balancing Authorities of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | [19 empty] | TOP
Inactive | TOP | TOP-001-3 | R9. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. | 2017-04-01 | 2018-06-30 | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-001-3 | R10. | Each Transmission Operator shall perform the following as necessary for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: | 2017-04-01 | 2018-06-30 | Medium | N/A | The Transmission Operator did not monitor one of the items listed in Requirement R10, Part 10.1. OR The Transmission Operator did not obtain and utilize one of the items listed in Requirement R10, Part 10.2. | The Transmission Operator did not monitor one of the items listed in Requirement R10, Part 10.1 and did not obtain and utilize one of the items listed in Requirement R10, Part 10.2. | The Transmission Operator did not monitor Facilities and the status of Special Protection Systems within its Transmission Operator Area and did not obtain and utilize data deemed as necessary from outside its Transmission Operator Area. | [19 empty] | TOP
Inactive | TOP | TOP-001-3 | R11. | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Special Protection Systems that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | 2017-04-01 | 2018-06-30 | High | N/A | N/A | The Balancing Authority did not monitor the status of Special Protection Systems that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | The Balancing Authority did not monitor its Balancing Authority Area, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  | BA
Inactive | TOP | TOP-001-3 | R12. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | 2017-04-01 | 2018-06-30 | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | [19 empty] | TOP
Inactive | TOP | TOP-001-3 | R13. | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | 2017-04-01 | 2018-06-30 | High | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for one 30-minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for two 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30-minute periods within that 24-hour period. | [19 empty] | TOP
Inactive | TOP | TOP-001-3 | R14. | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | 2017-04-01 | 2018-06-30 | High | N/A | N/A | N/A | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | [19 empty] | TOP
Inactive | TOP | TOP-001-3 | R15. | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. | 2017-04-01 | 2018-06-30 | Medium | N/A | N/A | N/A | The Transmission Operator did not inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | [19 empty] | TOP
Inactive | TOP | TOP-001-3 | R16. | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2017-04-01 | 2018-06-30 | High | N/A | N/A | N/A | The Transmission Operator did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | [19 empty] | TOP
Inactive | TOP | TOP-001-3 | R17. | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2017-04-01 | 2018-06-30 | High | N/A | N/A | N/A | The Balancing Authority did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | BA
Inactive | TOP | TOP-001-3 | R18. | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | 2017-04-01 | 2018-06-30 | High | N/A | N/A | N/A | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | [19 empty] | TOP
Inactive | TOP | TOP-001-3 | R19. | Each Transmission Operator shall have data exchange capabilities with the entities that it has identified that it needs data from in order to maintain reliability in its Transmission Operator Area. | 2017-04-01 | 2018-06-30 | High | The Transmission Operator did not have data exchange capabilities with one identified entity, or 5% or less of the applicable entities, whichever is greater. | The Transmission Operator did not have data exchange capabilities with two identified entities, or more than 5% or less than or equal to 10% of the applicable entities, whichever is greater. | The Transmission Operator did not have data exchange capabilities with three identified entities, or more than 10% or less than or equal to 15% of the applicable entities, whichever is greater. | The Transmission Operator did not have data exchange capabilities with four or more identified entities or greater than 15% of the applicable entities, whichever is greater. | [19 empty] | TOP
Inactive | TOP | TOP-001-3 | R20. | Each Balancing Authority shall have data exchange capabilities with the entities that it has identified that it needs data from in order to maintain reliability in its Balancing Authority Area. | 2017-04-01 | 2018-06-30 | High | The Balancing Authority did not have data exchange capabilities with one identified entity, or 5% or less of the applicable entities, whichever is greater. | The Balancing Authority did not have data exchange capabilities with two identified entities, or more than 5% or less than or equal to 10% of the applicable entities, whichever is greater. | The Balancing Authority did not have data exchange capabilities with three identified entities, or more than 10% or less than or equal to 15% of the applicable entities, whichever is greater. | The Balancing Authority did not have data exchange capabilities with four or more identified entities or greater than 15% of the applicable entities, whichever is greater. |  | BA
Inactive | TOP | TOP-001-4 | R1. | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | 2018-07-01 | 2021-03-31 | High | N/A | N/A | N/A | The Transmission Operator failed to act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | [19 empty] | TOP
Inactive | TOP | TOP-001-4 | R2. | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | 2018-07-01 | 2021-03-31 | High | N/A | N/A | N/A | The Balancing Authority failed to act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. |  | BA
Inactive | TOP | TOP-001-4 | R3. | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | 2018-07-01 | 2021-03-31 | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Transmission Operator, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. |  | BA | DP |  |  |  | GOP
Inactive | TOP | TOP-001-4 | R4. | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | 2018-07-01 | 2021-03-31 | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. |  | BA | DP |  |  |  | GOP
Inactive | TOP | TOP-001-4 | R5. | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | 2018-07-01 | 2021-03-31 | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Balancing Authority, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. |  |  | DP |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-4 | R6. | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | 2018-07-01 | 2021-03-31 | High | N/A | N/A | N/A | The responsible entity did not inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. |  |  | DP |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-4 | R7. | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | 2018-07-01 | 2021-03-31 | High | N/A | N/A | N/A | The Transmission Operator did not provide comparable assistance to other Transmission Operators within its Reliability Coordinator Area, when requested and able, and the requesting entity had implemented its Emergency procedures, and such actions could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | [19 empty] | TOP
Inactive | TOP | TOP-001-4 | R8. | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. | 2018-07-01 | 2021-03-31 | High | The Transmission Operator did not inform one known impacted Transmission Operator or 5% or less of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform one known impacted Balancing Authorities or 5% or less of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform two known impacted Transmission Operators or more than 5% and less than or equal to 10% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform two known impacted Balancing Authorities or more than 5% and less than or equal to 10% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas | The Transmission Operator did not inform three known impacted Transmission Operators or more than 10% and less than or equal to 15% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform three known impacted Balancing Authorities or more than 10% and less than or equal to 15% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform its Reliability Coordinator of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Transmission Operators or more than 15% of the known impacted Transmission Operators of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Balancing Authorities or more than 15% of the known impacted Balancing Authorities of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | [19 empty] | TOP
Inactive | TOP | TOP-001-4 | R9. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. | 2018-07-01 | 2021-03-31 | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-001-4 | R10. | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: | 2018-07-01 | 2021-03-31 | High | The Transmission Operator did not monitor, obtain, or utilize one of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize two of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize three of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize four or more of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10 Part 10.1 through 10.6. | [19 empty] | TOP
Inactive | TOP | TOP-001-4 | R11. | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | 2018-07-01 | 2021-03-31 | High | N/A | N/A | The Balancing Authority did not monitor the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | The Balancing Authority did not monitor its Balancing Authority Area, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  | BA
Inactive | TOP | TOP-001-4 | R12. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | 2018-07-01 | 2021-03-31 | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | [19 empty] | TOP
Inactive | TOP | TOP-001-4 | R13. | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | 2018-07-01 | 2021-03-31 | High | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for one 30-minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for two 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for four or more 30-minute periods within that 24-hour period. | [19 empty] | TOP
Inactive | TOP | TOP-001-4 | R14. | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | 2018-07-01 | 2021-03-31 | High | N/A | N/A | N/A | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | [19 empty] | TOP
Inactive | TOP | TOP-001-4 | R15. | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. | 2018-07-01 | 2021-03-31 | Medium | N/A | N/A | N/A | The Transmission Operator did not inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | [19 empty] | TOP
Inactive | TOP | TOP-001-4 | R16. | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2018-07-01 | 2021-03-31 | High | N/A | N/A | N/A | The Transmission Operator did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | [19 empty] | TOP
Inactive | TOP | TOP-001-4 | R17. | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2018-07-01 | 2021-03-31 | High | N/A | N/A | N/A | The Balancing Authority did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | BA
Inactive | TOP | TOP-001-4 | R18. | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | 2018-07-01 | 2021-03-31 | High | N/A | N/A | N/A | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | [19 empty] | TOP
Inactive | TOP | TOP-001-4 | R19. | Each Transmission Operator shall have data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. | 2018-07-01 | 2021-03-31 | Medium | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with one identified entity, or 5% or less of the applicable entities, whichever is greater. | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with two identified entities, or more than 5% or less than or equal to 10% of the applicable entities, whichever is greater. | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with three identified entities, or more than 10% or less than or equal to 15% of the applicable entities, whichever is greater. | The Transmission Operator did not have data exchange capabilities for performing its Operational Planning Analyses with four or more identified entities or greater than 15% of the applicable entities, whichever is greater. | [19 empty] | TOP
Inactive | TOP | TOP-001-4 | R20. | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. | 2018-07-01 | 2021-03-31 | High | N/A | N/A | The Transmission Operator had data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, as specified in the Requirement. | The Transmission Operator did not have data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments as specified in the Requirement. | [19 empty] | TOP
Inactive | TOP | TOP-001-4 | R21. | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. | 2018-07-01 | 2021-03-31 | Medium | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Transmission Operator did not test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | [19 empty] | TOP
Inactive | TOP | TOP-001-4 | R22. | Each Balancing Authority shall have data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. | 2018-07-01 | 2021-03-31 | Medium | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with one identified entity, or 5% or less of the applicable entities, whichever is greater. | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with two identified entities, or more than 5% or less than or equal to 10% of the applicable entities, whichever is greater. | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with three identified entities, or more than 10% or less than or equal to 15% of the applicable entities, whichever is greater. | The Balancing Authority did not have data exchange capabilities for developing its Operating Plan with four or more identified entities or greater than 15% of the applicable entities, whichever is greater. |  | BA
Inactive | TOP | TOP-001-4 | R23. | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. | 2018-07-01 | 2021-03-31 | High | N/A | N/A | The Balancing Authority had data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions, but did not have redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, as specified in the Requirement. | The Balancing Authority did not have data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions as specified in the Requirement. |  | BA
Inactive | TOP | TOP-001-4 | R24. | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. | 2018-07-01 | 2021-03-31 | Medium | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 180 calendar days since the previous test OR The Balancing Authority did not test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. |  | BA
Inactive | TOP | TOP-001-5 | R1. | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | 2021-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The Transmission Operator failed to act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | [19 empty] | TOP
Inactive | TOP | TOP-001-5 | R2. | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | 2021-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The Balancing Authority failed to act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. |  | BA
Inactive | TOP | TOP-001-5 | R3. | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | 2021-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Transmission Operator, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. |  | BA | DP |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-5 | R4. | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | 2021-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. |  | BA | DP |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-5 | R5. | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | 2021-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Balancing Authority, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. |  |  | DP |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-5 | R6. | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | 2021-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The responsible entity did not inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. |  |  | DP |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-001-5 | R7. | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | 2021-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The Transmission Operator did not provide comparable assistance to other Transmission Operators within its Reliability Coordinator Area, when requested and able, and the requesting entity had implemented its Emergency procedures, and such actions could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | [19 empty] | TOP
Inactive | TOP | TOP-001-5 | R8. | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. | 2021-04-01 | 2024-03-31 | High | The Transmission Operator did not inform one known impacted Transmission Operator or 5% or less of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform one known impacted Balancing Authorities or 5% or less of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform two known impacted Transmission Operators or more than 5% and less than or equal to 10% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform two known impacted Balancing Authorities or more than 5% and less than or equal to 10% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas | The Transmission Operator did not inform three known impacted Transmission Operators or more than 10% and less than or equal to 15% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR The Transmission Operator did not inform three known impacted Balancing Authorities or more than 10% and less than or equal to 15% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform its Reliability Coordinator of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Transmission Operators or more than 15% of the known impacted Transmission Operators of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Balancing Authorities or more than 15% of the known impacted Balancing Authorities of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | [19 empty] | TOP
Inactive | TOP | TOP-001-5 | R9. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. | 2021-04-01 | 2024-03-31 | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-001-5 | R10. | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: | 2021-04-01 | 2024-03-31 | High | The Transmission Operator did not monitor, obtain, or utilize one of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize two of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize three of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize four or more of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10 Part 10.1 through 10.6. | [19 empty] | TOP
Inactive | TOP | TOP-001-5 | R11. | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | 2021-04-01 | 2024-03-31 | High | N/A | N/A | The Balancing Authority did not monitor the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | The Balancing Authority did not monitor its Balancing Authority Area, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. |  | BA
Inactive | TOP | TOP-001-5 | R12. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | 2021-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | [19 empty] | TOP
Inactive | TOP | TOP-001-5 | R13. | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | 2021-04-01 | 2024-03-31 | High | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for one 30-minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for two 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30-minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for four or more 30-minute periods within that 24-hour period. | [19 empty] | TOP
Inactive | TOP | TOP-001-5 | R14. | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | 2021-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment | [19 empty] | TOP
Inactive | TOP | TOP-001-5 | R15. | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. | 2021-04-01 | 2024-03-31 | Medium | N/A | N/A | N/A | The Transmission Operator did not inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | [19 empty] | TOP
Inactive | TOP | TOP-001-5 | R16. | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2021-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The Transmission Operator did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | [19 empty] | TOP
Inactive | TOP | TOP-001-5 | R17. | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2021-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The Balancing Authority did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | BA
Inactive | TOP | TOP-001-5 | R18. | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | 2021-04-01 | 2024-03-31 | High | N/A | N/A | N/A | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | [19 empty] | TOP
Inactive | TOP | TOP-001-5 | R19. | Reserved. | 2021-04-01 | 2024-03-31
Inactive | TOP | TOP-001-5 | R20. | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. | 2021-04-01 | 2024-03-31 | High | N/A | N/A | The Transmission Operator had data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, as specified in the Requirement. | The Transmission Operator did not have data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments as specified in the Requirement. | [19 empty] | TOP
Inactive | TOP | TOP-001-5 | R21. | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. | 2021-04-01 | 2024-03-31 | Medium | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Transmission Operator did not test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | [19 empty] | TOP
Inactive | TOP | TOP-001-5 | R22. | Reserved. | 2021-04-01 | 2024-03-31
Inactive | TOP | TOP-001-5 | R23. | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. | 2021-04-01 | 2024-03-31 | High | N/A | N/A | The Balancing Authority had data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions, but did not have redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, as specified in the Requirement. | The Balancing Authority did not have data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions as specified in the Requirement. |  | BA
Inactive | TOP | TOP-001-5 | R24. | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. | 2021-04-01 | 2024-03-31 | Medium | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 180 calendar days since the previous test OR The Balancing Authority did not test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. |  | BA
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R1. | Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | 2024-04-01 |  | High | N/A | N/A | N/A | The Transmission Operator failed to act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R2. | Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | 2024-04-01 |  | High | N/A | N/A | N/A | The Balancing Authority failed to act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. |  | BA
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R3. | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | 2024-04-01 |  | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Transmission Operator, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. |  | BA | DP |  |  |  | GOP | [12 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R4. | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | 2024-04-01 |  | High | N/A | N/A | N/A | The responsible entity did not inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. |  | BA | DP |  |  |  | GOP | [12 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R5. | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | 2024-04-01 |  | High | N/A | N/A | N/A | The responsible entity did not comply with an Operating Instruction issued by the Balancing Authority, and such action could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. |  |  | DP |  |  |  | GOP | [12 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R6. | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | 2024-04-01 |  | High | N/A | N/A | N/A | The responsible entity did not inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. |  |  | DP |  |  |  | GOP | [12 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R7. | Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | 2024-04-01 |  | High | N/A | N/A | N/A | The Transmission Operator did not provide comparable assistance to other Transmission Operators within its Reliability Coordinator Area, when requested and able, and the requesting entity had implemented its Emergency procedures, and such actions could have been physically implemented and would not have violated safety, equipment, regulatory, or statutory requirements. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R8. | Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. | 2024-04-01 |  | High | The Transmission Operator did not inform one known impacted Transmission Operator or 5% or less of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR, The Transmission Operator did not inform one known impacted Balancing Authorities or 5% or less of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform two known impacted Transmission Operators or more than 5% and less than or equal to 10% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR, The Transmission Operator did not inform two known impacted Balancing Authorities or more than 5% and less than or equal to 10% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform three known impacted Transmission Operators or more than 10% and less than or equal to 15% of the known impacted Transmission Operators, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Transmission Operator Areas. OR, The Transmission Operator did not inform three known impacted Balancing Authorities or more than 10% and less than or equal to 15% of the known impacted Balancing Authorities, whichever is greater, of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | The Transmission Operator did not inform its Reliability Coordinator of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR The Transmission Operator did not inform four or more known impacted Transmission Operators or more than 15% of the known impacted Transmission Operators of its actual or expected operations that resulted in, or could have resulted in, an Emergency on those respective Transmission Operator Areas. OR, The Transmission Operator did not inform four or more known impacted Balancing Authorities or more than 15% of the known impacted Balancing Authorities of its actual or expected operations that resulted in, or could have resulted in, an Emergency on respective Balancing Authority Areas. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R9. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. | 2024-04-01 |  | Medium | The responsible entity did not notify one known impacted interconnected entity or 5% or less of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify two known impacted interconnected entities or more than 5% and less than or equal to 10% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify three known impacted interconnected entities or more than 10% and less than or equal to 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. | The responsible entity did not notify its Reliability Coordinator of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels. OR, The responsible entity did not notify four or more known impacted interconnected entities or more than 15% of the known impacted entities, whichever is greater, of a planned outage, or an unplanned outage of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, or associated communication channels between the affected entities. |  | BA | [17 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R10. | Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: | 2024-04-01 |  | High | The Transmission Operator did not monitor, obtain, or utilize one of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize two of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize three of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10, Part 10.1 through 10.6. | The Transmission Operator did not monitor, obtain, or utilize four or more of the items required or identified as necessary by the Transmission Operator and listed in Requirement R10 Part 10.1 through 10.6. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R11. | Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | 2024-04-01 |  | High | N/A | N/A | The Balancing Authority did not monitor the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load- interchange balance within its Balancing Authority Area and support Interconnection frequency. | The Balancing Authority did not monitor its Balancing Authority Area, in order to maintain generation-Load- interchange balance within its Balancing Authority Area and support Interconnection frequency. |  | BA
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R12. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | 2024-04-01 |  | High | N/A | N/A | N/A | The Transmission Operator exceeded an identified Interconnection Reliability Operating Limit (IROL) for a continuous duration greater than its associated IROL Tv. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R13. | Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | 2024-04-01 |  | High | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for one 30- minute period within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for two 30- minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for three 30- minute periods within that 24-hour period. | For any sample 24-hour period within the 30-day retention period, the Transmission Operator’s Real-time Assessment was not conducted for four or more 30-minute periods within that 24-hour period. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R14. | Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | 2024-04-01 |  | High | N/A | N/A | N/A | The Transmission Operator did not initiate its Operating Plan for mitigating a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R15. | Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded in accordance with its Reliability Coordinator’s SOL methodology. | 2024-04-01 |  | Medium | N/A | N/A | N/A | The Transmission Operator did not inform in accordance with its Reliability Coordinator’s SOL methodology its Reliability Coordinator of actions taken to return the System to within limits when a SOL had been exceeded. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R16. | Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2024-04-01 |  | High | N/A | N/A | N/A | The Transmission Operator did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R17. | Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | 2024-04-01 |  | High | N/A | N/A | N/A | The Balancing Authority did not provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. |  | BA
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R18. | Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | 2024-04-01 |  | High | N/A | N/A | N/A | The Transmission Operator failed to operate to the most limiting parameter in instances where there was a difference in SOLs. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R19. | Reserved. | 2024-04-01
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R20. | Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. | 2024-04-01 |  | High | N/A | N/A | The Transmission Operator had data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments, but did not have redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, as specified in the Requirement. | The Transmission Operator did not have data exchange capabilities with its Reliability Coordinator, Balancing Authority, and identified entities for performing Real-time monitoring and Real-time Assessments as specified in the Requirement. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R21. | Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. | 2024-04-01 |  | Medium | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Transmission Operator did not test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality; OR The Transmission Operator tested its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R22. | Reserved. | 2024-04-01
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R23. | Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. | 2024-04-01 |  | High | N/A | N/A | The Balancing Authority had data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real- time monitoring and analysis functions, but did not have redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, as specified in the Requirement. | The Balancing Authority did not have data exchange capabilities with its Reliability Coordinator, Transmission Operator, and identified entities for performing Real-time monitoring and analysis functions as specified in the Requirement. |  | BA | [17 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R24. | Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. | 2024-04-01 |  | Medium | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 90 calendar days but less than or equal to 120 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 2 hours and less than or equal to 4 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 120 calendar days but less than or equal to 150 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 4 hours and less than or equal to 6 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 150 calendar days but less than or equal to 180 calendar days since the previous test; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, initiated action to restore the redundant functionality in more than 6 hours and less than or equal to 8 hours. | The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality, but did so more than 180 calendar days since the previous test; OR The Balancing Authority did not test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality; OR The Balancing Authority tested its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days but, following an unsuccessful test, did not initiate action within 8 hours to restore the redundant functionality. |  | BA
Mandatory Subject to Enforcement | TOP | TOP-001-6 | R25. | Each Transmission Operator shall use the applicable Reliability Coordinator’s SOL methodology when determining SOL exceedances for Real-time Assessments, Real- time monitoring, and Operational Planning Analysis. | 2024-04-01 |  | High |  |  |  | The Transmission Operator failed to use the applicable Reliability Coordinator’s SOL methodology when determining SOL exceedances for Real-time Assessments, Real-time monitoring, and Operational Planning Analysis. | [19 empty] | TOP
Inactive | TOP | TOP-002-0 | R1. | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | 2007-08-07 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-0 | R2. | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | 2007-08-07 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-0 | R3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | 2007-08-07 | [11 empty] | GOP |  | LSE
Inactive | TOP | TOP-002-0 | R4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | 2007-08-07 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-0 | R5. | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | 2007-08-07 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-0 | R6. | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | 2007-08-07 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-0 | R7. | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | 2007-08-07 | [6 empty] | BA
Inactive | TOP | TOP-002-0 | R8. | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | 2007-08-07 | [6 empty] | BA
Inactive | TOP | TOP-002-0 | R9. | Each Balancing Authority shall plan to meet Interchange Schedules and ramps. |  | 2007-08-07 | [6 empty] | BA
Inactive | TOP | TOP-002-0 | R10. | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | 2007-08-07 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-0 | R11. | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject confidentiality requirements), and to its Reliability Coordinator. |  | 2007-08-07 | [24 empty] | TOP
Inactive | TOP | TOP-002-0 | R12. | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | 2007-08-07 | [26 empty] | TSP
Inactive | TOP | TOP-002-0 | R13. | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | 2007-08-07 | [6 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-002-0 | R14. | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | 2007-08-07 | [11 empty] | GOP
Inactive | TOP | TOP-002-0 | R15. | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | 2007-08-07 | [11 empty] | GOP
Inactive | TOP | TOP-002-0 | R16. | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | 2007-08-07 | [24 empty] | TOP
Inactive | TOP | TOP-002-0 | R17. | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | 2007-08-07 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-0 | R18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers and Load Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | 2007-08-07 | [6 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP
Inactive | TOP | TOP-002-0 | R19. | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | 2007-08-07 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-1 | R1. | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-1 | R2. | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-1 | R3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. |  | 2007-01-01 | [11 empty] | GOP |  | LSE
Inactive | TOP | TOP-002-1 | R4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-1 | R5. | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-1 | R6. | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-1 | R7. | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. |  | 2007-01-01 | [6 empty] | BA
Inactive | TOP | TOP-002-1 | R8. | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | 2007-01-01 | [6 empty] | BA
Inactive | TOP | TOP-002-1 | R9. | Each Balancing Authority shall plan to meet Interchange Schedules and ramps. |  | 2007-01-01 | [6 empty] | BA
Inactive | TOP | TOP-002-1 | R10. | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-1 | R11. | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject confidentiality requirements), and to its Reliability Coordinator. |  | 2007-01-01 | [24 empty] | TOP
Inactive | TOP | TOP-002-1 | R12. | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. |  | 2007-01-01 | [26 empty] | TSP
Inactive | TOP | TOP-002-1 | R13. | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. |  | 2007-01-01 | [6 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-002-1 | R14. | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: |  | 2007-01-01 | [11 empty] | GOP
Inactive | TOP | TOP-002-1 | R15. | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). |  | 2007-01-01 | [11 empty] | GOP
Inactive | TOP | TOP-002-1 | R16. | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: |  | 2007-01-01 | [24 empty] | TOP
Inactive | TOP | TOP-002-1 | R17. | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-1 | R18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers and Load Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. |  | 2007-01-01 | [6 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP |  | TSP
Inactive | TOP | TOP-002-1 | R19. | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. |  | 2007-01-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2 | R1. | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. | 2007-06-18 | 2009-12-01 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2 | R2. | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. | 2007-06-18 | 2009-12-01 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2 | R3. | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | 2007-06-18 | 2009-12-01 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP
Inactive | TOP | TOP-002-2 | R4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. | 2007-06-18 | 2009-12-01 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2 | R5. | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. | 2007-06-18 | 2009-12-01 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2 | R6. | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. | 2007-06-18 | 2009-12-01 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2 | R7. | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. | 2007-06-18 | 2009-12-01 | Medium | [5 empty] | BA
Inactive | TOP | TOP-002-2 | R8. | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. | 2007-06-18 | 2009-12-01 | Medium | [5 empty] | BA
Inactive | TOP | TOP-002-2 | R9. | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. | 2007-06-18 | 2009-12-01 | Low | [5 empty] | BA
Inactive | TOP | TOP-002-2 | R10. | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). | 2007-06-18 | 2009-12-01 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2 | R11. | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. | 2007-06-18 | 2009-12-01 | Medium | [23 empty] | TOP
Inactive | TOP | TOP-002-2 | R12. | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. | 2007-06-18 | 2009-12-01 | Medium | [25 empty] | TSP
Inactive | TOP | TOP-002-2 | R13. | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. | 2007-06-18 | 2009-12-01 | Medium | [10 empty] | GOP
Inactive | TOP | TOP-002-2 | R14. | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: | 2007-06-18 | 2009-12-01 | Medium | [10 empty] | GOP
Inactive | TOP | TOP-002-2 | R15. | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). | 2007-06-18 | 2009-12-01 | Low | [10 empty] | GOP
Inactive | TOP | TOP-002-2 | R16. | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: | 2007-06-18 | 2009-12-01 | Medium | [23 empty] | TOP
Inactive | TOP | TOP-002-2 | R17. | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. | 2007-06-18 | 2009-12-01 | High | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2 | R18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. | 2007-06-18 | 2009-12-01 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP
Inactive | TOP | TOP-002-2 | R19. | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. | 2007-06-18 | 2009-12-01 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2.1b | R1. | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. | 2012-09-13 | 2017-03-31 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2.1b | R2. | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. | 2012-09-13 | 2017-03-31 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2.1b | R3. | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | 2012-09-13 | 2017-03-31 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP
Inactive | TOP | TOP-002-2.1b | R4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. | 2012-09-13 | 2017-03-31 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2.1b | R5. | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. | 2012-09-13 | 2017-03-31 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2.1b | R6. | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. | 2012-09-13 | 2017-03-31 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2.1b | R7. | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. | 2012-09-13 | 2017-03-31 | Medium | [5 empty] | BA
Inactive | TOP | TOP-002-2.1b | R8. | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. | 2012-09-13 | 2017-03-31 | Medium | [5 empty] | BA
Inactive | TOP | TOP-002-2.1b | R9. | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. | 2012-09-13 | 2017-03-31 | Low | [5 empty] | BA
Inactive | TOP | TOP-002-2.1b | R10. | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). | 2012-09-13 | 2017-03-31 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2.1b | R11. | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. | 2012-09-13 | 2017-03-31 | Medium | [23 empty] | TOP
Inactive | TOP | TOP-002-2.1b | R12. | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. | 2012-09-13 | 2017-03-31 | Medium | [25 empty] | TSP
Inactive | TOP | TOP-002-2.1b | R13. | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. | 2012-09-13 | 2017-03-31 | Medium | [10 empty] | GOP
Inactive | TOP | TOP-002-2.1b | R14. | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: | 2012-09-13 | 2017-03-31 | Medium | [10 empty] | GOP
Inactive | TOP | TOP-002-2.1b | R15. | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). | 2012-09-13 | 2017-03-31 | Low | [10 empty] | GOP
Inactive | TOP | TOP-002-2.1b | R16. | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: | 2012-09-13 | 2017-03-31 | Medium | [23 empty] | TOP
Inactive | TOP | TOP-002-2.1b | R17. | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. | 2012-09-13 | 2017-03-31 | High | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2.1b | R18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. | 2012-09-13 | 2017-03-31 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP
Inactive | TOP | TOP-002-2.1b | R19. | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. | 2012-09-13 | 2017-03-31 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2a | R1. | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. | 2009-12-02 | 2011-10-19 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2a | R2. | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. | 2009-12-02 | 2011-10-19 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2a | R3. | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | 2009-12-02 | 2011-10-19 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP
Inactive | TOP | TOP-002-2a | R4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. | 2009-12-02 | 2011-10-19 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2a | R5. | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. | 2009-12-02 | 2011-10-19 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2a | R6. | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. | 2009-12-02 | 2011-10-19 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2a | R7. | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. | 2009-12-02 | 2011-10-19 | Medium | [5 empty] | BA
Inactive | TOP | TOP-002-2a | R8. | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. | 2009-12-02 | 2011-10-19 | Medium | [5 empty] | BA
Inactive | TOP | TOP-002-2a | R9. | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. | 2009-12-02 | 2011-10-19 | Low | [5 empty] | BA
Inactive | TOP | TOP-002-2a | R10. | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). | 2009-12-02 | 2011-10-19 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2a | R11. | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. | 2009-12-02 | 2011-10-19 | Medium | [23 empty] | TOP
Inactive | TOP | TOP-002-2a | R12. | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. | 2009-12-02 | 2011-10-19 | Medium | [25 empty] | TSP
Inactive | TOP | TOP-002-2a | R13. | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. | 2009-12-02 | 2011-10-19 | Medium | [10 empty] | GOP
Inactive | TOP | TOP-002-2a | R14. | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: | 2009-12-02 | 2011-10-19 | Medium | [10 empty] | GOP
Inactive | TOP | TOP-002-2a | R15. | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). | 2009-12-02 | 2011-10-19 | Low | [10 empty] | GOP
Inactive | TOP | TOP-002-2a | R16. | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: | 2009-12-02 | 2011-10-19 | Medium | [23 empty] | TOP
Inactive | TOP | TOP-002-2a | R17. | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. | 2009-12-02 | 2011-10-19 | High | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2a | R18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. | 2009-12-02 | 2011-10-19 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP
Inactive | TOP | TOP-002-2a | R19. | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. | 2009-12-02 | 2011-10-19 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2b | R1. | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. | 2011-10-20 | 2012-09-12 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2b | R2. | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. | 2011-10-20 | 2012-09-12 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2b | R3. | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | 2011-10-20 | 2012-09-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [12 empty] | TSP
Inactive | TOP | TOP-002-2b | R4. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. | 2011-10-20 | 2012-09-12 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2b | R5. | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. | 2011-10-20 | 2012-09-12 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2b | R6. | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. | 2011-10-20 | 2012-09-12 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2b | R7. | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. | 2011-10-20 | 2012-09-12 | Medium | [5 empty] | BA
Inactive | TOP | TOP-002-2b | R8. | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. | 2011-10-20 | 2012-09-12 | Medium | [5 empty] | BA
Inactive | TOP | TOP-002-2b | R9. | Each Balancing Authority shall plan to meet Interchange Schedules and Ramps. | 2011-10-20 | 2012-09-12 | Low | [5 empty] | BA
Inactive | TOP | TOP-002-2b | R10. | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). | 2011-10-20 | 2012-09-12 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2b | R11. | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. | 2011-10-20 | 2012-09-12 | Medium | [23 empty] | TOP
Inactive | TOP | TOP-002-2b | R12. | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. | 2011-10-20 | 2012-09-12 | Medium | [25 empty] | TSP
Inactive | TOP | TOP-002-2b | R13. | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. | 2011-10-20 | 2012-09-12 | Medium | [10 empty] | GOP
Inactive | TOP | TOP-002-2b | R14. | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: | 2011-10-20 | 2012-09-12 | Medium | [10 empty] | GOP
Inactive | TOP | TOP-002-2b | R15. | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). | 2011-10-20 | 2012-09-12 | Low | [10 empty] | GOP
Inactive | TOP | TOP-002-2b | R16. | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: | 2011-10-20 | 2012-09-12 | Medium | [23 empty] | TOP
Inactive | TOP | TOP-002-2b | R17. | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. | 2011-10-20 | 2012-09-12 | High | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-2b | R18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. | 2011-10-20 | 2012-09-12 | Medium | [5 empty] | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP
Inactive | TOP | TOP-002-2b | R19. | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. | 2011-10-20 | 2012-09-12 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-002-3 | R1. | Each Transmission Operator shall have an Operational Planning Analysis that represents projected System conditions that will allow it to assess whether the planned operations for the next day within its Transmission Operator Area will exceed any of its Facility Ratings or Stability Limits during anticipated normal and Contingency event conditions. |  | 2016-01-26 | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operational Planning Analysis that represented projected System conditions allowing it to assess whether the planned operations for the next day within its Transmission Operator Area will exceed any of its Facility Ratings or Stability Limits during anticipated normal and Contingency event conditions. | [19 empty] | TOP
Inactive | TOP | TOP-002-3 | R2. | Each Transmission Operator shall develop a plan to operate within each Interconnection Reliability Operating Limit (IROL) and each System Operating Limit (SOL) which, while not an IROL, has been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area, identified as a result of the Operational Planning Analysis performed in Requirement R1. |  | 2016-01-26 | Medium | N/A | N/A | N/A | The Transmission Operator did not develop a plan to operate within those IROLs and each SOL which, while not an IROL, has been identified by the Transmission Operator as supporting its internal area reliability, identified as a result of the Operational Planning Analysis performed in Requirement R1. | [19 empty] | TOP
Inactive | TOP | TOP-002-3 | R3. | Each Transmission Operator shall notify all NERC registered entities identified in the plan(s) cited in Requirement R2 as to their role in those plan(s). |  | 2016-01-26 | Medium | The Transmission Operator did not notify one NERC-registered entity, or 5% or less of the NERC-registered entities, whichever is less identified in the plan(s) cited, as to their role in the plan(s). | The Transmission Operator did not notify two NERC-registered entities, or more than 5%, and less than or equal to 10% of the NERC-registered entities, whichever is less, identified in the plan(s) as to their role in the plan(s). | The Transmission Operator did not notify three NERC-registered entities, or more than 10% and less than or equal to 15% of the NERC-registered entities, whichever is less, identified in the plan(s) as to their role in the plan(s). | The Transmission Operator did not notify four or more NERC-registered entities, or more than15% of the NERC-registered entities identified in the plan(s) as to their role in the plan(s). | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-002-4 | R1. | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). | 2017-04-01 | 2025-09-30 | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operational Planning Analysis allowing it to assess whether its planned operations for the next day within its Transmission Operator Area exceeded any of its System Operating Limits (SOLs). | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-002-4 | R2. | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. | 2017-04-01 | 2025-09-30 | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operating Plan to address potential System Operating Limit (SOL) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-002-4 | R3. | Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). | 2017-04-01 | 2025-09-30 | Medium | The Transmission Operator did not notify one impacted entity or 5% or less of the entities, whichever is greater identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify four or more entities or more than 15% of the impacted NERC identified in the Operating Plan(s) as to their role in the plan(s). For the Requirement R3 and R5 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-002-4 | R4. | Each Balancing Authority shall have an Operating Plan(s) for the next-day that addresses: | 2017-04-01 | 2025-09-30 | Medium | The Balancing Authority has an Operating Plan but it does not address one of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan but it does not address two of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan but it does not address three of the criteria in Requirement R4. | The Balancing Authority did not have an Operating Plan. |  | BA
Mandatory Subject to Enforcement | TOP | TOP-002-4 | R5. | Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). | 2017-04-01 | 2025-09-30 | Medium | The Balancing Authority did not notify one impacted entity or 5% or less of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify four or more entities or more than 15% of the impacted entities identified in the Operating Plan(s) as to their role in the plan(s). For the Requirement R3 and R5 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. |  | BA
Mandatory Subject to Enforcement | TOP | TOP-002-4 | R6. | Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. | 2017-04-01 | 2025-09-30 | Medium | N/A | N/A | N/A | The Transmission Operator did not provide its Operating Plan(s) for next-day operations as identified in Requirement R2 to its Reliability Coordinator. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-002-4 | R7. | Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. | 2017-04-01 | 2025-09-30 | Medium | N/A | N/A | N/A | The Balancing Authority did not provide its Operating Plan(s) for next-day operations as identified in Requirement R4 to its Reliability Coordinator. |  | BA
Subject to Future Enforcement | TOP | TOP-002-5 | R1. | Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs) | 2025-10-01 |  | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operational Planning Analysis allowing it to assess whether its planned operations for the next day within its Transmission Operator Area exceeded any of its System Operating Limits (SOLs). | [19 empty] | TOP
Subject to Future Enforcement | TOP | TOP-002-5 | R2. | Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. | 2025-10-01 |  | Medium | N/A | N/A | N/A | The Transmission Operator did not have an Operating Plan to address potential System Operating Limit (SOL) exceedances identified as a result of the Operational Planning Analysis performed in Requirement R1. | [19 empty] | TOP
Subject to Future Enforcement | TOP | TOP-002-5 | R3. | Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). | 2025-10-01 |  | Medium | The Transmission Operator did not notify one impacted entity or 5% or less of the entities, whichever is greater identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Transmission Operator did not notify four or more entities or more than 15% of the impacted NERC identified in the Operating Plan(s) as to their role in the plan(s). | [19 empty] | TOP
Subject to Future Enforcement | TOP | TOP-002-5 | R4. | Each Balancing Authority shall have an Operating Plan(s) for the next day that addresses: | 2025-10-01 |  | Medium | The Balancing Authority has an Operating Plan, but it does not address one of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan, but it does not address two of the criteria in Requirement R4. | The Balancing Authority has an Operating Plan, but it does not address three of the criteria in Requirement R4. | The Balancing Authority did not have an Operating Plan. |  | BA
Subject to Future Enforcement | TOP | TOP-002-5 | R5. | Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s) | 2025-10-01 |  | Medium | The Balancing Authority did not notify one impacted entity or 5% or less of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify two entities or more than 5% and less than or equal to 10% of the impacted entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify three impacted entities or more than 10% and less than or equal to 15% of the entities, whichever is greater, identified in the Operating Plan(s) as to their role in the plan(s). | The Balancing Authority did not notify four or more entities or more than 15% of the impacted entities identified in the Operating Plan(s) as to their role in the plan(s). |  | BA
Subject to Future Enforcement | TOP | TOP-002-5 | R6. | Each Transmission Operator shall provide its Operating Plan(s) for next day operations identified in Requirement R2 to its Reliability Coordinator. | 2025-10-01 |  | Medium | N/A | N/A | N/A | The Transmission Operator did not provide its Operating Plan(s) for next day operations as identified in Requirement R2 to its Reliability Coordinator. | [19 empty] | TOP
Subject to Future Enforcement | TOP | TOP-002-5 | R7. | Each Balancing Authority shall provide its Operating Plan(s) for next day operations identified in Requirement R4 to its Reliability Coordinator. | 2025-10-01 |  | Medium | N/A | N/A | N/A | The Transmission Operator did not provide its Operating Plan(s) for next day operations as identified in Requirement R2 to its Reliability Coordinator. |  | BA
Subject to Future Enforcement | TOP | TOP-002-5 | R8. | Each Balancing Authority shall have an extreme cold weather Operating Process for its Balancing Authority Area, addressing preparations for and operations during extreme cold weather periods. The extreme cold weather Operating Process shall include, but is not limited to: | 2025-10-01 |  | Medium | N/A | The Balancing Authority had an extreme cold weather Operating Process addressing preparations for and operations during extreme cold weather periods, but it did not address one of the Requirements or sub- Requirements of R8 Parts 8.1 through 8.3 | The Balancing Authority had an extreme cold weather Operating Process addressing preparations for and operations during extreme cold weather periods, but it did not address two of the Requirements or sub- Requirements of R8 Parts 8.1 through 8.3. | The Balancing Authority did not have an extreme cold weather Operating Process addressing preparations for and operations during extreme cold weather periods. |  | BA
Inactive | TOP | TOP-003-0 | R1. | Generator Operators and Transmission Operators shall provide planned outage information. | 2007-06-18 | 2011-09-30 | Medium | [10 empty] | GOP | [12 empty] | TOP
Inactive | TOP | TOP-003-0 | R2. | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. | 2007-06-18 | 2011-09-30 | Medium | [5 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-003-0 | R3. | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. | 2007-06-18 | 2011-09-30 | Medium | [5 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-003-0 | R4. | Each Reliability Coordinator shall resolve any scheduling of potential reliability conflicts. | 2007-06-18 | 2011-09-30 | Medium | [16 empty] | RC
Inactive | TOP | TOP-003-1 | R1. | Generator Operators and Transmission Operators shall provide planned outage information. | 2011-10-01 | 2017-03-31 | [11 empty] | GOP | [12 empty] | TOP
Inactive | TOP | TOP-003-1 | R2. | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. | 2011-10-01 | 2017-03-31 | Medium | [5 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-003-1 | R3. | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. | 2011-10-01 | 2017-03-31 | Medium | [5 empty] | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-003-1 | R4. | Each Reliability Coordinator shall resolve any scheduling of potential reliability conflicts. | 2011-10-01 | 2017-03-31 | Medium | [16 empty] | RC
Inactive | TOP | TOP-003-2 | R1. | Each Transmission Operator shall create a documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. The specification shall include: [See Standard pdf for further information] |  | 2016-01-26 | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for them to perform their Operational Planning Analyses and Real-time monitoring. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for them to perform their Operational Planning Analyses and Real-time monitoring. | [19 empty] | TOP
Inactive | TOP | TOP-003-2 | R2. | Each Balancing Authority shall create a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The specification shall include: [See Standard pdf for further information] |  | 2016-01-26 | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for them to perform their analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for them to perform their analysis functions and Real-time monitoring. |  | BA
Inactive | TOP | TOP-003-2 | R3. | Each Transmission Operator shall distribute its data specification, as developed in Requirement R1,to entities that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. |  | 2016-01-26 | Low | The Transmission Operator did not distribute its data specification, as developed in Requirement R1 to one entity, or 5% or less of the entities, whichever is less, that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | The Transmission Operator did not distribute its data specification, as developed in requirement R1 to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is less, that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | The Transmission Operator did not distribute its data specification, as developed in Requirement R1 to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is less, that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | The Transmission Operator did not distribute its data specification, as developed in Requirement R1 to four or more entities, or more than 15% of the entities, whichever is less, that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | [19 empty] | TOP
Inactive | TOP | TOP-003-2 | R4. | Each Balancing Authority shall distribute its data specification, as developed in Requirement R2, to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. |  | 2016-01-26 | Low | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to one entity, or 5% or less of the entities, whichever is less, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is less, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is less, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements . | The Balancing Authority did not distribute its data specification, as developed in Requirement R2 to four or more entities, or more than 15% of the entities, whichever is less,that have data required by the Balancing Authority’s analysis functions and Realtime monitoring process used in meeting its NERC-mandated reliability requirements. |  | BA
Inactive | TOP | TOP-003-2 | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications for data. |  | 2016-01-26 | Medium | N/A | N/A | N/A | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. |  | BA | DP |  |  | GO | GOP | IA | LSE | [9 empty] | TO | TOP
Inactive | TOP | TOP-003-3 | R1. | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] | 2017-01-01 | 2021-03-31 | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | [19 empty] | TOP
Inactive | TOP | TOP-003-3 | R2. | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] | 2017-01-01 | 2021-03-31 | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. OR The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. |  | BA
Inactive | TOP | TOP-003-3 | R3. | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. | 2017-01-01 | 2021-03-31 | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | [19 empty] | TOP
Inactive | TOP | TOP-003-3 | R4. | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | 2017-01-01 | 2021-03-31 | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA
Inactive | TOP | TOP-003-3 | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [See standard for additional information.] | 2017-04-01 | 2021-03-31 | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. |  | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP
Inactive | TOP | TOP-003-4 | R1. | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to:[See standard for additional information.] | 2021-04-01 | 2023-03-31 | Low | The Transmission Operator did not include one of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include two of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.4) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. OR The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | [19 empty] | TOP
Inactive | TOP | TOP-003-4 | R2. | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: [See standard for additional information.] | 2021-04-01 | 2023-03-31 | Low | The Balancing Authority did not include one of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include two of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.4) of the documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. OR The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. |  | BA
Inactive | TOP | TOP-003-4 | R3. | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. | 2021-04-01 | 2023-03-31 | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | [19 empty] | TOP
Inactive | TOP | TOP-003-4 | R4. | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | 2021-04-01 | 2023-03-31 | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA
Inactive | TOP | TOP-003-4 | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: | 2021-04-01 | 2023-03-31 | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. |  | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP
Mandatory Subject to Enforcement | TOP | TOP-003-5 | R1. | Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: | 2023-04-01 | 2025-06-30 | Low | The Transmission Operator did not include two or fewer of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not include any of the parts (Part 1.1 through Part 1.5) of the documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. OR, The Transmission Operator did not have a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003-5 | R2. | Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: | 2023-04-01 | 2025-06-30 | Low | The Balancing Authority did not include two or fewer of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Real- time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Real- time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Real- time monitoring. | The Balancing Authority did not include any of the parts (Part 2.1 through Part 2.5) of the documented specification for the data necessary for it to perform its analysis functions and Real- time monitoring. OR, The Balancing Authority did not have a documented specification for the data necessary for it to perform its analysis functions and Real- time monitoring. |  | BA
Mandatory Subject to Enforcement | TOP | TOP-003-5 | R3. | Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real- time monitoring, and Real-time Assessments. | 2023-04-01 | 2025-06-30 | Low | The Transmission Operator did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-003-5 | R4. | Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | 2023-04-01 | 2025-06-30 | Low | The Balancing Authority did not distribute its data specification to one entity, or 5% or less of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to three entities, or more than 10% and less than or equal to 15% of the entities, whichever is greater, that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its data specification to four or more entities, or more than 15% of the entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. |  | BA
Mandatory Subject to Enforcement | TOP | TOP-003-5 | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: | 2023-04-01 | 2025-06-30 | Medium | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet one of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet two of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 satisfied the obligations in the data specification but did not meet three of the criteria shown in Requirement R5 (Parts 5.1 – 5.3). | The responsible entity receiving a data specification in Requirement R3 or R4 did not satisfy the obligations of the documented specifications for data. |  | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP
Inactive | TOP | TOP-003-6 | R1. | Each Transmission Operator shall maintain documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. The specification shall include, but not be limited to: |  | 2023-08-23 | Low | The Transmission Operator did not include one or two of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐time monitoring, and Real‐ time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐ time monitoring, and Real‐ time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐time monitoring, and Real‐ time Assessments. | The Transmission Operator did not include any of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐time monitoring, and Real‐ time Assessments. OR, The Transmission Operator did not have a documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real‐ time monitoring, and Real‐ time Assessments. | [19 empty] | TOP
Inactive | TOP | TOP-003-6 | R2. | Each Balancing Authority shall maintain documented specification(s) for the data and information necessary for it to perform its analysis functions and Real‐time monitoring. The data specification shall include, but not be limited to: |  | 2023-08-23 | Low | The Balancing Authority did not include two or fewer of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real‐ time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real‐ time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real‐ time monitoring. | The Balancing Authority did not include any of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real‐ time monitoring. OR, The Balancing Authority did not have a documented specification(s) for the data and information necessary for it to perform its analysis functions and Real‐ time monitoring. |  | BA
Inactive | TOP | TOP-003-6 | R3. | Each Transmission Operator shall distribute its data and information specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. |  | 2023-08-23 | Low | The Transmission Operator did not distribute its Specification(s) to one entity, or 5% or less of the entities, whichever is greater, that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. | The Transmission Operator did not distribute its Specification(s) to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. | The Transmission Operator did not distribute its Specification(s) to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. | The Transmission Operator did not distribute its Specification(s) to four or more entities, or more than 15% of the entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real‐ time monitoring, and Real‐time Assessments. | [19 empty] | TOP
Inactive | TOP | TOP-003-6 | R4. | Each Balancing Authority shall distribute its data and information specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions and Real‐time monitoring. |  | 2023-08-23 | Low | The Balancing Authority did not distribute its Specification(s) to one entity, or 5% or less of the entities, whichever is greater, that have data and information required by the Balancing Authority’s analysis functions and Real‐time monitoring. | The Balancing Authority did not distribute its Specification(s) to two entities, or more than 5% and less than or equal to 10% of the entities,whichever is greater, that have data and information required by the Balancing Authority’s analysis functions and Real‐time monitoring. | The Balancing Authority did not distribute its Specification(s) to three entities, or more than10% and less than or equal to 15% of the entities,whichever is greater, that have data and information required by the Balancing Authority’s analysis functions and Real‐time monitoring. | The Balancing Authority did not distribute its Specification(s) to four or more entities, or more than 15% of the entities that have data and information required by the Balancing Authority’s analysis functions and Real‐time monitoring. | For the Requirement R3 and R4 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP
Inactive | TOP | TOP-003-6 | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data and information specification(s) in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using. |  | 2023-08-23 | Medium | The responsible entity receiving a specification(s) in Requirement R3 or R4 satisfied the obligations in the specification but failed to meet one of the parts in Requirement R1 Part1.5 or Requirement R2 Part 2.5. | The responsible entity receiving a specification(s) in Requirement R3 or R4 satisfied the obligations in the specification but failed to meet two of the parts in Requirement R1 Part 1.5 or Requirement R2 Part 2.5. | The responsible entity receiving a specification(s) in Requirement R3 or R4 satisfied the obligations in the specification but failed to meet three or more of the parts in Requirement R1 Part 1.5 or Requirement R2 Part 2.5. | The responsible entity receiving a specification(s) in Requirement R3 or R4 did not satisfy the obligations of the documented specifications. |  | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP
Subject to Future Enforcement | TOP | TOP-003-6.1 | R1. | Each Transmission Operator shall maintain documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The specification shall include, but not be limited to: | 2025-07-01 |  | Low | The Transmission Operator did not include one or two of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not include three of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not include four of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | The Transmission Operator did not include any of the parts (Part 1.1 through Part 1.5) of the documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. OR, The Transmission Operator did not have a documented specification(s) for the data and information necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments. | [19 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003-6.1 | R2. | Each Balancing Authority shall maintain documented specification(s) for the data and information necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: | 2025-07-01 |  | Low | The Balancing Authority did not include two or fewer of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real- time monitoring. | The Balancing Authority did not include three of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real- time monitoring. | The Balancing Authority did not include four of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real- time monitoring | The Balancing Authority did not include any of the parts (Part 2.1 through Part 2.5) of the documented specification(s) for the data and information necessary for it to perform its analysis functions and Real- time monitoring. OR, The Balancing Authority did not have a documented specification(s) for the data and information necessary for it to perform its analysis functions and Real- time monitoring. |  | BA
Subject to Future Enforcement | TOP | TOP-003-6.1 | R3. | Each Transmission Operator shall distribute its data and information specification(s) to entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real- time monitoring, and Real-time Assessments. | 2025-07-01 |  | Low | The Transmission Operator did not distribute its Specification(s) to one entity, or 5% or less of the entities, whichever is greater, that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its Specification(s) to two entities, or more than 5% and less than or equal to10% of the reliability entities, whichever is greater, that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its Specification(s) to three entities, or more than 10% and less than or equal to 15% of the reliability entities, whichever is greater, that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | The Transmission Operator did not distribute its Specification(s) to four or more entities, or more than 15% of the entities that have data and information required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments | For the Requirement R3 and R4 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | [18 empty] | TOP
Subject to Future Enforcement | TOP | TOP-003-6.1 | R4. | Each Balancing Authority shall distribute its data and information specification(s) to entities that have data and information required by the Balancing Authority’s analysis functions and Real-time monitoring. | 2025-07-01 |  | Low | The Balancing Authority did not distribute its Specification(s) to one entity, or 5% or less of the entities, whichever is greater, that have data and information required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its Specification(s) to two entities, or more than 5% and less than or equal to 10% of the entities, whichever is greater, that have data and information required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its Specification(s) to three entities, or more than10% and less than or equal to 15% of the entities, whichever is greater, that have data and information required by the Balancing Authority’s analysis functions and Real-time monitoring. | The Balancing Authority did not distribute its Specification(s) to four or more entities, or more than 15% of the entities that have data and information required by the Balancing Authority’s analysis functions and Real-time monitoring. | For the Requirement R3 and R4 VSLs only, the intent of the SDT is to start with the Severe VSL first and then to work your way to the left until you find the situation that fits. In this manner, the VSL will not be discriminatory by size of entity. If a small entity has just one affected reliability entity to inform, the intent is that that situation would be a Severe violation. | BA
Subject to Future Enforcement | TOP | TOP-003-6.1 | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data and information specification(s) in Requirement R3 or R4 shall satisfy the obligations of the documented specifications. | 2025-07-01 |  | Medium | The responsible entity receiving a specification(s) in Requirement R3 or R4 satisfied the obligations in the specification but failed to meet one of the parts in Requirement R1 Part1.5 or Requirement R2 Part 2.5. | The responsible entity receiving a specification(s) in Requirement R3 or R4 satisfied the obligations in the specification but failed to meet two of the parts in Requirement R1 Part 1.5 or Requirement R2 Part 2.5. | The responsible entity receiving a specification(s) in Requirement R3 or R4 satisfied the obligations in the specification but failed to meet three or more of the parts in Requirement R1 Part 1.5 or Requirement R2 Part 2.5. | The responsible entity receiving a specification(s) in Requirement R3 or R4 did not satisfy the obligations of the documented specifications. |  | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP
Inactive | TOP | TOP-004-0 | R1. | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). |  | 2005-04-01 | [24 empty] | TOP
Inactive | TOP | TOP-004-0 | R2. | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. |  | 2005-04-01 | [24 empty] | TOP
Inactive | TOP | TOP-004-0 | R3. | Each Transmission Operator shall, when practical, operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by Regional Reliability Organization policy. |  | 2005-04-01 | [24 empty] | TOP
Inactive | TOP | TOP-004-0 | R4. | If a Transmission Operator enters an unknown operating state (i.e. any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. |  | 2005-04-01 | [24 empty] | TOP
Inactive | TOP | TOP-004-0 | R5. | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. |  | 2005-04-01 | [24 empty] | TOP
Inactive | TOP | TOP-004-0 | R6. | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: |  | 2005-04-01 | [24 empty] | TOP
Inactive | TOP | TOP-004-1 | R1. | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). | 2007-06-18 | 2009-01-21 | High | [23 empty] | TOP
Inactive | TOP | TOP-004-1 | R2. | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. | 2007-06-18 | 2009-01-21 | High | [23 empty] | TOP
Inactive | TOP | TOP-004-1 | R3. | Each Transmission Operator shall, when practical, operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by Regional Reliability Organization policy. | 2007-06-18 | 2009-01-21 | High | [23 empty] | TOP
Inactive | TOP | TOP-004-1 | R4. | If a Transmission Operator enters an unknown operating state (i.e., any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. | 2007-06-18 | 2009-01-21 | High | [23 empty] | TOP
Inactive | TOP | TOP-004-1 | R5. | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. | 2007-06-18 | 2009-01-21 | High | [23 empty] | TOP
Inactive | TOP | TOP-004-1 | R6. | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: | 2007-06-18 | 2009-01-21 | Medium | [23 empty] | TOP
Inactive | TOP | TOP-004-2 | R1. | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). | 2009-01-22 | 2017-03-31 | High | [23 empty] | TOP
Inactive | TOP | TOP-004-2 | R2. | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. | 2009-01-22 | 2017-03-31 | High | [23 empty] | TOP
Inactive | TOP | TOP-004-2 | R3. | Each Transmission Operator shall operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by its Reliability Coordinator. | 2009-01-22 | 2017-03-31 | High | [23 empty] | TOP
Inactive | TOP | TOP-004-2 | R4. | If a Transmission Operator enters an unknown operating state (i.e. any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. | 2009-01-22 | 2017-03-31 | High |  |  |  | The Transmission Operator entering an unknown operating state (i.e., any state for which valid operating limits have not been determined), failed to restore operations to respect proven reliable power system limits for more than 45 minutes. | [19 empty] | TOP
Inactive | TOP | TOP-004-2 | R5. | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. | 2009-01-22 | 2017-03-31 | High | [23 empty] | TOP
Inactive | TOP | TOP-004-2 | R6. | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: | 2009-01-22 | 2017-03-31 | Medium | [23 empty] | TOP
Inactive | TOP | TOP-005-0 | R1. | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. |  | 2006-11-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-005-0 | R2. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | 2006-11-01
Inactive | TOP | TOP-005-0 | R3. | Upon request, each Reliability Coordinator shall, via the ISN or equivalent system, exchange with other Reliability Coordinators operating data that are necessary to allow the Reliability Coordinators to perform operational reliability assessments and coordinate reliable operations. Reliability Coordinators shall share with each other the types of data listed in Attachment 1- TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to. |  | 2006-11-01 | [17 empty] | RC
Inactive | TOP | TOP-005-0 | R4. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | 2006-11-01 | [6 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-005-0 | R5. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | 2006-11-01 | [16 empty] | PSE
Inactive | TOP | TOP-005-1 | R1. | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. | 2007-06-18 | 2009-05-12 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-005-1 | R2. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” | 2007-06-18 | 2009-05-12 | Low | [5 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-005-1 | R3. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. | 2007-06-18 | 2009-05-12 | Medium | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. |  |  | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-005-1 | R4. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. | 2007-06-18 | 2009-05-12 | Medium | [15 empty] | PSE
Inactive | TOP | TOP-005-1.1 | R1. | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. | 2009-05-13 | 2011-05-25 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-005-1.1 | R2. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” | 2009-05-13 | 2011-05-25 | Low | [5 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-005-1.1 | R3. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. | 2009-05-13 | 2011-05-25 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-005-1.1 | R4. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. | 2009-05-13 | 2011-05-25 | Medium | [15 empty] | PSE
Inactive | TOP | TOP-005-1.1a | R1. | Each Transmission Operator and Balancing Authority shall provide its Reliability Coordinator with the operating data that the Reliability Coordinator requires to perform operational reliability assessments and to coordinate reliable operations within the Reliability Coordinator Area. | 2011-05-26 | 2011-09-30 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-005-1.1a | R2. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” | 2011-05-26 | 2011-09-30 | Low | [5 empty] | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-005-1.1a | R3. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005-0 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. | 2011-05-26 | 2011-09-30 | Medium | [5 empty] | BA | [17 empty] | TOP
Inactive | TOP | TOP-005-1.1a | R4. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. | 2011-05-26 | 2011-09-30 | Medium | [15 empty] | PSE
Inactive | TOP | TOP-005-2 | R1. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | 2011-05-25 |  | N/A | N/A | N/A | The ISN data recipient failed to sign the NERC Confidentiality Agreement for “Electric System Reliability Data”. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-005-2 | R2. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | 2011-05-25 |  | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-005-2 | R3. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | 2011-05-25 |  | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. | [11 empty] | PSE
Inactive | TOP | TOP-005-2a | R1. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” | 2011-10-01 | 2017-03-31 |  | N/A | N/A | N/A | The ISN data recipient failed to sign the NERC Confidentiality Agreement for “Electric System Reliability Data”. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-005-2a | R2. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. | 2011-10-01 | 2017-03-31 |  | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-005-2a | R3. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. | 2011-10-01 | 2017-03-31 |  | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. | N/A | N/A | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. | [11 empty] | PSE
Inactive | TOP | TOP-005-3a | R1. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” |  | 2014-11-13 |  | N/A | N/A | N/A | The ISN data recipient failed to sign the NERC Confidentiality Agreement for “Electric System Reliability Data”. |  | BA | [9 empty] | PSE | [7 empty] | TOP
Inactive | TOP | TOP-005-3a | R2. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. |  | 2014-11-13 |  | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. |  |  | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-005-3a | R3. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. |  | 2014-11-13 |  | The responsible entity failed to provide any of the data requested by other Balancing Authorities or Transmission Operators. |  |  | The responsible entity failed to provide all of the data requested by its host Balancing Authority or Transmission Operator. | [11 empty] | PSE
Inactive | TOP | TOP-006-0 | R1. | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  | 2007-01-01 |  |  |  |  | The responsible entity failed to know the status of all generation and transmission resources available for use, even though said information was reported by the Generator Operator, Transmission Operator, or Balancing Authority. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-006-0 | R2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | 2007-01-01 |  | The responsible entity failed to monitor 3% or less of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 3% up to (and including) 6% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 6% up to (and including) 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-0 | R3. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. |  | 2007-01-01 |  |  |  | The responsible entity failed to provide appropriate technical information concerning protective relays to all of its operating personnel. | The responsible entity failed to provide appropriate technical information concerning protective relays to any of its operating personnel. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-0 | R4. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | 2007-01-01 |  |  |  | The responsible entity has either weather forecasts or past load patterns, available to predict the system’s near-term load pattern, but not both. | The responsible entity failed to have both weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-0 | R5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  | 2007-01-01 |  |  |  | The responsible entity used monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions, but does not have indication of the need for corrective action | The responsible entity failed to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-0 | R6. | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | 2007-01-01 |  |  |  |  | The responsible entity failed to use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-006-0 | R7. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  | 2007-01-01 |  |  |  |  | The responsible entity failed to monitor system frequency. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-1 | R1. | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. | 2007-06-18 | 2011-09-30 | Medium |  |  |  | The responsible entity failed to know the status of all generation and transmission resources available for use, even though said information was reported by the Generator Operator, Transmission Operator, or Balancing Authority. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-006-1 | R2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | 2007-06-18 | 2011-09-30 | High |  | The responsible entity monitors the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, but is not aware of the status of rotating and static reactive resources. | The responsible entity fails to monitor all of the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of all rotating and static reactive resources. | The responsible entity fails to monitor any of the applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-1 | R3. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. | 2007-06-18 | 2011-09-30 | Medium | The responsible entity failed to provide any of the appropriate technical information concerning protective relays to their operating personnel. |  |  | The responsible entity failed to provide all of the appropriate technical information concerning protective relays to their operating personnel. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-1 | R4. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. | 2007-06-18 | 2011-09-30 | Medium |  |  | The responsible entity has either weather forecasts or past load patterns, available to predict the system’s near-term load pattern, but not both. | The responsible entity failed to have both weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-1 | R5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. | 2007-06-18 | 2011-09-30 | Medium |  |  | The responsible entity used monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions, but does not have indication of the need for corrective action. | The responsible entity failed to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-1 | R6. | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. | 2007-06-18 | 2011-09-30 | High |  |  |  | The responsible entity failed to use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-006-1 | R7. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. | 2007-06-18 | 2011-09-30 | High |  |  |  | The responsible entity failed to monitor system frequency. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-2 | R1. | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. | 2011-10-01 | 2017-03-31 | Medium | N/A | N/A | N/A | The responsible entity failed to know the status of all generation and transmission resources available for use, even though said information was reported by the Generator Operator, Transmission Operator, or Balancing Authority. |  | BA |  |  |  |  | GOP | [12 empty] | TOP
Inactive | TOP | TOP-006-2 | R2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | 2011-10-01 | 2017-03-31 | High | The responsible entity failed to monitor 3% or less of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 3% up to (and including) 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 6% up to (and including) 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 9% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-2 | R3. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. | 2011-10-01 | 2017-03-31 | Medium | N/A | N/A | The responsible entity failed to provide appropriate technical information concerning protective relays to all of its operating personnel. | The responsible entity failed to provide appropriate technical information concerning protective relays to any of its operating personnel. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-2 | R4. | Each Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. | 2011-10-01 | 2017-03-31 | Medium | N/A | N/A | The responsible entity has either weather forecasts or past load patterns, available to predict the system’s near-term load pattern, but not both. | The responsible entity failed to have both weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-006-2 | R5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. | 2011-10-01 | 2017-03-31 | Medium | N/A | N/A | The responsible entity used monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions, but does not have indication of the need for corrective action. | The responsible entity failed to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-2 | R6. | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. | 2011-10-01 | 2017-03-31 | High | N/A | N/A | N/A | The responsible entity failed to use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-006-2 | R7. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. | 2011-10-01 | 2017-03-31 | High | N/A | N/A | N/A | The responsible entity failed to monitor system frequency. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-3 | R1. | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. |  | 2015-03-18 | Medium | N/A | N/A | N/A | The responsible entity failed to know the status of all generation and transmission resources available for use, even though said information was reported by the Generator Operator, Transmission Operator, or Balancing Authority. OR The Generator Operator failed to inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. OR The responsible entity failed to inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-006-3 | R2. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | 2015-03-18 | High | The responsible entity failed to monitor 5% or less of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 5% up to (and including) 10% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 10% up to (and including) 15% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | The responsible entity failed to monitor more than 15% of applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-3 | R3. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide its operating personnel with appropriate technical information concerning protective relays within the Reliability Coordinator Area, the Transmission Operator Area, and the Balancing Authority Area, respectively. |  | 2015-03-18 | Medium | The responsible entity failed to provide 5% or less of the appropriate technical information concerning protective relays to its operating personnel. | The responsible entity failed to provide more than 5% up to (and including) 10% of the appropriate technical information concerning protective relays to its operating personnel. | The responsible entity failed to provide more than 10% up to (and including) 15% of the appropriate technical information concerning protective relays to its operating personnel. | The responsible entity failed to provide more than 15% of the appropriate technical information concerning protective relays to its operating personnel. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-3 | R4. | Each Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | 2015-03-18 | Medium | N/A | N/A | The responsible entity has either weather forecasts or past load patterns, available to predict the system’s near-term load pattern, but not both. | The responsible entity failed to have both weather forecasts and past load patterns, available to predict the system’s near-term load pattern. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-006-3 | R5. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. |  | 2015-03-18 | Medium | N/A | N/A | The responsible entity used monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions, but does not have indication of the need for corrective action. | The responsible entity failed to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-006-3 | R6. | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | 2015-03-18 | High | N/A | N/A | N/A | The responsible entity failed to use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under both normal and emergency situations. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-006-3 | R7. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. |  | 2015-03-18 | High | N/A | N/A | N/A | The responsible entity failed to monitor system frequency. |  | BA | [10 empty] | RC | [6 empty] | TOP
Inactive | TOP | TOP-007-0 | R1. | A Transmission Operator shall inform its Reliability Coordinator when an IROL or SOL has been exceeded and the actions being taken to return the system to within limits. | 2007-06-18 | 2017-03-31 | High | [23 empty] | TOP
Inactive | TOP | TOP-007-0 | R2. | Following a Contingency or other event that results in an IROL violation, the Transmission Operator shall return its transmission system to within IROL as soon as possible, but not longer than 30 minutes. | 2007-06-18 | 2017-03-31 | High | [23 empty] | TOP
Inactive | TOP | TOP-007-0 | R3. | A Transmission Operator shall take all appropriate actions up to and including shedding firm load, or directing the shedding of firm load, in order to comply with Requirement R2. | 2007-06-18 | 2017-03-31 | High | [23 empty] | TOP
Inactive | TOP | TOP-007-0 | R4. | The Reliability Coordinator shall evaluate actions taken to address an IROL or SOL violation and, if the actions taken are not appropriate or sufficient, direct actions required to return the system to within limits. | 2007-06-18 | 2017-03-31 | High | [16 empty] | RC
Inactive | TOP | TOP-007-WECC-1 | R1. | When the actual power flow exceeds an SOL for a Transmission path, the Transmission Operators shall take immediate action to reduce the actual power flow across the path such that at no time shall the power flow for the Transmission path exceed the SOL for more than 30 minutes. [Time Horizon: Real-time Operations] | 2011-07-01 | 2014-06-17 | High | [23 empty] | TOP
Inactive | TOP | TOP-007-WECC-1 | R2. | The Transmission Operator shall not have the Net Scheduled Interchange for power flow over an interconnection or Transmission path above the path’s SOL when the Transmission Operator implements its real-time schedules for the next hour. For paths internal to a Transmission Operator Area that are not scheduled, this requirement does not apply. [Time Horizon: Real-time Operations] | 2011-07-01 | 2014-06-17 | Medium | [23 empty] | TOP
Inactive | TOP | TOP-007-WECC-1a | R1. | When the actual power flow exceeds an SOL for a Transmission path, the Transmission Operators shall take immediate action to reduce the actual power flow across the path such that at no time shall the power flow for the Transmission path exceed the SOL for more than 30 minutes. | 2014-06-18 | 2017-03-10 | High | [23 empty] | TOP
Inactive | TOP | TOP-007-WECC-1a | R2. | The Transmission Operator shall not have the Net Scheduled Interchange for power flow over an interconnection or Transmission path above the path’s SOL when the Transmission Operator implements its real-time schedules for the next hour. For paths internal to a Transmission Operator Area that are not scheduled, this requirement does not apply. | 2014-06-18 | 2017-03-10 | Medium | [23 empty] | TOP
Inactive | TOP | TOP-008-0 | R1. | The Transmission Operator experiencing or contributing to an IROL or SOL violation shall take immediate steps to relieve the condition, which may include shedding firm load. |  | 2007-01-01 | [24 empty] | TOP
Inactive | TOP | TOP-008-0 | R2. | Each Transmission Operator shall operate to prevent the likelihood that a disturbance, action, or inaction will result in an IROL or SOL violation in its area or another area of the Interconnection. In instances where there is a difference in derived operating limits, the Transmission Operator shall always operate the Bulk Electric System to the most limiting parameter. |  | 2007-01-01 | [24 empty] | TOP
Inactive | TOP | TOP-008-0 | R3. | The Transmission Operator shall disconnect the affected facility if the overload on a transmission facility or abnormal voltage or reactive condition persists and equipment is endangered. In doing so, the transmission Operator shall notify its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permits, otherwise, immediately thereafter. |  | 2007-01-01 | [24 empty] | TOP
Inactive | TOP | TOP-008-0 | R4. | The Transmission Operator shall have sufficient information and analysis tools to determine the cause(s) of SOL violations. This analysis shall be conducted in all operating timeframes. The Transmission operator shall use the results of these analyses to immediately mitigate the SOL violation. |  | 2007-01-01 | [24 empty] | TOP
Inactive | TOP | TOP-008-1 | R1. | The Transmission Operator experiencing or contributing to an IROL or SOL violation shall take immediate steps to relieve the condition, which may include shedding firm load. | 2007-06-18 | 2017-03-31 | High | [23 empty] | TOP
Inactive | TOP | TOP-008-1 | R2. | Each Transmission Operator shall operate to prevent the likelihood that a disturbance, action, or inaction will result in an IROL or SOL violation in its area or another area of the Interconnection. In instances where there is a difference in derived operating limits, the Transmission Operator shall always operate the Bulk Electric System to the most limiting parameter. | 2007-06-18 | 2017-03-31 | High |  |  |  | The Transmission Operator failed to operate to prevent the likelihood that a disturbance, action, or inaction would result in an IROL or SOL violation in its area or another area of the Interconnection. | [19 empty] | TOP
Inactive | TOP | TOP-008-1 | R3. | The Transmission Operator shall disconnect the affected facility if the overload on a transmission facility or abnormal voltage or reactive condition persists and equipment is endangered. In doing so, the Transmission Operator shall notify its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permits, otherwise, immediately thereafter. | 2007-06-18 | 2017-03-31 | High | [23 empty] | TOP
Inactive | TOP | TOP-008-1 | R4. | The Transmission Operator shall have sufficient information and analysis tools to determine the cause(s) of SOL violations. This analysis shall be conducted in all operating timeframes. The Transmission Operator shall use the results of these analyses to immediately mitigate the SOL violation. | 2007-06-18 | 2017-03-31 | Medium | [23 empty] | TOP
Inactive | TOP | TOP-010-1 | R1. | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | 2018-03-31 | Medium | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include one of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include two of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include any of the elements listed in Part 1.1 through Part 1.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. | [19 empty] | TOP
Inactive | TOP | TOP-010-1 | R2. | Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: |  | 2018-03-31 | Medium | N/A | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include one of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include two of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include any of the elements listed in Part 2.1 through Part 2.3; OR The Balancing Authority did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. |  | BA
Inactive | TOP | TOP-010-1 | R3. | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: |  | 2018-03-31 | Medium | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include one of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include two of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include any of the elements listed in Part 3.1 through Part 3.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. | [19 empty] | TOP
Inactive | TOP | TOP-010-1 | R4. | Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. |  | 2018-03-31 | Medium | N/A | N/A | The responsible entity has an alarm process monitor but the alarm process monitor did not provide notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor occurred. | The responsible entity does not have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. |  | BA | [17 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-010-1(i) | R1. | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: | 2018-04-01 |  | High | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include one of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include two of the elements listed in Part 1.1 through Part 1.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments did not include any of the elements listed in Part 1.1 through Part 1.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-010-1(i) | R2. | Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: | 2018-04-01 |  | High | N/A | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include one of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include two of the elements listed in Part 2.1 through Part 2.3. | The Balancing Authority's Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring did not include any of the elements listed in Part 2.1 through Part 2.3; OR The Balancing Authority did not implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. |  | BA
Mandatory Subject to Enforcement | TOP | TOP-010-1(i) | R3. | Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: | 2018-04-01 |  | Medium | N/A | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include one of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include two of the elements listed in Part 3.1 through Part 3.3. | The Transmission Operator's Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments did not include any of the elements listed in Part 3.1 through Part 3.3; OR The Transmission Operator did not implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. | [19 empty] | TOP
Mandatory Subject to Enforcement | TOP | TOP-010-1(i) | R4. | Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | 2018-04-01 |  | Medium | N/A | N/A | The responsible entity has an alarm process monitor but the alarm process monitor did not provide notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor occurred. | The responsible entity does not have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. |  | BA | [17 empty] | TOP
Inactive | TOP | TOP-STD-007-0 | WR1. | Operating Transfer Capability Limit Criteria Actual power flow and net scheduled power flow over an interconnection or transfer path shall be maintained within Operating Transfer Capability Limits (“OTC”). The OTC is the maximum amount of actual power that can be transferred over direct or parallel transmission elements comprising: • An interconnection from one Transmission Operator area to another Transmission Operator area; or • A transfer path within a Transmission Operator area. The net schedule over an interconnection or transfer path within a Transmission Operator area shall not exceed the OTC, regardless of the prevailing actual power flow on the interconnection or transfer path. a. Operating limits. No elements within the interconnection shall be scheduled above continuous operating limits. An element is defined as any generating unit, transmission line, transformer, bus, or piece of electrical equipment involved in the transfer of power within an interconnection. b. Stability. The interconnected power system shall remain stable upon loss of any one single element without system cascading that could result in the successive loss of additional elements. The system voltages shall be within acceptable limits defined in the WECC Reliability Criteria for Transmission System Planning. If a single event could cause loss of multiple elements, these shall be considered in lieu of a single element outage. This could occur in exceptional cases such as two lines on the same right-of-way next to an airport. In either case, loss of either single or multiple elements should not cause uncontrolled, widespread collapse of the interconnected power system. For purposes of this WECC Standard TOP-STD-007-0 - Operating Transfer Capability Section, stability shall include transient stability, post transient stability or dynamic stability whichever is most limiting to OTC. c. System contingency response. Following the outage and before adjustments can be made: (i) No remaining element shall exceed its short-time emergency rating. (ii) The steady-state system voltages shall be within emergency limits. The limiting event shall be determined by conducting power flow and stability studies while simulating various operating conditions. These studies shall be updated as system configurations introduce significant changes in the interconnection.(Source: WECC Criterion) | 2007-06-18 | 2011-06-30 | [24 empty] | TOP
Inactive | TPL | TPL-001-0 | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: | 2007-06-18 | 2009-05-12 | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-0 | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0_R1, the Planning Authority and Transmission Planner shall each: | 2007-06-18 | 2009-05-12 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-0 | R3. | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | 2007-06-18 | 2009-05-12 | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-0.1 | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: | 2009-05-13 | 2015-12-31 | High | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-0.1 | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0_R1, the Planning Authority and Transmission Planner shall each: | 2009-05-13 | 2015-12-31 | Medium | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-0.1 | R3. | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | 2009-05-13 | 2015-12-31 | Low | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-0.1(i) | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | 2015-12-31 | High | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-0.1(i) | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-0.1(i)_R1, the Planning Authority and Transmission Planner shall each: |  | 2015-12-31 | Medium | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-0.1(i) | R3. | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | 2015-12-31 | Low | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-1 | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | 2012-07-06 | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-1 | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-1_R1, the Planning Authority and Transmission Planner shall each: |  | 2012-07-06 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-1 | R3. | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | 2012-07-06 | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-2 | R1. | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. [See standard for further information regarding R1] |  | 2013-12-23 | Medium | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.6. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The resp | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-2 | R2. | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. [See standard for further information regarding R2] |  | 2013-12-23 | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-2 | R3. | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. [See standard for further information regarding R3] |  | 2013-12-23 | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform Continge | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perfor | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-2 | R4. | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. [See standard for further information regarding R4] |  | 2013-12-23 | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Continge | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base i | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-2 | R5. | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | 2013-12-23 | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-2 | R6. | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | 2013-12-23 | Low | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-2 | R7. | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | 2013-12-23 | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-2 | R8. | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. [See standard for further information regarding R8] |  | 2013-12-23 | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-3 | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that, with all transmission facilities in service and with normal (pre-contingency) operating procedures in effect, the Network can be operated to supply projected customer demands and projected Firm (non- recallable reserved) Transmission Services at all Demand levels over the range of forecast system demands, under the conditions defined in Category A of Table I. To be considered valid, the Planning Authority and Transmission Planner assessments shall: |  | 2014-12-31 | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-3 | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-001-1_R1, the Planning Authority and Transmission Planner shall each: |  | 2014-12-31 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-3 | R3. | The Planning Authority and Transmission Planner shall each document the results of these reliability assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | 2014-12-31 | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-4 | R1. | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. System models shall represent: | 2015-01-01 | 2023-06-30 | High | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.6. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.6. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The responsible entity’s System model did not use data consistent with that provided in accordance with the MOD-010 and MOD-012 standards and other sources, including items represented in the Corrective Action Plan. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-4 | R2. | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. | 2016-01-01 | 2023-06-30 | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-4 | R3. | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. | 2016-01-01 | 2023-06-30 | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R3, Part 3.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1 OR The responsible entity did not perform Contingency analysis as described in Requirement R3, Part 3.3. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies to determine that the BES meets the performance requirements for the P0 or P1 categories in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-4 | R4. | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. | 2016-01-01 | 2023-06-30 | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R4, Part 4.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R4, Part 4.3. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-4 | R5. | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. | 2016-01-01 | 2023-06-30 | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-4 | R6. | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. | 2016-01-01 | 2023-06-30 | Medium | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-4 | R7. | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. | 2015-01-01 | 2023-06-30 | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-4 | R8. | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. | 2016-01-01 | 2023-06-30 | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-5 | R1. | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-032 standard, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. |  | 2020-06-10 | High | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.5. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The responsible entity’s System model did not use data consistent with that provided in accordance with the MOD-032 standard and other sources, including items represented in the Corrective Action Plan. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-5 | R2. | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. |  | 2020-06-10 | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-5 | R3. | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | 2020-06-10 | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R3, Part 3.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R3, Part 3.3. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies to determine that the BES meets the performance requirements for the P0 or P1 categories in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-5 | R4. | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. |  | 2020-06-10 | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R4, Part 4.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R4, Part 4.3. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-5 | R5. | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. |  | 2020-06-10 | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-5 | R6. | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. |  | 2020-06-10 | Medium | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-5 | R7. | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. |  | 2020-06-10 | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-001-5 | R8. | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. |  | 2020-06-10 | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001-5.1 | R1. | Each Transmission Planner and Planning Coordinator shall maintain System models within its respective area for performing the studies needed to complete its Planning Assessment. The models shall use data consistent with that provided in accordance with the MOD-032 standard, supplemented by other sources as needed, including items represented in the Corrective Action Plan, and shall represent projected System conditions. This establishes Category P0 as the normal System condition in Table 1. | 2023-07-01 |  | High | The responsible entity’s System model failed to represent one of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent two of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent three of the Requirement R1, Parts 1.1.1 through 1.1.5. | The responsible entity’s System model failed to represent four or more of the Requirement R1, Parts 1.1.1 through 1.1.5. OR The responsible entity’s System model did not represent projected System conditions as described in Requirement R1. OR The responsible entity’s System model did not use data consistent with that provided in accordance with the MOD-032 standard and other sources, including items represented in the Corrective Action Plan. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001-5.1 | R2. | Each Transmission Planner and Planning Coordinator shall prepare an annual Planning Assessment of its portion of the BES. This Planning Assessment shall use current or qualified past studies (as indicated in Requirement R2, Part 2.6), document assumptions, and document summarized results of the steady state analyses, short circuit analyses, and Stability analyses. | 2023-07-01 |  | High | The responsible entity failed to comply with Requirement R2, Part 2.6. | The responsible entity failed to comply with Requirement R2, Part 2.3 or Part 2.8. | The responsible entity failed to comply with one of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, Part 2.5, or Part 2.7. | The responsible entity failed to comply with two or more of the following Parts of Requirement R2: Part 2.1, Part 2.2, Part 2.4, or Part 2.7. OR The responsible entity does not have a completed annual Planning Assessment. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001-5.1 | R3. | For the steady state portion of the Planning Assessment, each Transmission Planner and Planning Coordinator shall perform studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2. The studies shall be based on computer simulation models using data provided in Requirement R1. | 2023-07-01 |  | Medium | The responsible entity did not identify planning events as described in Requirement R3, Part 3.4 or extreme events as described in Requirement R3, Part 3.5. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for one of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R3, Part 3.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for two of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R3, Part 3.3. | The responsible entity did not perform studies as specified in Requirement R3, Part 3.1 to determine that the BES meets the performance requirements for three or more of the categories (P2 through P7) in Table 1. OR The responsible entity did not perform studies to determine that the BES meets the performance requirements for the P0 or P1 categories in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001-5.1 | R4. | For the Stability portion of the Planning Assessment, as described in Requirement R2, Parts 2.4 and 2.5, each Transmission Planner and Planning Coordinator shall perform the Contingency analyses listed in Table 1. The studies shall be based on computer simulation models using data provided in Requirement R1. 4.1. Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. 4.1.1. For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Remedial Action Scheme is not considered pulling out of synchronism. 4.1.2. For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. 4.1.3. For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. 4.2. Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event (s) shall be conducted. 4.3. Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall : 4.3.1. Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: 4.3.1.1. Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. 4.3.1.2. Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. 4.3.1.3. Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. 4.3.2. Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. 4.4. Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. 4.4.1. Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. 4.5. Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. | 2023-07-01 |  | Medium | The responsible entity did not identify planning events as described in Requirement R4, Part 4.4 or extreme events as described in Requirement R4, Part 4.5. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for one of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform studies as specified in Requirement R4, Part 4.2 to assess the impact of extreme events. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for two of the categories (P1 through P7) in Table 1. OR The responsible entity did not perform Contingency analysis as described in Requirement R4, Part 4.3. | The responsible entity did not perform studies as specified in Requirement R4, Part 4.1 to determine that the BES meets the performance requirements for three or more of the categories (P1 through P7) in Table 1. OR The responsible entity did not base its studies on computer simulation models using data provided in Requirement R1. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001-5.1 | R5. | Each Transmission Planner and Planning Coordinator shall have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, and the transient voltage response for its System. For transient voltage response, the criteria shall at a minimum, specify a low voltage level and a maximum length of time that transient voltages may remain below that level. | 2023-07-01 |  | Medium | N/A | N/A | N/A | The responsible entity does not have criteria for acceptable System steady state voltage limits, post-Contingency voltage deviations, or the transient voltage response for its System. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001-5.1 | R6. | Each Transmission Planner and Planning Coordinator shall define and document, within their Planning Assessment, the criteria or methodology used in the analysis to identify System instability for conditions such as Cascading, voltage instability, or uncontrolled islanding. | 2023-07-01 |  | Medium | N/A | N/A | N/A | The responsible entity failed to define and document the criteria or methodology for System instability used within its analysis as described in Requirement R6. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001-5.1 | R7. | Each Planning Coordinator, in conjunction with each of its Transmission Planners, shall determine and identify each entity’s individual and joint responsibilities for performing the required studies for the Planning Assessment. | 2023-07-01 |  | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with each of its Transmission Planners, failed to determine and identify individual or joint responsibilities for performing required studies. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-001-5.1 | R8. | Each Planning Coordinator and Transmission Planner shall distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 calendar days of completing its Planning Assessment, and to any functional entity that has a reliability related need and submits a written request for the information within 30 days of such a request. 8.1. If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | 2023-07-01 |  | Medium | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 90 days but less than or equal to 120 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 30 days but less than or equal to 40 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 120 days but less than or equal to 130 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 40 days but less than or equal to 50 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 130 days but less than or equal to 140 days following its completion. OR, The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 50 days but less than or equal to 60 days following the request. | The responsible entity distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners but it was more than 140 days following its completion. OR The responsible entity did not distribute its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners. OR The responsible entity distributed its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing but it was more than 60 days following the request. OR The responsible entity did not distribute its Planning Assessment results to functional entities having a reliability related need who requested the Planning Assessment in writing. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-0 | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: | 2007-06-18 | 2010-04-22 | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-0 | R2. | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: | 2007-06-18 | 2010-04-22 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-0 | R3. | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. | 2007-06-18 | 2010-04-22 | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-0a | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: | 2010-04-23 | 2011-10-23 | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-0a | R2. | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: | 2010-04-23 | 2011-10-23 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-0a | R3. | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. | 2010-04-23 | 2011-10-23 | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-0b | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: | 2011-10-24 | 2015-12-31 | High | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-0b | R2. | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: | 2011-10-24 | 2015-12-31 | Medium | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-0b | R3. | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. | 2011-10-24 | 2015-12-31 | Low | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-0(i)b | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | 2015-12-31 | [15 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-0(i)b | R2. | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0(i)b_R1, the Planning Authority and Transmission Planner shall each: |  | 2015-12-31 | [15 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-0(i)b | R3. | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | 2015-12-31 | [15 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-1b | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | 2012-07-06 | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-1b | R2. | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-1_R1, the Planning Authority and Transmission Planner shall each: |  | 2012-07-06 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-1b | R3. | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | 2012-07-06 | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-2b | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | 2014-12-31 | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-2b | R2. | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: |  | 2014-12-31 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-002-2b | R3. | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | 2014-12-31 | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-0 | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I. The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: See standard for table. | 2007-06-18 | 2010-04-22 | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-0 | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: | 2007-06-18 | 2010-04-22 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-0 | R3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | 2007-06-18 | 2010-04-22 | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-0a | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: | 2010-04-23 | 2013-06-19 | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-0a | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: | 2010-04-23 | 2013-06-19 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-0a | R3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | 2010-04-23 | 2013-06-19 | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-0b | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: | 2013-06-20 | 2015-12-31 | High | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-0b | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: | 2013-06-20 | 2015-12-31 | Medium | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-0b | R3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | 2013-06-20 | 2015-12-31 | Low | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-0(i)b | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | 2015-12-31 | High | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-0(i)b | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0(i)b_R1, the Planning Authority and Transmission Planner shall each: |  | 2015-12-31 | Medium | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-0(i)b | R3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | 2015-12-31 | Low | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-1a | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | 2012-07-06 | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-1a | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-1_R1, the Planning Authority and Transmission Planner shall each: |  | 2012-07-06 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-1a | R3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | 2012-07-06 | Low | N/A | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-2a | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | 2014-12-31 | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-2a | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | 2014-12-31 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-2a | R3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | 2014-12-31 | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-2b | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: |  | 2013-12-23 | High | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-2b | R2. | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: |  | 2013-12-23 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-003-2b | R3. | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | 2013-12-23 | Low |  | The responsible entity documented the results of its reliability assessments and corrective plans but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments and corrective plans AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organizat | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-004-0 | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: | 2007-06-18 | 2013-06-19 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-004-0 | R2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | 2007-06-18 | 2013-06-19 | Low |  | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization |  | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-004-0a | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: | 2013-06-20 | 2015-12-31 | Medium | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-004-0a | R2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | 2013-06-20 | 2015-12-31 | Low | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-004-0(i)a | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | 2015-12-31 | Medium | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-004-0(i)a | R2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | 2015-12-31 | Low | [14 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-004-1 | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | 2012-07-06 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-004-1 | R2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | 2012-07-06 | Low | N/A | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-004-2 | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | 2014-12-31 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-004-2 | R2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | 2014-12-31 | Low | N/A | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-004-2a | R1. | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: |  | 2013-12-23 | Medium | The responsible entity is non-compliant with 25% or less of the sub-components. | The responsible entity is non-compliant with more than 25% but less than 50% of the sub-components. | The responsible entity is non-compliant with 50% or more but less than 75% of the sub-components. | The responsible entity is non-compliant with 75% or more of the sub-components. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-004-2a | R2. | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. |  | 2013-12-23 | Low | N/A | The responsible entity documented the results of its reliability assessments but did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | N/A | The responsible entity DID NOT document the results of its annual reliability assessments AND did not annually provided them to its respective NERC Regional Reliability Organization(s) as required by the Regional Reliability Organization | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-005-0 | R1. | Each Regional Reliability Organization shall annually conduct reliability assessments of its respective existing and planned Regional Bulk Electric System (generation and transmission facilities) for: |  | 2014-12-31 | Medium | [19 empty] | RRO
Inactive | TPL | TPL-005-0 | R2. | The Regional Reliability Organization shall provide its Regional and Inter-Regional seasonal, near-term, and longer-term reliability assessments to NERC on an annual basis. |  | 2014-12-31 | Low | [19 empty] | RRO
Inactive | TPL | TPL-005-0 | R3. | The Regional Reliability Organization shall perform special reliability assessments as requested by NERC or the NERC Board of Trustees under their specific directions and criteria. Such assessments may include, but are not limited to: |  | 2014-12-31 | Medium | [19 empty] | RRO
Inactive | TPL | TPL-006-0 | R1. | Each Regional Reliability Organization shall provide, as requested (seasonally, annually, or as otherwise specified) by NERC, system data, including past, existing, and future facility and Bulk Electric System data, reports, and system performance information, necessary to assess reliability and compliance with the NERC Reliability Standards and the respective Regional planning criteria. The facility and Bulk Electric System data, reports, and system performance information shall include, but not be limited to, one or more of the following types of information as outlined below: |  | 2009-04-15 | Medium | [19 empty] | RRO
Inactive | TPL | TPL-006-0.1 | R1. | Each Regional Reliability Organization shall provide, as requested (seasonally, annually, or as otherwise specified) by NERC, system data, including past, existing, and future facility and Bulk Electric System data, reports, and system performance information, necessary to assess reliability and compliance with the NERC Reliability Standards and the respective Regional planning criteria. The facility and Bulk Electric System data, reports, and system performance information shall include, but not be limited to, one or more of the following types of information as outlined below: |  | 2014-12-31 | Medium | [19 empty] | RRO
Inactive | TPL | TPL-007-1 | R1. | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s). | 2017-07-01 | 2019-06-30 | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planners in the Planning Coordinator’s planning area for maintaining models and performing the study or studies needed to complete GMD Vulnerability Assessment(s). | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-1 | R2. | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | 2018-07-01 | 2019-06-30 | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete GMD Vulnerability Assessment(s). | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-1 | R3. | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the benchmark GMD event described in Attachment 1. | 2022-01-01 | 2019-06-30 | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the benchmark GMD event described in Attachment 1 as required. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-1 | R4. | Each responsible entity, as determined in Requirement R1, shall complete a GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon once every 60 calendar months. This GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | 2022-01-01 | 2019-06-30 | High | The responsible entity completed a GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last GMD Vulnerability Assessment. | The responsible entity's completed GMD Vulnerability Assessment failed to satisfy one of elements listed in Requirement R4 Parts 4.1 through 4.3; OR The responsible entity completed a GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last GMD Vulnerability Assessment. | The responsible entity's completed GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4 Parts 4.1 through 4.3; OR The responsible entity completed a GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last GMD Vulnerability Assessment. | The responsible entity's completed GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4 Parts 4.1 through 4.3; OR The responsible entity completed a GMD Vulnerability Assessment, but it was more than 72 calendar months since the last GMD Vulnerability Assessment; OR The responsible entity does not have a completed GMD Vulnerability Assessment. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-1 | R5. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the transformer thermal impact assessment specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | 2019-01-01 | 2019-06-30 | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-1 | R6. | Each Transmission Owner and Generator Owner shall conduct a thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A per phase or greater. The thermal impact assessment shall: | 2021-01-01 | 2019-06-30 | Medium | The responsible entity failed to conduct a thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase; OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5. | The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5. OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5; OR The responsible entity failed to include one of the required elements as listed in Requirement R6 Parts 6.1 through 6.3. | The responsible entity failed to conduct a thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase; OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5; OR The responsible entity failed to include two of the required elements as listed in Requirement R6 Parts 6.1 through 6.3. | The responsible entity failed to conduct a thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase; OR The responsible entity conducted a thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5 Part 5.1 is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5; OR The responsible entity failed to include three of the required elements as listed in Requirement R6 Parts 6.1 through 6.3. | [5 empty] | GO | [12 empty] | TO
Inactive | TPL | TPL-007-1 | R7. | Each responsible entity, as determined in Requirement R1, that concludes, through the GMD Vulnerability Assessment conducted in Requirement R4, that their System does not meet the performance requirements of Table 1 shall develop a Corrective Action Plan addressing how the performance requirements will be met. The Corrective Action Plan shall: | 2022-01-01 | 2019-06-30 | High | N/A | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7 Parts 7.1 through 7.3. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7 Parts 7.1 through 7.3. | The responsible entity's Corrective Action Plan failed to comply with all three of the elements in Requirement R7 Parts 7.1 through 7.3; OR The responsible entity did not have a Corrective Action Plan as required by Requirement R7. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-2 | R1. | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | 2019-07-01 | 2019-06-30 | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-2 | R2. | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | 2019-07-01 | 2019-06-30 | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-2 | R3. | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1. | 2023-01-01 | 2019-06-30 | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 as required. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-2 | R4. | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | 2023-01-01 | 2019-06-30 | High | The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 72 calendar months since the last benchmark GMD Vulnerability Assessment; OR The responsible entity does not have a completed benchmark GMD Vulnerability Assessment. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-2 | R5. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | 2020-01-01 | 2019-06-30 | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; Or The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-2 | R6. | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: | 2022-01-01 | 2019-06-30 | Medium | The responsible entity failed to conduct a benchmark thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include one of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | [5 empty] | GO | [12 empty] | TO
Inactive | TPL | TPL-007-2 | R7. | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: | 2024-01-01 | 2019-06-30 | High | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with three of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with four or more of the elements in Requirement R7, Parts 7.1 through 7.5; OR The responsible entity did not have a Corrective Action Plan as required by Requirement R7. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-2 | R8. | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | 2023-01-01 | 2019-06-30 | High | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy one of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy two of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy four of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 72 calendar months since the last supplemental GMD Vulnerability Assessment; OR The responsible entity does not have a completed supplemental GMD Vulnerability Assessment. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-2 | R9. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | 2020-01-01 | 2019-06-30 | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-2 | R10. | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: | 2022-01-01 | 2019-06-30 | Medium | The responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1 OR The responsible entity failed to include one of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | [5 empty] | GO | [12 empty] | TO
Inactive | TPL | TPL-007-2 | R11. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. | 2021-07-01 | 2019-06-30 | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System Model. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-2 | R12. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | 2021-07-01 | 2019-06-30 | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-3 | R1. | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | 2019-07-01 | 2020-09-30 | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-3 | R2. | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | 2019-07-01 | 2020-09-30 | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-3 | R3. | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 | 2023-01-01 | 2020-09-30 | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 as required. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-3 | R4. | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | 2023-01-01 | 2020-09-30 | High | The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR onths since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 72 calendar months since the last benchmark GMD Vulnerability Assessment; OR The responsible entity does not have a completed benchmark GMD Vulnerability Assessment. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-3 | R5. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | 2020-01-01 | 2020-09-30 | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-3 | R6. | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: | 2022-01-01 | 2020-09-30 | Medium | The responsible entity failed to conduct a benchmark thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include one of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | [5 empty] | GO | [12 empty] | TO
Inactive | TPL | TPL-007-3 | R7. | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: | 2024-01-01 | 2020-09-30 | High | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with three of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with four or more of the elements in Requirement R7, Parts 7.1 through 7.5; OR The responsible entity did not have a Corrective Action Plan as required by Requirement R7. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-3 | R8. | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | 2023-01-01 | 2020-09-30 | High | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy one of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy two of elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity's completed supplemental GMD Vulnerability Assessment failed to satisfy four of the elements listed in Requirement R8, Parts 8.1 through 8.4; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 72 calendar months since the last supplemental GMD Vulnerability Assessment; OR The responsible entity does not have a completed supplemental GMD Vulnerability Assessment. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-3 | R9. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | 2020-01-01 | 2020-09-30 | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-3 | R10. | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: | 2022-01-01 | 2020-09-30 | Medium | The responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase;The responsible entity failed to conduct a supplemental thermal impact asseThe responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1 OR The responsible entity failed to include one of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | [5 empty] | GO | [12 empty] | TO
Inactive | TPL | TPL-007-3 | R11. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. | 2021-07-01 | 2020-09-30 | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System Model. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-3 | R12. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | 2021-07-01 | 2020-09-30 | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | [10 empty] | PCPA | [9 empty] | TP
Inactive | TPL | TPL-007-3 | D.A.7.3. | Include a timetable, subject to revision by the responsible entity in Part D.A.7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  | 2020-09-30 | [15 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | R1. | Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | 2020-10-01 |  | Low | N/A | N/A | N/A | The Planning Coordinator, in conjunction with its Transmission Planner(s), failed to determine and identify individual or joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | R2. | Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | 2020-10-01 |  | High | N/A | N/A | The responsible entity did not maintain either System models or GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | The responsible entity did not maintain both System models and GIC System models of the responsible entity’s planning area for performing the studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | R3. | Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 | 2023-01-01 |  | Medium | N/A | N/A | N/A | The responsible entity did not have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1 as required. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | R4. | Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | 2023-01-01 |  | High | The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR onths since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last benchmark GMD Vulnerability Assessment. | The responsible entity's completed benchmark GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R4, Parts 4.1 through 4.3; OR The responsible entity completed a benchmark GMD Vulnerability Assessment, but it was more than 72 calendar months since the last benchmark GMD Vulnerability Assessment; OR The responsible entity does not have a completed benchmark GMD Vulnerability Assessment. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | R5. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | 2020-10-01 |  | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | R6. | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: | 2022-01-01 |  | Medium | The responsible entity failed to conduct a benchmark thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include one of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | The responsible entity failed to conduct a benchmark thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase; OR The responsible entity conducted a benchmark thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R6, Parts 6.1 through 6.3. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | TPL | TPL-007-4 | R7. | Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: | 2024-01-01 |  | High | The responsible entity's Corrective Action Plan failed to comply with one of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with two of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity's Corrective Action Plan failed to comply with three of the elements in Requirement R7, Parts 7.1 through 7.5. | The responsible entity’s Corrective Action Plan failed to comply with four or more of the elements in Requirement R7, Parts 7.1 through 7.5; OR The responsible entity did not develop a Corrective Action Plan as required by Requirement R7. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | R8. | Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. | 2023-01-01 |  | High | The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 60 calendar months and less than or equal to 64 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity’s completed supplemental GMD Vulnerability Assessment failed to satisfy one of the elements listed in Requirement R8, Parts 8.1 through 8.3; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 64 calendar months and less than or equal to 68 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity’s completed supplemental GMD Vulnerability Assessment failed to satisfy two of the elements listed in Requirement R8, Parts 8.1 through 8.3; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 68 calendar months and less than or equal to 72 calendar months since the last supplemental GMD Vulnerability Assessment. | The responsible entity’s completed supplemental GMD Vulnerability Assessment failed to satisfy three of the elements listed in Requirement R8, Parts 8.1 through 8.3; OR The responsible entity completed a supplemental GMD Vulnerability Assessment, but it was more than 72 calendar months since the last supplemental GMD Vulnerability Assessment; OR The responsible entity does not have a completed supplemental GMD Vulnerability Assessment. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | R9. | Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: | 2020-10-01 |  | Medium | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 90 calendar days and less than or equal to 100 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 100 calendar days and less than or equal to 110 calendar days after receipt of a written request. | The responsible entity provided the effective GIC time series, GIC(t), in response to written request, but did so more than 110 calendar days after receipt of a written request. | The responsible entity did not provide the maximum effective GIC value to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area; OR The responsible entity did not provide the effective GIC time series, GIC(t), upon written request. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | R10. | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: | 2022-01-01 |  | Medium | The responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase;The responsible entity failed to conduct a supplemental thermal impact asseThe responsible entity failed to conduct a supplemental thermal impact assessment for 5% or less or one of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 24 calendar months and less than or equal to 26 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 5% up to (and including) 10% or two of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 26 calendar months and less than or equal to 28 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1 OR The responsible entity failed to include one of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 10% up to (and including) 15% or three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 28 calendar months and less than or equal to 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include two of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | The responsible entity failed to conduct a supplemental thermal impact assessment for more than 15% or more than three of its solely owned and jointly owned applicable BES power transformers (whichever is greater) where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase; OR The responsible entity conducted a supplemental thermal impact assessment for its solely owned and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A or greater per phase but did so more than 30 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1; OR The responsible entity failed to include three of the required elements as listed in Requirement R10, Parts 10.1 through 10.3. | [5 empty] | GO | [12 empty] | TO
Mandatory Subject to Enforcement | TPL | TPL-007-4 | R11. | Each responsible entity, as determined in Requirement R1, that concludes through the supplemental GMD Vulnerability Assessment conducted in Requirement R8 that their System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: | 2024-01-01 |  | High | The responsible entity’s Corrective Action Plan failed to comply with one of the elements in Requirement R11, Parts 11.1 through 11.5. | The responsible entity’s Corrective Action Plan failed to comply with two of the elements in Requirement R11, Parts 11.1 through 11.5. | The responsible entity’s Corrective Action Plan failed to comply with three of the elements in Requirement R11, Parts 11.1 through 11.5. | The responsible entity’s Corrective Action Plan failed to comply with four or more of the elements in Requirement R11, Parts 11.1 through 11.5; OR The responsible entity did not develop a Corrective Action Plan as required by Requirement R11. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | R12. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator's planning area or other part of the system included in the Planning Coordinator's GIC System model. | 2021-07-01 |  | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System Model. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | R13. | Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | 2021-07-01 |  | Low | N/A | N/A | N/A | The responsible entity did not implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | [10 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | D.A.7.4. | Be revised if the responsible entity is unable to implement the CAP within the timetable for implementation provided in Part D.A.7.3. The revised CAP shall document the following: | 2020-10-01 | [16 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | D.A.7.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.7.4 within 90 calendar days of revision. | 2020-10-01 | [16 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | D.A.11.3. | Include a timetable, subject to revision by the responsible entity in Part D.A.11.4, for implementing the selected actions from Part 11.1. The timetable shall: | 2020-10-01 | [16 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | D.A.11.4. | Be revised if the responsible entity is unable to implement the CAP within the timetable for implementation provided in Part D.A.11.3. The revised CAP shall document the following: | 2020-10-01 | [16 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | D.A.11.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.11.4 within 90 calendar days of revision. | 2020-10-01 | [16 empty] | PCPA | [9 empty] | TP
Mandatory Subject to Enforcement | TPL | TPL-007-4 | D.A.7.3. | Include a timetable, subject to revision by the responsible entity in Part D.A.7.4, for implementing the selected actions from Part 7.1. The timetable shall: | 2020-10-01 | [11 empty] | GO |  |  |  |  | PCPA | [7 empty] | TO |  | TP
Inactive | VAR | VAR-001-0 | R1. | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and MVAR flows within their individual areas and with the areas of neighboring Transmission Operators. |  | 2007-01-01 | [24 empty] | TOP
Inactive | VAR | VAR-001-0 | R2. | Each Transmission Operator shall acquire sufficient reactive resources within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | 2007-01-01 | [24 empty] | TOP
Inactive | VAR | VAR-001-0 | R3. | Each Purchasing-Selling Entity shall arrange for (self-provide or purchase) reactive resources to satisfy its reactive requirements identified by its Transmission Service Provider |  | 2007-01-01 | [16 empty] | PSE
Inactive | VAR | VAR-001-0 | R4. | The Transmission Operator shall know the status of all transmission reactive power resources, including the status of voltage regulators and power system stabilizers. |  | 2007-01-01 | [24 empty] | TOP
Inactive | VAR | VAR-001-0 | R5. | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | 2007-01-01 | [24 empty] | TOP
Inactive | VAR | VAR-001-0 | R6. | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. |  | 2007-01-01 | [24 empty] | TOP
Inactive | VAR | VAR-001-0 | R7. | Each Transmission Operator shall maintain reactive resources to support its voltage under first Contingency conditions. |  | 2007-01-01 | [24 empty] | TOP
Inactive | VAR | VAR-001-0 | R8. | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. |  | 2007-01-01 | [24 empty] | TOP
Inactive | VAR | VAR-001-0 | R9. | Each Generator Operator shall provide information to its Transmission Operator on the status of all generation reactive power resources, including the status of voltage regulators and power system stabilizers. |  | 2007-01-01 | [11 empty] | GOP | [12 empty] | TOP
Inactive | VAR | VAR-001-0 | R10. | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. |  | 2007-01-01 | [24 empty] | TOP
Inactive | VAR | VAR-001-1 | R1. | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. | 2007-06-18 | 2011-09-30 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-1 | R2. | Each Transmission Operator shall acquire sufficient reactive resources within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. | 2007-06-18 | 2011-09-30 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-1 | R3. | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. | 2007-06-18 | 2011-09-30 | Low | [23 empty] | TOP
Inactive | VAR | VAR-001-1 | R4. | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). | 2007-06-18 | 2011-09-30 | Medium |  |  |  | The Transmission Operator provide No evidence that voltage or Reactive Power schedules were provided to Generator Operators as required in R4. | [19 empty] | TOP
Inactive | VAR | VAR-001-1 | R5. | Each Purchasing-Selling Entity shall arrange for (self-provide or purchase) reactive resources to satisfy its reactive requirements identified by its Transmission Service Provider. | 2007-06-18 | 2011-09-30 | High | [15 empty] | PSE
Inactive | VAR | VAR-001-1 | R6. | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. | 2007-06-18 | 2011-09-30 | Medium | [23 empty] | TOP
Inactive | VAR | VAR-001-1 | R7. | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. | 2007-06-18 | 2011-09-30 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-1 | R8. | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area - including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding - to maintain system and Interconnection voltages within established limits. | 2007-06-18 | 2007-01-01 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-1 | R9. | Each Transmission Operator shall maintain reactive resources to support its voltage under first Contingency conditions. | 2007-06-18 | 2007-01-01 | High | The Transmission Operator maintains 95% or more of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 85% or more but less than 95% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains 75% or more but less then 85% of the reactive resources needed to support its voltage under first Contingency conditions. | The Transmission Operator maintains less than 75% of the reactive resources needed to support its voltage under first Contingency conditions. | [19 empty] | TOP
Inactive | VAR | VAR-001-1 | R10. | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. | 2007-06-18 | 2007-01-01 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-1 | R11. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | 2007-06-18 | 2011-09-30 | Low | [23 empty] | TOP
Inactive | VAR | VAR-001-1 | R12. | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. | 2007-06-18 | 2011-09-30 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-1a | R1. | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. |  | 2009-05-21 | [24 empty] | TOP
Inactive | VAR | VAR-001-1a | R2. | Each Transmission Operator shall acquire sufficient reactive resources within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. |  | 2009-05-21 | [24 empty] | TOP
Inactive | VAR | VAR-001-1a | R3. | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. |  | 2009-05-21 | [24 empty] | TOP
Inactive | VAR | VAR-001-1a | R4. | Each Transmission Operator shall specify a voltage or Reactive Power schedule 1 at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). |  | 2009-05-21 | [24 empty] | TOP
Inactive | VAR | VAR-001-1a | R5. | Each Purchasing-Selling Entity shall arrange for (self-provide or purchase) reactive resources to satisfy its reactive requirements identified by its Transmission Service Provider. |  | 2009-05-21 | [16 empty] | PSE
Inactive | VAR | VAR-001-1a | R6. | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. |  | 2009-05-21 | [24 empty] | TOP
Inactive | VAR | VAR-001-1a | R7. | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. |  | 2009-05-21 | [24 empty] | TOP
Inactive | VAR | VAR-001-1a | R8. | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area - including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding - to maintain system and Interconnection voltages within established limits. |  | 2009-05-21 | [24 empty] | TOP
Inactive | VAR | VAR-001-1a | R9. | Each Transmission Operator shall maintain reactive resources to support its voltage under first Contingency conditions. |  | 2009-05-21 | [24 empty] | TOP
Inactive | VAR | VAR-001-1a | R10. | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. | 2007-06-18 | 2011-09-30 | [24 empty] | TOP
Inactive | VAR | VAR-001-1a | R11. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | 2007-06-18 | 2011-09-30 | [24 empty] | TOP
Inactive | VAR | VAR-001-1a | R12. | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. | 2007-06-18 | 2011-09-30 | [24 empty] | TOP
Inactive | VAR | VAR-001-2 | R1. | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. | 2011-10-01 | 2013-12-31 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-2 | R2. | Each Transmission Operator shall acquire sufficient reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load – within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. | 2011-10-01 | 2013-12-31 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-2 | R3. | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. | 2011-10-01 | 2013-12-31 | Low | [23 empty] | TOP
Inactive | VAR | VAR-001-2 | R4. | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). | 2011-10-01 | 2013-12-31 | Medium | [23 empty] | TOP
Inactive | VAR | VAR-001-2 | R5. | Each Purchasing-Selling Entity and Load Serving Entity shall arrange for (self-provide or purchase) reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to satisfy its reactive requirements identified by its Transmission Service Provider. | 2011-10-01 | 2014-01-21 | High | [12 empty] | LSE |  |  | PSE
Inactive | VAR | VAR-001-2 | R6. | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. | 2011-10-01 | 2013-12-31 | Medium | [23 empty] | TOP
Inactive | VAR | VAR-001-2 | R7. | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. | 2011-10-01 | 2013-12-31 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-2 | R8. | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; controllable load; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. | 2011-10-01 | 2013-12-31 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-2 | R9. | Each Transmission Operator shall maintain reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to support its voltage under first Contingency conditions. | 2011-10-01 | 2013-12-31 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-2 | R10. | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. | 2011-10-01 | 2009-05-21 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-2 | R11. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | 2011-10-01 | 2009-05-21 | Low | [23 empty] | TOP
Inactive | VAR | VAR-001-2 | R12. | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. | 2011-10-01 | 2009-05-21 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-3 | R1. | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. | 2014-01-01 | 2014-09-30 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-3 | R2. | Each Transmission Operator shall acquire sufficient reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load – within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. | 2014-01-01 | 2014-09-30 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-3 | R3. | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. | 2014-01-01 | 2014-09-30 | Low | [23 empty] | TOP
Inactive | VAR | VAR-001-3 | R4. | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). | 2014-01-01 | 2014-09-30 | Medium | [23 empty] | TOP
Inactive | VAR | VAR-001-3 | R5. | Each Purchasing-Selling Entity and Load Serving Entity shall arrange for (self-provide or purchase) reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to satisfy its reactive requirements identified by its Transmission Service Provider. | 2014-01-01 | 2014-01-21 | High | [12 empty] | LSE |  |  | PSE
Inactive | VAR | VAR-001-3 | R6. | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. | 2014-01-01 | 2014-09-30 | Medium | [23 empty] | TOP
Inactive | VAR | VAR-001-3 | R7. | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. | 2014-01-01 | 2014-09-30 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-3 | R8. | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; controllable load; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. | 2014-01-01 | 2014-09-30 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-3 | R9. | Each Transmission Operator shall maintain reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; and controllable load– to support its voltage under first Contingency conditions. | 2014-01-01 | 2014-09-30 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-3 | R10. | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. | 2011-10-01 | 2013-12-31 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-3 | R11. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | 2013-06-20 | 2014-09-30 | [24 empty] | TOP
Inactive | VAR | VAR-001-3 | R12. | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. | 2013-06-20 | 2014-09-30 | High | [23 empty] | TOP
Inactive | VAR | VAR-001-3 | E.A.13 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. | 2014-01-01 | 2014-09-30 | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | [19 empty] | TOP
Inactive | VAR | VAR-001-3 | E.A.14 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. | 2014-01-01 | 2014-09-30 | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | [19 empty] | TOP
Inactive | VAR | VAR-001-3 | E.A.15 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. | 2014-01-01 | 2014-09-30 | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | [6 empty] | GOP
Inactive | VAR | VAR-001-3 | E.A.16 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. | 2014-01-01 | 2014-09-30 | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | [6 empty] | GOP
Inactive | VAR | VAR-001-3 | E.A.17 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. | 2013-06-20 | 2014-09-30 | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | [19 empty] | TOP
Inactive | VAR | VAR-001-3 | E.A.18 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: E.A.18.1. Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. E.A.18.2. Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. | 2013-06-20 | 2014-09-30 | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | [6 empty] | GOP
Inactive | VAR | VAR-001-4 | R1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. | 2014-10-01 | 2015-11-12 | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | [19 empty] | TOP
Inactive | VAR | VAR-001-4 | R2. | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | 2014-10-01 | 2015-11-12 | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | [19 empty] | TOP
Inactive | VAR | VAR-001-4 | R3. | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | 2014-10-01 | 2015-11-12 | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | [19 empty] | TOP
Inactive | VAR | VAR-001-4 | R4. | The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. | 2014-10-01 | 2015-11-12 | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | [19 empty] | TOP
Inactive | VAR | VAR-001-4 | R5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. | 2014-10-01 | 2015-11-12 | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. Or The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | [19 empty] | TOP
Inactive | VAR | VAR-001-4 | R6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | 2014-08-01 | 2015-11-12 | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | [19 empty] | TOP
Inactive | VAR | VAR-001-4 | E.A.13 | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: •A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. | 2014-08-01 | 2015-11-12 | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are online and part of the BES in the Transmission Operator Area. | [19 empty] | TOP
Inactive | VAR | VAR-001-4 | E.A.14 | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. •The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. | 2014-08-01 | 2015-11-12 | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | [19 empty] | TOP
Inactive | VAR | VAR-001-4 | E.A.15 | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. | 2014-08-01 | 2015-11-12 | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | [6 empty] | GOP
Inactive | VAR | VAR-001-4 | E.A.16 | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. | 2014-08-01 | 2015-11-12 | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | [6 empty] | GOP
Inactive | VAR | VAR-001-4 | E.A.17 | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. | 2014-01-01 | 2014-09-30 | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | [19 empty] | TOP
Inactive | VAR | VAR-001-4 | E.A.18 | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: E.A.18.1. Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. E.A.18.2. Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. | 2014-01-01 | 2014-09-30 | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | [6 empty] | GOP
Inactive | VAR | VAR-001-4.1 | E.A.13. | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. | 2017-09-26 | 2018-12-31 | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on- line and part of the BES in the Transmission Operator Area. | [19 empty] | TOP
Inactive | VAR | VAR-001-4.1 | E.A.14. | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. | 2017-09-26 | 2018-12-31 | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | [19 empty] | TOP
Inactive | VAR | VAR-001-4.1 | E.A.15. | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. | 2017-09-26 | 2018-12-31 | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | [6 empty] | GOP
Inactive | VAR | VAR-001-4.1 | E.A.16. | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. | 2017-09-26 | 2018-12-31 | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | [6 empty] | GOP
Inactive | VAR | VAR-001-4.1 | E.A.17. | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. | 2015-11-13 | 2017-09-25 | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | [19 empty] | TOP
Inactive | VAR | VAR-001-4.1 | E.A.18. | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the Automatic Voltage Regulators (AVR) to manage MVar loading: | 2015-11-13 | 2017-09-25 | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | [6 empty] | GOP
Inactive | VAR | VAR-001-4.1 | R1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. | 2015-11-13 | 2017-09-25 | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | [19 empty] | TOP
Inactive | VAR | VAR-001-4.1 | R2. | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | 2015-11-13 | 2017-09-25 | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | [19 empty] | TOP
Inactive | VAR | VAR-001-4.1 | R3. | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | 2015-11-13 | 2017-09-25 | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | [19 empty] | TOP
Inactive | VAR | VAR-001-4.1 | R4. | The Transmission Operator shall specify the criteria that will exempt generators from: 1) following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. | 2015-11-13 | 2017-09-25 | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | [19 empty] | TOP
Inactive | VAR | VAR-001-4.1 | R5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. | 2015-11-13 | 2017-09-25 | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. OR The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | [19 empty] | TOP
Inactive | VAR | VAR-001-4.1 | R6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | 2014-10-01 | 2015-11-12 | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | [19 empty] | TOP
Inactive | VAR | VAR-001-4.2 | E.A.13. | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. | 2019-01-01 | 2018-12-31 | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | [19 empty] | TOP
Inactive | VAR | VAR-001-4.2 | E.A.14. | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its Area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. | 2019-01-01 | 2018-12-31 | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | [19 empty] | TOP
Inactive | VAR | VAR-001-4.2 | E.A.15. | Each Generator Operator shall convert each voltage schedule specified in Requirement E.A.13 into the voltage set point for the generator excitation system. | 2019-01-01 | 2018-12-31 | Medium | The Generator Operator failed to convert at least one voltage schedule in Requirement E.A.13 into the voltage set point for the AVR for less than 25% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 25% or more but less than 50% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 50% or more but less than 75% of the voltage schedules. | The Generator Operator failed to convert the voltage schedules in Requirement E.A.13 into the voltage set point for the AVR for 75% or more of the voltage schedules. | [6 empty] | GOP
Inactive | VAR | VAR-001-4.2 | E.A.16. | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. | 2019-01-01 | 2018-12-31 | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | [6 empty] | GOP
Inactive | VAR | VAR-001-4.2 | E.A.17. | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. | 2015-11-13 | 2017-09-25 | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | [19 empty] | TOP
Inactive | VAR | VAR-001-4.2 | E.A.18. | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: | 2015-11-13 | 2017-09-25 | Medium | N/A | The Generator Operator did not meet the control loop specifications in EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in EA18.1 through EA18.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | [6 empty] | GOP
Inactive | VAR | VAR-001-4.2 | R1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. | 2017-09-26 | 2018-12-31 | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | [19 empty] | TOP
Inactive | VAR | VAR-001-4.2 | R2. | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | 2017-09-26 | 2018-12-31 | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | [19 empty] | TOP
Inactive | VAR | VAR-001-4.2 | R3. | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | 2017-09-26 | 2018-12-31 | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | [19 empty] | TOP
Inactive | VAR | VAR-001-4.2 | R4. | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. | 2017-09-26 | 2018-12-31 | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | [19 empty] | TOP
Inactive | VAR | VAR-001-4.2 | R5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. | 2017-09-26 | 2018-12-31 | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. OR The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | [19 empty] | TOP
Inactive | VAR | VAR-001-4.2 | R6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | 2015-11-13 | 2017-09-25 | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | [19 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001-5 | E.A.13. | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. | 2018-10-15 |  | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | [19 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001-5 | E.A.14. | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. | 2018-10-15 |  | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | [19 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001-5 | E.A.15. | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. | 2018-10-15 |  | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | [6 empty] | GOP
Mandatory Subject to Enforcement | VAR | VAR-001-5 | E.A.16. | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. | 2018-10-15 |  | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | [19 empty] | TOP
Inactive | VAR | VAR-001-5 | E.A.17. | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: | 2017-09-26 | 2018-12-31 | Medium | N/A | The Generator Operator did not meet the control loop specifications in E.A.17.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in E.A.17.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in E.A.17.1 through E.A.17.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | [6 empty] | GOP
Mandatory Subject to Enforcement | VAR | VAR-001-5 | R1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. | 2019-01-01 |  | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | [19 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001-5 | R2. | Each Transmission Operator shall schedule sufficient reactive resources to regulate voltage levels under normal and Contingency conditions. Transmission Operators can provide sufficient reactive resources through various means including, but not limited to, reactive generation scheduling, transmission line and reactive resource switching, and using controllable load. | 2019-01-01 |  | High | N/A | N/A | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an SOL. | The Transmission Operator does not schedule sufficient reactive resources as necessary to avoid violating an IROL. | [19 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001-5 | R3. | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. | 2019-01-01 |  | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | [19 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001-5 | R4. | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. | 2019-01-01 |  | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | [19 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001-5 | R5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. | 2019-01-01 |  | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. Or The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | [19 empty] | TOP
Mandatory Subject to Enforcement | VAR | VAR-001-5 | R6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | 2019-01-01 |  | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | [19 empty] | TOP
Inactive | VAR | VAR-001-6 | E.A.13. | Each Transmission Operator shall issue any one of the following types of voltage schedules to the Generator Operators for each of their generation resources that are on-line and part of the Bulk Electric System within the Transmission Operator Area: • A voltage set point with a voltage tolerance band and a specified period. • An initial volt-ampere reactive output or initial power factor output with a voltage tolerance band for a specified period that the Generator Operator uses to establish a generator bus voltage set point. • A voltage band for a specified period. |  | 2020-05-14 | Medium | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to at least one generation resource but less than or equal to 5% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 5% but less than or equal to 10% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 10% but less than or equal to 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | For the specified period, the Transmission Operator did not issue one of the voltage schedules listed in E.A.13 to more than 15% of the generation resources that are on-line and part of the BES in the Transmission Operator Area. | [19 empty] | TOP
Inactive | VAR | VAR-001-6 | E.A.14. | Each Transmission Operator shall provide one of the following voltage schedule reference points for each generation resource in its area to the Generator Operator. • The generator terminals. • The high side of the generator step-up transformer. • The point of interconnection. • A location designated by mutual agreement between the Transmission Operator and Generator Operator. |  | 2020-05-14 | Medium | The Transmission Operator did not provide a voltage schedule reference point for at least one but less than or equal to 5% of the generation resources in the Transmission Operator area. | The Transmission Operator did not provide a voltage schedule reference point for more than 5% but less than or equal to 10% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not a voltage schedule reference point for more than 10% but less than or equal to 15% of the generation resources in the Transmission Operator Area. | The Transmission Operator did not provide a voltage schedule reference point for more than 15% of the generation resources in the Transmission Operator Area. | [19 empty] | TOP
Inactive | VAR | VAR-001-6 | E.A.15. | Each Generator Operator shall provide its voltage set point conversion methodology from the point in Requirement E.A.14 to the generator terminals within 30 calendar days of request by its Transmission Operator. |  | 2020-05-14 | Low | The Generator Operator provided its voltage set point conversion methodology greater than 30 days but less than or equal to 60 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Transmission Operator. | The Generator Operator provided its voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Transmission Operator. | The Generator Operator did not provide its voltage set point conversion methodology within 120 days of a request by the Transmission Operator. | [6 empty] | GOP
Inactive | VAR | VAR-001-6 | E.A.16. | Each Transmission Operator shall provide to the Generator Operator, within 30 calendar days of a request for data by the Generator Operator, its transmission equipment data and operating data that supports development of the voltage set point conversion methodology. |  | 2020-05-14 | Low | The Transmission Operator provided its data to support development of the voltage set point conversion methodology than 30 days but less than or equal to 60 days of a request by the Generator Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 60 days but less than or equal to 90 days of a request by the Generator. Operator. | The Transmission Operator provided its data to support development of the voltage set point conversion methodology greater than 90 days but less than or equal to 120 days of a request by the Generator. Operator. | The Transmission Operator did not provide its data to support development of the voltage set point conversion methodology within 120 days of a request by the Generator Operator. | [19 empty] | TOP
Inactive | VAR | VAR-001-6 | E.A.17. | Each Generator Operator shall meet the following control loop specifications if the Generator Operator uses control loops external to the automatic voltage regulators (AVR) to manage Mvar loading: | 2019-01-01 | 2020-05-14 | Medium | N/A | The Generator Operator did not meet the control loop specifications in E.A.17.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in E.A.17.1 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | The Generator Operator did not meet the control loop specifications in E.A.17.1 through E.A.17.2 when the Generator Operator uses control loop external to the AVR to manage Mvar loading. | [6 empty] | GOP
Inactive | VAR | VAR-001-6 | R1. | Each Transmission Operator shall specify a system voltage schedule (which is either a range or a target value with an associated tolerance band) as part of its plan to operate within System Operating Limits and Interconnection Reliability Operating Limits. |  | 2020-05-14 | High | N/A | N/A | N/A | The Transmission Operator does not specify a system voltage schedule (which is either a range or a target value with an associated tolerance band). | [19 empty] | TOP
Inactive | VAR | VAR-001-6 | R2. | Reserved. |  | 2020-05-14
Inactive | VAR | VAR-001-6 | R3. | Each Transmission Operator shall operate or direct the Real-time operation of devices to regulate transmission voltage and reactive flow as necessary. |  | 2020-05-14 | High | N/A | N/A | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an SOL. | The Transmission Operator does not operate or direct any real-time operation of devices as necessary to avoid violating an IROL. | [19 empty] | TOP
Inactive | VAR | VAR-001-6 | R4. | Each Transmission Operator shall specify the criteria that will exempt generators: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any associated notifications. |  | 2020-05-14 | Low | N/A | N/A | The Transmission Operator has exemption criteria and notified the Generator Operator, but the Transmission Operator does not have evidence of the notification to the Generator Operator. | The Transmission Operator does not have exemption criteria. | [19 empty] | TOP
Inactive | VAR | VAR-001-6 | R5. | Each Transmission Operator shall specify a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) at either the high voltage side or low voltage side of the generator step-up transformer at the Transmission Operator’s discretion. |  | 2020-05-14 | Medium | N/A | The Transmission Operator does not provide the criteria for voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) after 30 days of a request. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to all Generator Operators. | The Transmission Operator does not provide voltage or Reactive Power schedules (which is either a range or a target value with an associated tolerance band) to any Generator Operators. Or The Transmission Operator does not provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | [19 empty] | TOP
Inactive | VAR | VAR-001-6 | R6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. |  | 2020-05-14 | Low | The Transmission Operator does not provide either the technical justification or timeframe for changing generator step-up tap settings. | N/A | N/A | The Transmission Operator does not provide the technical justification and the timeframe for changing generator step-up tap settings. | [19 empty] | TOP
Inactive | VAR | VAR-002-1 | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. | 2007-08-02 | 2008-08-26 | Medium | [10 empty] | GOP
Inactive | VAR | VAR-002-1 | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings. [1] as directed by the Transmission Operator | 2007-08-02 | 2008-08-26 | Medium | [10 empty] | GOP
Inactive | VAR | VAR-002-1 | R3. | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: | 2007-08-02 | 2008-08-26 | Medium | [10 empty] | GOP
Inactive | VAR | VAR-002-1 | R4. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. | 2007-08-02 | 2008-08-26 | Low | [9 empty] | GO
Inactive | VAR | VAR-002-1 | R5. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. | 2007-06-18 | 2008-08-26 | Medium | [9 empty] | GO
Inactive | VAR | VAR-002-1.1a | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. | 2009-05-13 | 2010-09-15 | Medium | [10 empty] | GOP
Inactive | VAR | VAR-002-1.1a | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings ) as directed by the Transmission Operator. | 2009-05-13 | 2010-09-15 | Medium | [10 empty] | GOP
Inactive | VAR | VAR-002-1.1a | R3. | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: | 2009-05-13 | 2010-09-15 | Medium | [10 empty] | GOP
Inactive | VAR | VAR-002-1.1a | R4. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. | 2009-05-13 | 2010-09-15 | Low | [9 empty] | GO
Inactive | VAR | VAR-002-1.1a | R5. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. | 2007-08-02 | 2008-08-26 | Medium | [9 empty] | GO
Inactive | VAR | VAR-002-1.1b | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. | 2010-09-16 | 2013-06-30 | Medium | [10 empty] | GOP
Inactive | VAR | VAR-002-1.1b | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings ) as directed by the Transmission Operator. | 2010-09-16 | 2013-06-30 | Medium | [10 empty] | GOP
Inactive | VAR | VAR-002-1.1b | R3. | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: | 2010-09-16 | 2013-06-30 | Medium | [10 empty] | GOP
Inactive | VAR | VAR-002-1.1b | R4. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. | 2010-09-16 | 2013-06-30 | Low | [9 empty] | GO
Inactive | VAR | VAR-002-1.1b | R5. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. | 2009-05-13 | 2010-09-15 | Medium | [9 empty] | GO
Inactive | VAR | VAR-002-1a | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator. | 2008-08-27 | 2009-05-12 | [11 empty] | GOP
Inactive | VAR | VAR-002-1a | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power output (within applicable Facility Ratings [see footnote in standard]) as directed by the Transmission Operator. | 2008-08-27 | 2009-05-12 | [11 empty] | GOP
Inactive | VAR | VAR-002-1a | R3. | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: | 2008-08-27 | 2009-05-12 | [11 empty] | GOP
Inactive | VAR | VAR-002-1a | R4. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. | 2008-08-27 | 2009-05-12 | [10 empty] | GO
Inactive | VAR | VAR-002-1a | R5. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. | 2010-09-16 | 2013-06-30 |  | The Generator Owner had one (1) incident of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment rating, a regulat | The Generator Owner had more than one (1) incident but less than or equal to five (5) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would n | The Generator Owner had more than five (5) incident but less than or equal to ten (10) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would | The Generator Owner had more than ten (10) incidents of failing to change the step-up transformer tap settings in accordance with the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment ratin | [5 empty] | GO
Inactive | VAR | VAR-002-2b | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator of one of the following: -That the generator is being operated in start-up or shutdown mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or -That the generator is not being operated in the automatic voltage control mode for a reason other than start-up or shutdown. | 2013-07-01 | 2014-09-30 | Medium | N/A | N/A | N/A | The responsible entity did not operate each generator in the automatic voltage control mode and failed to notify the Transmission Operator as identified in R1. | [6 empty] | GOP
Inactive | VAR | VAR-002-2b | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within applicable Facility Ratings as directed by the Transmission Operator. | 2013-07-01 | 2014-09-30 | Medium | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for up to and including 45 minutes. | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for more than 45 minutes up to and including 60 minutes. OR When a generator’s automatic voltage regulator is out of service, the Generator Operator failed to use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. OR The Generator Operator failed to provide an explanation of why the voltage schedule could not be met. | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for more than 60 minutes up to and including 75 minutes. | When directed by the Transmission Operator to maintain the generator voltage or reactive power schedule the Generator Operator failed to meet the directed values for more than 75 minutes. OR When a generator’s automatic voltage regulator is out of service, the Generator Operator failed to use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator and the Generator Operator failed to provide an explanation of why the voltage schedule could not be met. | [6 empty] | GOP
Inactive | VAR | VAR-002-2b | R3. | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: | 2013-07-01 | 2014-09-30 | Medium | N/A | N/A | The Generator Operator failed to notify the Transmission Operator within 30 minutes of the information as specified in either R3.1 or R3.2 | The Generator Operator failed to notify the Transmission Operator within 30 minutes of the information as specified in both R3.1 and R3.2 | [6 empty] | GOP
Inactive | VAR | VAR-002-2b | R4. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. | 2013-07-01 | 2014-09-30 | Low | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner one of the types of data as specified in R4.1.1 or R 4.1.2 or 4.1.3 or 4.1.4 OR The information was provided in more than 30, but less than or equal to 35 calendar days of the request. | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner two of the types of data as specified in R4.1.1 or R 4.1.2 or 4.1.3 or 4.1.4 OR The information was provided in more than 35, but less than or equal to 40 calendar days of the request. | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner three of the types of data as specified in R4.1.1 or R 4.1.2 or 4.1.3 or 4.1.4 OR The information was provided in more than 40, but less than or equal to 45 calendar days of the request. | The Responsible entity failed to provide to its associated Transmission Operator and Transmission Planner any of the types of data as specified in R4.1.1 and R 4.1.2 and 4.1.3 and 4.1.4 OR The information was provided in more than 45 calendar days of the request. | [5 empty] | GO
Inactive | VAR | VAR-002-2b | R5. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. | 2008-08-27 | 2009-05-12 | Medium | N/A | N/A | N/A | The responsible entity failed to ensure that transformer tap positions were changed according to the specifications provided by the Transmission Operator when said actions would not have violated safety, an equipment rating, a regulatory requirement, or a statutory requirement. | [5 empty] | GO
Inactive | VAR | VAR-002-3 | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up, shutdown, or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | 2014-10-01 | 2015-05-28 | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. | [6 empty] | GOP
Inactive | VAR | VAR-002-3 | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within each generating Facility’s capabilities ) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. | 2014-10-01 | 2015-05-28 | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. | [6 empty] | GOP
Inactive | VAR | VAR-002-3 | R3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change | 2014-10-01 | 2015-05-28 | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. | [6 empty] | GOP
Inactive | VAR | VAR-002-3 | R4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. | 2014-10-01 | 2015-05-28 | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. | [6 empty] | GOP
Inactive | VAR | VAR-002-3 | R5. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. | 2013-07-01 | 2014-09-30 | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | [5 empty] | GO
Inactive | VAR | VAR-002-3 | R6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. | 2014-08-01 | 2015-05-28 | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. | [5 empty] | GO
Inactive | VAR | VAR-002-4 | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | 2015-05-29 | 2017-09-25 | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. | [6 empty] | GOP
Inactive | VAR | VAR-002-4 | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator.[See standard for additional information.] | 2015-05-29 | 2017-09-25 | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. | [6 empty] | GOP
Inactive | VAR | VAR-002-4 | R3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. | 2015-05-29 | 2017-09-25 | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. | [6 empty] | GOP
Inactive | VAR | VAR-002-4 | R4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | 2015-05-29 | 2017-09-25 | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. | [6 empty] | GOP
Inactive | VAR | VAR-002-4 | R5. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [See standard for additional information.] | 2015-05-29 | 2017-09-25 | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | [5 empty] | GO
Inactive | VAR | VAR-002-4 | R6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [See standard for additional information.] | 2014-10-01 | 2015-05-28 | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. | [5 empty] | GO
Mandatory Subject to Enforcement | VAR | VAR-002-4.1 | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: • That the generator is being operated in start-up, shutdown, or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. Footnote: Start-up is deemed to have ended when the generator is ramped up to its minimum continuously sustainable load and the generator is prepared for continuous operation. Shutdown is deemed to begin when the generator is ramped down to its minimum continuously sustainable load and the generator is prepared to go offline. | 2017-09-26 |  | Medium | N/A | N/A | N/A | Unless exempted, the Generator Operator did not operate each generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator, and failed to provide the required notifications to Transmission Operator as identified in Requirement R1. | [6 empty] | GOP
Mandatory Subject to Enforcement | VAR | VAR-002-4.1 | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within each generating Facility’s capabilities ) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. (Footnote: The voltage or Reactive Power schedule is a target value with a tolerance band or a voltage or Reactive Power range communicated by the Transmission Operator to the Generator Operator. Generating Facility capability may be established by test or other means, and may not be sufficient at times to pull the system voltage within the schedule tolerance band. Also, when a generator is operating in manual control, Reactive Power capability may change based on stability considerations.) | 2017-09-26 |  | Medium | N/A | N/A | The Generator Operator did not have a conversion methodology when it monitors voltage at a location different from the schedule provided by the Transmission Operator. | The Generator Operator did not maintain the voltage or Reactive Power schedule as instructed by the Transmission Operator and did not make the necessary notifications required by the Transmission Operator. OR The Generator Operator did not have an operating AVR, and the responsible entity did not use an alternative method for controlling voltage. OR The Generator Operator did not modify voltage when directed, and the responsible entity did not provide any explanation. | [6 empty] | GOP
Mandatory Subject to Enforcement | VAR | VAR-002-4.1 | R3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. | 2017-09-26 |  | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of the status change. | [6 empty] | GOP
Mandatory Subject to Enforcement | VAR | VAR-002-4.1 | R4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | 2017-09-26 |  | Medium | N/A | N/A | N/A | The Generator Operator did not make the required notification within 30 minutes of becoming aware of the capability change. | [6 empty] | GOP
Mandatory Subject to Enforcement | VAR | VAR-002-4.1 | R5. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. | 2017-09-26 |  | Low | N/A | N/A | The Generator Owner failed to provide its associated Transmission Operator and Transmission Planner one of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | The Generator Owner failed to provide to its associated Transmission Operator and Transmission Planner two or more of the types of data specified in Requirement R5 Parts 5.1.1, 5.1.2, and 5.1.3. | [5 empty] | GO
Mandatory Subject to Enforcement | VAR | VAR-002-4.1 | R6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. | 2017-09-26 |  | Low | N/A | N/A | N/A | The Generator Owner did not ensure the tap changes were made according the Transmission Operator’s specifications. OR The Generator Owner failed to perform the tap changes, and the Generator Owner did not provide technical justification for why it could not comply with the Transmission Operator specifications. | [5 empty] | GO
Inactive | VAR | VAR-002-WECC-1 | R1. | Generator Operators and Transmission Operators shall have AVR in service and in automatic voltage control mode 98% of all operating hours for synchronous generators or synchronous condensers. Generator Operators and Transmission Operators may exclude hours for R1.1 through R1.10 to achieve the 98% requirement. [Time Horizon: Operations Assessment] | 2011-07-01 | 2015-03-31 | Medium | [10 empty] | GOP | [12 empty] | TOP
Inactive | VAR | VAR-002-WECC-1 | R2. | Generator Operators and Transmission Operators shall have documentation identifying the number of hours excluded for each requirement in R1.1 through R1.10. [Time Horizon: Operations Assessment] | 2011-06-27 | 2015-03-31 | Low | [10 empty] | GOP | [12 empty] | TOP
Inactive | VAR | VAR-002-WECC-2 | R1. | Generator Operators and Transmission Operators shall have AVR in service and in automatic voltage control mode 98% of all operating hours for synchronous generators or synchronous condensers. Generator Operators and Transmission Operators may exclude hours for R1.1 through R1.10 to achieve the 98% requirement. [See Standard for additional information.] | 2015-04-01 | 2018-09-05 | Medium | There shall be a Lower Level of non-compliance if AVR is in service less than 98% but at least 90% or more of all hours during which the synchronous generating unit or synchronous condenser is on line for each calendar quarter. | There shall be a Moderate Level of non- compliance if AVR is in service less than 90% but at least 80% or more of all hours during which the synchronous generating unit or synchronous condenser is on line for each calendar quarter. | There shall be a High Level of non- compliance if AVR is in service less than 80% but at least 70% or more of all hours during which the synchronous generating unit or synchronous condenser is on line for each calendar quarter. | There shall be a Severe Level of non- compliance if AVR is in service less than 70% of all hours during which the synchronous generating unit or synchronous condenser is on line for each calendar quarter. | [6 empty] | GOP | [12 empty] | TOP
Inactive | VAR | VAR-501-WECC-1 | R1. | Generator Operators shall have PSS in service 98% of all operating hours for synchronous generators equipped with PSS. Generator Operators may exclude hours for R1.1 through R1.12 to achieve the 98% requirement. [Time Horizon: Operations Assessment] | 2011-07-01 | 2015-03-31 | Medium | [10 empty] | GOP
Inactive | VAR | VAR-501-WECC-1 | R2. | Generator Operators shall have documentation identifying the number of hours excluded for each requirement in R1.1 through R1.12. [Time Horizon: Operations Assessment] | 2011-06-27 | 2015-03-31 | Low | [10 empty] | GOP
Inactive | VAR | VAR-501-WECC-2 | R1. | Generator Operators shall have PSS in service 98% of all operating hours for synchronous generators equipped with PSS. Generator Operators may exclude hours for R1.1 through R1.12 to achieve the 98% requirement. [See Standard for additional information.] | 2015-04-01 | 2017-06-30 | Medium | There shall be a Lower Level of non-compliance if PSS is in service less than 98% but at least 90% or more of all hours during which the synchronous generating unit is on line for each calendar quarter. | There shall be a Moderate Level of non-compliance if PSS is in service less than 90% but at least 80% or more of all hours during which the synchronous generating unit is on line for each calendar quarter. | There shall be a High Level of non- compliance if is in service less than 80% but at least 70% or more of all hours during which the synchronous generating unit is on line for each calendar quarter. | There shall be a Severe Level of non- compliance if PSS is in service less than 70% of all hours during which the synchronous generating unit is on line for each calendar quarter. | [6 empty] | GOP
Inactive | VAR | VAR-501-WECC-3 | R1. | Each Generator Owner shall provide to its Transmission Operator, the Generator Owner’s written Operating Procedure or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the Automatic Voltage Regulator (AVR), within 180 days of any of the following events: • The effective date of this standard; • The PSS’s Commercial Operation date, or; • Any changes to the PSS operating specifications. | 2017-07-01 | 2017-09-25 | Low | N/A | N/A | N/A | The Generator Owner failed to provide its PSS operating specifications to the Transmission Planner as required in Requirement R1. | [5 empty] | GO
Inactive | VAR | VAR-501-WECC-3 | R2. | Each Generator Operator shall have its PSS in service while synchronized, except during any of the following: • Component failure • Testing of a Bulk Electric System Element affecting or affected by the PSS • Maintenance • As agreed upon by the Generator Operator and the Transmission Operator A PSS that is out of service for less than 30 minutes does not create a violation of this Requirement, regardless of cause. | 2017-07-01 | 2017-09-25 | Medium | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 30 minutes but less than 60 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 60 minutes but less than 120 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 120 minutes but less than 180 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 180 minutes. | [6 empty] | GOP
Inactive | VAR | VAR-501-WECC-3 | R3. | Each Generator Owner shall tune its PSS to meet the following inter-area mode criteria, except as specified in Requirement R3, Part 3.5 below: | 2017-07-01 | 2017-09-25 | Medium | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, two times or fewer during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, three times during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, four times during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, five times or more during the audit period. | [5 empty] | GO
Inactive | VAR | VAR-501-WECC-3 | R4. | Each Generator Owner shall install and complete start-up testing of a PSS on its generator within 180 days of either of the following events: • The Generator Owner connects a generator to the BES, after achieving Commercial Operation, and after the Effective Date of this standard. • The Generator Owner replaces the voltage regulator on its existing excitation system, after achieving Commercial Operation for its generator that is connected to the BES, and after the Effective Date of this standard. | 2017-04-28 | 2017-09-25 | Medium | N/A | N/A | N/A | The Generator Owner failed to install on its generator a PSS, as required in Requirement R4. | [5 empty] | GO
Inactive | VAR | VAR-501-WECC-3 | R5. | Each Generator Owner shall repair or replace a PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications stated in Requirement R3. | 2017-04-28 | 2017-09-25 | Medium | N/A | N/A | N/A | The Generator Owner failed to repair or replace a non-operational PSS as required in Requirement R5. | [5 empty] | GO
Pending Inactive | VAR | VAR-501-WECC-3.1 | R1. | Each Generator Owner shall provide to its Transmission Operator, the Generator Owner’s written Operating Procedure or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the Automatic Voltage Regulator (AVR), within 180 days of any of the following events: • The effective date of this standard; • The PSS’s Commercial Operation date; or • Any changes to the PSS operating specifications. | 2017-09-26 | 2024-03-31 | Low | N/A | N/A | N/A | The Generator Owner failed to provide its PSS operating specifications to the Transmission Operator as required in Requirement R1. | [5 empty] | GO
Pending Inactive | VAR | VAR-501-WECC-3.1 | R2. | Each Generator Operator shall have its PSS in service while synchronized, except during any of the following: • Component failure • Testing of a Bulk Electric System Element affecting or affected by the PSS • Maintenance • As agreed upon by the Generator Operator and the Transmission Operator A PSS that is out of service for less than 30 minutes does not create a violation of this Requirement, regardless of cause. | 2017-09-26 | 2024-03-31 | Medium | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 30 minutes but less than 60 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 60 minutes but less than 120 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 120 minutes but less than 180 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 180 minutes. | [6 empty] | GOP
Pending Inactive | VAR | VAR-501-WECC-3.1 | R3. | Each Generator Owner shall tune its PSS to meet the following inter-area mode criteria, except as specified in Requirement R3, Part 3.5 below: | 2017-09-26 | 2024-03-31 | Medium | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, two times or fewer during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, three times during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, four times during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, five times or more during the audit period. | [5 empty] | GO
Pending Inactive | VAR | VAR-501-WECC-3.1 | R4. | Each Generator Owner shall install and complete start-up testing of a PSS on its generator within 180 days of either of the following events: • The Generator Owner connects a generator to the BES, after achieving Commercial Operation, and after the Effective Date of this standard. • The Generator Owner replaces the voltage regulator on its existing excitation system, after achieving Commercial Operation for its generator that is connected to the BES, and after the Effective Date of this standard. | 2017-09-26 | 2024-03-31 | Medium | N/A | N/A | N/A | The Generator Owner failed to install on its generator a PSS, as required in Requirement R4. | [5 empty] | GO
Pending Inactive | VAR | VAR-501-WECC-3.1 | R5. | Each Generator Owner shall repair or replace a PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications stated in Requirement R3. | 2017-09-26 | 2024-03-31 | Medium | N/A | N/A | N/A | The Generator Owner failed to repair or replace a non-operational PSS as required in Requirement R5. | [5 empty] | GO
Mandatory Subject to Enforcement | VAR | VAR-501-WECC-4 | R1. | Each Generator Owner shall provide to its Transmission Operator, the Generator Owner’s written Operating Procedure or other document(s) describing those known circumstances during which the Generator Owner’s PSS will not be providing an active signal to the Automatic Voltage Regulator (AVR), within 180 days of any of the following events: [Violation Risk Factor: Low] [Time Horizon: Planning Horizon] · The effective date of this standard; · The PSS’s Commercial Operation date; or · Any changes to the PSS operating specifications. | 2024-04-01 |  | Low | NA | NA | NA | The Generator Owner failed to provide its PSS operating specifications to the Transmission Operator as required in Requirement R1. | [5 empty] | GO | GOP
Mandatory Subject to Enforcement | VAR | VAR-501-WECC-4 | R2. | Each Generator Operator shall have its PSS in service while synchronized, except during any of the following: - Component failure - Testing of a Bulk Electric System Element affecting or affected by the PSS - Maintenance - As agreed upon by the Generator Operator and the Transmission Operator A PSS that is out of service for less than 30 minutes does not create a violation of this Requirement, regardless of cause. | 2024-04-01 |  | Medium | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 30 minutes but less than 60 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 60 minutes but less than 120 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 120 minutes but less than 180 minutes. | Each Generator Operator not having its PSS in service while synchronized in accordance with Requirement R2, for more than 180 minutes. | [5 empty] | GO | GOP
Mandatory Subject to Enforcement | VAR | VAR-501-WECC-4 | R3. | Each Generator Owner shall tune its PSS to meet the following inter-area mode criteria, except as specified in Requirement R3, Part 3.5 below | 2024-04-01 |  | Medium | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, two times or fewer during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, three times during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, four times during the audit period. | The Generator Owner’s PSS failed to meet any of the required performances in Requirement R3, five times or more during the audit period. | [5 empty] | GO | GOP
Mandatory Subject to Enforcement | VAR | VAR-501-WECC-4 | R4. | Each Generator Owner shall install and complete start-up testing of a PSS on its generator within 180 days of either of the following events: - The Generator Owner connects a generator to the BES, after achieving Commercial Operation, and after the Effective Date of this standard. - The Generator Owner replaces the voltage regulator on its existing excitation system, after achieving Commercial Operation for its generator that is connected to the BES, and after the Effective Date of this standard. | 2024-04-01 |  | Medium | NA | NA | NA | The Generator Owner failed to install on its generator a PSS, as required in Requirement R4. | [5 empty] | GO | GOP
Mandatory Subject to Enforcement | VAR | VAR-501-WECC-4 | R5. | Each Generator Owner shall repair or replace a PSS within 24 months of that PSS becoming incapable of meeting the tuning specifications stated in Requirement R3. | 2024-04-01 |  | Medium | NA | NA | NA | The Generator Owner failed to repair or replace a non-operational PSS as required in Requirement R5. | [5 empty] | GO | GOP
Inactive | VAR | VAR-STD-002a-1 | WR1. | Automatic voltage control equipment on synchronous generators shall be kept in service at all times, unless one of the exemptions listed in Section C (Measures) applies, with outages coordinated to minimize the number out of service at any one time. All synchronous generators with automatic voltage control equipment shall normally be operated in voltage control mode and set to respond effectively to voltage deviations. (Source: WECC Criterion) | 2007-06-18 | 2011-06-30 | [11 empty] | GOP
Inactive | VAR | VAR-STD-002b-1 | WR1. | Power System Stabilizers on generators shall be kept in service at all times, unless one of the exemptions listed in Section C (Measures) applies, and shall be properly tuned in accordance with WECC requirements. (Source: WECC Criterion) | 2007-06-18 | 2011-06-30 | [11 empty] | GOP