## Part
Standard | Requirement | Parent Part | Part Number | Part ID | Part Displaystring | Part Language | Additional Information | Part Applicability | BA | DP | DP-UFLS | FRSG | GO | GOP | IA | LSE | NERC | PCPA | PSE | RC | RE | RP | RRO | RRSG | RSG | TO | TOP | TP | TSP | Measure | Effective Date of Part | Pending Inactive? | Inactive Date of Part | Additional Effective Date Details | Additional Applicability Details | RankId (Part) | Region - Jurisdiction | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10 | 92 |  | 1. | 93 | BAL-003-0b R1.1. | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10 | 92 |  | 2. | 94 | BAL-003-0b R1.2. | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10 | 95 |  | 1. | 96 | BAL-003-0b R2.1. | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10 | 95 |  | 2. | 97 | BAL-003-0b R2.2. | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10 | 99 |  | 1. | 100 | BAL-003-0b R4.1. | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10 | 99 |  | 2. | 101 | BAL-003-0b R4.2. | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10 | 102 |  | 1. | 103 | BAL-003-0b R5.1. | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1151 |  | 1. | 1152 | MOD-001-1 R2.1. | Hourly values for at least the next 48 hours. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1151 |  | 2. | 1153 | MOD-001-1 R2.2. | Daily values for at least the next 31 calendar days. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1151 |  | 3. | 1154 | MOD-001-1 R2.3. | Monthly values for at least the next 12 months (months 2-13). |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1155 | 1157 | 1. | 1158 | MOD-001-1 R3.2.1. | How confirmed Transmission reservations, expected Interchange and internal counterflow are addressed in firm and non-firm ATC or AFC calculations. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1155 | 1157 | 2. | 1159 | MOD-001-1 R3.2.2. | A rationale for that accounting specified in R3.2. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1155 | 1163 | 1. | 1164 | MOD-001-1 R3.6.1. | The criteria used to determine when an outage that is in effect part of a day impacts a daily calculation. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  | 361000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1155 | 1163 | 2. | 1165 | MOD-001-1 R3.6.2. | The criteria used to determine when an outage that is in effect part of a month impacts a monthly calculation. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  | 362000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1155 | 1163 | 3. | 1166 | MOD-001-1 R3.6.3. | How outages from other Transmission Service Providers that can not be mapped to the Transmission model used to calculate transfer or Flowgate capability are addressed. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  | 363000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1155 |  | 1. | 1156 | MOD-001-1 R3.1. | Information describing how the selected methodology (or methodologies) has been implemented, in such detail that, given the same information used by the Transmission Service Provider, the results of the ATC or AFC calculations can be validated. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1155 |  | 2. | 1157 | MOD-001-1 R3.2. | A description of the manner in which the Transmission Service Provider will account for counterflows including: |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1155 |  | 3. | 1160 | MOD-001-1 R3.3. | The identity of the Transmission Operators and Transmission Service Providers from which the Transmission Service Provider receives data for use in calculating ATC or AFC. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1155 |  | 4. | 1161 | MOD-001-1 R3.4. | The identity of the Transmission Service Providers and Transmission Operators to which it provides data for use in calculating transfer or Flowgate capability. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1155 |  | 5. | 1162 | MOD-001-1 R3.5. | A description of the allocation processes listed below that are applicable to the Transmission Service Provider: • Processes used to allocate transfer or Flowgate capability among multiple lines or sub-paths within a larger ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities among multiple owners or users of an ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities between Transmission Service Providers to address issues such as forward looking congestion management and seams coordination. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1155 |  | 6. | 1163 | MOD-001-1 R3.6. | A description of how generation and transmission outages are considered in transfer or Flowgate capability calculations, including: |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 360000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1167 |  | 1. | 1168 | MOD-001-1 R4.1. | Each Planning Coordinator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1167 |  | 2. | 1169 | MOD-001-1 R4.2. | Each Reliability Coordinator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1167 |  | 3. | 1170 | MOD-001-1 R4.3. | Each Transmission Operator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1167 |  | 4. | 1171 | MOD-001-1 R4.4. | Each Planning Coordinator adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1167 |  | 5. | 1172 | MOD-001-1 R4.5. | Each Reliability Coordinator adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1167 |  | 6. | 1173 | MOD-001-1 R4.6. | Each Transmission Service Provider whose area is adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 460000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1177 |  | 1. | 1178 | MOD-001-1 R8.1. | Hourly values, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the ATC equation. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1177 |  | 2. | 1179 | MOD-001-1 R8.2. | Daily values, once per day. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1177 |  | 3. | 1180 | MOD-001-1 R8.3. | Monthly values, once per week. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1181 | 1182 | 1. | 1183 | MOD-001-1 R9.1.1. | If the Transmission Service Provider uses the data requested in its transfer or Flowgate capability calculations, it shall make the data used available |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  | 911000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1181 | 1182 | 2. | 1184 | MOD-001-1 R9.1.2. | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, but maintains that data, it shall make that data available. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  | 912000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1181 | 1182 | 3. | 1185 | MOD-001-1 R9.1.3. | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, and does not maintain that data, it shall not be required to make that data available. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  | 913000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1181 |  | 1. | 1182 | MOD-001-1 R9.1. | The Transmission Service Provider shall make its own current data available, in the format maintained by the Transmission Service Provider, for up to 13 months into the future (subject to confidentiality and security requirements). |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
100 | 1181 |  | 2. | RP-2021-06-07-0000001 | MOD-001-1 R9.2. | This data shall be made available by the Transmission Provider on the schedule specified by the requestor (but no more frequently than once per hour, unless mutually agreed to by the requester and the provider). |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
102 | 1190 |  | 1. | 1191 | MOD-003-0 R1.1. | The name, telephone number and email address of a contact person to whom concerns are to be addressed. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
102 | 1190 |  | 2. | 1192 | MOD-003-0 R1.2. | The amount of time it will take for a response. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
102 | 1190 |  | 3. | 1193 | MOD-003-0 R1.3. | The manner in which the response will be communicated (e.g., email, letter, telephone, etc). |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
102 | 1190 |  | 4. | RP-2021-06-07-0000002 | MOD-003-0 R1.4. | What recourse a customer has if the response is deemed unsatisfactory. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
103 | 1196 |  | 1. | 1197 | MOD-004-0 R1.1. | Specify that the method used by each Regional Reliability Organization member to determine its generation reliability requirements as the basis for CBM shall be consistent with its generation planning criteria. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
103 | 1196 |  | 10. | 1198 | MOD-004-0 R1.10. | Describe the inclusion or exclusion rationale for generation reserve sharing arrangements in the CBM values. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
103 | 1196 |  | 2. | 1199 | MOD-004-0 R1.2. | Specify the frequency of calculation of the generation reliability requirement and associated CBM values. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
103 | 1196 |  | 3. | 1200 | MOD-004-0 R1.3. | Require that generation unit outages considered in a Transmission Service Provider’s CBM calculation be restricted to those units within the Transmission Service Provider’s system. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
103 | 1196 |  | 4. | 1201 | MOD-004-0 R1.4. | Require that CBM be preserved only on the Transmission Service Provider’s System where the Load-Serving Entity’s Load is located (i.e., CBM is an import quantity only). |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
103 | 1196 |  | 5. | 1202 | MOD-004-0 R1.5. | Describe the inclusion or exclusion rationale for generation resources of each Load-Serving Entity including those generation resources not directly connected to the Transmission Service Provider’s system but serving Load-Serving Entity loads connected to the Transmission Service Provider’s system. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
103 | 1196 |  | 6. | 1203 | MOD-004-0 R1.6. | Describe the inclusion or exclusion rationale for generation connected to the Transmission Service Provider’s system but not obligated to serve Native/Network Load connected to the Transmission Service Provider’s system. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
103 | 1196 |  | 7. | 1204 | MOD-004-0 R1.7. | Describe the formal process and rationale for the Regional Reliability Organization to grant any variances to individual Transmission Service Providers from the Regional Reliability Organization’s CBM methodology. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
103 | 1196 |  | 8. | 1205 | MOD-004-0 R1.8. | Specify the relationship of CBM to the generation reliability requirement and the allocation of the CBM values to the appropriate transmission facilities. The sum of the CBM values allocated to all interfaces shall not exceed that portion of the generation reliability requirement that is to be provided by outside resources. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
103 | 1196 |  | 9. | 1206 | MOD-004-0 R1.9. | Describe the inclusion or exclusion rationale for the loads of each Load-Serving Entity, including interruptible demands and buy-through contracts (type of service contract that offers the customer the option to be interrupted or to accept a higher rate for service under certain conditions). |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1208 |  | 1. | 1209 | MOD-004-1 R1.1. | The process through which a Load-Serving Entity within a Balancing Authority Area associated with the Transmission Service Provider, or the Resource Planner associated with that Balancing Authority Area, may ensure that its need for Transmission capacity to be set aside as CBM will be reviewed and accommodated by the Transmission Service Provider to the extent Transmission capacity is available. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider that maintains CBM shall produce its CBMID evidencing inclusion of all information specified in R1. (R1) | 2010-02-08 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1208 |  | 2. | 1210 | MOD-004-1 R1.2. | The procedure and assumptions for establishing CBM for each Available Transfer Capability (ATC) Path or Flowgate. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider that maintains CBM shall produce its CBMID evidencing inclusion of all information specified in R1. (R1) | 2010-02-08 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1208 |  | 3. | 1211 | MOD-004-1 R1.3. | The procedure for a Load-Serving Entity or Balancing Authority to use Transmission capacity set aside as CBM, including the manner in which the Transmission Service Provider will manage situations where the requested use of CBM exceeds the amount of CBM available. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider that maintains CBM shall produce its CBMID evidencing inclusion of all information specified in R1. (R1) | 2010-02-08 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1219 |  | 1. | 1215 | MOD-004-1 R3.1. | Using one or more of the following to determine the GCIR:  Loss of Load Expectation (LOLE) studies  Loss of Load Probability (LOLP) studies  Deterministic risk-analysis studies  Reserve margin or resource adequacy requirements established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities |  | LSE | [7 empty] | LSE | [13 empty] | Each Load-Serving Entity that determined a need for Transmission capacity to be set aside as CBM shall provide evidence (including studies and/or requirements) that it met the criteria in R3. (R3) | 2010-02-08 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1219 |  | 2. | 1216 | MOD-004-1 R3.2. | Identifying expected import path(s) or source region(s). |  | LSE | [7 empty] | LSE | [13 empty] | Each Load-Serving Entity that determined a need for Transmission capacity to be set aside as CBM shall provide evidence (including studies and/or requirements) that it met the criteria in R3. (R3) | 2010-02-08 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1222 |  | 1. | 1217 | MOD-004-1 R4.1. | Using one or more of the following to determine the GCIR:  Loss of Load Expectation (LOLE) studies  Loss of Load Probability (LOLP) studies  Deterministic risk-analysis studies  Reserve margin or resource adequacy requirements established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities |  | RP | [13 empty] | RP | [7 empty] | Each Resource Planner that determined a need for Transmission capacity to be set aside as CBM shall provide evidence (including studies and/or requirements) that it met the criteria in R4. (R4) | 2010-02-08 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1222 |  | 2. | RP-2021-07-06-0000003 | MOD-004-1 R4.2. | Identifying expected import path(s) or source region(s). |  | RP | [13 empty] | RP | [7 empty] | Each Resource Planner that determined a need for Transmission capacity to be set aside as CBM shall provide evidence (including studies and/or requirements) that it met the criteria in R4. (R4) | 2011-04-01 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1225 |  | 1. | 1226 | MOD-004-1 R5.1. | Reflect consideration of each of the following if available: Any studies (as described in R3.1) performed by Load-Serving Entities for loads within the Transmission Service Provider’s area; Any studies (as described in R4.1) performed by Resource Planners for loads within the Transmission Service Provider’s area; Any reserve margin or resource adequacy requirements for loads within the Transmission Service Provider’s area established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities |  | TSP | [20 empty] | TSP | Each Transmission Service Provider that maintains CBM shall provide evidence (such as studies, requirements, and dated CBM values) that it established 13 months of CBM values consistent with the requirements in R5.1 and allocated the values consistent with the requirements in R5.2. (Note that CBM values may legitimately be zero.) (R5) | 2010-02-08 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1225 |  | 2. | 1227 | MOD-004-1 R5.2. | Be allocated as follows: For ATC Paths, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners; For Flowgates, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners and the distribution factors associated with those paths or regions, as determined by the Transmission Service Provider |  | TSP | [20 empty] | TSP | Each Transmission Service Provider that maintains CBM shall provide evidence (such as studies, requirements, and dated CBM values) that it established 13 months of CBM values consistent with the requirements in R5.1 and allocated the values consistent with the requirements in R5.2. (Note that CBM values may legitimately be zero.) (R5) | 2010-02-08 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1228 |  | 1. | 1229 | MOD-004-1 R6.1. | Reflect consideration of each of the following if available: Any studies (as described in R3.1) performed by Load-Serving Entities for loads within the Transmission Planner’s area; Any studies (as described in R4.1) performed by Resource Planners for loads within the Transmission Planner’s area; Any reserve margin or resource adequacy requirements for loads within the Transmission Planner’s area established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities |  | TP | [19 empty] | TP |  | Each Transmission Planner with an associated Transmission Service Provider that maintains CBM shall provide evidence (such as studies, requirements, and dated CBM values) that it established CBM values for years two through ten consistent with the requirements in R6.1 and allocated the values consistent with the requirements in R6.2. Inclusion of GCIR based on R6.1 and R6.2 within the transmission base case meets this requirement. (Note that CBM values may legitimately be zero.) (R6) | 2010-02-08 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1228 |  | 2. | 1230 | MOD-004-1 R6.2. | Be allocated as follows: For ATC Paths, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners; For Flowgates, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners and the distribution factors associated with those paths or regions, as determined by the Transmission Planner. |  | TP | [19 empty] | TP |  | Each Transmission Planner with an associated Transmission Service Provider that maintains CBM shall provide evidence (such as studies, requirements, and dated CBM values) that it established CBM values for years two through ten consistent with the requirements in R6.1 and allocated the values consistent with the requirements in R6.2. Inclusion of GCIR based on R6.1 and R6.2 within the transmission base case meets this requirement. (Note that CBM values may legitimately be zero.) (R6) | 2010-02-08 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1233 |  | 1. | RP-2021-07-06-0000004 | MOD-004-1 R9.1. | Each of its associated Transmission Operators within 30 calendar days of their making a request for the data. |  | TP, TSP | [19 empty] | TP | TSP | Each Transmission Service Provider that maintains CBM and each Transmission Planner shall provide evidence including copies of dated requests for data supporting the calculation of CBM along with other evidences such as copies of electronic messages or other evidence to show that it provided the required entities with copies of the supporting data, including any models, used for allocating CBM as specified in R9. (R9) | 2011-04-01 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1233 |  | 2. | 1235 | MOD-004-1 R9.2. | To any Transmission Service Provider, Reliability Coordinator, Transmission Planner, Resource Planner, or Planning Coordinator within 30 calendar days of their making a request for the data. |  | TP, TSP | [19 empty] | TP | TSP |  | 2010-02-08 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1214 |  | 1. | 1221 | MOD-004-1 R12.1. | The CBM is available |  | TSP | [20 empty] | TSP | Each Transmission Service Provider that maintains CBM shall provide evidence including copies of CBM values along with other evidence (such as tags, reports, and supporting data) to show that it approved any Arranged Interchange meeting the criteria in R12. (R12) | 2010-02-08 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1214 |  | 2. | 1224 | MOD-004-1 R12.2. | The EEA 2 is declared within the Balancing Authority Area of the “energy deficient entity,” and |  | TSP | [20 empty] | TSP | Each Transmission Service Provider that maintains CBM shall provide evidence including copies of CBM values along with other evidence (such as tags, reports, and supporting data) to show that it approved any Arranged Interchange meeting the criteria in R12. (R12) | 2010-02-08 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
104 | 1214 |  | 3. | 1234 | MOD-004-1 R12.3. | The Load of the “energy deficient entity” is located within the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider that maintains CBM shall provide evidence including copies of CBM values along with other evidence (such as tags, reports, and supporting data) to show that it approved any Arranged Interchange meeting the criteria in R12. (R12) | 2010-02-08 |  | 2024-02-01 |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
105 | 1236 |  | 1. | 1237 | MOD-005-0 R1.1. | Indicate the frequency under which the verification review shall be implemented. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
105 | 1236 |  | 2. | 1238 | MOD-005-0 R1.2. | Require review of the process by which CBM values are updated, and their frequency of update, to ensure that the most current CBM values are available to transmission users. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
105 | 1236 |  | 3. | 1239 | MOD-005-0 R1.3. | Require review of the consistency of the Transmission Service Provider’s CBM components with its published planning criteria. A CBM value is considered consistent with published planning criteria if the components that comprise CBM are addressed in the planning criteria. The methodology used to determine and apply CBM does not have to involve the same mechanics as the planning process, but the same uncertainties must be considered and any simplifying assumptions explained. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
105 | 1236 |  | 4. | 1240 | MOD-005-0 R1.4. | Require CBM values to be periodically updated (at least annually) and available to the Regional Reliability Organizations, NERC, and transmission users. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
106 | 1243 |  | 1. | 1244 | MOD-006-0 R1.1. | Require that CBM be used only after the following steps have been taken (as time permits): all non-firm sales have been terminated, Direct-Control Load Management has been implemented, and customer interruptible demands have been interrupted. CBM may be used to reestablish Operating Reserves. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2009-05-12 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
106 | 1243 |  | 2. | 1245 | MOD-006-0 R1.2. | Require that CBM shall only be used if the Load-Serving Entity calling for its use is experiencing a generation deficiency and its Transmission Service Provider is also experiencing Transmission Constraints relative to imports of energy on its transmission system. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2009-05-12 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
106 | 1243 |  | 3. | 1246 | MOD-006-0 R1.3. | Describe the conditions under which CBM may be available as Non-Firm Transmission Service. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2009-05-12 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
107 | 1248 |  | 1. | 1249 | MOD-006-0.1 R1.1. | Require that CBM be used only after the following steps have been taken (as time permits): all non-firm sales have been terminated, Direct-Control Load Management has been implemented, and customer interruptible demands have been interrupted. CBM may be used to reestablish Operating Reserves. |  | TSP | [20 empty] | TSP |  | 2009-05-13 |  | 2011-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
107 | 1248 |  | 2. | 1250 | MOD-006-0.1 R1.2. | Require that CBM shall only be used if the Load-Serving Entity calling for its use is experiencing a generation deficiency and its Transmission Service Provider is also experiencing Transmission Constraints relative to imports of energy on its transmission system. |  | TSP | [20 empty] | TSP |  | 2009-05-13 |  | 2011-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
107 | 1248 |  | 3. | 1251 | MOD-006-0.1 R1.3. | Describe the conditions under which CBM may be available as Non-Firm Transmission Service. |  | TSP | [20 empty] | TSP |  | 2009-05-13 |  | 2011-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
108 | 1254 |  | 1. | 1255 | MOD-007-0 R2.1. | Circumstances. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2011-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
108 | 1254 |  | 2. | 1256 | MOD-007-0 R2.2. | Duration. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2011-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
108 | 1254 |  | 3. | 1257 | MOD-007-0 R2.3. | Amount of CBM used. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2011-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
109 | 1258 | 1261 | 1. | 1262 | MOD-008-0 R1.3.1. | Aggregate Load forecast error (not included in determining generation reliability requirements). |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
109 | 1258 | 1261 | 2. | 1263 | MOD-008-0 R1.3.2. | Load distribution error. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
109 | 1258 | 1261 | 3. | 1264 | MOD-008-0 R1.3.3. | Variations in facility Loadings due to balancing of generation within a Balancing Authority Area. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
109 | 1258 | 1261 | 4. | 1265 | MOD-008-0 R1.3.4. | Forecast uncertainty in transmission system topology. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
109 | 1258 | 1261 | 5. | 1266 | MOD-008-0 R1.3.5. | Allowances for parallel path (loop flow) impacts. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
109 | 1258 | 1261 | 6. | 1267 | MOD-008-0 R1.3.6. | Allowances for simultaneous path interactions. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
109 | 1258 | 1261 | 7. | 1268 | MOD-008-0 R1.3.7. | Variations in generation dispatch. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
109 | 1258 | 1261 | 8. | 1269 | MOD-008-0 R1.3.8. | Short-term System Operator response (Operating Reserve actions not exceeding a 59-minute window). |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
109 | 1258 |  | 1. | 1259 | MOD-008-0 R1.1. | Specify the update frequency of TRM calculations. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
109 | 1258 |  | 2. | 1260 | MOD-008-0 R1.2. | Specify how TRM values are incorporated into Available Transfer Capability calculations. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
109 | 1258 |  | 3. | 1261 | MOD-008-0 R1.3. | Specify the uncertainties accounted for in TRM and the methods used to determine their impacts on the TRM values. Any component of uncertainty, other than those identified in MOD-008-0_R1.3.1 through MOD-008-0_R1.3.7, shall benefit the interconnected transmission systems as a whole before they shall be permitted to be included in TRM calculations. The components of uncertainty identified in MOD-008-0_R1.3.1 through MOD-008-0_R1.3.7, if applied, shall be accounted for solely in TRM and not CBM. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
109 | 1258 |  | 4. | 1270 | MOD-008-0 R1.4. | Describe the conditions, if any, under which TRM may be available to the market as Non-Firm Transmission Service. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
109 | 1258 |  | 5. | 1271 | MOD-008-0 R1.5. | Describe the formal process for the Regional Reliability Organization to grant any variances to individual Transmission Service Providers from the Regional TRM methodology. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
110 | 1273 | 1276 | 1. | 1277 | MOD-008-1 R1.3.1. | Same day and real-time. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2024-02-01 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
110 | 1273 | 1276 | 2. | 1278 | MOD-008-1 R1.3.2. | Day-ahead and pre-schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2024-02-01 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
110 | 1273 | 1276 | 3. | 1279 | MOD-008-1 R1.3.3. | Beyond day-ahead and pre-schedule, up to thirteen months ahead. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2024-02-01 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
110 | 1273 |  | 1. | 1274 | MOD-008-1 R1.1. | Identification of (on each of its respective ATC Paths or Flowgates) each of the following components of uncertainty if used in establishing TRM, and a description of how that component is used to establish a TRM value: Aggregate Load forecast.; Load distribution uncertainty.; Forecast uncertainty in Transmission system topology (including, but not limited to, forced or unplanned outages and maintenance outages).; Allowances for parallel path (loop flow) impacts.; Allowances for simultaneous path interactions.; Variations in generation dispatch (including, but not limited to, forced or unplanned outages, maintenance outages and location of future generation).; Short-term System Operator response (Operating Reserve actions ).; Reserve sharing requirements.; Inertial response and frequency bias. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2024-02-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
110 | 1273 |  | 2. | 1275 | MOD-008-1 R1.2. | The description of the method used to allocate TRM across ATC Paths or Flowgates. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2024-02-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
110 | 1273 |  | 3. | 1276 | MOD-008-1 R1.3. | The identification of the TRM calculation used for the following time periods: |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2024-02-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
111 | 1284 |  | 1. | 1285 | MOD-009-0 R1.1. | Indicate the frequency under which the verification review shall be implemented. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
111 | 1284 |  | 2. | 1286 | MOD-009-0 R1.2. | Require review of the process by which TRM values are updated, and their frequency of update, to ensure that the most current TRM values are available to transmission users. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
111 | 1284 |  | 3. | 1287 | MOD-009-0 R1.3. | Require review of the consistency of the Transmission Service Provider’s TRM components with its published planning criteria. A TRM value is considered consistent with published planning criteria if the same components that comprise TRM are also addressed in the planning criteria. The methodology used to determine and apply TRM does not have to involve the same mechanics as the planning process, but the same uncertainties must be considered and any simplifying assumption explained. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
111 | 1284 |  | 4. | 1288 | MOD-009-0 R1.4. | Require TRM values to be periodically updated (at least prior to each season — winter, spring, summer, and fall), as necessary, and made available to the Regional Reliability Organizations, NERC, and transmission users. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
113 | 1293 |  | 1. | 1294 | MOD-011-0 R1.1. | Bus (substation): name, nominal voltage, electrical demand supplied (consistent with the aggregated and dispersed substation demand data supplied per Reliability Standards MOD-016-0, MOD-017-0, and MOD-020-0 ), and location. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
113 | 1293 |  | 2. | 1295 | MOD-011-0 R1.2. | Generating Units (including synchronous condensers, pumped storage, etc.): location, minimum and maximum Ratings (net Real and Reactive Power), regulated bus and voltage set point, and equipment status. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
113 | 1293 |  | 3. | 1296 | MOD-011-0 R1.3. | AC Transmission Line or Circuit (overhead and underground): nominal voltage, impedance, line charging, Normal and Emergency Ratings (consistent with methodologies defined and Ratings supplied per Reliability Standard FAC-004-0 and FAC-005-0 ) equipment status, and metering locations. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
113 | 1293 |  | 4. | 1297 | MOD-011-0 R1.4. | DC Transmission Line (overhead and underground): line parameters, Normal and Emergency Ratings, control parameters, rectifier data, and inverter data. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
113 | 1293 |  | 5. | 1298 | MOD-011-0 R1.5. | Transformer (voltage and phase-shifting): nominal voltages of windings, impedance, tap ratios (voltage and/or phase angle or tap step size), regulated bus and voltage set point, Normal and Emergency Ratings (consistent with methodologies defined and Ratings supplied per Reliability Standard FAC-004-0 and FAC-005-0.), and equipment status. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
113 | 1293 |  | 6. | 1299 | MOD-011-0 R1.6. | Reactive Compensation (shunt and series capacitors and reactors): nominal Ratings, impedance, percent compensation, connection point, and controller device. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
113 | 1293 |  | 7. | 1300 | MOD-011-0 R1.7. | Interchange Schedules: Existing and future Interchange Schedules and/or assumptions. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
115 | 1304 | 1305 | 1. | 1306 | MOD-013-1 R1.1.1. | If design data is unavailable from the manufacturer 3 months prior to the installation date, estimated or typical manufacturer’s data, based on excitation systems of similar design and characteristics, shall be provided. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
115 | 1304 | RP-2021-06-22-0000014 | 1. | 1308 | MOD-013-1 R1.2.1. | Estimated or typical manufacturer’s dynamics data, based on units of similar design and characteristics, may be submitted when unit-specific dynamics data cannot be obtained. In no case shall other than unit-specific data be reported for generator units installed after 1990. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
115 | 1304 | RP-2021-06-22-0000014 | 2. | 1309 | MOD-013-1 R1.2.2. | The Interconnection-wide requirements shall specify unit size thresholds for permitting: The use of non-detailed vs. detailed models, The netting of small generating units with bus load, and The combining of multiple generating units at one plant. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
115 | 1304 |  | 1. | 1305 | MOD-013-1 R1.1. | Design data shall be provided for new or refurbished excitation systems (for synchronous generators and synchronous condensers) at least three months prior to the installation date. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
115 | 1304 |  | 2. | RP-2021-06-22-0000014 | MOD-013-1 R1.2. | Unit-specific dynamics data shall be reported for generators and synchronous condensers (including, as appropriate to the model, items such as inertia constant, damping coefficient, saturation parameters, and direct and quadrature axes reactances and time constants), excitation systems, voltage regulators, turbine-governor systems, power system stabilizers, and other associated generation equipment. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
115 | 1304 |  | 3. | 1310 | MOD-013-1 R1.3. | Device specific dynamics data shall be reported for dynamic devices, including, among others, static VAR controllers, high voltage direct current systems, flexible AC transmission systems, and static compensators. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
115 | 1304 |  | 4. | 1311 | MOD-013-1 R1.4. | Dynamics data representing electrical Demand characteristics as a function of frequency and voltage. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
115 | 1304 |  | 5. | 1312 | MOD-013-1 R1.5. | Dynamics data shall be consistent with the reported steady-state (power flow) data supplied per Reliability Standard MOD-010 Requirement 1. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
117 | 1316 |  | 1. | 1317 | MOD-015-0 R1.1. | The Regional Reliability Organization(s) shall develop Interconnectionspecific dynamics system models for at least two timeframes (present or nearterm model and a future or longer-term model), and additional seasonal and demand level models, as necessary, to analyze the dynamic response of that Interconnection. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
118 | 1319 |  | 1. | 1320 | MOD-015-0.1 R1.1. | The Regional Reliability Organization(s) shall develop Interconnection specific dynamics system models for at least two timeframes (present or near-term model and a future or longer-term model), and additional seasonal and demand level models, as necessary, to analyze the dynamic response of that Interconnection. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
119 | 1322 |  | 1. | 1323 | MOD-016-1 R1.1. | The aggregated and dispersed data submittal requirements shall ensure that consistent data is supplied for Reliability Standards TPL-005, TPL-006, MOD-010, MOD-011, MOD-012, MOD-013, MOD-014, MOD-015, MOD-016, MOD-017, MOD-018, MOD-019, MOD-020, and MOD-021. The data submittal requirements shall stipulate that each Load-Serving Entity count its customer Demand once and only once, on an aggregated and dispersed basis, in developing its actual and forecast customer Demand values. |  | PCPA, RRO | [9 empty] | PCPA |  |  |  |  | RRO | [7 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
119 | 1324 |  | 1. | 1325 | MOD-016-1 R2.1. | The Regional Reliability Organization shall make this distribution within 30 calendar days of approval. |  | RRO | [14 empty] | RRO | [7 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
119 | 1326 |  | 1. | 1327 | MOD-016-1 R3.1. | The Planning Authority shall make this distribution within 30 calendar days of approval. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12 | 115 |  | 1. | 116 | BAL-004-0 R3.1. | The Balancing Authority shall offset its frequency schedule by 0.02 Hertz, leaving the Frequency Bias Setting normal; or |  | BA, RC | BA | [10 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-04-01 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12 | 115 |  | 2. | 117 | BAL-004-0 R3.2. | The Balancing Authority shall offset its Net Interchange Schedule (MW) by an amount equal to the computed bias contribution during a 0.02 Hertz Frequency Deviation (i.e. 20% of the Frequency Bias Setting). |  | BA, RC | BA | [10 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-04-01 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12 | 118 |  | 1. | 119 | BAL-004-0 R4.1. | Balancing Authorities that have reliability concerns with the execution of a Time Error Correction shall notify their Reliability Coordinator and request the termination of a Time Error Correction in progress. |  | BA, RC | BA | [10 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-04-01 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
120 | 1328 |  | 1. | 1329 | MOD-016-1.1 R1.1. | The aggregated and dispersed data submittal requirements shall ensure that consistent data is supplied for Reliability Standards TPL-005, TPL-006, MOD-010, MOD-011, MOD-012, MOD-013, MOD-014, MOD-015, MOD-016, MOD-017, MOD-018, MOD-019, MOD-020, and MOD-021. The data submittal requirements shall stipulate that each Load-Serving Entity count its customer Demand once and only once, on an aggregated and dispersed basis, in developing its actual and forecast customer Demand values. |  | PCPA, RRO | [9 empty] | PCPA |  |  |  |  | RRO | [7 empty] | 2009-05-13 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
120 | 1330 |  | 1. | 1331 | MOD-016-1.1 R2.1. | The Regional Reliability Organization shall make this distribution within 30 calendar days of approval. |  | RRO | [14 empty] | RRO | [7 empty] | 2009-05-13 |  | 2016-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
120 | 1332 |  | 1. | 1333 | MOD-016-1.1 R3.1. | The Planning Authority shall make this distribution within 30 calendar days of approval. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-05-13 |  | 2016-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
121 | 1334 |  | 1. | 1335 | MOD-017-0 R1.1. | Integrated hourly demands in megawatts (MW) for the prior year. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PCPA |  |  |  | RP | [8 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
121 | 1334 |  | 2. | 1336 | MOD-017-0 R1.2. | Monthly and annual peak hour actual demands in MW and Net Energy for Load in gigawatthours (GWh) for the prior year. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PCPA |  |  |  | RP | [8 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
121 | 1334 |  | 3. | 1337 | MOD-017-0 R1.3. | Monthly peak hour forecast demands in MW and Net Energy for Load in GWh for the next two years. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PCPA |  |  |  | RP | [8 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
121 | 1334 |  | 4. | 1338 | MOD-017-0 R1.4. | Annual Peak hour forecast demands (summer and winter) in MW and annual Net Energy for load in GWh for at least five years and up to ten years into the future, as requested. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PCPA |  |  |  | RP | [8 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
122 | 1339 |  | 1. | 1340 | MOD-017-0.1 R1.1. | Integrated hourly demands in megawatts (MW) for the prior year. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PCPA |  |  |  | RP | [8 empty] | 2009-05-13 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
122 | 1339 |  | 2. | 1341 | MOD-017-0.1 R1.2. | Monthly and annual peak hour actual demands in MW and Net Energy for Load in gigawatthours (GWh) for the prior year. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PCPA |  |  |  | RP | [8 empty] | 2009-05-13 |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
122 | 1339 |  | 3. | 1342 | MOD-017-0.1 R1.3. | Monthly peak hour forecast demands in MW and Net Energy for Load in GWh for the next two years. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PCPA |  |  |  | RP | [8 empty] | 2009-05-13 |  | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
122 | 1339 |  | 4. | 1343 | MOD-017-0.1 R1.4. | Annual Peak hour forecast demands (summer and winter) in MW and annual Net Energy for load in GWh for at least five years and up to ten years into the future, as requested. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PCPA |  |  |  | RP | [8 empty] | 2009-05-13 |  | 2016-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
123 | 1344 |  | 1. | 1345 | MOD-018-0 R1.1. | Indicate whether the demand data of nonmember entities within an area or Regional Reliability Organization are included, and |  | LSE, PCPA, RP, TP | [7 empty] | LSE |  | PCPA |  |  |  | RP | [5 empty] | TP |  |  | 2007-06-18 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
123 | 1344 |  | 2. | 1346 | MOD-018-0 R1.2. | Address assumptions, methods, and the manner in which uncertainties are treated in the forecasts of aggregated peak demands and Net Energy for Load. |  | LSE, PCPA, RP, TP | [7 empty] | LSE |  | PCPA |  |  |  | RP | [5 empty] | TP |  |  | 2007-06-18 |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
123 | 1344 |  | 3. | 1347 | MOD-018-0 R1.3. | Items (MOD-018-0_R 1.1) and (MOD-018-0_R 1.2) shall be addressed as described in the reporting procedures developed for Standard MOD-016-1_R 1. |  | LSE, PCPA, RP, TP | [7 empty] | LSE |  | PCPA |  |  |  | RP | [5 empty] | TP |  |  | 2007-06-18 |  | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
128 | 1355 | 1360 | 1. | 1361 | MOD-024-1 R1.5.1. | Seasonal gross and net Real Power generating capabilities. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
128 | 1355 | 1360 | 2. | 1362 | MOD-024-1 R1.5.2. | Real power requirements of auxiliary loads. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
128 | 1355 | 1360 | 3. | 1363 | MOD-024-1 R1.5.3. | Method of verification, including date and conditions. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 153000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
128 | 1355 |  | 1. | 1356 | MOD-024-1 R1.1. | Generating unit exemption criteria including documentation of those units that are exempt from a portion or all of these procedures. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
128 | 1355 |  | 2. | 1357 | MOD-024-1 R1.2. | Criteria for reporting generating unit auxiliary loads. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
128 | 1355 |  | 3. | 1358 | MOD-024-1 R1.3. | Acceptable methods for model and data verification, including any applicable conditions under which the data should be verified. Such methods can include use of manufacturer data, commissioning data, performance tracking, and testing, etc. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
128 | 1355 |  | 4. | 1359 | MOD-024-1 R1.4. | Periodicity and schedule of model and data verification and reporting. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
128 | 1355 |  | 5. | 1360 | MOD-024-1 R1.5. | Information to be verified and reported: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
129 | 1366 | 1371 | 1. | 1372 | MOD-025-1 R1.5.1. | Verified maximum gross and net Reactive Power capability (both lagging and leading) at Seasonal Real Power generating capabilities as reported in accordance with Reliability Standard MOD-024 Requirement 1.5.1. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
129 | 1366 | 1371 | 2. | 1373 | MOD-025-1 R1.5.2. | Verified Reactive Power limitations, such as generator terminal voltage limitations, shorted rotor turns, etc. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
129 | 1366 | 1371 | 3. | 1374 | MOD-025-1 R1.5.3. | Verified Reactive Power of auxiliary loads. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 153000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
129 | 1366 | 1371 | 4. | 1375 | MOD-025-1 R1.5.4. | Method of verification, including date and conditions. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 154000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
129 | 1366 |  | 1. | 1367 | MOD-025-1 R1.1. | Generating unit exemption criteria including documentation of those units that are exempt from a portion or all of these procedures. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
129 | 1366 |  | 2. | 1368 | MOD-025-1 R1.2. | Criteria for reporting generating unit auxiliary loads. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
129 | 1366 |  | 3. | 1369 | MOD-025-1 R1.3. | Acceptable methods for model and data verification, including any applicable conditions under which the data should be verified. Such methods can include use of commissioning data, performance tracking, engineering analysis, testing, etc. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
129 | 1366 |  | 4. | 1370 | MOD-025-1 R1.4. | Periodicity and schedule of model and data verification and reporting. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
129 | 1366 |  | 5. | 1371 | MOD-025-1 R1.5. | Information to be reported: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
13 | 121 |  | 1. | 122 | BAL-004-1 R2.1. | The Balancing Authority shall offset its frequency schedule by 0.02 Hertz, leaving the Frequency Bias Setting normal; or |  | BA, RC | BA | [10 empty] | RC | [12 empty] | 2012-08-16 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
13 | 121 |  | 2. | 123 | BAL-004-1 R2.2. | The Balancing Authority shall offset its Net Interchange Schedule (MW) by an amount equal to the computed bias contribution during a 0.02 Hertz Frequency Deviation (i.e., 20% of the Frequency Bias Setting). |  | BA, RC | BA | [10 empty] | RC | [12 empty] | 2012-08-16 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
13 | 124 |  | 1. | 125 | BAL-004-1 R3.1. | Balancing Authorities that have reliability concerns with the execution of a Time Error Correction shall notify their Reliability Coordinator and request the termination of a Time Error Correction in progress. |  | BA, RC | BA | [10 empty] | RC | [12 empty] | 2012-08-16 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1378 | 1383 | 1. | 1384 | MOD-028-1 R1.5.1. | Define if the source used for Available Transfer Capability (ATC) calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2013-09-30 |  |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1378 | 1383 | 2. | 1385 | MOD-028-1 R1.5.2. | Define if the sink used for ATC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2013-09-30 |  |  | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1378 | 1383 | 3. | 1386 | MOD-028-1 R1.5.3. | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2013-09-30 |  |  | 153000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1378 | 1383 | 4. | 1387 | MOD-028-1 R1.5.4. | If the Transmission Service Provider’s ATC calculation process involves a grouping of generation, the ATCID must identify how these generators participate in the group. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2013-09-30 |  |  | 154000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1378 |  | 1. | 1379 | MOD-028-1 R1.1. | Information describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Operator, the results of the TTC calculations can be validated. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2013-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1378 |  | 2. | 1380 | MOD-028-1 R1.2. | A description of the manner in which the Transmission Operator will account for Interchange Schedules in the calculation of TTC. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2013-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1378 |  | 3. | 1381 | MOD-028-1 R1.3. | Any contractual obligations for allocation of TTC. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2013-09-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1378 |  | 4. | 1382 | MOD-028-1 R1.4. | A description of the manner in which Contingencies are identified for use in the TTC process. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2013-09-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1378 |  | 5. | 1383 | MOD-028-1 R1.5. | The following information on how source and sink for transmission service is accounted for in ATC calculations including: |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2013-09-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1390 |  | 1. | 1391 | MOD-028-1 R2.1. | Modeling data and topology of its Reliability Coordinator’s area of responsibility. Equivalent representation of radial lines and facilities 161 kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1390 |  | 2. | 1392 | MOD-028-1 R2.2. | Modeling data and topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination areas. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1390 |  | 3. | 1393 | MOD-028-1 R2.3. | Facility Ratings specified by the Generator Owners and Transmission Owners. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1394 | 1395 | 1. | 1396 | MOD-028-1 R3.1.1. | Expected generation and Transmission outages, additions, and retirements, included as specified in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1394 | 1395 | 2. | 1397 | MOD-028-1 R3.1.2. | Load forecast for the applicable period being calculated. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1394 | 1395 | 3. | 1398 | MOD-028-1 R3.1.3. | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1394 | 1399 | 1. | 1400 | MOD-028-1 R3.2.1. | Expected generation and Transmission outages, additions, and Retirements, included as specified in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1394 | 1399 | 2. | 1401 | MOD-028-1 R3.2.2. | Daily load forecast for the days two through 31 TTCs being calculated and monthly forecast for months two through 13 months TTCs being calculated. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1394 | 1399 | 3. | 1402 | MOD-028-1 R3.2.3. | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  | 323000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1394 |  | 1. | 1395 | MOD-028-1 R3.1. | For on-peak and off-peak intra-day and next-day TTCs, use the following (as well as any other values and additional parameters as specified in the ATCID): |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1394 |  | 2. | 1399 | MOD-028-1 R3.2. | For days two through 31 TTCs and for months two through 13 TTCs, use the following (as well as any other values and internal parameters as specified in the ATCID): |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1403 |  | 1. | 1404 | MOD-028-1 R4.1. | Use all Contingencies meeting the criteria described in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1403 |  | 2. | 1405 | MOD-028-1 R4.2. | Respect any contractual allocations of TTC. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1403 |  | 3. | 1406 | MOD-028-1 R4.3. | Include, for each time period, the Firm Transmission Service expected to be scheduled as specified in the ATCID (filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers) for the Transmission Service Provider, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed modeling the source and sink as follows: - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point shall as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can not be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is to be delivered as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is being delivered as the sink. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1407 |  | 1. | 1408 | MOD-028-1 R5.1. | At least once within the seven calendar days prior to the specified period for TTCs used in hourly and daily ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1407 |  | 2. | 1409 | MOD-028-1 R5.2. | At least once per calendar month for TTCs used in monthly ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1407 |  | 3. | 1410 | MOD-028-1 R5.3. | Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1411 |  | 1. | 1412 | MOD-028-1 R6.1. | Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either: - A System Operating Limit is reached on the Transmission Service Provider’s system, or - A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater . |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1411 |  | 2. | 1413 | MOD-028-1 R6.2. | If the limit in step R6.1 can not be reached by adjusting any combination of load or generation, then set the incremental Transfer Capability by the results of the case where the maximum adjustments were applied. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1411 |  | 3. | 1414 | MOD-028-1 R6.3. | Use (as the TTC) the lesser of: The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or The sum of Facility Ratings of all ties comprising the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1411 |  | 4. | 1415 | MOD-028-1 R6.4. | For ATC Paths whose capacity uses jointly-owned or allocated Facilities, limit TTC for each Transmission Service Provider so the TTC does not exceed each Transmission Service Provider’s contractual rights. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1416 |  | 1. | 1417 | MOD-028-1 R7.1. | One calendar day after its determination for TTCs used in hourly and daily ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
130 | 1416 |  | 2. | 1418 | MOD-028-1 R7.2. | Seven calendar days after its determination for TTCs used in monthly ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1421 | 1422 | 1. | 1423 | MOD-029-1 R1.1.1. | Includes at least: |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1421 | 1422 | 10. | 1427 | MOD-029-1 R1.1.10. | Includes any other modeling requirements or criteria specified in the ATCID. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 1110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1421 | 1422 | 2. | 1428 | MOD-029-1 R1.1.2. | Models all system Elements as in-service for the assumed initial conditions. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1421 | 1422 | 3. | 1429 | MOD-029-1 R1.1.3. | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1421 | 1422 | 4. | 1430 | MOD-029-1 R1.1.4. | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1421 | 1422 | 5. | 1431 | MOD-029-1 R1.1.5. | Uses Load forecast by Balancing Authority. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1421 | 1422 | 6. | 1432 | MOD-029-1 R1.1.6. | Uses Transmission Facility additions and retirements. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 116000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1421 | 1422 | 7. | 1433 | MOD-029-1 R1.1.7. | Uses Generation Facility additions and retirements. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 117000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1421 | 1422 | 8. | 1434 | MOD-029-1 R1.1.8. | Uses Special Protection System (SPS) models where currently existing or projected for implementation within the studied time horizon. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 118000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1421 | 1422 | 9. | 1435 | MOD-029-1 R1.1.9. | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 119000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1421 | 1423 | 1. | 1424 | MOD-029-1 R1.1.1.1. | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 11110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1421 | 1423 | 2. | 1425 | MOD-029-1 R1.1.1.2. | All Transmission Operator areas contiguous with its own Transmission Operator area. (Equivalent representation is allowed.) |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 11120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1421 | 1423 | 3. | 1426 | MOD-029-1 R1.1.1.3. | Any other Transmission Operator area linked to the Transmission Operator’s area by joint operating agreement. (Equivalent representation is allowed.) |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 11130000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1421 |  | 1. | 1422 | MOD-029-1 R1.1. | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1421 |  | 2. | 1436 | MOD-029-1 R1.2. | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1437 | 1438 | 1. | 1439 | MOD-029-1 R2.1.1. | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1437 | 1438 | 2. | 1440 | MOD-029-1 R2.1.2. | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1437 | 1438 | 3. | 1441 | MOD-029-1 R2.1.3. | Uncontrolled separation shall not occur. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1437 |  | 1. | 1438 | MOD-029-1 R2.1. | Except where otherwise specified within MOD-029-1, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1437 |  | 2. | 1442 | MOD-029-1 R2.2. | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependant on a Special Protection System (SPS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a SPS. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1437 |  | 3. | 1443 | MOD-029-1 R2.3. | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1437 |  | 4. | 1444 | MOD-029-1 R2.4. | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1437 |  | 5. | 1445 | MOD-029-1 R2.5. | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1437 |  | 6. | 1446 | MOD-029-1 R2.6. | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1437 |  | 7. | 1447 | MOD-029-1 R2.7. | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | 270000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
131 | 1437 |  | 8. | 1448 | MOD-029-1 R2.8. | Create a study report that describes the steps above that were undertaken (R2.1 - R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | 280000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1455 | 1457 | 1. | 1458 | MOD-030-1 R1.2.1. | Define if the source used for AFC calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1455 | 1457 | 2. | 1459 | MOD-030-1 R1.2.2. | Define if the sink used for AFC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1455 | 1457 | 3. | 1460 | MOD-030-1 R1.2.3. | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1455 | 1457 | 4. | 1461 | MOD-030-1 R1.2.4. | If the Transmission Service Provider’s AFC calculation process involves a grouping of generators, the ATCID must identify how these generators participate in the group. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1455 |  | 1. | 1456 | MOD-030-1 R1.1. | The criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates that are to be considered in Available Flowgate Capability (AFC) calculations. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1455 |  | 2. | 1457 | MOD-030-1 R1.2. | The following information on how source and sink for transmission service is accounted for in AFC calculations including: |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 | 1468 | 1. | 1469 | MOD-030-1 R2.1.1. | Results of a first Contingency transfer analysis for ATC Paths internal to a Transmission Operator’s system up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an OTDF of at least 5% and within the Transmission Operator’s system are included as Flowgates. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 | 1468 | 2. | 1472 | MOD-030-1 R2.1.2. | Results of a first Contingency transfer analyses from all adjacent Balancing Authority source and sink (as defined in the ATCID) combinations up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an Outage Transfer Distribution Factor (OTDF) of at least 5% and within the Transmission Operator’s system are included as Flowgates unless the interface between such adjacent Balancing Authorities is accounted for using another ATC methodology. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 | 1468 | 3. | 1475 | MOD-030-1 R2.1.3. | Any limiting Element/Contingency combination at least within the Transmission model identified in R3.4 and R3.5 that has been subjected to an Interconnection-wide congestion management procedure within the last 12 months, unless the limiting Element/Contingency combination is accounted for using another ATC methodology. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 | 1468 | 4. | 1476 | MOD-030-1 R2.1.4. | Any limiting Element/Contingency combination within the Transmission model that has been requested to be included by any other Transmission Service Provider using the Flowgate Methodology or Area Interchange Methodology, where: |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 | 1469 | 1. | 1470 | MOD-030-1 R2.1.1.1. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 21110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 | 1469 | 2. | 1471 | MOD-030-1 R2.1.1.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 21120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 | 1472 | 1. | 1473 | MOD-030-1 R2.1.2.1. | Use first Contingency criteria consistent with those first Contignency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 21210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 | 1472 | 2. | 1474 | MOD-030-1 R2.1.2.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 21220000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 | 1476 | 1. | 1477 | MOD-030-1 R2.1.4.1. | The coordination of the limiting Element/Contingency combination is not already addressed through a different methodology, and -Any generator within the Transmission Service Provider’s area has at least a 5% Power Transfer Distribution Factor (PTDF) or Outage Transfer Distribution Factor (OTDF) impact on the Flowgate when delivered to the aggregate load of its own area, or -A transfer from any Balancing Area within the Transmission Service Provider’s area to a Balancing Area adjacent has at least a 5% PTDF or OTDF impact on the Flowgate. -The Transmission Operator may utilize distribution factors less than 5% if desired. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 21410000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 | 1476 | 2. | 1478 | MOD-030-1 R2.1.4.2. | The limiting Element/Contingency combination is included in the requesting Transmission Service Provider’s methodology. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 21420000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 | 1482 | 1. | 1483 | MOD-030-1 R2.5.1. | If notified of a change in the Rating by the Transmission Owner that would affect the TFC of a flowgate used in the AFC process, the TFC should be updated within seven calendar days of the notification. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 251000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 |  | 1. | 1468 | MOD-030-1 R2.1. | Include Flowgates used in the AFC process based, at a minimum, on the following criteria: |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 |  | 2. | 1479 | MOD-030-1 R2.2. | At a minimum, establish the list of Flowgates to create, modify, or delete internal Flowgates definitions at least once per calendar year. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 |  | 3. | 1480 | MOD-030-1 R2.3. | At a minimum, establish the list of Flowgates to create, modify, or delete external Flowgates that have been requested as part of R2.1.4 within thirty calendar days from the request. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 |  | 4. | 1481 | MOD-030-1 R2.4. | Establish the TFC of each of the defined Flowgates as equal to: - For thermal limits, the System Operating Limit (SOL) of the Flowgate. - For voltage or stability limits, the flow that will respect the SOL of the Flowgate. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 |  | 5. | 1482 | MOD-030-1 R2.5. | At a minimum, establish the TFC once per calendar year. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1467 |  | 6. | 1484 | MOD-030-1 R2.6. | Provide the Transmission Service Provider with the TFCs within seven calendar days of their establishment. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1485 |  | 1. | 1486 | MOD-030-1 R3.1. | Contains generation Facility Ratings, such as generation maximum and minimum output levels, specified by the Generator Owners of the Facilities within the model. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1485 |  | 2. | 1487 | MOD-030-1 R3.2. | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1485 |  | 3. | 1488 | MOD-030-1 R3.3. | Updated at least once per month for AFC calculations for months two through 13. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1485 |  | 4. | 1489 | MOD-030-1 R3.4. | Contains modeling data and system topology for the Facilities within its Reliability Coordinator’s Area. Equivalent representation of radial lines and Facilities161kV or below is allowed. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1485 |  | 5. | 1490 | MOD-030-1 R3.5. | Contains modeling data and system topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination Areas. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1492 |  | 1. | 1493 | MOD-030-1 R5.1. | Use the models provided by the Transmission Operator. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1492 |  | 2. | 1494 | MOD-030-1 R5.2. | Include in the transmission model expected generation and Transmission outages, additions, and retirements within the scope of the model as specified in the ATCID and in effect during the applicable period of the AFC calculation for the Transmission Service Provider’s area, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1492 |  | 3. | 1495 | MOD-030-1 R5.3. | For external Flowgates, identified in R2.1.4, use the AFC provided by the Transmission Service Provider that calculates AFC for that Flowgate. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1496 | 1497 | 1. | 1498 | MOD-030-1 R6.1.1. | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 611000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1496 | 1497 | 2. | 1499 | MOD-030-1 R6.1.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 612000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1496 | 1500 | 1. | 1501 | MOD-030-1 R6.2.1. | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 621000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1496 | 1500 | 2. | 1502 | MOD-030-1 R6.2.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 622000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1496 |  | 1. | 1497 | MOD-030-1 R6.1. | The impact of firm Network Integration Transmission Service, including the impacts of generation to load, in the model referenced in R5.2 for the Transmission Service Provider’s area, based on: |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1496 |  | 2. | 1500 | MOD-030-1 R6.2. | The impact of any firm Network Integration Transmission Service, including the impacts of generation to load in the model referenced in R5.2 and has a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed based on:. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1496 |  | 3. | 1503 | MOD-030-1 R6.3. | The impact of all confirmed firm Point-to-Point Transmission Service expected to be scheduled, including roll-over rights for Firm Transmission Service contracts, for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1496 |  | 4. | 1504 | MOD-030-1 R6.4. | The impact of any confirmed firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, including roll-over rights for Firm Transmission Service contracts having a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1496 |  | 5. | 1505 | MOD-030-1 R6.5. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1496 |  | 6. | 1506 | MOD-030-1 R6.6. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 660000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1496 |  | 7. | 1507 | MOD-030-1 R6.7. | The impact of other firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 670000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1508 |  | 1. | 1509 | MOD-030-1 R7.1. | The impact of all confirmed non-firm Point-to-Point Transmission Service expected to be scheduled for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1508 |  | 2. | 1510 | MOD-030-1 R7.2. | The impact of any confirmed non-firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1508 |  | 3. | 1511 | MOD-030-1 R7.3. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1508 |  | 4. | 1512 | MOD-030-1 R7.4. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1508 |  | 5. | 1513 | MOD-030-1 R7.5. | The impact of non-firm Network Integration Transmission Service serving Load within the Transmission Service Provider’s area (i.e., secondary service), to include load growth, and losses not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 750000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1508 |  | 6. | 1514 | MOD-030-1 R7.6. | The impact of any non-firm Network Integration Transmission Service (secondary service) with a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 760000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1508 |  | 7. | 1515 | MOD-030-1 R7.7. | The impact of other non-firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 770000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1462 |  | 1. | 1463 | MOD-030-1 R10.1. | For hourly AFC, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the AFC equation. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1462 |  | 2. | 1464 | MOD-030-1 R10.2. | For daily AFC, once per day. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
132 | 1462 |  | 3. | 1465 | MOD-030-1 R10.3. | For monthly AFC, once per week. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1518 | 1520 | 1. | 1521 | MOD-030-2 R1.2.1. | Define if the source used for AFC calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1518 | 1520 | 2. | 1522 | MOD-030-2 R1.2.2. | Define if the sink used for AFC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1518 | 1520 | 3. | 1523 | MOD-030-2 R1.2.3. | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1518 | 1520 | 4. | 1524 | MOD-030-2 R1.2.4. | If the Transmission Service Provider’s AFC calculation process involves a grouping of generators, the ATCID must identify how these generators participate in the group. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1518 |  | 1. | 1519 | MOD-030-2 R1.1. | The criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates that are to be considered in Available Flowgate Capability (AFC) calculations. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1518 |  | 2. | 1520 | MOD-030-2 R1.2. | The following information on how source and sink for transmission service is accounted for in AFC calculations including: |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 | 1531 | 1. | 1532 | MOD-030-2 R2.1.1. | Results of a first Contingency transfer analysis for ATC Paths internal to a Transmission Operator’s system up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an OTDF of at least 5% and within the Transmission Operator’s system are included as Flowgates. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 | 1531 | 2. | 1536 | MOD-030-2 R2.1.2. | Results of a first Contingency transfer analysis from all adjacent Balancing Authority source and sink (as defined in the ATCID) combinations up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an Outage Transfer Distribution Factor (OTDF) of at least 5% and within the Transmission Operator’s system are included as Flowgates unless the interface between such adjacent Balancing Authorities is accounted for using another ATC methodology. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 | 1531 | 3. | 1540 | MOD-030-2 R2.1.3. | Any limiting Element/Contingency combination at least within its Reliability Coordinator’s Area that has been subjected to an Interconnection-wide congestion management procedure within the last 12 months, unless the limiting Element/Contingency combination is accounted for using another ATC methodology or was created to address temporary operating conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 | 1531 | 4. | 1541 | MOD-030-2 R2.1.4. | Any limiting Element/Contingency combination within the Transmission model that has been requested to be included by any other Transmission Service Provider using the Flowgate Methodology or Area Interchange Methodology, where: |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 | 1532 | 1. | 1533 | MOD-030-2 R2.1.1.1. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 21110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 | 1532 | 2. | 1534 | MOD-030-2 R2.1.1.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 21120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 | 1532 | 3. | 1535 | MOD-030-2 R2.1.1.3. | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 21130000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 | 1536 | 1. | 1537 | MOD-030-2 R2.1.2.1. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 21210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 | 1536 | 2. | 1538 | MOD-030-2 R2.1.2.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 21220000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 | 1536 | 3. | 1539 | MOD-030-2 R2.1.2.3. | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 21230000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 | 1541 | 1. | 1542 | MOD-030-2 R2.1.4.1. | The coordination of the limiting Element/Contingency combination is not already addressed through a different methodology, and - Any generator within the Transmission Service Provider’s area has at least a 5% Power Transfer Distribution Factor (PTDF) or Outage Transfer Distribution Factor (OTDF) impact on the Flowgate when delivered to the aggregate load of its own area, or - A transfer from any Balancing Area within the Transmission Service Provider’s area to a Balancing Area adjacent has at least a 5% PTDF or OTDF impact on the Flowgate. - The Transmission Operator may utilize distribution factors less than 5% if desired. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 21410000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 | 1541 | 2. | 1543 | MOD-030-2 R2.1.4.2. | The limiting Element/Contingency combination is included in the requesting Transmission Service Provider’s methodology. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 21420000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 | 1547 | 1. | 1548 | MOD-030-2 R2.5.1. | If notified of a change in the Rating by the Transmission Owner that would affect the TFC of a flowgate used in the AFC process, the TFC should be updated within seven calendar days of the notification. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 251000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 |  | 1. | 1531 | MOD-030-2 R2.1. | Include Flowgates used in the AFC process based, at a minimum, on the following criteria: |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 |  | 2. | 1544 | MOD-030-2 R2.2. | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgate definitions at least once per calendar year. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 |  | 3. | 1545 | MOD-030-2 R2.3. | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgates that have been requested as part of R2.1.4 within thirty calendar days from the request. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 |  | 4. | 1546 | MOD-030-2 R2.4. | Establish the TFC of each of the defined Flowgates as equal to: - For thermal limits, the System Operating Limit (SOL) of the Flowgate. - For voltage or stability limits, the flow that will respect the SOL of the Flowgate. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 |  | 5. | 1547 | MOD-030-2 R2.5. | At a minimum, establish the TFC once per calendar year. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1530 |  | 6. | 1549 | MOD-030-2 R2.6. | Provide the Transmission Service Provider with the TFCs within seven calendar days of their establishment. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1550 |  | 1. | 1551 | MOD-030-2 R3.1. | Contains generation Facility Ratings, such as generation maximum and minimum output levels, specified by the Generator Owners of the Facilities within the model. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1550 |  | 2. | RP-2021-06-22-0000031 | MOD-030-2 R3.2. | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1550 |  | 3. | RP-2021-06-22-0000032 | MOD-030-2 R3.3. | Updated at least once per month for AFC calculations for months two through 13. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1550 |  | 4. | 1554 | MOD-030-2 R3.4. | Contains modeling data and system topology for the Facilities within its Reliability Coordinator’s Area. Equivalent representation of radial lines and Facilities161kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1550 |  | 5. | 1555 | MOD-030-2 R3.5. | Contains modeling data and system topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination Areas. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1557 |  | 1. | RP-2021-06-22-0000033 | MOD-030-2 R5.1. | Use the models provided by the Transmission Operator. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1557 |  | 2. | 1559 | MOD-030-2 R5.2. | Include in the transmission model expected generation and Transmission outages, additions, and retirements within the scope of the model as specified in the ATCID and in effect during the applicable period of the AFC calculation for the Transmission Service Provider’s area, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1557 |  | 3. | 1560 | MOD-030-2 R5.3. | For external Flowgates, identified in R2.1.4, use the AFC provided by the Transmission Service Provider that calculates AFC for that Flowgate. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1561 | 1562 | 1. | 1563 | MOD-030-2 R6.1.1. | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  | 611000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1561 | 1562 | 2. | 1564 | MOD-030-2 R6.1.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  | 612000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1561 | 1565 | 1. | 1566 | MOD-030-2 R6.2.1. | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  | 621000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1561 | 1565 | 2. | 1567 | MOD-030-2 R6.2.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  | 622000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1561 |  | 1. | 1562 | MOD-030-2 R6.1. | The impact of firm Network Integration Transmission Service, including the impacts of generation to load, in the model referenced in R5.2 for the Transmission Service Provider’s area, based on: |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1561 |  | 2. | 1565 | MOD-030-2 R6.2. | The impact of any firm Network Integration Transmission Service, including the impacts of generation to load in the model referenced in R5.2 and has a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed based on:. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1561 |  | 3. | 1568 | MOD-030-2 R6.3. | The impact of all confirmed firm Point-to-Point Transmission Service expected to be scheduled, including roll-over rights for Firm Transmission Service contracts, for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1561 |  | 4. | 1569 | MOD-030-2 R6.4. | The impact of any confirmed firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, including roll-over rights for Firm Transmission Service contracts having a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1561 |  | 5. | 1570 | MOD-030-2 R6.5. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1561 |  | 6. | 1571 | MOD-030-2 R6.6. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 660000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1561 |  | 7. | 1572 | MOD-030-2 R6.7. | The impact of other firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 670000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1573 |  | 1. | 1574 | MOD-030-2 R7.1. | The impact of all confirmed non-firm Point-to-Point Transmission Service expected to be scheduled for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1573 |  | 2. | 1575 | MOD-030-2 R7.2. | The impact of any confirmed non-firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1573 |  | 3. | 1576 | MOD-030-2 R7.3. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1573 |  | 4. | 1577 | MOD-030-2 R7.4. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1573 |  | 5. | 1578 | MOD-030-2 R7.5. | The impact of non-firm Network Integration Transmission Service serving Load within the Transmission Service Provider’s area (i.e., secondary service), to include load growth, and losses not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 750000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1573 |  | 6. | 1579 | MOD-030-2 R7.6. | The impact of any non-firm Network Integration Transmission Service (secondary service) with a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 760000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1573 |  | 7. | 1580 | MOD-030-2 R7.7. | The impact of other non-firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 770000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1525 |  | 1. | 1526 | MOD-030-2 R10.1. | For hourly AFC, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the AFC equation. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1525 |  | 2. | 1527 | MOD-030-2 R10.2. | For daily AFC, once per day. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
133 | 1525 |  | 3. | 1528 | MOD-030-2 R10.3. | For monthly AFC, once per week. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1586 |  | 1. | 1587 | NUC-001-1 R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1586 |  | 2. | 1588 | NUC-001-1 R4.2. | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1586 |  | 3. | 1589 | NUC-001-1 R4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1595 | 1. | 1596 | NUC-001-1 R9.1.1. | Definitions of key terms used in the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 911000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1595 | 2. | 1597 | NUC-001-1 R9.1.2. | Names of the responsible entities, organizational relationships, andresponsibilities related to the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 912000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1595 | 3. | 1598 | NUC-001-1 R9.1.3. | A requirement to review the agreement(s) at least every three years. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 913000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1595 | 4. | 1599 | NUC-001-1 R9.1.4. | A dispute resolution mechanism. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 914000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1600 | 1. | 1601 | NUC-001-1 R9.2.1. | Identification of parameters, limits, configurations, and operatingscenarios included in the NPIRs and, as applicable, procedures forproviding any specific data not provided within the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 921000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1600 | 2. | 1602 | NUC-001-1 R9.2.2. | Identification of facilities, components, and configuration restrictionsthat are essential for meeting the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 922000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1600 | 3. | 1603 | NUC-001-1 R9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  | 923000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1604 | 1. | 1605 | NUC-001-1 R9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 931000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1604 | 2. | 1606 | NUC-001-1 R9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 932000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1604 | 3. | 1607 | NUC-001-1 R9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 933000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1604 | 4. | 1608 | NUC-001-1 R9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 934000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1604 | 5. | 1609 | NUC-001-1 R9.3.5. | Provision to consider nuclear plant coping times required by the NPLRs and their relation to the coordination of grid and nuclear plant restoration following a nuclear plant loss of Off-site Power. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 935000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1604 | 6. | 1610 | NUC-001-1 R9.3.6. | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 936000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1604 | 7. | 1611 | NUC-001-1 R9.3.7. | Coordination of the NPIRs with transmission system Special Protection Systems and underfrequency and undervoltage load shedding programs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 937000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1612 | 1. | 1613 | NUC-001-1 R9.4.1. | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 941000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1612 | 2. | 1614 | NUC-001-1 R9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 942000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1612 | 3. | 1615 | NUC-001-1 R9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 943000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1612 | 4. | 1616 | NUC-001-1 R9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 944000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 | 1612 | 5. | 1617 | NUC-001-1 R9.4.5. | Provisions for personnel training, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2010-03-31 |  |  | 945000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 |  | 1. | 1595 | NUC-001-1 R9.1. | Administrative elements: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 |  | 2. | 1600 | NUC-001-1 R9.2. | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 |  | 3. | 1604 | NUC-001-1 R9.3. | Operations and maintenance coordination: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  | 930000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
134 | 1594 |  | 4. | 1612 | NUC-001-1 R9.4. | Communications and training: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  | 940000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
136 | 1620 |  | 1. | 1621 | PER-002-0 R2.1. | Positions that have the primary responsibility, either directly or through communications with others, for the real-time operation of the interconnected Bulk Electric System. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
136 | 1620 |  | 2. | 1622 | PER-002-0 R2.2. | Positions directly responsible for complying with NERC standards. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
136 | 1623 |  | 1. | 1624 | PER-002-0 R3.1. | A set of training program objectives must be defined, based on NERC and Regional Reliability Organization standards, entity operating procedures, and applicable regulatory requirements. These objectives shall reference the knowledge and competencies needed to apply those standards, procedures, and requirements to normal, emergency, and restoration conditions for the Transmission Operator and Balancing Authority operating positions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
136 | 1623 |  | 2. | 1625 | PER-002-0 R3.2. | The training program must include a plan for the initial and continuing training of Transmission Operator and Balancing Authority operating personnel. That plan shall address knowledge and competencies required for reliable system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
136 | 1623 |  | 3. | 1626 | PER-002-0 R3.3. | The training program must include training time for all Transmission Operator and Balancing Authority operating personnel to ensure their operating proficiency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
136 | 1623 |  | 4. | 1627 | PER-002-0 R3.4. | Training staff must be identified, and the staff must be competent in both knowledge of system operations and instructional capabilities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
137 | 1629 |  | 1. | 1630 | PER-003-0 R1.1. | Positions that have the primary responsibility, either directly or through communications with others, for the real-time operation of the interconnected Bulk Electric System. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2012-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
137 | 1629 |  | 2. | 1631 | PER-003-0 R1.2. | Positions directly responsible for complying with NERC standards. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2012-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
14 | 126 |  | 1. | 127 | BAL-004-WECC-01 R1.1. | The absolute value of the WECC Automatic Time Error Correction term is limited as follows: Where Lmax is chosen by the Balancing Authority and is bounded as follows: 0.20 * ¦Bi¦ <= Lmax<= L10. L10 is the Balancing Authority CPS2 limit in MW. If the WECC Automatic Time Error Correction term is less than the upper limit, use the calculated WECC Automatic Time Error Correction term. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2014-03-31 |  |  | 110000000 | WECC-US | [5 empty] | WECC-US
14 | 126 |  | 2. | 128 | BAL-004-WECC-01 R1.2. | Large accumulations of primary inadvertent point to an invalid implementation of ATEC, loose control, metering or accounting errors. A BA in such a situation should identify the source of the error(s) and make the corrections, recalculate the primary inadvertent from the time of the error, adjust the accumulated primary inadvertent caused by the error(s), validate the implementation of ATEC, set Lmax equal to L10 and continue to operate with ATEC reducing the accumulation as system parameters allow. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2014-03-31 |  |  | 120000000 | WECC-US | [5 empty] | WECC-US
14 | 131 |  | 1. | 132 | BAL-004-WECC-01 R4.1. | Each BA in the Western Interconnection shall use the change in Time Error distributed by the Interconnection Time Monitor. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2014-03-31 |  |  | 410000000 | WECC-US | [5 empty] | WECC-US
14 | 131 |  | 2. | 133 | BAL-004-WECC-01 R4.2. | All corrections to any previous hour Primary Inadvertent Interchange shall be added to the appropriate On- or Off-Peak accumulated Primary Inadvertent Interchange. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2014-03-31 |  |  | 420000000 | WECC-US | [5 empty] | WECC-US
14 | 131 |  | 3. | 134 | BAL-004-WECC-01 R4.3. | Month end Inadvertent Adjustments are 100% Primary Inadvertent Interchange and shall be added to the appropriate On- or Off-Peak accumulated Primary Inadvertent Interchange, unless such adjustments can be pinpointed to specific hours in which case R4.2 applies. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2014-03-31 |  |  | 430000000 | WECC-US | [5 empty] | WECC-US
14 | 131 |  | 4. | 135 | BAL-004-WECC-01 R4.4. | Each BA in the Western Interconnection shall synchronize its Time Error to the nearest 0.001 seconds of the system Time Error by comparing its reading at the designated time each day to the reading broadcast by the Interconnection Time Monitor. Any difference shall be applied as an adjustment to its current Time Error. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2014-03-31 |  |  | 440000000 | WECC-US | [5 empty] | WECC-US
140 | 1639 | 1640 | 1. | 1641 | PER-005-1 R1.1.1. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall update its list of BES company-specific reliability-related tasks performed by its System Operators each calendar year to identify new or modified tasks for inclusion in training. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-04-01 |  | 2016-06-30 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
140 | 1639 |  | 1. | 1640 | PER-005-1 R1.1. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall create a list of BES company-specific reliability-related tasks performed by its System Operators. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.1 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection its company-specific reliability-related task list, with the date of the last review and/or revision, as specified in R1.1. | 2013-04-01 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
140 | 1639 |  | 2. | 1642 | PER-005-1 R1.2. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall design and develop learning objectives and training materials based on the task list created in R1.1. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.2 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection its learning objectives and training materials, as specified in R1.2. | 2013-04-01 |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
140 | 1639 |  | 3. | 1643 | PER-005-1 R1.3. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall deliver the training established in R1.2. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.3 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection System Operator training records showing the names of the people trained, the title of the training delivered and the dates of delivery to show that it delivered the training, as specified in R1.3. | 2013-04-01 |  | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
140 | 1639 |  | 4. | 1644 | PER-005-1 R1.4. | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall conduct an annual evaluation of the training program established in R1, to identify any needed changes to the training program and shall implement the changes identified. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internalaudit results) that it performed an annual training program evaluation, as specified in R1.4 | 2013-04-01 |  | 2016-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
140 | 1645 |  | 1. | 1646 | PER-005-1 R2.1. | Within six months of a modification of the BES company-specific reliability-related tasks, each Reliability Coordinator, Balancing Authority and Transmission Operator shall verify each of its System Operator’s capabilities to perform the new or modified tasks. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-04-01 |  | 2016-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
140 | 1647 |  | 1. | 1648 | PER-005-1 R3.1. | Each Reliability Coordinator, Balancing Authority and Transmission Operator that has operational authority or control over Facilities with established IROLs or has established operating guides or protection systems to mitigate IROL violations shall provide each System Operator with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES during normal and emergency conditions. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2014-04-01 |  | 2016-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
141 | 1650 |  | 1. | 1651 | PRC-001-1 R2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2013-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
141 | 1650 |  | 2. | 1652 | PRC-001-1 R2.2. | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
141 | 1653 |  | 1. | 1654 | PRC-001-1 R3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2013-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
141 | 1653 |  | 2. | 1655 | PRC-001-1 R3.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
141 | 1657 |  | 1. | 1658 | PRC-001-1 R5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s protection systems. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2013-03-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
141 | 1657 |  | 2. | 1659 | PRC-001-1 R5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ protection systems. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1661 | 1662 | 1. | 1663 | PRC-002-1 R1.1.1. | Criteria for equipment location (e.g., by voltage, geographic area, station size, etc.). |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1661 | 1662 | 2. | 1664 | PRC-002-1 R1.1.2. | Devices to be monitored. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1661 |  | 1. | 1662 | PRC-002-1 R1.1. | Location, monitoring and recording requirements, including the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1665 | 1666 | 1. | 1667 | PRC-002-1 R2.1.1. | Criteria for equipment location (e.g., by voltage, geographic area, station size, etc.). |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1665 | 1666 | 2. | 1668 | PRC-002-1 R2.1.2. | Elements to be monitored at each location. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1665 | 1666 | 3. | 1669 | PRC-002-1 R2.1.3. | Electrical quantities to be recorded for each monitored element shall be sufficient to determine the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1665 | 1669 | 1. | 1670 | PRC-002-1 R2.1.3.1. | Three phase to neutral voltages. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 21310000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1665 | 1669 | 2. | 1671 | PRC-002-1 R2.1.3.2. | Three phase currents and neutral currents. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 21320000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1665 | 1669 | 3. | 1672 | PRC-002-1 R2.1.3.3. | Polarizing currents and voltages, if used. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 21330000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1665 | 1669 | 4. | 1673 | PRC-002-1 R2.1.3.4. | Frequency. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 21340000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1665 | 1669 | 5. | 1674 | PRC-002-1 R2.1.3.5. | Megawatts and megavars. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 21350000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1665 | 1675 | 1. | 1676 | PRC-002-1 R2.2.1. | Recording duration requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1665 | 1675 | 2. | 1677 | PRC-002-1 R2.2.2. | Minimum sampling rate of 16 samples per cycle. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1665 | 1675 | 3. | 1678 | PRC-002-1 R2.2.3. | Event triggering requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1665 |  | 1. | 1666 | PRC-002-1 R2.1. | Location, monitoring and recording requirements, including the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1665 |  | 2. | 1675 | PRC-002-1 R2.2. | Technical requirements, including the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1679 | 1680 | 1. | 1681 | PRC-002-1 R3.1.1. | Criteria for equipment location giving consideration to the following: - Site(s) in or near major load centers - Site(s) in or near major generation clusters - Site(s) in or near major voltage sensitive areas - Site(s) on both sides of major transmission interfaces - A major transmission junction - Elements associated with Interconnection Reliability Operating Limits - Major EHV interconnections between control areas - Coordination with neighboring regions within the interconnection |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1679 | 1680 | 2. | 1682 | PRC-002-1 R3.1.2. | Elements and number of phases to be monitored at each location. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1679 | 1680 | 3. | 1683 | PRC-002-1 R3.1.3. | Electrical quantities to be recorded for each monitored element shall be sufficient to determine the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1679 | 1683 | 1. | 1684 | PRC-002-1 R3.1.3.1. | Voltage, current and frequency. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 31310000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1679 | 1683 | 2. | 1685 | PRC-002-1 R3.1.3.2. | Megawatts and megavars. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 31320000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1679 | 1686 | 1. | 1687 | PRC-002-1 R3.2.1. | Capability for continuous recording for devices installed after January 1, 2009. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1679 | 1686 | 2. | 1688 | PRC-002-1 R3.2.2. | Each device shall sample data at a rate of at least 960 samples per second and shall record the RMS value of electrical quantities at a rate of at least 6 records per second. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1679 |  | 1. | 1680 | PRC-002-1 R3.1. | Location, monitoring and recording requirements including the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1679 |  | 2. | 1686 | PRC-002-1 R3.2. | Technical requirements, including the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1689 |  | 1. | 1690 | PRC-002-1 R4.1. | Criteria for events that require the collection of data from DMEs. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1689 |  | 2. | 1691 | PRC-002-1 R4.2. | List of entities that must be provided with recorded Disturbance data. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1689 |  | 3. | RP-2021-06-23-0000009 | PRC-002-1 R4.3. | Timetable for response to data request. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1689 |  | 4. | 1693 | PRC-002-1 R4.4. | Provision for reporting Disturbance data in a format which is capable of being viewed, read and analyzed with a generic COMTRADE1 analysis tool, |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1689 |  | 5. | 1694 | PRC-002-1 R4.5. | Naming of data files in conformance with the IEEE C37.232 Recommended Practice for Naming Time Sequence Data Files2. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
142 | 1689 |  | 6. | 1695 | PRC-002-1 R4.6. | Data content requirements and guidelines. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 460000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
143 | 1698 |  | 1. | 1699 | PRC-003-1 R1.1. | The Protection Systems to be reviewed and analyzed for Misoperations (due to theirpotential impact on BES reliability). |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
143 | 1698 |  | 2. | 1700 | PRC-003-1 R1.2. | Data reporting requirements (periodicity and format) for Misoperations. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
143 | 1698 |  | 3. | 1701 | PRC-003-1 R1.3. | Process for review, analysis follow up, and documentation of Corrective Action Plans for Misoperations. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
143 | 1698 |  | 4. | 1702 | PRC-003-1 R1.4. | Identification of the Regional Reliability Organization group responsible for the procedures and the process for approval of the procedures. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
145 | 1708 |  | 1. | 1709 | PRC-004-WECC-1 R1.1. | System Operators shall review all tripping of transmission elements and RAS operations to identify apparent Misoperations within 24 hours. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M1.1 Transmission Owners and Generation Owners shall have evidence that System Operating personnel reviewed all operations of Protection System and RAS within 24 hours. | 2011-06-27 |  | 2017-03-31 |  |  | 110000000 | WECC-US | [5 empty] | WECC-US
145 | 1708 |  | 2. | 1710 | PRC-004-WECC-1 R1.2. | System Protection personnel shall analyze all operations of Protection Systems and RAS within 20 business days for correctness to characterize whether a Misoperation has occurred that may not have been identified by System Operators. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M1.2 Transmission Owners and Generation Owners shall have evidence that System Protection personnel analyzed all operations of Protection System and RAS for correctness within 20 business days. | 2011-06-27 |  | 2017-03-31 |  |  | 120000000 | WECC-US | [5 empty] | WECC-US
145 | 1711 | 1713 | 1. | 1714 | PRC-004-WECC-1 R2.2.1. | Following identification of the Protection System or RAS Misoperation, Transmission Owners and Generator Owners shall remove from service within 22 hours for repair or modification the Protection System or RAS that misoperated. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. | 2011-10-01 |  | 2017-03-31 |  |  | 221000000 | WECC-US | [5 empty] | WECC-US
145 | 1711 | 1713 | 2. | 1715 | PRC-004-WECC-1 R2.2.2. | The Transmission Owner or Generator Owner shall repair or replace any Protection System or RAS that misoperated with a FEPS or FERAS within 20 business days of the date of removal. The Transmission Owner or Generator Owner shall remove the Element from service or disable the RAS if repair or replacement is not completed within 20 business days. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. | 2011-10-01 |  | 2017-03-31 |  |  | 222000000 | WECC-US | [5 empty] | WECC-US
145 | 1711 | 1716 | 1. | 1717 | PRC-004-WECC-1 R2.3.1. | When a FEPS is not available, the Transmission Owners shall remove the associated Element from service. |  | TO | [17 empty] | TO |  |  |  | M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. | 2011-10-01 |  | 2017-03-31 |  |  | 231000000 | WECC-US | [5 empty] | WECC-US
145 | 1711 | 1716 | 2. | 1718 | PRC-004-WECC-1 R2.3.2. | When FERAS is not available, then |  | GO, TOP |  |  |  |  | GO | [13 empty] | TOP |  |  | M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. | 2011-10-01 |  | 2017-03-31 |  |  | 232000000 | WECC-US | [5 empty] | WECC-US
145 | 1711 | 1718 | 1. | 1719 | PRC-004-WECC-1 R2.3.2.1. | The Generator Owners shall adjust generation to a reliable operating level, or |  | GO |  |  |  |  | GO | [16 empty] | M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. | 2011-10-01 |  | 2017-03-31 |  |  | 23210000 | WECC-US | [5 empty] | WECC-US
145 | 1711 | 1718 | 2. | 1720 | PRC-004-WECC-1 R2.3.2.2. | Transmission Operators shall adjust the SOL and operate the facilities within established limits. |  | TOP | [18 empty] | TOP |  |  |  | 2011-10-01 |  | 2017-03-31 |  |  | 23220000 | WECC-US | [5 empty] | WECC-US
145 | 1711 | 1721 | 1. | 1722 | PRC-004-WECC-1 R2.4.1. | Transmission Owners or Generator Owners shall repair or replace any Protection System or RAS that misoperated with FEPS and FERAS within 20 business days of the date of the Misoperation identification, or |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. | 2011-10-01 |  | 2017-03-31 |  |  | 241000000 | WECC-US | [5 empty] | WECC-US
145 | 1711 | 1721 | 2. | 1723 | PRC-004-WECC-1 R2.4.2. | Transmission Owners or Generator Owners shall remove from service the associated Element or RAS. [Time Horizon: Operations Assessment] |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | 2011-10-01 |  | 2017-03-31 |  |  | 242000000 | WECC-US | [5 empty] | WECC-US
145 | 1711 |  | 1. | 1712 | PRC-004-WECC-1 R2.1. | If the Protection System or RAS has a Security-Based Misoperation and two or more Functionally Equivalent Protection Systems (FEPS) or Functionally Equivalent RAS (FERAS) remain in service to ensure Bulk Electric System (BES) reliability, the Transmission Owners or Generator Owners shall remove from service the Protection System or RAS that misoperated within 22 hours following identification of the Misoperation. Repair or replacement of the failed Protection System or RAS is at the Transmission Owners’ and Generator Owners’ discretion. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. | 2011-06-27 |  | 2017-03-31 |  |  | 210000000 | WECC-US | [5 empty] | WECC-US
145 | 1711 |  | 2. | 1713 | PRC-004-WECC-1 R2.2. | If the Protection System or RAS has a Security-Based Misoperation and only one FEPS or FERAS remains in service to ensure BES reliability, the Transmission Owner or Generator Owner shall perform the following. [Time Horizon: Same-day Operations] |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. | 2011-06-27 |  | 2017-03-31 |  |  | 220000000 | WECC-US | [5 empty] | WECC-US
145 | 1711 |  | 3. | 1716 | PRC-004-WECC-1 R2.3. | If the Protection System or RAS has a Security-Based or Dependability-Based Misoperation and a FEPS and FERAS is not in service to ensure BES reliability, Transmission Owners or Generator Owners shall repair and place back in service within 22 hours the Protection System or RAS that misoperated. If this cannot be done, then Transmission Owners and Generator Owners shall perform the following. |  | GO, TO, TOP |  |  |  |  | GO | [12 empty] | TO | TOP |  |  | M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. | 2011-06-27 |  | 2017-03-31 |  |  | 230000000 | WECC-US | [5 empty] | WECC-US
145 | 1711 |  | 4. | 1721 | PRC-004-WECC-1 R2.4. | If the Protection System or RAS has a Dependability-Based Misoperation but has one or more FEPS or FERAS that operated correctly, the associated Element or transmission path may remain in service without removing from service the Protection System or RAS |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-06-27 |  | 2017-03-31 |  |  | 240000000 | WECC-US | [5 empty] | WECC-US
145 | 1724 |  | 1. | 1725 | PRC-004-WECC-1 R3.1. | Identification of a Misoperation of a Protection System and/or RAS, |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M3.1 Identification of all Protection System and RAS Misoperations and corrective actions taken or planned. | 2011-06-27 |  | 2017-03-31 |  |  | 310000000 | WECC-US | [5 empty] | WECC-US
145 | 1724 |  | 2. | 1726 | PRC-004-WECC-1 R3.2. | Completion of repairs or the replacement of Protection System and/or RAS that misoperated. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M3.2 Completion of repair or replacement of Protection System and/or RAS that misoperated. | 2011-06-27 |  | 2017-03-31 |  |  | 320000000 | WECC-US | [5 empty] | WECC-US
146 | 1727 |  | 1. | 1728 | PRC-005-1 R1.1. | Maintenance and testing intervals and their basis. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2011-09-25 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
146 | 1727 |  | 2. | 1729 | PRC-005-1 R1.2. | Summary of maintenance and testing procedures. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2011-09-25 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
146 | 1730 |  | 1. | 1731 | PRC-005-1 R2.1. | Evidence Protection System devices were maintained and tested within the defined intervals. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2011-09-25 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
146 | 1730 |  | 2. | 1732 | PRC-005-1 R2.2. | Date each Protection System device was last tested/maintained. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2011-09-25 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
147 | 1733 | 1735 | 1. | 1736 | PRC-006-0 R1.2.1. | Frequency set points. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
147 | 1733 | 1735 | 2. | 1737 | PRC-006-0 R1.2.2. | Size of corresponding load shedding blocks (% of connected loads.) |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
147 | 1733 | 1735 | 3. | 1738 | PRC-006-0 R1.2.3. | Intentional and total tripping time delays. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
147 | 1733 | 1735 | 4. | 1739 | PRC-006-0 R1.2.4. | Generation protection. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
147 | 1733 | 1735 | 5. | 1740 | PRC-006-0 R1.2.5. | Tie tripping schemes. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
147 | 1733 | 1735 | 6. | 1741 | PRC-006-0 R1.2.6. | Islanding schemes. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
147 | 1733 | 1735 | 7. | 1742 | PRC-006-0 R1.2.7. | Automatic load restoration schemes. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | 127000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
147 | 1733 | 1735 | 8. | 1743 | PRC-006-0 R1.2.8. | Any other schemes that are part of or impact the UFLS programs. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | 128000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
147 | 1733 | 1745 | 1. | 1746 | PRC-006-0 R1.4.1. | A review of the frequency set points and timing, and |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
147 | 1733 | 1745 | 2. | 1747 | PRC-006-0 R1.4.2. | Dynamic simulation of possible Disturbance that cause the Region or portions of the Region to experience the largest imbalance between Demand (Load) and generation. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
147 | 1733 |  | 1. | 1734 | PRC-006-0 R1.1. | Requirements for coordination of UFLS programs within the subregions, Regional Reliability Organization and, where appropriate, among Regional Reliability Organizations. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
147 | 1733 |  | 2. | 1735 | PRC-006-0 R1.2. | Design details shall include, but are not limited to: |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
147 | 1733 |  | 3. | 1744 | PRC-006-0 R1.3. | A Regional Reliability Organization UFLS program database. This database shall be updated as specified in the Regional Reliability Organization program (but at least every five years) and shall include sufficient information to model the UFLS program in dynamic simulations of the interconnected transmission systems. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
147 | 1733 |  | 4. | 1745 | PRC-006-0 R1.4. | Assessment and documentation of the effectiveness of the design and implementation of the Regional UFLS program. This assessment shall be conducted periodically and shall (at least every five years or as required by changes in system conditions) include, but not be limited to: |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
15 | 136 |  | 1. | 137 | BAL-005-0 R1.1. | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
15 | 136 |  | 2. | 138 | BAL-005-0 R1.2. | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
15 | 136 |  | 3. | 139 | BAL-005-0 R1.3. | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
15 | 157 |  | 1. | 158 | BAL-005-0 R8.1. | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
15 | 159 |  | 1. | 160 | BAL-005-0 R9.1. | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
15 | 142 |  | 1. | 143 | BAL-005-0 R12.1. | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
15 | 142 |  | 2. | 144 | BAL-005-0 R12.2. | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
15 | 142 |  | 3. | 145 | BAL-005-0 R12.3. | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
150 | 1755 |  | 1. | 1756 | PRC-009-0 R1.1. | A description of the event including initiating conditions. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2013-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
150 | 1755 |  | 2. | 1757 | PRC-009-0 R1.2. | A review of the UFLS set points and tripping times. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2013-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
150 | 1755 |  | 3. | 1758 | PRC-009-0 R1.3. | A simulation of the event. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2013-09-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
150 | 1755 |  | 4. | 1759 | PRC-009-0 R1.4. | A summary of the findings. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2013-09-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
151 | 1761 | 1762 | 1. | 1763 | PRC-010-0 R1.1.1. | Coordination of the UVLS programs with other protection and control systems in the Region and with other Regional Reliability Organizations, as appropriate. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
151 | 1761 | 1762 | 2. | 1764 | PRC-010-0 R1.1.2. | Simulations that demonstrate that the UVLS programs performance is consistent with Reliability Standards TPL-001-0, TPL-002-0, TPL-003-0 and TPL-004-0. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
151 | 1761 | 1762 | 3. | 1765 | PRC-010-0 R1.1.3. | A review of the voltage set points and timing. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
151 | 1761 |  | 1. | 1762 | PRC-010-0 R1.1. | This assessment shall include, but is not limited to: |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
152 | 1767 | 1768 | 1. | 1769 | PRC-011-0 R1.1.1. | Relays. |  | DP, TO |  | DP | [15 empty] | TO |  |  |  | Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. | 2007-06-18 |  | 2027-03-31 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
152 | 1767 | 1768 | 2. | 1770 | PRC-011-0 R1.1.2. | Instrument transformers. |  | DP, TO |  | DP | [15 empty] | TO |  |  |  | Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. | 2007-06-18 |  | 2027-03-31 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
152 | 1767 | 1768 | 3. | 1771 | PRC-011-0 R1.1.3. | Communications systems, where appropriate. |  | DP, TO |  | DP | [15 empty] | TO |  |  |  | Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. | 2007-06-18 |  | 2027-03-31 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
152 | 1767 | 1768 | 4. | 1772 | PRC-011-0 R1.1.4. | Batteries. |  | DP, TO |  | DP | [15 empty] | TO |  |  |  | Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. | 2007-06-18 |  | 2027-03-31 |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
152 | 1767 |  | 1. | 1768 | PRC-011-0 R1.1. | The UVLS system identification which shall include but is not limited to: |  | DP, TO |  | DP | [15 empty] | TO |  |  |  |  | 2007-06-18 |  | 2027-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
152 | 1767 |  | 1. DO NOT USE | RP-2021-07-09-0000040 | PRC-011-0 R1.1. DO NOT USE | The UVLS system identification which shall include but is not limited to: |  | DP, TO |  | DP | [15 empty] | TO |  |  |  | Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. | 2007-06-18 |  | 2027-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
152 | 1767 |  | 2. | 1773 | PRC-011-0 R1.2. | Documentation of maintenance and testing intervals and their basis. |  | DP, TO |  | DP | [15 empty] | TO |  |  |  | Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. | 2007-06-18 |  | 2027-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
152 | 1767 |  | 3. | 1774 | PRC-011-0 R1.3. | Summary of testing procedure. |  | DP, TO |  | DP | [15 empty] | TO |  |  |  | Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. | 2007-06-18 |  | 2027-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
152 | 1767 |  | 4. | 1775 | PRC-011-0 R1.4. | Schedule for system testing. |  | DP, TO |  | DP | [15 empty] | TO |  |  |  | Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. | 2007-06-18 |  | 2027-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
152 | 1767 |  | 5. | 1776 | PRC-011-0 R1.5. | Schedule for system maintenance. |  | DP, TO |  | DP | [15 empty] | TO |  |  |  | Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. | 2007-06-18 |  | 2027-03-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
152 | 1767 |  | 6. | 1777 | PRC-011-0 R1.6. | Date last tested/maintained. |  | DP, TO |  | DP | [15 empty] | TO |  |  |  | Each Transmission Owner and Distribution Provider that owns a UVLS system shall have documentation that its UVLS equipment maintenance and testing program conforms with Reliability Standard PRC-011-0_R1. | 2007-06-18 |  | 2027-03-31 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
153 | 1779 |  | 1. | 1780 | PRC-012-0 R1.1. | Description of the process for submitting a proposed SPS for Regional Reliability Organization review. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
153 | 1779 |  | 2. | 1781 | PRC-012-0 R1.2. | Requirements to provide data that describes design, operation, and modeling of an SPS. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
153 | 1779 |  | 3. | 1782 | PRC-012-0 R1.3. | Requirements to demonstrate that the SPS shall be designed so that a single SPS component failure, when the SPS was intended to operate, does not prevent the interconnected transmission system from meeting the performance requirements defined in Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
153 | 1779 |  | 4. | 1783 | PRC-012-0 R1.4. | Requirements to demonstrate that the inadvertent operation of an SPS shall meet the same performance requirement (TPL-001-0, TPL-002-0, and TPL-003-0) as that required of the contingency for which it was designed, and not exceed TPL-003-0. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
153 | 1779 |  | 5. | 1784 | PRC-012-0 R1.5. | Requirements to demonstrate the proposed SPS will coordinate with other protection and control systems and applicable Regional Reliability Organization Emergency procedures. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
153 | 1779 |  | 6. | 1785 | PRC-012-0 R1.6. | Regional Reliability Organization definition of misoperation. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
153 | 1779 |  | 7. | 1786 | PRC-012-0 R1.7. | Requirements for analysis and documentation of corrective action plans for all SPS misoperations. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
153 | 1779 |  | 8. | 1787 | PRC-012-0 R1.8. | Identification of the Regional Reliability Organization group responsible for the Regional Reliability Organization’s review procedure and the process for Regional Reliability Organization approval of the procedure. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
153 | 1779 |  | 9. | 1788 | PRC-012-0 R1.9. | Determination, as appropriate, of maintenance and testing requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
154 | 1790 |  | 1. | 1791 | PRC-013-0 R1.1. | Design Objectives — Contingencies and system conditions for which the SPS was designed, |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
154 | 1790 |  | 2. | 1792 | PRC-013-0 R1.2. | Operation — The actions taken by the SPS in response to Disturbance conditions, and |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
154 | 1790 |  | 3. | 1793 | PRC-013-0 R1.3. | Modeling — Information on detection logic or relay settings that control operation of the SPS. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
155 | 1797 |  | 1. | 1798 | PRC-014-0 R3.1. | Identification of group conducting the assessment and the date the assessment was performed. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
155 | 1797 |  | 2. | 1799 | PRC-014-0 R3.2. | Study years, system conditions, and contingencies analyzed in the technical studies on which the assessment is based and when those technical studies were performed. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
155 | 1797 |  | 3. | 1800 | PRC-014-0 R3.3. | Identification of SPSs that were found not to comply with NERC standards and Regional Reliability Organization criteria. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
155 | 1797 |  | 4. | 1801 | PRC-014-0 R3.4. | Discussion of any coordination problems found between a SPS and other protection and control systems. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
155 | 1797 |  | 5. | 1802 | PRC-014-0 R3.5. | Provide corrective action plans for non-compliant SPSs. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
159 | 1812 | 1813 | 1. | 1814 | PRC-017-0 R1.1.1. | Relays. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
159 | 1812 | 1813 | 2. | 1815 | PRC-017-0 R1.1.2. | Instrument transformers. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
159 | 1812 | 1813 | 3. | 1816 | PRC-017-0 R1.1.3. | Communications systems, where appropriate. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
159 | 1812 | 1813 | 4. | 1817 | PRC-017-0 R1.1.4. | Batteries. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
159 | 1812 |  | 1. | 1813 | PRC-017-0 R1.1. | SPS identification shall include but is not limited to: |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
159 | 1812 |  | 2. | 1818 | PRC-017-0 R1.2. | Documentation of maintenance and testing intervals and their basis. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
159 | 1812 |  | 3. | 1819 | PRC-017-0 R1.3. | Summary of testing procedure. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
159 | 1812 |  | 4. | 1820 | PRC-017-0 R1.4. | Schedule for system testing. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
159 | 1812 |  | 5. | 1821 | PRC-017-0 R1.5. | Schedule for system maintenance. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
159 | 1812 |  | 6. | 1822 | PRC-017-0 R1.6. | Date last tested/maintained. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
16 | 161 |  | 1. | 162 | BAL-005-0.1b R1.1. | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
16 | 161 |  | 2. | 163 | BAL-005-0.1b R1.2. | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
16 | 161 |  | 3. | 164 | BAL-005-0.1b R1.3. | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
16 | 182 |  | 1. | 183 | BAL-005-0.1b R8.1. | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
16 | 184 |  | 1. | 185 | BAL-005-0.1b R9.1. | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
16 | 167 |  | 1. | 168 | BAL-005-0.1b R12.1. | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
16 | 167 |  | 2. | 169 | BAL-005-0.1b R12.2. | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
16 | 167 |  | 3. | 170 | BAL-005-0.1b R12.3. | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
160 | 1824 |  | 1. | 1825 | PRC-018-1 R1.1. | Internal Clocks in DME devices shall be synchronized to within 2 milliseconds or less of Universal Coordinated Time scale (UTC) |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner and Generator Owner shall each have evidence that DMEs it is required to have meet the functional requirements specified in Requirement 1 and are installed in accordance with its associated Regional Reliability Organization’s requirements (R2). | 2007-06-18 |  | 2022-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
160 | 1824 |  | 2. | 1826 | PRC-018-1 R1.2. | Recorded data from each Disturbance shall be retrievable for ten calendar days.. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner and Generator Owner shall each have evidence that DMEs it is required to have meet the functional requirements specified in Requirement 1 and are installed in accordance with its associated Regional Reliability Organization’s requirements (R2). | 2007-06-18 |  | 2022-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
160 | 1828 |  | 1. | 1829 | PRC-018-1 R3.1. | Type of DME (sequence of event recorder, fault recorder, or dynamic disturbance recorder). |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2022-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
160 | 1828 |  | 1. DO NOT USE | RP-2021-07-09-0000044 | PRC-018-1 R3.1. DO NOT USE | Type of DME (sequence of event recorder, fault recorder, or dynamic disturbance recorder). |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) | 2007-06-18 |  | 2022-06-30 |  100% compliant six months after BOT adoption for already installed DME.  100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
160 | 1828 |  | 2. | 1830 | PRC-018-1 R3.2. | Make and model of equipment. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) | 2007-06-18 |  | 2022-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
160 | 1828 |  | 3. | 1831 | PRC-018-1 R3.3. | Installation location. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) | 2007-06-18 |  | 2022-06-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
160 | 1828 |  | 4. | 1832 | PRC-018-1 R3.4. | Operational status. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) | 2007-06-18 |  | 2022-06-30 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
160 | 1828 |  | 5. | 1833 | PRC-018-1 R3.5. | Date last tested. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) | 2007-06-18 |  | 2022-06-30 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
160 | 1828 |  | 6. | 1834 | PRC-018-1 R3.6. | Monitored elements, such as transmission circuit, bus section, etc. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) | 2007-06-18 |  | 2022-06-30 |  |  | 360000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
160 | 1828 |  | 7. | 1835 | PRC-018-1 R3.7. | Monitored devices, such as circuit breaker, disconnect status, alarms, etc. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) | 2007-06-18 |  | 2022-06-30 |  |  | 370000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
160 | 1828 |  | 8. | 1836 | PRC-018-1 R3.8. | Monitored electrical quantities, such as voltage, current, etc. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner and Generator Owner shall each have evidence it retained and provided recorded Disturbance data to entities in accordance with its associated Regional Reliability Organization’s Disturbance data reporting requirements. (R4 R5) | 2007-06-18 |  | 2022-06-30 |  |  | 380000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
160 | 1839 |  | 1. | 1840 | PRC-018-1 R6.1. | Maintenance and testing intervals and their basis. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2022-06-30 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
160 | 1839 |  | 2. | 1841 | PRC-018-1 R6.2. | Summary of maintenance and testing procedures. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2022-06-30 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
161 | 1842 |  | 1. | 1843 | PRC-020-1 R1.1. | Owner and operator of the UVLS program. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
161 | 1842 |  | 2. | 1844 | PRC-020-1 R1.2. | Size and location of customer load, or percent of connected load, to be interrupted. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
161 | 1842 |  | 3. | 1845 | PRC-020-1 R1.3. | Corresponding voltage set points and overall scheme clearing times. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
161 | 1842 |  | 4. | 1846 | PRC-020-1 R1.4. | Time delay from initiation to trip signal. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
161 | 1842 |  | 5. | 1847 | PRC-020-1 R1.5. | Breaker operating times. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
161 | 1842 |  | 6. | 1848 | PRC-020-1 R1.6. | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems. |  | RRO | [14 empty] | RRO | [9 empty] | 2017-03-31 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
162 | 1850 |  | 1. | 1851 | PRC-021-1 R1.1. | Size and location of customer load, or percent of connected load, to be interrupted. |  | DP, TO |  | DP | [15 empty] | TO |  |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
162 | 1850 |  | 2. | 1852 | PRC-021-1 R1.2. | Corresponding voltage set points and overall scheme clearing times. |  | DP, TO |  | DP | [15 empty] | TO |  |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
162 | 1850 |  | 3. | 1853 | PRC-021-1 R1.3. | Time delay from initiation to trip signal. |  | DP, TO |  | DP | [15 empty] | TO |  |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
162 | 1850 |  | 4. | 1854 | PRC-021-1 R1.4. | Breaker operating times. |  | DP, TO |  | DP | [15 empty] | TO |  |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
162 | 1850 |  | 5. | 1855 | PRC-021-1 R1.5. | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems. |  | DP, TO |  | DP | [15 empty] | TO |  |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
163 | 1857 |  | 1. | 1858 | PRC-022-1 R1.1. | A description of the event including initiating conditions. |  | DP, LSE, TOP |  | DP | [5 empty] | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
163 | 1857 |  | 2. | 1859 | PRC-022-1 R1.2. | A review of the UVLS set points and tripping times. |  | DP, LSE, TOP |  | DP | [5 empty] | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
163 | 1857 |  | 3. | 1860 | PRC-022-1 R1.3. | A simulation of the event, if deemed appropriate by the Regional Reliability Organization. For most events, analysis of sequence of events may be sufficient and dynamic simulations may not be needed. |  | DP, LSE, TOP |  | DP | [5 empty] | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
163 | 1857 |  | 4. | 1861 | PRC-022-1 R1.4. | A summary of the findings. |  | DP, LSE, TOP |  | DP | [5 empty] | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
163 | 1857 |  | 5. | 1862 | PRC-022-1 R1.5. | For any Misoperation, a Corrective Action Plan to avoid future Misoperations of a similar nature. |  | DP, LSE, TOP |  | DP | [5 empty] | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 | 1868 | 1. | 1869 | PRC-023-1 R1.12.1. | Set the maximum torque angle (MTA) to 90 degrees or the highest supported by the manufacturer. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 1121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 | 1868 | 2. | 1870 | PRC-023-1 R1.12.2. | Evaluate the relay loadability in amperes at the relay trip point at 0.85 per unit voltage and a power factor angle of 30 degrees. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 1122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 | 1868 | 3. | 1871 | PRC-023-1 R1.12.3. | Include a relay setting component of 87% of the current calculated in R1.12.2 in the Facility Rating determination for the circuit. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 1123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 | 1874 | 1. | 1875 | PRC-023-1 R1.3.1. | An infinite source (zero source impedance) with a 1.00 per unit bus voltage at each end of the line. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 | 1874 | 2. | 1876 | PRC-023-1 R1.3.2. | An impedance at each end of the line, which reflects the actual system source impedance with a 1.05 per unit voltage behind each source impedance. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 |  | 1. | 1865 | PRC-023-1 R1.1. | Set transmission line relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes). |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 |  | 10. | 1866 | PRC-023-1 R1.10. | Set transformer fault protection relays and transmission line relays on transmission lines terminated only with a transformer so that they do not operate at or below the greater of: - 150% of the applicable maximum transformer nameplate rating (expressed in amperes), including the forced cooled ratings corresponding to all installed supplemental cooling equipment. - 115% of the highest operator established emergency transformer rating. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 |  | 11. | 1867 | PRC-023-1 R1.11. | For transformer overload protection relays that do not comply with R1.10 set the relays according to one of the following: - Set the relays to allow the transformer to be operated at an overload level of at least 150% of the maximum applicable nameplate rating, or 115% of the highest operator established emergency transformer rating, whichever is greater. The protection must allow this overload for at least 15 minutes to allow for the operator to take controlled action to relieve the overload. - Install supervision for the relays using either a top oil or simulated winding hot spot temperature element. The setting should be no less than 100° C for the top oil or 140° C for the winding hot spot temperature . |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 |  | 12. | 1868 | PRC-023-1 R1.12. | When the desired transmission line capability is limited by the requirement to adequately protect the transmission line, set the transmission line distance relays to a maximum of 125% of the apparent impedance (at the impedance angle of the transmission line) subject to the following constraints: |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 |  | 13. | 1872 | PRC-023-1 R1.13. | Where other situations present practical limitations on circuit capability, set the phase protection relays so they do not operate at or below 115% of such limitations. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 |  | 2. | 1873 | PRC-023-1 R1.2. | Set transmission line relays so they do not operate at or below 115% of the highest seasonal 15-minute Facility Rating2 of a circuit (expressed in amperes). |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 |  | 3. | 1874 | PRC-023-1 R1.3. | Set transmission line relays so they do not operate at or below 115% of the maximum theoretical power transfer capability (using a 90-degree angle between the sending-end and receiving-end voltages and either reactance or complex impedance) of the circuit (expressed in amperes) using one of the following to perform the power transfer calculation: |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 |  | 4. | 1877 | PRC-023-1 R1.4. | Set transmission line relays on series compensated transmission lines so they do not operate at or below the maximum power transfer capability of the line, determined as the greater of: - 115% of the highest emergency rating of the series capacitor. - 115% of the maximum power transfer capability of the circuit (expressed in amperes), calculated in accordance with R1.3, using the full line inductive reactance. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 |  | 5. | 1878 | PRC-023-1 R1.5. | Set transmission line relays on weak source systems so they do not operate at or below 170% of the maximum end-of-line three-phase fault magnitude (expressed in amperes). |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 |  | 6. | 1879 | PRC-023-1 R1.6. | Set transmission line relays applied on transmission lines connected to generation stations remote to load so they do not operate at or below 230% of the aggregated generation nameplate capability. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 |  | 7. | 1880 | PRC-023-1 R1.7. | Set transmission line relays applied at the load center terminal, remote from generation stations, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 |  | 8. | 1881 | PRC-023-1 R1.8. | Set transmission line relays applied on the bulk system-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the system to the load under any system configuration. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1864 |  | 9. | 1882 | PRC-023-1 R1.9. | Set transmission line relays applied on the load-end of transmission lines that serve load remote to the bulk system so they do not operate at or below 115% of the maximum current flow from the load to the system under any system configuration. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2010-07-01 |  | 2012-06-30 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1884 | 1885 | 1. | 1886 | PRC-023-1 R3.1.1. | This process shall consider input from adjoining Planning Coordinators and affected Reliability Coordinators. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-11-17 |  | 2012-06-30 |  |  | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1884 |  | 1. | 1885 | PRC-023-1 R3.1. | The Planning Coordinator shall have a process to determine the facilities that are critical to the reliability of the Bulk Electric System. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-11-17 |  | 2012-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1884 |  | 2. | 1887 | PRC-023-1 R3.2. | The Planning Coordinator shall maintain a current list of facilities determined according to the process described in R3.1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-11-17 |  | 2012-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
164 | 1884 |  | 3. | 1888 | PRC-023-1 R3.3. | The Planning Coordinator shall provide a list of facilities to its Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within 30 days of the establishment of the initial list and within 30 days of any changes to the list. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-11-17 |  | 2012-06-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
168 | 1898 |  | 1. | 1899 | TOP-001-1 R7.1. | For a generator outage, the Generator Operator shall notify and coordinate with the Transmission Operator. The Transmission Operator shall notify the Reliability Coordinator and other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-11-20 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
168 | 1898 |  | 2. | 1900 | TOP-001-1 R7.2. | For a transmission facility, the Transmission Operator shall notify and coordinate with its Reliability Coordinator. The Transmission Operator shall notify other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-11-20 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
168 | 1898 |  | 3. | RP-2021-06-09-0000007 | TOP-001-1 R7.3. | When time does not permit such notifications and coordination, or when immediate action is required to prevent a hazard to the public, lengthy customer service interruption, or damage to facilities, the Generator Operator shall notify the Transmission Operator, and the Transmission Operator shall notify its Reliability Coordinator and adjacent Transmission Operators, at the earliest possible time. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-11-20 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
169 | 1908 |  | 1. | 1909 | TOP-002-2 R14.1. | Changes in real output capabilities. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2009-12-01 |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
169 | 1908 |  | 2. | 1910 | TOP-002-2 R14.2. | Automatic Voltage Regulator status and mode setting. (Retired August 1, 2007) |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2009-12-01 |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
169 | 1912 |  | 1. | 1913 | TOP-002-2 R16.1. | Changes in transmission facility status. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-12-01 |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
169 | 1912 |  | 2. | 1914 | TOP-002-2 R16.2. | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-12-01 |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
17 | 186 |  | 1. | 187 | BAL-005-0b R1.1. | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
17 | 186 |  | 2. | 188 | BAL-005-0b R1.2. | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
17 | 186 |  | 3. | 189 | BAL-005-0b R1.3. | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
17 | 207 |  | 1. | 208 | BAL-005-0b R8.1. | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
17 | 209 |  | 1. | 210 | BAL-005-0b R9.1. | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
17 | 192 |  | 1. | 193 | BAL-005-0b R12.1. | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
17 | 192 |  | 2. | 194 | BAL-005-0b R12.2. | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
17 | 192 |  | 3. | 195 | BAL-005-0b R12.3. | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
170 | 1931 |  | 1. | 1932 | TOP-002-2a R14.1. | Changes in real output capabilities. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-12-02 |  | 2011-10-19 |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
170 | 1931 |  | 2. | 1933 | TOP-002-2a R14.2. | Automatic Voltage Regulator status and mode setting. (Retired August 1, 2007) |  | GOP | [5 empty] | GOP | [16 empty] | 2009-12-02 |  | 2011-10-19 |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
170 | 1935 |  | 1. | 1936 | TOP-002-2a R16.1. | Changes in transmission facility status. |  | TOP | [18 empty] | TOP |  |  |  | 2009-12-02 |  | 2011-10-19 |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
170 | 1935 |  | 2. | 1937 | TOP-002-2a R16.2. | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP |  |  |  | 2009-12-02 |  | 2011-10-19 |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
171 | 1949 |  | 1. | 1950 | TOP-003-0 R1.1. | Each Generator Operator shall provide outage information daily to its Transmission Operator for scheduled generator outages planned for the next day (any foreseen outage of a generator greater than 50 MW). The Transmission Operator shall establish the outage reporting requirements. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
171 | 1949 |  | 2. | 1951 | TOP-003-0 R1.2. | Each Transmission Operator shall provide outage information daily to its Reliability Coordinator, and to affected Balancing Authorities and Transmission Operators for scheduled generator and bulk transmission outages planned for the next day (any foreseen outage of a transmission line or transformer greater than 100 kV or generator greater than 50 MW) that may collectively cause or contribute to an SOL or IROL violation or a regional operating area limitation. The Reliability Coordinator shall establish the outage reporting requirements. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
171 | 1949 |  | 3. | 1952 | TOP-003-0 R1.3. | Such information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
172 | 1956 |  | 1. | 1957 | TOP-003-1 R1.1. | Each Generator Operator shall provide outage information daily to its Transmission Operator for scheduled generator outages planned for the next day (any foreseen outage of a generator greater than 50 MW). The Transmission Operator shall establish the outage reporting requirements. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-05-23 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
172 | 1956 |  | 2. | 1958 | TOP-003-1 R1.2. | Each Transmission Operator shall provide outage information daily to affected Balancing Authorities and Transmission Operators for scheduled generator and bulk transmission outages planned for the next day (any foreseen outage of a transmission line or transformer greater than 100 kV or generator greater than 50 MW) that may collectively cause or contribute to an SOL or IROL violation or a regional operating area limitation. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2017-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
172 | 1956 |  | 3. | 1959 | TOP-003-1 R1.3. | Such information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-05-23 |  | 2017-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
173 | 1968 |  | 1. | 1969 | TOP-004-1 R6.1. | Equipment ratings. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
173 | 1968 |  | 2. | 1970 | TOP-004-1 R6.2. | Monitoring and controlling voltage levels and real and reactive power flows. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
173 | 1968 |  | 3. | 1971 | TOP-004-1 R6.3. | Switching transmission elements. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
173 | 1968 |  | 4. | 1972 | TOP-004-1 R6.4. | Planned outages of transmission elements. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
173 | 1968 |  | 5. | 1973 | TOP-004-1 R6.5. | Development of IROLs and SOLs. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
173 | 1968 |  | 6. | 1974 | TOP-004-1 R6.6. | Responding to IROL and SOL violations. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  | 660000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
174 | 1980 |  | 1. | 1981 | TOP-004-2 R6.1. | Monitoring and controlling voltage levels and real and reactive power flows. |  | TOP | [18 empty] | TOP |  |  |  | 2009-01-22 |  | 2017-03-31 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
174 | 1980 |  | 2. | 1982 | TOP-004-2 R6.2. | Switching transmission elements. |  | TOP | [18 empty] | TOP |  |  |  | 2009-01-22 |  | 2017-03-31 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
174 | 1980 |  | 3. | 1983 | TOP-004-2 R6.3. | Planned outages of transmission elements. |  | TOP | [18 empty] | TOP |  |  |  | 2009-01-22 |  | 2017-03-31 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
174 | 1980 |  | 4. | 1984 | TOP-004-2 R6.4. | Responding to IROL and SOL violations. |  | TOP | [18 empty] | TOP |  |  |  | 2009-01-22 |  | 2017-03-31 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
175 | 1985 |  | 1. | 1986 | TOP-005-1 R1.1. | Each Reliability Coordinator shall identify the data requirements from the list in Attachment 1-TOP-005-0 “Electric System Reliability Data” and any additional operating information requirements relating to operation of the bulk power system within the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
176 | 1990 |  | 1. | 1991 | TOP-005-1.1 R1.1. | Each Reliability Coordinator shall identify the data requirements from the list in Attachment 1-TOP-005-0 “Electric System Reliability Data” and any additional operating information requirements relating to operation of the bulk power system within the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2009-05-13 |  | 2011-05-25 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
179 | 2003 |  | 1. | 2004 | TOP-006-1 R1.1. | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2011-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
179 | 2003 |  | 2. | 2005 | TOP-006-1 R1.2. | Each Transmission Operator and Balancing Authority shall inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  | VSL Severe The responsible entity failed to inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
18 | 214 | 215 | 1. | 216 | BAL-006-1 R4.1.1. | The hourly values of Net Interchange Schedule. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
18 | 214 | 215 | 2. | 217 | BAL-006-1 R4.1.2. | The hourly integrated megawatt-hour values of Net Actual Interchange. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
18 | 214 |  | 1. | 215 | BAL-006-1 R4.1. | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
18 | 214 |  | 2. | 218 | BAL-006-1 R4.2. | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and Off-Peak hours of the month. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
18 | 214 |  | 3. | 219 | BAL-006-1 R4.3. | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
180 | 2012 |  | 1. | 2013 | TOP-006-2 R1.1. | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. | VSL - Severe The Generator Operator failed to inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. | GOP | [5 empty] | GOP | [16 empty] | 2011-05-23 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
180 | 2012 |  | 2. | 2014 | TOP-006-2 R1.2. | Each Transmission Operator and Balancing Authority shall inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2017-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
182 | 2026 |  | 1. | 2027 | TOP-007-WECC-1 R2.1. | If the path SOL decreases within 20 minutes before the start of the hour, the Transmission Operator shall adjust the Net Scheduled Interchange within 30 minutes to the new SOL value. Net Scheduled Interchange exceeding the new SOL during this 30-minute period will not be a violation of R2. |  | TOP | [18 empty] | TOP |  |  |  | 2011-06-27 |  | 2014-06-17 |  |  | 210000000 | WECC-US | [5 empty] | WECC-US
185 | 2033 | 2036 | 1. | 2037 | TPL-001-0 R1.3.1. | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2033 | 2036 | 2. | 2038 | TPL-001-0 R1.3.2. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2033 | 2036 | 3. | 2039 | TPL-001-0 R1.3.3. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2033 | 2036 | 4. | 2040 | TPL-001-0 R1.3.4. | Have established normal (pre-contingency) operating procedures in place. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2033 | 2036 | 5. | 2041 | TPL-001-0 R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2033 | 2036 | 6. | 2042 | TPL-001-0 R1.3.6. | Be performed for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2033 | 2036 | 7. | 2043 | TPL-001-0 R1.3.7. | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2033 | 2036 | 8. | 2044 | TPL-001-0 R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2033 | 2036 | 9. | 2045 | TPL-001-0 R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2033 |  | 1. | 2034 | TPL-001-0 R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2033 |  | 2. | 2035 | TPL-001-0 R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2033 |  | 3. | 2036 | TPL-001-0 R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2033 |  | 4. | 2046 | TPL-001-0 R1.4. | Address any planned upgrades needed to meet the performance requirements of Category A. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2047 | 2048 | 1. | 2049 | TPL-001-0 R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2047 | 2048 | 2. | 2050 | TPL-001-0 R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2047 | 2048 | 3. | 2051 | TPL-001-0 R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2047 |  | 1. | 2048 | TPL-001-0 R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
185 | 2047 |  | 2. | 2052 | TPL-001-0 R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2054 | 2057 | 1. | 2058 | TPL-001-0.1 R1.3.1. | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2054 | 2057 | 2. | 2059 | TPL-001-0.1 R1.3.2. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2054 | 2057 | 3. | 2060 | TPL-001-0.1 R1.3.3. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2054 | 2057 | 4. | 2061 | TPL-001-0.1 R1.3.4. | Have established normal (pre-contingency) operating procedures in place. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2054 | 2057 | 5. | 2062 | TPL-001-0.1 R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2054 | 2057 | 6. | 2063 | TPL-001-0.1 R1.3.6. | Be performed for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2054 | 2057 | 7. | 2064 | TPL-001-0.1 R1.3.7. | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2054 | 2057 | 8. | 2065 | TPL-001-0.1 R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2054 | 2057 | 9. | 2066 | TPL-001-0.1 R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2054 |  | 1. | 2055 | TPL-001-0.1 R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2054 |  | 2. | 2056 | TPL-001-0.1 R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2054 |  | 3. | 2057 | TPL-001-0.1 R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2054 |  | 4. | 2067 | TPL-001-0.1 R1.4. | Address any planned upgrades needed to meet the performance requirements of Category A. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2068 | 2069 | 1. | 2070 | TPL-001-0.1 R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2068 | 2069 | 2. | 2071 | TPL-001-0.1 R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2068 | 2069 | 3. | 2072 | TPL-001-0.1 R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2068 |  | 1. | 2069 | TPL-001-0.1 R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
186 | 2068 |  | 2. | 2073 | TPL-001-0.1 R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 | 2078 | 1. | 2079 | TPL-002-0 R1.3.1. | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 | 2078 | 10. | 2080 | TPL-002-0 R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 1310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 | 2078 | 11. | 2081 | TPL-002-0 R1.3.11. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 1311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 | 2078 | 12. | 2082 | TPL-002-0 R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 1312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 | 2078 | 2. | 2083 | TPL-002-0 R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 | 2078 | 3. | 2084 | TPL-002-0 R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 | 2078 | 4. | 2085 | TPL-002-0 R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 | 2078 | 5. | 2086 | TPL-002-0 R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 | 2078 | 6. | 2087 | TPL-002-0 R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 | 2078 | 7. | 2088 | TPL-002-0 R1.3.7. | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 | 2078 | 8. | 2089 | TPL-002-0 R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 | 2078 | 9. | 2090 | TPL-002-0 R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 |  | 1. | 2076 | TPL-002-0 R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 |  | 2. | 2077 | TPL-002-0 R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 |  | 3. | 2078 | TPL-002-0 R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 |  | 4. | 2091 | TPL-002-0 R1.4. | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2075 |  | 5. | 2092 | TPL-002-0 R1.5. | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2093 | 2094 | 1. | 2095 | TPL-002-0 R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2093 | 2094 | 2. | 2096 | TPL-002-0 R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2093 | 2094 | 3. | 2097 | TPL-002-0 R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2093 |  | 1. | 2094 | TPL-002-0 R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
187 | 2093 |  | 2. | 2098 | TPL-002-0 R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 | 2103 | 1. | 2104 | TPL-002-0a R1.3.1. | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 | 2103 | 10. | 2105 | TPL-002-0a R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 1310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 | 2103 | 11. | 2106 | TPL-002-0a R1.3.11. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 1311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 | 2103 | 12. | 2107 | TPL-002-0a R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 1312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 | 2103 | 2. | 2108 | TPL-002-0a R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 | 2103 | 3. | 2109 | TPL-002-0a R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 | 2103 | 4. | 2110 | TPL-002-0a R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 | 2103 | 5. | 2111 | TPL-002-0a R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 | 2103 | 6. | 2112 | TPL-002-0a R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 | 2103 | 7. | 2113 | TPL-002-0a R1.3.7. | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 | 2103 | 8. | 2114 | TPL-002-0a R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 | 2103 | 9. | 2115 | TPL-002-0a R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 |  | 1. | 2101 | TPL-002-0a R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 |  | 2. | 2102 | TPL-002-0a R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 |  | 3. | 2103 | TPL-002-0a R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories,, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 |  | 4. | 2116 | TPL-002-0a R1.4. | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2100 |  | 5. | 2117 | TPL-002-0a R1.5. | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2118 | 2119 | 1. | 2120 | TPL-002-0a R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2118 | 2119 | 2. | 2121 | TPL-002-0a R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2118 | 2119 | 3. | 2122 | TPL-002-0a R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2118 |  | 1. | 2119 | TPL-002-0a R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
188 | 2118 |  | 2. | 2123 | TPL-002-0a R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 | 2128 | 1. | 2129 | TPL-003-0 R1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 | 2128 | 10. | 2130 | TPL-003-0 R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 1310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 | 2128 | 11. | 2131 | TPL-003-0 R1.3.11. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 1311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 | 2128 | 12. | 2132 | TPL-003-0 R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 1312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 | 2128 | 2. | 2133 | TPL-003-0 R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 | 2128 | 3. | 2134 | TPL-003-0 R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 | 2128 | 4. | 2135 | TPL-003-0 R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 | 2128 | 5. | 2136 | TPL-003-0 R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 | 2128 | 6. | 2137 | TPL-003-0 R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 | 2128 | 7. | 2138 | TPL-003-0 R1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 | 2128 | 8. | 2139 | TPL-003-0 R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 | 2128 | 9. | 2140 | TPL-003-0 R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 |  | 1. | 2126 | TPL-003-0 R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 |  | 2. | 2127 | TPL-003-0 R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 |  | 3. | 2128 | TPL-003-0 R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 |  | 4. | 2141 | TPL-003-0 R1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2125 |  | 5. | 2142 | TPL-003-0 R1.5. | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2143 | 2144 | 1. | 2145 | TPL-003-0 R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2143 | 2144 | 2. | 2146 | TPL-003-0 R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2143 | 2144 | 3. | 2147 | TPL-003-0 R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2143 |  | 1. | 2144 | TPL-003-0 R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
189 | 2143 |  | 2. | 2148 | TPL-003-0 R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
19 | 224 | 225 | 1. | 226 | BAL-006-1.1 R4.1.1. | The hourly values of Net Interchange Schedule. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-03-31 |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
19 | 224 | 225 | 2. | 227 | BAL-006-1.1 R4.1.2. | The hourly integrated megawatt-hour values of Net Actual Interchange. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-03-31 |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
19 | 224 |  | 1. | 225 | BAL-006-1.1 R4.1. | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
19 | 224 |  | 2. | 228 | BAL-006-1.1 R4.2. | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and Off-Peak hours of the month. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
19 | 224 |  | 3. | 229 | BAL-006-1.1 R4.3. | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 | 2153 | 1. | 2154 | TPL-003-0a R1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 | 2153 | 10. | 2155 | TPL-003-0a R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 1310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 | 2153 | 11. | 2156 | TPL-003-0a R1.3.11. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 1311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 | 2153 | 12. | 2157 | TPL-003-0a R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 1312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 | 2153 | 2. | 2158 | TPL-003-0a R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 | 2153 | 3. | 2159 | TPL-003-0a R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 | 2153 | 4. | 2160 | TPL-003-0a R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 | 2153 | 5. | 2161 | TPL-003-0a R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 | 2153 | 6. | 2162 | TPL-003-0a R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 | 2153 | 7. | 2163 | TPL-003-0a R1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 | 2153 | 8. | 2164 | TPL-003-0a R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 | 2153 | 9. | 2165 | TPL-003-0a R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 |  | 1. | 2151 | TPL-003-0a R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 |  | 2. | 2152 | TPL-003-0a R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 |  | 3. | 2153 | TPL-003-0a R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 |  | 4. | 2166 | TPL-003-0a R1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2150 |  | 5. | 2167 | TPL-003-0a R1.5. | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2168 | 2169 | 1. | 2170 | TPL-003-0a R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2168 | 2169 | 2. | 2171 | TPL-003-0a R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2168 | 2169 | 3. | 2172 | TPL-003-0a R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2168 |  | 1. | 2169 | TPL-003-0a R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
190 | 2168 |  | 2. | 2173 | TPL-003-0a R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
191 | 2175 | 2178 | 1. | 2179 | TPL-004-0 R1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
191 | 2175 | 2178 | 2. | 2180 | TPL-004-0 R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
191 | 2175 | 2178 | 3. | 2181 | TPL-004-0 R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
191 | 2175 | 2178 | 4. | 2182 | TPL-004-0 R1.3.4. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
191 | 2175 | 2178 | 5. | 2183 | TPL-004-0 R1.3.5. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
191 | 2175 | 2178 | 6. | 2184 | TPL-004-0 R1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
191 | 2175 | 2178 | 7. | 2185 | TPL-004-0 R1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
191 | 2175 | 2178 | 8. | 2186 | TPL-004-0 R1.3.8. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
191 | 2175 | 2178 | 9. | 2187 | TPL-004-0 R1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
191 | 2175 |  | 1. | 2176 | TPL-004-0 R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
191 | 2175 |  | 2. | 2177 | TPL-004-0 R1.2. | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
191 | 2175 |  | 3. | 2178 | TPL-004-0 R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
191 | 2175 |  | 4. | 2188 | TPL-004-0 R1.4. | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
192 | 2190 | 2191 | 1 | RP-2021-06-14-0000001 | TPL-005-0 R1.1.1 | Winter |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
192 | 2190 | 2191 | 2. | 2193 | TPL-005-0 R1.1.2. | Summer. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
192 | 2190 | 2191 | 3. | 2194 | TPL-005-0 R1.1.3. | Other system conditions as deemed appropriate by the Regional Reliability Organization. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
192 | 2190 |  | 1. | 2191 | TPL-005-0 R1.1. | Current year: |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
192 | 2190 |  | 2. | 2195 | TPL-005-0 R1.2. | Near-term planning horizons (years one through five). Detailed assessments shall be conducted. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
192 | 2190 |  | 3. | 2196 | TPL-005-0 R1.3. | Longer-term planning horizons (years six through ten). Assessment shall focus on the analysis of trends in resources and transmission Adequacy, other industry trends and developments, and reliability concerns. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
192 | 2190 |  | 4. | 2197 | TPL-005-0 R1.4. | Inter-Regional reliability assessments to demonstrate that the performance of these systems is in compliance with NERC Reliability Standards TPL-001-0, TPL-002-0, TPL-003-0, TPL-004-0 and respective Regional transmission and generation criteria. These assessments shall also identify key reliability issues and the risks and uncertainties affecting Adequacy and Security. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
192 | 2199 |  | 1. | 2200 | TPL-005-0 R3.1. | Security assessments. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
192 | 2199 |  | 2. | 2201 | TPL-005-0 R3.2. | Operational assessments. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
192 | 2199 |  | 3. | 2202 | TPL-005-0 R3.3. | Evaluations of emergency response preparedness. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
192 | 2199 |  | 4. | 2203 | TPL-005-0 R3.4. | Adequacy of fuel supply and hydro conditions. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
192 | 2199 |  | 5. | 2204 | TPL-005-0 R3.5. | Reliability impacts of new or proposed environmental rules and regulations. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
192 | 2199 |  | 6. | 2205 | TPL-005-0 R3.6. | Reliability impacts of new or proposed legislation that affects, has affected, or has the potential to affect the Adequacy of the interconnected Bulk Electric Systems in North America. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 360000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
193 | 2206 |  | 1. | 2207 | TPL-006-0 R1.1. | Electric Demand and Net Energy for Load (actual and projected demands and Net Energy for Load, forecast methodologies, forecast assumptions and uncertainties, and treatment of Demand-Side Management.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
193 | 2206 |  | 2. | 2208 | TPL-006-0 R1.2. | Resource Adequacy and supporting information (Regional assessment reports, existing and planned resource data, resource availability and characteristics, and fuel types and requirements.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
193 | 2206 |  | 3. | 2209 | TPL-006-0 R1.3. | Demand-Side resources and their characteristics (program ratings, effects on annual system loads and load shapes, contractual arrangements, and program durations.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
193 | 2206 |  | 4. | 2210 | TPL-006-0 R1.4. | Supply-side resources and their characteristics (existing and planned generator units, Ratings, performance characteristics, fuel types and availability, and real and reactive capabilities.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
193 | 2206 |  | 5. | 2211 | TPL-006-0 R1.5. | Transmission system and supporting information (thermal, voltage, and Stability Limits, contingency analyses, system restoration, system modeling and data requirements, and protection systems.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
193 | 2206 |  | 6. | 2212 | TPL-006-0 R1.6. | System operations and supporting information (extreme weather impacts, Interchange Transactions, and Congestion impacts on the reliability of the interconnected Bulk Electric Systems.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
193 | 2206 |  | 7. | 2213 | TPL-006-0 R1.7. | Environmental and regulatory issues and impacts (air and water quality issues, and impacts of existing, new, and proposed regulations and legislation.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
194 | 2219 |  | 1. | 2220 | VAR-001-1 R3.1. | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
194 | 2219 |  | 2. | 2221 | VAR-001-1 R3.2. | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
194 | 2224 |  | 1. | RP-2021-06-03-0000001 | VAR-001-1 R6.1. | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
194 | 2228 |  | 1. | 2229 | VAR-001-1 R9.1. | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
195 | 2235 |  | 1. | 2236 | VAR-001-1a R3.1. | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-05-21 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
195 | 2235 |  | 2. | 2237 | VAR-001-1a R3.2. | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-05-21 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
195 | 2240 |  | 1. | RP-2021-06-03-0000002 | VAR-001-1a R6.1. | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-05-21 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
195 | 2244 |  | 1. | 2245 | VAR-001-1a R9.1. | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-05-21 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
196 | 2247 |  | 1. | RP-2021-06-03-0000005 | VAR-002-1 R2.1. | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-08-02 |  | 2008-08-26 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
196 | 2247 |  | 2. | RP-2021-06-03-0000006 | VAR-002-1 R2.2. | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-08-02 |  | 2008-08-26 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
196 | 2250 |  | 1. | 2251 | VAR-002-1 R3.1. | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2008-08-26 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
196 | 2250 |  | 2. | 2252 | VAR-002-1 R3.2. | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2008-08-26 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
196 | 2253 | 2254 | 1. | 2255 | VAR-002-1 R4.1.1. | Tap settings. |  | GO |  |  |  |  | GO | [17 empty] | 2007-08-02 |  | 2008-08-26 |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
196 | 2253 | 2254 | 2. | 2256 | VAR-002-1 R4.1.2. | Available fixed tap ranges. |  | GO |  |  |  |  | GO | [17 empty] | 2007-08-02 |  | 2008-08-26 |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
196 | 2253 | 2254 | 3. | 2257 | VAR-002-1 R4.1.3. | Impedance data. |  | GO |  |  |  |  | GO | [17 empty] | 2007-08-02 |  | 2008-08-26 |  |  | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
196 | 2253 | 2254 | 4. | 2258 | VAR-002-1 R4.1.4. | The +/- voltage range with step-change in % for load-tap changing transformers. |  | GO |  |  |  |  | GO | [17 empty] | 2007-08-02 |  | 2008-08-26 |  |  | 414000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
196 | 2253 |  | 1. | 2254 | VAR-002-1 R4.1. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2008-08-26 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
196 | 2259 |  | 1. | 2260 | VAR-002-1 R5.1. | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2008-08-26 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
197 | 2262 |  | 1. | RP-2021-06-03-0000007 | VAR-002-1.1a R2.1. | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
197 | 2262 |  | 2. | RP-2021-06-03-0000008 | VAR-002-1.1a R2.2. | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
197 | 2265 |  | 1. | 2266 | VAR-002-1.1a R3.1. | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
197 | 2265 |  | 2. | 2267 | VAR-002-1.1a R3.2. | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
197 | 2268 | 2269 | 1. | 2270 | VAR-002-1.1a R4.1.1. | Tap settings. |  | GO |  |  |  |  | GO | [17 empty] | 2009-05-13 |  | 2010-09-15 |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
197 | 2268 | 2269 | 2. | 2271 | VAR-002-1.1a R4.1.2. | Available fixed tap ranges. |  | GO |  |  |  |  | GO | [17 empty] | 2009-05-13 |  | 2010-09-15 |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
197 | 2268 | 2269 | 3. | 2272 | VAR-002-1.1a R4.1.3. | Impedance data. |  | GO |  |  |  |  | GO | [17 empty] | 2009-05-13 |  | 2010-09-15 |  |  | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
197 | 2268 | 2269 | 4. | 2273 | VAR-002-1.1a R4.1.4. | The +/- voltage range with step-change in % for load-tap changing transformers. |  | GO |  |  |  |  | GO | [17 empty] | 2009-05-13 |  | 2010-09-15 |  |  | 414000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
197 | 2268 |  | 1. | 2269 | VAR-002-1.1a R4.1. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO |  |  |  |  | GO | [17 empty] | 2009-05-13 |  | 2010-09-15 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
197 | 2274 |  | 1. | 2275 | VAR-002-1.1a R5.1. | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
198 | 2277 |  | 1. | RP-2021-06-03-0000009 | VAR-002-1.1b R2.1. | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
198 | 2277 |  | 2. | RP-2021-06-03-0000010 | VAR-002-1.1b R2.2. | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
198 | 2280 |  | 1. | 2281 | VAR-002-1.1b R3.1. | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
198 | 2280 |  | 2. | 2282 | VAR-002-1.1b R3.2. | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
198 | 2283 | 2284 | 1. | 2285 | VAR-002-1.1b R4.1.1. | Tap settings. |  | GO |  |  |  |  | GO | [17 empty] | 2010-09-16 |  | 2013-06-30 |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
198 | 2283 | 2284 | 2. | 2286 | VAR-002-1.1b R4.1.2. | Available fixed tap ranges. |  | GO |  |  |  |  | GO | [17 empty] | 2010-09-16 |  | 2013-06-30 |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
198 | 2283 | 2284 | 3. | 2287 | VAR-002-1.1b R4.1.3. | Impedance data. |  | GO |  |  |  |  | GO | [17 empty] | 2010-09-16 |  | 2013-06-30 |  |  | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
198 | 2283 | 2284 | 4. | 2288 | VAR-002-1.1b R4.1.4. | The +/- voltage range with step-change in % for load-tap changing transformers. |  | GO |  |  |  |  | GO | [17 empty] | 2010-09-16 |  | 2013-06-30 |  |  | 414000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
198 | 2283 |  | 1. | 2284 | VAR-002-1.1b R4.1. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO |  |  |  |  | GO | [17 empty] | 2010-09-16 |  | 2013-06-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
198 | 2289 |  | 1. | 2290 | VAR-002-1.1b R5.1. | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
199 | 2292 |  | 1. | RP-2021-06-03-0000011 | VAR-002-1a R2.1. | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
199 | 2292 |  | 2. | RP-2021-06-03-0000012 | VAR-002-1a R2.2. | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
199 | 2295 |  | 1. | 2296 | VAR-002-1a R3.1. | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
199 | 2295 |  | 2. | 2297 | VAR-002-1a R3.2. | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
199 | 2298 | 2299 | 1. | 2300 | VAR-002-1a R4.1.1. | Tap settings. |  | GO |  |  |  |  | GO | [17 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
199 | 2298 | 2299 | 2. | 2301 | VAR-002-1a R4.1.2. | Available fixed tap ranges. |  | GO |  |  |  |  | GO | [17 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
199 | 2298 | 2299 | 3. | 2302 | VAR-002-1a R4.1.3. | Impedance data. |  | GO |  |  |  |  | GO | [17 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
199 | 2298 | 2299 | 4. | 2303 | VAR-002-1a R4.1.4. | The +/- voltage range with step-change in % for load-tap changing transformers. |  | GO |  |  |  |  | GO | [17 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 414000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
199 | 2298 |  | 1. | 2299 | VAR-002-1a R4.1. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO |  |  |  |  | GO | [17 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
199 | 2304 |  | 1. | 2305 | VAR-002-1a R5.1. | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
200 | 2306 |  | 1. | RP-2021-06-24-0000076 | VAR-002-WECC-1 R1.1. | The synchronous generator or synchronous condenser operates for less than five percent of all hours during any calendar quarter. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-07-01 |  | 2015-03-31 |  |  | 110000000 | WECC-US | [5 empty] | WECC-US
200 | 2306 |  | 10. | 2308 | VAR-002-WECC-1 R1.10. | If AVR exhibits instability due to operation of a Load Tap Changer (LTC) transformer in the area, the Transmission Operator may authorize the Generator Operator to operate the excitation system in modes other than automatic voltage control until the system configuration changes. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | 110000000 | WECC-US | [5 empty] | WECC-US
200 | 2306 |  | 2. | 2309 | VAR-002-WECC-1 R1.2. | Performing maintenance and testing up to a maximum of seven calendar days per calendar quarter. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | 120000000 | WECC-US | [5 empty] | WECC-US
200 | 2306 |  | 3. | 2310 | VAR-002-WECC-1 R1.3. | AVR exhibits instability due to abnormal system configuration. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | 130000000 | WECC-US | [5 empty] | WECC-US
200 | 2306 |  | 4. | 2311 | VAR-002-WECC-1 R1.4. | Due to component failure, the AVR may be out of service up to 60 consecutive days for repair per incident. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | 140000000 | WECC-US | [5 empty] | WECC-US
200 | 2306 |  | 5. | 2312 | VAR-002-WECC-1 R1.5. | Due to a component failure, the AVR may be out of service up to one year provided the Generator Operator or Transmission Operator submits documentation identifying the need for time to obtain replacement parts and if required to schedule an outage. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | 150000000 | WECC-US | [5 empty] | WECC-US
200 | 2306 |  | 6. | 2313 | VAR-002-WECC-1 R1.6. | Due to a component failure, the AVR may be out of service up to 24 months provided the Generator Operator or Transmission Operator submits documentation identifying the need for time for excitation system replacement (replace the AVR, limiters, and controls but not necessarily the power source and power bridge) and to schedule an outage. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | 160000000 | WECC-US | [5 empty] | WECC-US
200 | 2306 |  | 7. | 2314 | VAR-002-WECC-1 R1.7. | The synchronous generator or synchronous condenser has not achieved Commercial Operation. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | 170000000 | WECC-US | [5 empty] | WECC-US
200 | 2306 |  | 8. | RP-2021-06-24-0000077 | VAR-002-WECC-1 R1.8. | The Transmission Operator directs the Generator Operator to operate the synchronous generator, and the AVR is unavailable for service. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-07-01 |  | 2015-03-31 |  |  | 180000000 | WECC-US | [5 empty] | WECC-US
200 | 2306 |  | 9. | 2316 | VAR-002-WECC-1 R1.9. | The Reliability Coordinator directs Transmission Operator to operate the synchronous condenser, and the AVR is unavailable for service. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | 190000000 | WECC-US | [5 empty] | WECC-US
201 | 2318 |  | 1. | RP-2021-06-25-0000008 | VAR-501-WECC-1 R1.1. | The synchronous generator operates for less than five percent of all hours during any calendar quarter. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-07-01 |  | 2015-03-31 |  |  | 110000000 | WECC-US | [5 empty] | WECC-US
201 | 2318 |  | 10. | 2320 | VAR-501-WECC-1 R1.10. | Due to a component failure, the PSS may be out of service up to 24 months provided the Generator Operator submits documentation identifying the need for time for PSS replacement and to schedule an outage. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | 110000000 | WECC-US | [5 empty] | WECC-US
201 | 2318 |  | 11. | 2321 | VAR-501-WECC-1 R1.11. | The synchronous generator has not achieved Commercial Operation. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | 111000000 | WECC-US | [5 empty] | WECC-US
201 | 2318 |  | 12. | 2322 | VAR-501-WECC-1 R1.12. | The Transmission Operator directs the Generator Operator to operate the synchronous generator, and the PSS is unavailable for service. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | 112000000 | WECC-US | [5 empty] | WECC-US
201 | 2318 |  | 2. | 2323 | VAR-501-WECC-1 R1.2. | Performing maintenance and testing up to a maximum of seven calendar days per calendar quarter. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | 120000000 | WECC-US | [5 empty] | WECC-US
201 | 2318 |  | 3. | 2324 | VAR-501-WECC-1 R1.3. | PSS exhibits instability due to abnormal system configuration. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | 130000000 | WECC-US | [5 empty] | WECC-US
201 | 2318 |  | 4. | RP-2021-06-25-0000004 | VAR-501-WECC-1 R1.4. | Unit is operating in the synchronous condenser mode (very near zero real power level). |  | GOP | [5 empty] | GOP | [16 empty] | 2011-07-01 |  | 2015-03-31 |  |  | 140000000 | WECC-US | [5 empty] | WECC-US
201 | 2318 |  | 5. | RP-2021-06-25-0000006 | VAR-501-WECC-1 R1.5. | Unit is generating less power than its design limit for effective PSS operation. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-07-01 |  | 2015-03-31 |  |  | 150000000 | WECC-US | [5 empty] | WECC-US
201 | 2318 |  | 6. | RP-2021-06-25-0000007 | VAR-501-WECC-1 R1.6. | Unit is passing through a range of output that is a known “rough zone” (range in which a hydro unit is experiencing excessive vibration). |  | GOP | [5 empty] | GOP | [16 empty] | 2011-07-01 |  | 2015-03-31 |  |  | 160000000 | WECC-US | [5 empty] | WECC-US
201 | 2318 |  | 7. | 2328 | VAR-501-WECC-1 R1.7. | The generator AVR is not in service. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | 170000000 | WECC-US | [5 empty] | WECC-US
201 | 2318 |  | 8. | 2329 | VAR-501-WECC-1 R1.8. | Due to component failure, the PSS may be out of service up to 60 consecutive days for repair per incident. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | 180000000 | WECC-US | [5 empty] | WECC-US
201 | 2318 |  | 9. | 2330 | VAR-501-WECC-1 R1.9. | Due to a component failure, the PSS may be out of service up to one year provided the Generator Operator submits documentation identifying the need for time to obtain replacement parts and if required to schedule an outage. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | 190000000 | WECC-US | [5 empty] | WECC-US
204 | 2334 |  | 1. | 2335 | IRO-006-4.1 R1.1. | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection provided in Attachment 1-IRO-006-4. The TLR procedure alone is an inappropriate and ineffective tool to mitigate an IROL violation due to the time required to implement the procedure. Other acceptable and more effective procedures to mitigate actual IROL violations include: reconfiguration, redispatch, or load shedding. |  | RC | [11 empty] | RC | [10 empty] | 2009-12-10 |  | 2011-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
204 | 2334 |  | 2. | 2336 | IRO-006-4.1 R1.2. | The Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is the WECC Unscheduled Flow Reduction Procedure provided at: http://www.wecc.biz/documents/library/UFAS/UFAS_mitigation_plan_rev_2001-clean_8-8-03.pdf. |  | RC | [11 empty] | RC | [10 empty] | 2009-12-10 |  | 2011-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
204 | 2334 |  | 3. | 2337 | IRO-006-4.1 R1.3. | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: http://www.ercot.com/mktrules/protocols/current.html |  | RC | [11 empty] | RC | [10 empty] | 2009-12-10 |  | 2011-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
207 | 2346 |  | 1. | 2347 | TPL-006-0.1 R1.1. | Electric Demand and Net Energy for Load (actual and projected demands and Net Energy for Load, forecast methodologies, forecast assumptions and uncertainties, and treatment of Demand-Side Management.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
207 | 2346 |  | 2. | 2348 | TPL-006-0.1 R1.2. | Resource Adequacy and supporting information (Regional assessment reports, existing and planned resource data, resource availability and characteristics, and fuel types and requirements.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
207 | 2346 |  | 3. | 2349 | TPL-006-0.1 R1.3. | Demand-Side resources and their characteristics (program ratings, effects on annual system loads and load shapes, contractual arrangements, and program durations.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
207 | 2346 |  | 4. | 2350 | TPL-006-0.1 R1.4. | Supply-side resources and their characteristics (existing and planned generator units, Ratings, performance characteristics, fuel types and availability, and real and reactive capabilities.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
207 | 2346 |  | 5. | 2351 | TPL-006-0.1 R1.5. | Transmission system and supporting information (thermal, voltage, and Stability Limits, contingency analyses, system restoration, system modeling and data requirements, and protection systems.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
207 | 2346 |  | 6. | 2352 | TPL-006-0.1 R1.6. | System operations and supporting information (extreme weather impacts, Interchange Transactions, and Congestion impacts on the reliability of the interconnected Bulk Electric Systems.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
207 | 2346 |  | 7. | 2353 | TPL-006-0.1 R1.7. | Environmental and regulatory issues and impacts (air and water quality issues, and impacts of existing, new, and proposed regulations and legislation.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
208 | 2354 | 2356 | 1. | 2357 | CIP-002-2 R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
208 | 2354 | 2356 | 2. | 2358 | CIP-002-2 R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
208 | 2354 | 2356 | 3. | 2359 | CIP-002-2 R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
208 | 2354 | 2356 | 4. | 2360 | CIP-002-2 R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
208 | 2354 | 2356 | 5. | 2361 | CIP-002-2 R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
208 | 2354 | 2356 | 6. | 2362 | CIP-002-2 R1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
208 | 2354 | 2356 | 7. | 2363 | CIP-002-2 R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 127000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
208 | 2354 |  | 1. | 2355 | CIP-002-2 R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
208 | 2354 |  | 2. | 2356 | CIP-002-2 R1.2. | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
208 | 2365 |  | 1. | 2366 | CIP-002-2 R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
208 | 2365 |  | 2. | 2367 | CIP-002-2 R3.2. | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
208 | 2365 |  | 3. | 2368 | CIP-002-2 R3.3. | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2370 |  | 1. | 2371 | CIP-003-2 R1.1. | The cyber security policy addresses the requirements in Standards CIP-002-2 through CIP-009-2, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2370 |  | 2. | 2372 | CIP-003-2 R1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2370 |  | 3. | 2373 | CIP-003-2 R1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2374 |  | 1. | 2375 | CIP-003-2 R2.1. | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2374 |  | 2. | 2376 | CIP-003-2 R2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2374 |  | 3. | 2377 | CIP-003-2 R2.3. | Where allowed by Standards CIP-002-2 through CIP-009-2, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2374 |  | 4. | 2378 | CIP-003-2 R2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2379 |  | 1. | 2380 | CIP-003-2 R3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2379 |  | 2. | 2381 | CIP-003-2 R3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2379 |  | 3. | 2382 | CIP-003-2 R3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2383 |  | 1. | 2384 | CIP-003-2 R4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-2, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2383 |  | 3. | 2386 | CIP-003-2 R4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2387 | 2388 | 1. | 2389 | CIP-003-2 R5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2387 | 2388 | 2. | 2390 | CIP-003-2 R5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2387 |  | 1. | 2388 | CIP-003-2 R5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2387 |  | 2. | 2391 | CIP-003-2 R5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
209 | 2387 |  | 3. | 2392 | CIP-003-2 R5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
210 | 2395 | 2397 | 1. | 2398 | CIP-004-2 R2.2.1. | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
210 | 2395 | 2397 | 2. | 2399 | CIP-004-2 R2.2.2. | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
210 | 2395 | 2397 | 3. | 2400 | CIP-004-2 R2.2.3. | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
210 | 2395 | 2397 | 4. | 2401 | CIP-004-2 R2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 224000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
210 | 2395 |  | 1. | 2396 | CIP-004-2 R2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
210 | 2395 |  | 2. | 2397 | CIP-004-2 R2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-2, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
210 | 2395 |  | 3. | 2402 | CIP-004-2 R2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
210 | 2403 |  | 1. | 2404 | CIP-004-2 R3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
210 | 2403 |  | 2. | 2405 | CIP-004-2 R3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
210 | 2403 |  | 3. | 2406 | CIP-004-2 R3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
210 | 2407 |  | 1. | 2408 | CIP-004-2 R4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
210 | 2407 |  | 2. | 2409 | CIP-004-2 R4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2410 |  | 1. | 2411 | CIP-005-2 R1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2410 |  | 2. | 2412 | CIP-005-2 R1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2410 |  | 3. | 2413 | CIP-005-2 R1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2410 |  | 4. | 2414 | CIP-005-2 R1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2410 |  | 5. | 2415 | CIP-005-2 R1.5. | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirement R3; Standard CIP-007-2 Requirements R1 and R3 through R9; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2410 |  | 6. | 2416 | CIP-005-2 R1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2417 | 2422 | 1. | 2423 | CIP-005-2 R2.5.1. | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 251000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2417 | 2422 | 2. | 2424 | CIP-005-2 R2.5.2. | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 252000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2417 | 2422 | 3. | 2425 | CIP-005-2 R2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 253000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2417 | 2422 | 4. | 2426 | CIP-005-2 R2.5.4. | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 254000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2417 |  | 1. | 2418 | CIP-005-2 R2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2417 |  | 2. | 2419 | CIP-005-2 R2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2417 |  | 3. | 2420 | CIP-005-2 R2.3. | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2417 |  | 4. | 2421 | CIP-005-2 R2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2417 |  | 5. | 2422 | CIP-005-2 R2.5. | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2417 |  | 6. | 2427 | CIP-005-2 R2.6. | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2428 |  | 1. | 2429 | CIP-005-2 R3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2428 |  | 2. | 2430 | CIP-005-2 R3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2431 |  | 1. | 2432 | CIP-005-2 R4.1. | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2431 |  | 2. | 2433 | CIP-005-2 R4.2. | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2431 |  | 3. | 2434 | CIP-005-2 R4.3. | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2431 |  | 4. | 2435 | CIP-005-2 R4.4. | A review of controls for default accounts, passwords, and network management community strings; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2431 |  | 5. | 2436 | CIP-005-2 R4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2437 |  | 1. | 2438 | CIP-005-2 R5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-2 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-2 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2437 |  | 2. | 2439 | CIP-005-2 R5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
211 | 2437 |  | 3. | 2440 | CIP-005-2 R5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
212 | 2441 |  | 1. | 2442 | CIP-006-2 R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
212 | 2441 |  | 2. | 2443 | CIP-006-2 R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
212 | 2441 |  | 3. | 2444 | CIP-006-2 R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
212 | 2441 |  | 4. | 2445 | CIP-006-2 R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
212 | 2441 |  | 5. | 2446 | CIP-006-2 R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
212 | 2441 |  | 6. | 2447 | CIP-006-2 R1.6. | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
212 | 2441 |  | 7. | RP-2021-06-15-0000012 | CIP-006-2 R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-07-14 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
212 | 2441 |  | 8. | 2449 | CIP-006-2 R1.8. | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
212 | 2450 |  | 1. | 2451 | CIP-006-2 R2.1. | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
212 | 2450 |  | 2. | 2452 | CIP-006-2 R2.2. | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
212 | 2458 |  | 1. | 2459 | CIP-006-2 R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
212 | 2458 |  | 2. | 2460 | CIP-006-2 R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
212 | 2458 |  | 3. | 2461 | CIP-006-2 R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2462 |  | 1. | 2463 | CIP-007-2 R1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2462 |  | 2. | 2464 | CIP-007-2 R1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2462 |  | 3. | 2465 | CIP-007-2 R1.3. | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2466 |  | 1. | 2467 | CIP-007-2 R2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2466 |  | 2. | 2468 | CIP-007-2 R2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2466 |  | 3. | 2469 | CIP-007-2 R2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2470 |  | 1. | 2471 | CIP-007-2 R3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2470 |  | 2. | 2472 | CIP-007-2 R3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2473 |  | 1. | 2474 | CIP-007-2 R4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2473 |  | 2. | 2475 | CIP-007-2 R4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2476 | 2477 | 1. | 2478 | CIP-007-2 R5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-2 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2476 | 2477 | 2. | 2479 | CIP-007-2 R5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2476 | 2477 | 3. | 2480 | CIP-007-2 R5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-2 Requirement R5 and Standard CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2476 | 2481 | 1. | 2482 | CIP-007-2 R5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  | 521000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2476 | 2481 | 2. | 2483 | CIP-007-2 R5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  | 522000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2476 | 2481 | 3. | 2484 | CIP-007-2 R5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  | 523000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2476 | 2485 | 1. | 2486 | CIP-007-2 R5.3.1. | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  | 531000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2476 | 2485 | 2. | 2487 | CIP-007-2 R5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  | 532000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2476 | 2485 | 3. | 2488 | CIP-007-2 R5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  | 533000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2476 |  | 1. | 2477 | CIP-007-2 R5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2476 |  | 2. | 2481 | CIP-007-2 R5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2476 |  | 3. | 2485 | CIP-007-2 R5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2489 |  | 1. | 2490 | CIP-007-2 R6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2489 |  | 2. | 2491 | CIP-007-2 R6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2489 |  | 3. | 2492 | CIP-007-2 R6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2489 |  | 4. | 2493 | CIP-007-2 R6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2489 |  | 5. | 2494 | CIP-007-2 R6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2495 |  | 1. | 2496 | CIP-007-2 R7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2495 |  | 2. | 2497 | CIP-007-2 R7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2495 |  | 3. | 2498 | CIP-007-2 R7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2499 |  | 1. | 2500 | CIP-007-2 R8.1. | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2499 |  | 2. | 2501 | CIP-007-2 R8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2499 |  | 3. | 2502 | CIP-007-2 R8.3. | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
213 | 2499 |  | 4. | 2503 | CIP-007-2 R8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | 840000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
214 | 2505 |  | 1. | 2506 | CIP-008-2 R1.1. | Procedures to characterize and classify events as reportable Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
214 | 2505 |  | 2. | 2507 | CIP-008-2 R1.2. | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
214 | 2505 |  | 3. | 2508 | CIP-008-2 R1.3. | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
214 | 2505 |  | 4. | 2509 | CIP-008-2 R1.4. | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
214 | 2505 |  | 5. | 2510 | CIP-008-2 R1.5. | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
214 | 2505 |  | 6. | 2511 | CIP-008-2 R1.6. | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. Testing the Cyber Security Incident response plan does not require removing a component or system from service during the test. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
215 | 2513 |  | 1. | 2514 | CIP-009-2 R1.1. | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
215 | 2513 |  | 2. | 2515 | CIP-009-2 R1.2. | Define the roles and responsibilities of responders. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2523 |  | 1. | 2524 | NUC-001-2 R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2523 |  | 2. | 2525 | NUC-001-2 R4.2. | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2523 |  | 3. | 2526 | NUC-001-2 R4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2532 | 1. | 2533 | NUC-001-2 R9.1.1. | Definitions of key terms used in the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2014-01-21 |  |  | 911000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2532 | 2. | 2534 | NUC-001-2 R9.1.2. | Names of the responsible entities, organizational relationships, and responsibilities related to the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2014-01-21 |  |  | 912000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2532 | 3. | 2535 | NUC-001-2 R9.1.3. | A requirement to review the agreement(s) at least every three years. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2014-01-21 |  |  | 913000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2532 | 4. | 2536 | NUC-001-2 R9.1.4. | A dispute resolution mechanism. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2014-01-21 |  |  | 914000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2537 | 1. | 2538 | NUC-001-2 R9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 921000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2537 | 2. | 2539 | NUC-001-2 R9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 922000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2537 | 3. | 2540 | NUC-001-2 R9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 923000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2541 | 1. | 2542 | NUC-001-2 R9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 931000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2541 | 2. | 2543 | NUC-001-2 R9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 932000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2541 | 3. | 2544 | NUC-001-2 R9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 933000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2541 | 4. | 2545 | NUC-001-2 R9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 934000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2541 | 5. | 2546 | NUC-001-2 R9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. . |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 935000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2541 | 6. | 2547 | NUC-001-2 R9.3.6. | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 936000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2541 | 7. | 2548 | NUC-001-2 R9.3.7. | Coordination of the NPIRs with transmission system Special Protection Systems and underfrequency and undervoltage load shedding programs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 937000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2549 | 1. | 2550 | NUC-001-2 R9.4.1. | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 941000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2549 | 2. | 2551 | NUC-001-2 R9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 942000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2549 | 3. | 2552 | NUC-001-2 R9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 943000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2549 | 4. | 2553 | NUC-001-2 R9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 944000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 | 2549 | 5. | 2554 | NUC-001-2 R9.4.5. | Provisions for personnel training, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 945000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 |  | 1. | 2532 | NUC-001-2 R9.1. | Administrative elements: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2014-01-21 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 |  | 2. | 2537 | NUC-001-2 R9.2. | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 |  | 3. | 2541 | NUC-001-2 R9.3. | Operations and maintenance coordination: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 930000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
216 | 2531 |  | 4. | 2549 | NUC-001-2 R9.4. | Communications and training: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | 940000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
217 | 2556 |  | 1. | 2557 | EOP-001-2 R2.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
217 | 2556 |  | 2. | 2558 | EOP-001-2 R2.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
217 | 2556 |  | 3. | 2559 | EOP-001-2 R2.3. | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
217 | 2560 |  | 1. | 2561 | EOP-001-2 R3.1. | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
217 | 2560 |  | 2. | 2562 | EOP-001-2 R3.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
217 | 2560 |  | 3. | 2563 | EOP-001-2 R3.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
217 | 2560 |  | 4. | 2564 | EOP-001-2 R3.4. | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
217 | 2567 |  | 1. | 2568 | EOP-001-2 R6.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
217 | 2567 |  | 2. | 2569 | EOP-001-2 R6.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
217 | 2567 |  | 3. | 2570 | EOP-001-2 R6.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
217 | 2567 |  | 4. | 2571 | EOP-001-2 R6.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2572 |  | 1. | 2573 | EOP-005-2 R1.1. | Strategies for system restoration that are coordinated with the Reliability Coordinator’s high level strategy for restoring the Interconnection. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2572 |  | 2. | 2574 | EOP-005-2 R1.2. | A description of how all Agreements or mutually agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2572 |  | 3. | 2575 | EOP-005-2 R1.3. | Procedures for restoring interconnections with other Transmission Operators under the direction of the Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2572 |  | 4. | 2576 | EOP-005-2 R1.4. | Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2572 |  | 5. | 2577 | EOP-005-2 R1.5. | Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2572 |  | 6. | 2578 | EOP-005-2 R1.6. | Identification of acceptable operating voltage and frequency limits during restoration. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2572 |  | 7. | 2579 | EOP-005-2 R1.7. | Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2572 |  | 8. | 2580 | EOP-005-2 R1.8. | Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2572 |  | 9. | 2581 | EOP-005-2 R1.9. | Operating Processes for transferring authority back to the Balancing Authority in accordance with the Reliability Coordinator’s criteria. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2600 |  | 1. | 2601 | EOP-005-2 R3.1. | If there are no changes to the previously submitted restoration plan, the Transmission Operator shall confirm annually on a predetermined schedule to its Reliability Coordinator that it has reviewed its restoration plan and no changes were necessary. (Retirement approved by FERC effective January 21, 2014.) |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2602 |  | 1. | 2603 | EOP-005-2 R4.1. | Each Transmission Operator shall submit its revised restoration plan to its Reliability Coordinator for approval within the same 90 calendar day period. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2605 |  | 1. | 2606 | EOP-005-2 R6.1. | The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2605 |  | 2. | 2607 | EOP-005-2 R6.2. | The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2605 |  | 3. | 2608 | EOP-005-2 R6.3. | The capability of generating resources required to control voltages and frequency within acceptable operating limits. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2611 | 2613 | 1. | 2614 | EOP-005-2 R9.2.1. | The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. |  | TOP | [18 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  | 921000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2611 | 2613 | 2. | 2615 | EOP-005-2 R9.2.2. | The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. |  | TOP | [18 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  | 922000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2611 |  | 1. | 2612 | EOP-005-2 R9.1. | The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2611 |  | 2. | 2613 | EOP-005-2 R9.2. | A list of required tests including: |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2611 |  | 3. | 2616 | EOP-005-2 R9.3. | The minimum duration of each of the required tests. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 930000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2582 |  | 1. | 2583 | EOP-005-2 R10.1. | System restoration plan including coordination with the Reliability Coordinator and Generator Operators included in the restoration plan. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2582 |  | 2. | 2584 | EOP-005-2 R10.2. | Restoration priorities. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2582 |  | 3. | 2585 | EOP-005-2 R10.3. | Building of cranking paths. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2582 |  | 4. | 2586 | EOP-005-2 R10.4. | Synchronizing (re-energized sections of the System). |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2592 |  | 1. | 2593 | EOP-005-2 R16.1. | Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R9. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2592 |  | 2. | 2594 | EOP-005-2 R16.2. | Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2595 |  | 1. | 2596 | EOP-005-2 R17.1. | System restoration plan including coordination with the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 171000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
218 | 2595 |  | 2. | 2597 | EOP-005-2 R17.2. | The procedures documented in Requirement R14. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 172000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
219 | 2617 |  | 1. | 2618 | EOP-006-2 R1.1. | A description of the high level strategy to be employed during restoration events for restoring the Interconnection including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
219 | 2617 |  | 2. | 2619 | EOP-006-2 R1.2. | Operating Processes for restoring the Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
219 | 2617 |  | 3. | 2620 | EOP-006-2 R1.3. | Descriptions of the elements of coordination between individual Transmission Operator restoration plans. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
219 | 2617 |  | 4. | 2621 | EOP-006-2 R1.4. | Descriptions of the elements of coordination of restoration plans with neighboring Reliability Coordinators. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
219 | 2617 |  | 5. | 2622 | EOP-006-2 R1.5. | Criteria and conditions for reestablishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
219 | 2617 |  | 6. | 2623 | EOP-006-2 R1.6. | Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
219 | 2617 |  | 7. | 2624 | EOP-006-2 R1.7. | Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
219 | 2617 |  | 8. | 2625 | EOP-006-2 R1.8. | Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
219 | 2617 |  | 9. | 2626 | EOP-006-2 R1.9. | Criteria for transferring operations and authority back to the Balancing Authority. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
219 | 2631 |  | 1. | 2632 | EOP-006-2 R4.1. | If the Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved in 30 calendar days. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
219 | 2633 |  | 1. | 2634 | EOP-006-2 R5.1. | The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall approve or disapprove, with stated reasons, the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
219 | 2638 |  | 1. | 2639 | EOP-006-2 R9.1. | The coordination role of the Reliability Coordinator. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
219 | 2638 |  | 2. | 2640 | EOP-006-2 R9.2. | Reestablishing the Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
219 | 2627 |  | 1. | 2628 | EOP-006-2 R10.1. | Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least every two calendar years. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2644 |  | 1. | 2651 | CIP-007-2a R1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2644 |  | 2. | 2652 | CIP-007-2a R1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2644 |  | 3. | 2650 | CIP-007-2a R1.3. | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2643 |  | 1. | 2654 | CIP-007-2a R2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2643 |  | 2. | 2653 | CIP-007-2a R2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2643 |  | 3. | 2655 | CIP-007-2a R2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2649 |  | 1. | 2656 | CIP-007-2a R3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2649 |  | 2. | 2657 | CIP-007-2a R3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2646 |  | 1. | 2659 | CIP-007-2a R4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2646 |  | 2. | 2658 | CIP-007-2a R4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2647 | 2660 | 1. | 2667 | CIP-007-2a R5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 521000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2647 | 2660 | 2. | 2668 | CIP-007-2a R5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 522000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2647 | 2660 | 3. | 2666 | CIP-007-2a R5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 523000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2647 | 2661 | 1. | 2664 | CIP-007-2a R5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-2 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2647 | 2661 | 2. | 2663 | CIP-007-2a R5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2647 | 2661 | 3. | 2665 | CIP-007-2a R5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-2 Requirement R5 and Standard CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2647 | 2662 | 1. | 2670 | CIP-007-2a R5.3.1. | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 531000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2647 | 2662 | 2. | 2671 | CIP-007-2a R5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 532000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2647 | 2662 | 3. | 2669 | CIP-007-2a R5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  | 533000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2647 |  | 1. | 2661 | CIP-007-2a R5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2647 |  | 2. | 2660 | CIP-007-2a R5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2647 |  | 3. | 2662 | CIP-007-2a R5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2641 |  | 1. | 2676 | CIP-007-2a R6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2641 |  | 2. | 2674 | CIP-007-2a R6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2641 |  | 3. | 2675 | CIP-007-2a R6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2641 |  | 4. | 2673 | CIP-007-2a R6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2641 |  | 5. | 2672 | CIP-007-2a R6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2642 |  | 1. | 2678 | CIP-007-2a R7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2642 |  | 2. | 2677 | CIP-007-2a R7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2642 |  | 3. | 2679 | CIP-007-2a R7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2645 |  | 1. | 2683 | CIP-007-2a R8.1. | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2645 |  | 2. | 2680 | CIP-007-2a R8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2645 |  | 3. | 2681 | CIP-007-2a R8.3. | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
220 | 2645 |  | 4. | 2682 | CIP-007-2a R8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | 840000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2685 |  | 1. | 2690 | FAC-010-2.1 R1.1. | Be applicable for developing SOLs used in the planning horizon. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2685 |  | 2. | 2691 | FAC-010-2.1 R1.2. | State that SOLs shall not exceed associated Facility Ratings. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2685 |  | 3. | 2689 | FAC-010-2.1 R1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2688 | 2692 | 1. | 2702 | FAC-010-2.1 R2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 231000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2688 | 2692 | 2. | 2701 | FAC-010-2.1 R2.3.2. | System reconfiguration through manual or automatic control or protection actions. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 232000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2688 | 2693 | 1. | 2700 | FAC-010-2.1 R2.2.1. | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2688 | 2693 | 2. | 2699 | FAC-010-2.1 R2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2688 | 2693 | 3. | 2698 | FAC-010-2.1 R2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2688 | 2697 | 1. | 2703 | FAC-010-2.1 R2.6.1. | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 261000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2688 |  | 1. | 2694 | FAC-010-2.1 R2.1. | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2688 |  | 2. | 2693 | FAC-010-2.1 R2.2. | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2688 |  | 3. | 2692 | FAC-010-2.1 R2.3. | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2688 |  | 4. | RP-2021-06-22-0000001 | FAC-010-2.1 R2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2688 |  | 5. | 2696 | FAC-010-2.1 R2.5. | Starting with all Facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2688 |  | 6. | 2697 | FAC-010-2.1 R2.6. | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2684 |  | 1. | 2708 | FAC-010-2.1 R3.1. | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2684 |  | 2. | 2709 | FAC-010-2.1 R3.2. | Selection of applicable Contingencies. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2684 |  | 3. | 2704 | FAC-010-2.1 R3.3. | Level of detail of system models used to determine SOLs. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2684 |  | 4. | 2705 | FAC-010-2.1 R3.4. | Allowed uses of Special Protection Systems or Remedial Action Plans. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2684 |  | 5. | 2706 | FAC-010-2.1 R3.5. | Anticipated transmission system configuration, generation dispatch and Load level. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2684 |  | 6. | 2707 | FAC-010-2.1 R3.6. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 360000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2686 |  | 1. | 2712 | FAC-010-2.1 R4.1. | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2686 |  | 2. | 2710 | FAC-010-2.1 R4.2. | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
221 | 2686 |  | 3. | 2711 | FAC-010-2.1 R4.3. | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
222 | 2713 | 2715 | 1. | 2716 | CIP-002-3 R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
222 | 2713 | 2715 | 2. | 2717 | CIP-002-3 R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
222 | 2713 | 2715 | 3. | 2718 | CIP-002-3 R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
222 | 2713 | 2715 | 4. | 2719 | CIP-002-3 R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
222 | 2713 | 2715 | 5. | 2720 | CIP-002-3 R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
222 | 2713 | 2715 | 6. | 2721 | CIP-002-3 R1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
222 | 2713 | 2715 | 7. | 2722 | CIP-002-3 R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | 127000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
222 | 2713 |  | 1. | 2714 | CIP-002-3 R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
222 | 2713 |  | 2. | 2715 | CIP-002-3 R1.2. | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
222 | 2724 |  | 1. | 2725 | CIP-002-3 R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
222 | 2724 |  | 2. | 2726 | CIP-002-3 R3.2. | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
222 | 2724 |  | 3. | 2727 | CIP-002-3 R3.3. | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2729 |  | 1. | 2730 | CIP-003-3 R1.1. | The cyber security policy addresses the requirements in Standards CIP-002-3 through CIP-009-3, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2729 |  | 2. | 2731 | CIP-003-3 R1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2729 |  | 3. | 2732 | CIP-003-3 R1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2733 |  | 1. | 2734 | CIP-003-3 R2.1. | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2733 |  | 2. | 2735 | CIP-003-3 R2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2733 |  | 3. | 2736 | CIP-003-3 R2.3. | Where allowed by Standards CIP-002-3 through CIP-009-3, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2733 |  | 4. | 2737 | CIP-003-3 R2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2738 |  | 1. | 2739 | CIP-003-3 R3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2738 |  | 2. | 2740 | CIP-003-3 R3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2738 |  | 3. | 2741 | CIP-003-3 R3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2742 |  | 1. | 2743 | CIP-003-3 R4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-3, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2742 |  | 2. | 2744 | CIP-003-3 R4.2. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2742 |  | 3. | 2745 | CIP-003-3 R4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2746 | 2747 | 1. | 2748 | CIP-003-3 R5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2746 | 2747 | 2. | 2749 | CIP-003-3 R5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2746 |  | 1. | 2747 | CIP-003-3 R5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2746 |  | 2. | 2750 | CIP-003-3 R5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
223 | 2746 |  | 3. | 2751 | CIP-003-3 R5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
224 | 2754 | 2756 | 1. | 2757 | CIP-004-3 R2.2.1. | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2012-12-11 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
224 | 2754 | 2756 | 2. | 2758 | CIP-004-3 R2.2.2. | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2012-12-11 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
224 | 2754 | 2756 | 3. | 2759 | CIP-004-3 R2.2.3. | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2012-12-11 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
224 | 2754 | 2756 | 4. | 2760 | CIP-004-3 R2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2012-12-11 |  |  | 224000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
224 | 2754 |  | 1. | 2755 | CIP-004-3 R2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
224 | 2754 |  | 2. | 2756 | CIP-004-3 R2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-3, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
224 | 2754 |  | 3. | 2761 | CIP-004-3 R2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
224 | 2762 |  | 1. | 2763 | CIP-004-3 R3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
224 | 2762 |  | 2. | 2764 | CIP-004-3 R3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
224 | 2762 |  | 3. | 2765 | CIP-004-3 R3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
224 | 2766 |  | 1. | 2767 | CIP-004-3 R4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
224 | 2766 |  | 2. | 2768 | CIP-004-3 R4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2769 |  | 1. | 2770 | CIP-005-3 R1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2769 |  | 2. | 2771 | CIP-005-3 R1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2769 |  | 3. | 2772 | CIP-005-3 R1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2769 |  | 4. | 2773 | CIP-005-3 R1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2769 |  | 5. | 2774 | CIP-005-3 R1.5. | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirement R3; Standard CIP-007-3 Requirements R1 and R3 through R9; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2769 |  | 6. | 2775 | CIP-005-3 R1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2776 | 2781 | 1. | 2782 | CIP-005-3 R2.5.1. | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  | 251000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2776 | 2781 | 2. | 2783 | CIP-005-3 R2.5.2. | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  | 252000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2776 | 2781 | 3. | 2784 | CIP-005-3 R2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  | 253000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2776 | 2781 | 4. | 2785 | CIP-005-3 R2.5.4. | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  | 254000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2776 |  | 1. | 2777 | CIP-005-3 R2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2776 |  | 2. | 2778 | CIP-005-3 R2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2776 |  | 3. | 2779 | CIP-005-3 R2.3. | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2776 |  | 4. | RP-2021-06-15-0000003 | CIP-005-3 R2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2776 |  | 5. | 2781 | CIP-005-3 R2.5. | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2776 |  | 6. | 2786 | CIP-005-3 R2.6. | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2787 |  | 1. | 2788 | CIP-005-3 R3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2787 |  | 2. | RP-2021-06-15-0000004 | CIP-005-3 R3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2790 |  | 1. | 2791 | CIP-005-3 R4.1. | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2790 |  | 2. | 2792 | CIP-005-3 R4.2. | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2790 |  | 3. | 2793 | CIP-005-3 R4.3. | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2790 |  | 4. | 2794 | CIP-005-3 R4.4. | A review of controls for default accounts, passwords, and network management community strings; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2790 |  | 5. | 2795 | CIP-005-3 R4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2796 |  | 1. | 2797 | CIP-005-3 R5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-3 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-3 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2796 |  | 2. | 2798 | CIP-005-3 R5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
225 | 2796 |  | 3. | 2799 | CIP-005-3 R5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
226 | 2800 | 2806 | 1. | 2807 | CIP-006-3 R1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-09-30 |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
226 | 2800 | 2806 | 2. | 2808 | CIP-006-3 R1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-09-30 |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
226 | 2800 |  | 1. | 2801 | CIP-006-3 R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
226 | 2800 |  | 2. | 2802 | CIP-006-3 R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
226 | 2800 |  | 3. | 2803 | CIP-006-3 R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
226 | 2800 |  | 4. | 2804 | CIP-006-3 R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
226 | 2800 |  | 5. | 2805 | CIP-006-3 R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
226 | 2800 |  | 6. | 2806 | CIP-006-3 R1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
226 | 2800 |  | 7. | RP-2021-06-15-0000016 | CIP-006-3 R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-09-30 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
226 | 2800 |  | 8. | 2810 | CIP-006-3 R1.8. | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
226 | 2811 |  | 1. | 2812 | CIP-006-3 R2.1. | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
226 | 2811 |  | 2. | 2813 | CIP-006-3 R2.2. | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
226 | 2819 |  | 1. | 2820 | CIP-006-3 R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
226 | 2819 |  | 2. | 2821 | CIP-006-3 R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
226 | 2819 |  | 3. | 2822 | CIP-006-3 R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2823 |  | 1. | 2824 | CIP-007-3a R1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2823 |  | 2. | 2825 | CIP-007-3a R1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2823 |  | 3. | 2826 | CIP-007-3a R1.3. | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2827 |  | 1. | 2828 | CIP-007-3a R2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2827 |  | 2. | 2829 | CIP-007-3a R2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2827 |  | 3. | 2830 | CIP-007-3a R2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2831 |  | 1. | 2832 | CIP-007-3a R3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2831 |  | 2. | 2833 | CIP-007-3a R3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2834 |  | 1. | 2835 | CIP-007-3a R4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2834 |  | 2. | 2836 | CIP-007-3a R4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2837 | 2838 | 1. | 2839 | CIP-007-3a R5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2837 | 2838 | 2. | 2840 | CIP-007-3a R5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2837 | 2838 | 3. | 2841 | CIP-007-3a R5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2837 | 2842 | 1. | 2843 | CIP-007-3a R5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 521000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2837 | 2842 | 2. | 2844 | CIP-007-3a R5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 522000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2837 | 2842 | 3. | 2845 | CIP-007-3a R5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 523000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2837 | 2846 | 1. | 2847 | CIP-007-3a R5.3.1. | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 531000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2837 | 2846 | 2. | 2848 | CIP-007-3a R5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 532000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2837 | 2846 | 3. | 2849 | CIP-007-3a R5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 533000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2837 |  | 1. | 2838 | CIP-007-3a R5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2837 |  | 2. | 2842 | CIP-007-3a R5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2837 |  | 3. | 2846 | CIP-007-3a R5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2850 |  | 1. | 2851 | CIP-007-3a R6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2850 |  | 2. | 2852 | CIP-007-3a R6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2850 |  | 3. | 2853 | CIP-007-3a R6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2850 |  | 4. | 2854 | CIP-007-3a R6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2850 |  | 5. | 2855 | CIP-007-3a R6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2856 |  | 1. | 2857 | CIP-007-3a R7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2856 |  | 2. | 2858 | CIP-007-3a R7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2856 |  | 3. | 2859 | CIP-007-3a R7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2860 |  | 1. | 2861 | CIP-007-3a R8.1. | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2860 |  | 2. | 2862 | CIP-007-3a R8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2860 |  | 3. | 2863 | CIP-007-3a R8.3. | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
227 | 2860 |  | 4. | 2864 | CIP-007-3a R8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 840000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
228 | 2866 |  | 1. | 2867 | CIP-008-3 R1.1. | Procedures to characterize and classify events as reportable Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
228 | 2866 |  | 2. | 2868 | CIP-008-3 R1.2. | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
228 | 2866 |  | 3. | 2869 | CIP-008-3 R1.3. | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
228 | 2866 |  | 4. | 2870 | CIP-008-3 R1.4. | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
228 | 2866 |  | 5. | 2871 | CIP-008-3 R1.5. | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
228 | 2866 |  | 6. | 2872 | CIP-008-3 R1.6. | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
229 | 2874 |  | 1. | 2875 | CIP-009-3 R1.1. | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
229 | 2874 |  | 2. | 2876 | CIP-009-3 R1.2. | Define the roles and responsibilities of responders. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
23 | 244 | 246 | 1. | 247 | CIP-002-1 R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
23 | 244 | 246 | 2. | 248 | CIP-002-1 R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
23 | 244 | 246 | 3. | 249 | CIP-002-1 R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
23 | 244 | 246 | 4. | 250 | CIP-002-1 R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
23 | 244 | 246 | 5. | 251 | CIP-002-1 R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
23 | 244 | 246 | 6. | 252 | CIP-002-1 R1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
23 | 244 | 246 | 7. | 253 | CIP-002-1 R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 127000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
23 | 244 |  | 1. | 245 | CIP-002-1 R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
23 | 244 |  | 2. | 246 | CIP-002-1 R1.2. | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-04-07 |  | 2010-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
23 | 255 |  | 1. | 256 | CIP-002-1 R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
23 | 255 |  | 2. | 257 | CIP-002-1 R3.2. | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
23 | 255 |  | 3. | 258 | CIP-002-1 R3.3. | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
230 | 2883 |  | 1. | 2893 | CIP-006-2b R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
230 | 2883 |  | 2. | 2894 | CIP-006-2b R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
230 | 2883 |  | 3. | 2895 | CIP-006-2b R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
230 | 2883 |  | 4. | 2892 | CIP-006-2b R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
230 | 2883 |  | 5. | 2891 | CIP-006-2b R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
230 | 2883 |  | 6. | 2889 | CIP-006-2b R1.6. | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
230 | 2883 |  | 7. | RP-2021-06-15-0000014 | CIP-006-2b R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
230 | 2883 |  | 8. | 2890 | CIP-006-2b R1.8. | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
230 | 2885 |  | 1. | 2898 | CIP-006-2b R2.1. | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
230 | 2885 |  | 2. | 2897 | CIP-006-2b R2.2. | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
230 | 2886 |  | 1. | 2899 | CIP-006-2b R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
230 | 2886 |  | 2. | 2900 | CIP-006-2b R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
230 | 2886 |  | 3. | 2901 | CIP-006-2b R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
231 | 2904 |  | 1. | 2914 | CIP-006-2c R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
231 | 2904 |  | 2. | 2915 | CIP-006-2c R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
231 | 2904 |  | 3. | 2916 | CIP-006-2c R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
231 | 2904 |  | 4. | 2913 | CIP-006-2c R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
231 | 2904 |  | 5. | 2912 | CIP-006-2c R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
231 | 2904 |  | 6. | 2910 | CIP-006-2c R1.6. | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
231 | 2904 |  | 7. | RP-2021-06-15-0000015 | CIP-006-2c R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-09-30 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
231 | 2904 |  | 8. | 2911 | CIP-006-2c R1.8. | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
231 | 2906 |  | 1. | 2919 | CIP-006-2c R2.1. | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
231 | 2906 |  | 2. | 2918 | CIP-006-2c R2.2. | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
231 | 2907 |  | 1. | 2920 | CIP-006-2c R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
231 | 2907 |  | 2. | 2921 | CIP-006-2c R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
231 | 2907 |  | 3. | 2922 | CIP-006-2c R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2925 |  | 1. | 2936 | CIP-006-1b R1.1. | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2925 |  | 2. | 2935 | CIP-006-1b R1.2. | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2925 |  | 3. | 2934 | CIP-006-1b R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2925 |  | 4. | 2929 | CIP-006-1b R1.4. | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2925 |  | 5. | 2930 | CIP-006-1b R1.5. | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2925 |  | 6. | 2933 | CIP-006-1b R1.6. | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2925 |  | 7. | 2937 | CIP-006-1b R1.7. | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2925 |  | 8. | 2931 | CIP-006-1b R1.8. | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2925 |  | 9. | 2932 | CIP-006-1b R1.9. | Process for ensuring that the physical security plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2926 |  | 1. | 2941 | CIP-006-1b R2.1. | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2926 |  | 2. | 2938 | CIP-006-1b R2.2. | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2926 |  | 3. | 2940 | CIP-006-1b R2.3. | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2926 |  | 4. | 2939 | CIP-006-1b R2.4. | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2927 |  | 1. | 2942 | CIP-006-1b R3.1. | Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2927 |  | 2. | 2943 | CIP-006-1b R3.2. | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2923 |  | 1. | 2945 | CIP-006-1b R4.1. | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2923 |  | 2. | RP-2021-06-15-0000010 | CIP-006-1b R4.2. | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2923 |  | 3. | 2946 | CIP-006-1b R4.3. | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2928 |  | 1. | 2947 | CIP-006-1b R6.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2928 |  | 2. | 2948 | CIP-006-1b R6.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
232 | 2928 |  | 3. | 2949 | CIP-006-1b R6.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2955 |  | 1. | 2959 | CIP-006-1c R1.1. | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2955 |  | 2. | 2961 | CIP-006-1c R1.2. | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2955 |  | 3. | 2965 | CIP-006-1c R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2955 |  | 4. | 2967 | CIP-006-1c R1.4. | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2955 |  | 5. | 2964 | CIP-006-1c R1.5. | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2955 |  | 6. | 2963 | CIP-006-1c R1.6. | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2955 |  | 7. | 2962 | CIP-006-1c R1.7. | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2955 |  | 8. | 2960 | CIP-006-1c R1.8. | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2955 |  | 9. | 2966 | CIP-006-1c R1.9. | Process for ensuring that the physical security plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2950 |  | 1. | 2971 | CIP-006-1c R2.1. | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2950 |  | 2. | 2970 | CIP-006-1c R2.2. | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2950 |  | 3. | 2969 | CIP-006-1c R2.3. | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2950 |  | 4. | 2968 | CIP-006-1c R2.4. | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2953 |  | 1. | 2973 | CIP-006-1c R3.1. | Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2953 |  | 2. | 2972 | CIP-006-1c R3.2. | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2951 |  | 1. | 2958 | CIP-006-1c R4.1. | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2951 |  | 2. | RP-2021-06-15-0000011 | CIP-006-1c R4.2. | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2951 |  | 3. | 2957 | CIP-006-1c R4.3. | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2952 |  | 1. | 2976 | CIP-006-1c R6.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2952 |  | 2. | 2975 | CIP-006-1c R6.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
233 | 2952 |  | 3. | 2974 | CIP-006-1c R6.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
234 | 2979 | 2988 | 1. | 2993 | CIP-006-3c R1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
234 | 2979 | 2988 | 2. | 2994 | CIP-006-3c R1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
234 | 2979 |  | 1. | 2989 | CIP-006-3c R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
234 | 2979 |  | 2. | 2990 | CIP-006-3c R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
234 | 2979 |  | 3. | 2991 | CIP-006-3c R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
234 | 2979 |  | 4. | 2992 | CIP-006-3c R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
234 | 2979 |  | 5. | 2985 | CIP-006-3c R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
234 | 2979 |  | 6. | 2988 | CIP-006-3c R1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
234 | 2979 |  | 7. | RP-2021-06-17-0000013 | CIP-006-3c R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
234 | 2979 |  | 8. | 2987 | CIP-006-3c R1.8. | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
234 | 2984 |  | 1. | 2995 | CIP-006-3c R2.1. | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
234 | 2984 |  | 2. | 2996 | CIP-006-3c R2.2. | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
234 | 2978 |  | 1. | 2997 | CIP-006-3c R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
234 | 2978 |  | 2. | 2998 | CIP-006-3c R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
234 | 2978 |  | 3. | 2999 | CIP-006-3c R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3003 |  | 1. | 3010 | MOD-001-1a R2.1. | Hourly values for at least the next 48 hours. |  | TSP | [20 empty] | TSP | M2.1 - There has been at least 48 hours of hourly values calculated at all times. | 2010-09-16 |  | 2024-02-01 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3003 |  | 2. | 3009 | MOD-001-1a R2.2. | Daily values for at least the next 31 calendar days. |  | TSP | [20 empty] | TSP | M2.2 -- There has been at least 31 consecutive calendar days of daily values calculated at all times. | 2010-09-16 |  | 2024-02-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3003 |  | 3. | 3011 | MOD-001-1a R2.3. | Monthly values for at least the next 12 months (months 2-13). |  | TSP | [20 empty] | TSP | M2.3 - - There has been at least the next 12 months of monthly values calculated at all times (Months 2-13). | 2010-09-16 |  | 2024-02-01 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3000 | 3016 | 1. | 3022 | MOD-001-1a R3.6.1. | The criteria used to determine when an outage that is in effect part of a day impacts a daily calculation. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2024-02-01 |  |  | 361000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3000 | 3016 | 2. | 3021 | MOD-001-1a R3.6.2. | The criteria used to determine when an outage that is in effect part of a month impacts a monthly calculation. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2024-02-01 |  |  | 362000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3000 | 3016 | 3. | 3020 | MOD-001-1a R3.6.3. | How outages from other Transmission Service Providers that can not be mapped to the Transmission model used to calculate transfer or Flowgate capability are addressed. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2024-02-01 |  |  | 363000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3000 | 3017 | 1. | 3019 | MOD-001-1a R3.2.1. | How confirmed Transmission reservations, expected Interchange and internal counterflow are addressed in firm and non-firm ATC or AFC calculations. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2024-02-01 |  |  | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3000 | 3017 | 2. | 3018 | MOD-001-1a R3.2.2. | A rationale for that accounting specified in R3.2. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2024-02-01 |  |  | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3000 |  | 1. | 3014 | MOD-001-1a R3.1. | Information describing how the selected methodology (or methodologies) has been implemented, in such detail that, given the same information used by the Transmission Service Provider, the results of the ATC or AFC calculations can be validated. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3000 |  | 2. | 3017 | MOD-001-1a R3.2. | A description of the manner in which the Transmission Service Provider will account for counterflows including: |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3000 |  | 3. | 3012 | MOD-001-1a R3.3. | The identity of the Transmission Operators and Transmission Service Providers from which the Transmission Service Provider receives data for use in calculating ATC or AFC. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3000 |  | 4. | 3015 | MOD-001-1a R3.4. | The identity of the Transmission Service Providers and Transmission Operators to which it provides data for use in calculating transfer or Flowgate capability. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3000 |  | 5. | 3013 | MOD-001-1a R3.5. | A description of the allocation processes listed below that are applicable to the Transmission Service Provider: • Processes used to allocate transfer or Flowgate capability among multiple lines or sub-paths within a larger ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities among multiple owners or users of an ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities between Transmission Service Providers to address issues such as forward looking congestion management and seams coordination. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3000 |  | 6. | 3016 | MOD-001-1a R3.6. | A description of how generation and transmission outages are considered in transfer or Flowgate capability calculations, including: |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 360000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3005 |  | 1. | 3028 | MOD-001-1a R4.1. | Each Planning Coordinator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3005 |  | 2. | 3027 | MOD-001-1a R4.2. | Each Reliability Coordinator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3005 |  | 3. | 3023 | MOD-001-1a R4.3. | Each Transmission Operator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3005 |  | 4. | 3025 | MOD-001-1a R4.4. | Each Planning Coordinator adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3005 |  | 5. | 3024 | MOD-001-1a R4.5. | Each Reliability Coordinator adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3005 |  | 6. | 3026 | MOD-001-1a R4.6. | Each Transmission Service Provider whose area is adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 460000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3001 |  | 1. | 3030 | MOD-001-1a R8.1. | Hourly values, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the ATC equation. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3001 |  | 2. | 3029 | MOD-001-1a R8.2. | Daily values, once per day. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3001 |  | 3. | 3031 | MOD-001-1a R8.3. | Monthly values, once per week. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3006 | 3032 | 1. | RP-2021-07-06-0000002 | MOD-001-1a R9.1.1. | If the Transmission Service Provider uses the data requested in its transfer or Flowgate capability calculations, it shall make the data used available |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2024-02-01 |  |  | 911000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3006 | 3032 | 2. | 3036 | MOD-001-1a R9.1.2. | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, but maintains that data, it shall make that data available |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2024-02-01 |  |  | 912000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3006 | 3032 | 3. | 3034 | MOD-001-1a R9.1.3. | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, and does not maintain that data, it shall not be required to make that data available |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2024-02-01 |  |  | 913000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3006 |  | 1. | 3032 | MOD-001-1a R9.1. | The Transmission Service Provider shall make its own current data available, in the format maintained by the Transmission Service Provider, for up to 13 months into the future (subject to confidentiality and security requirements). |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
235 | 3006 |  | 2. | 3033 | MOD-001-1a R9.2. | This data shall be made available by the Transmission Provider on the schedule specified by the requestor (but no more frequently than once per hour, unless mutually agreed to by the requester and the provider). |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  | 2024-02-01 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3039 | 3045 | 1. | 3054 | MOD-029-1a R1.1.1. | Includes at least: |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3039 | 3045 | 10. | 3053 | MOD-029-1a R1.1.10. | Includes any other modeling requirements or criteria specified in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 1110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3039 | 3045 | 2. | 3052 | MOD-029-1a R1.1.2. | Models all system Elements as in-service for the assumed initial conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3039 | 3045 | 3. | 3056 | MOD-029-1a R1.1.3. | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3039 | 3045 | 4. | 3055 | MOD-029-1a R1.1.4. | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3039 | 3045 | 5. | 3048 | MOD-029-1a R1.1.5. | Uses Load forecast by Balancing Authority. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3039 | 3045 | 6. | 3047 | MOD-029-1a R1.1.6. | Uses Transmission Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 116000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3039 | 3045 | 7. | 3050 | MOD-029-1a R1.1.7. | Uses Generation Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 117000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3039 | 3045 | 8. | 3051 | MOD-029-1a R1.1.8. | Uses Special Protection System (SPS) models where currently existing or projected for implementation within the studied time horizon. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 118000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3039 | 3045 | 9. | 3049 | MOD-029-1a R1.1.9. | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 119000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3039 | 3054 | 1. | 3057 | MOD-029-1a R1.1.1.1. | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 11110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3039 | 3054 | 2. | 3058 | MOD-029-1a R1.1.1.2. | All Transmission Operator areas contiguous with its own Transmission Operator area. (Equivalent representation is allowed.) |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 11120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3039 | 3054 | 3. | 3059 | MOD-029-1a R1.1.1.3. | Any other Transmission Operator area linked to the Transmission Operator’s area by joint operating agreement. (Equivalent representation is allowed.) |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 11130000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3039 |  | 1. | 3045 | MOD-029-1a R1.1. | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: |  | TOP | [18 empty] | TOP |  |  | M1.1. Production shall be in the same form and format used by the Transmission Operator to calculate the TTC, as required in R1. | 2010-09-16 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3039 |  | 2. | RP-2021-06-22-0000023 | MOD-029-1a R1.2. | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3044 | 3061 | 1. | 3068 | MOD-029-1a R2.1.1. | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3044 | 3061 | 2. | 3069 | MOD-029-1a R2.1.2. | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3044 | 3061 | 3. | 3070 | MOD-029-1a R2.1.3. | Uncontrolled separation shall not occur. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3044 |  | 1. | 3061 | MOD-029-1a R2.1. | Except where otherwise specified within MOD-029-1, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3044 |  | 2. | RP-2021-06-22-0000024 | MOD-029-1a R2.2. | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependant on a Special Protection System (SPS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a SPS. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3044 |  | 3. | 3060 | MOD-029-1a R2.3. | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3044 |  | 4. | 3062 | MOD-029-1a R2.4. | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3044 |  | 5. | 3063 | MOD-029-1a R2.5. | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3044 |  | 6. | RP-2021-06-22-0000028 | MOD-029-1a R2.6. | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3044 |  | 7. | 3065 | MOD-029-1a R2.7. | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  | 270000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
236 | 3044 |  | 8. | 3064 | MOD-029-1a R2.8. | Create a study report that describes the steps above that were undertaken (R2.1 - R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  | 280000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
237 | 3071 |  | 1. | 3075 | IRO-010-1a R1.1. | List of required data and information needed by the Reliability Coordinator to support Real-Time Monitoring, Operational Planning Analyses, and Real-Time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
237 | 3071 |  | 2. | 3074 | IRO-010-1a R1.2. | Mutually agreeable format. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2017-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
237 | 3071 |  | 3. | RP-2021-06-22-0000004 | IRO-010-1a R1.3. | Timeframe and periodicity for providing data and information (based on its hardware and software requirements, and the time needed to do its Operational Planning Analyses). |  | RC | [11 empty] | RC | [10 empty] | 2011-10-01 |  | 2017-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
237 | 3071 |  | 4. | 3077 | IRO-010-1a R1.4. | Process for data provision when automated Real-Time system operating data is unavailable. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2017-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 260 |  | 1. | 261 | CIP-003-1 R1.1. | The cyber security policy addresses the requirements in Standards CIP-002 through CIP-009, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 260 |  | 2. | 262 | CIP-003-1 R1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 260 |  | 3. | 263 | CIP-003-1 R1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 264 |  | 1. | 265 | CIP-003-1 R2.1. | The senior manager shall be identified by name, title, business phone, business address, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 264 |  | 2. | 266 | CIP-003-1 R2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 264 |  | 3. | 267 | CIP-003-1 R2.3. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 268 |  | 1. | 269 | CIP-003-1 R3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 268 |  | 2. | 270 | CIP-003-1 R3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures, or a statement accepting risk. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 268 |  | 3. | 271 | CIP-003-1 R3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 272 |  | 1. | 273 | CIP-003-1 R4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 272 |  | 2. | 274 | CIP-003-1 R4.2. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 272 |  | 3. | 275 | CIP-003-1 R4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 276 | 277 | 1. | 278 | CIP-003-1 R5.1.1. | Personnel shall be identified by name, title, business phone and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 276 | 277 | 2. | 279 | CIP-003-1 R5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 276 |  | 1. | 277 | CIP-003-1 R5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 276 |  | 2. | 280 | CIP-003-1 R5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
24 | 276 |  | 3. | 281 | CIP-003-1 R5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3153 |  | 1. | 3160 | CIP-005-3a R1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3153 |  | 2. | 3162 | CIP-005-3a R1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3153 |  | 3. | 3157 | CIP-005-3a R1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3153 |  | 4. | 3158 | CIP-005-3a R1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3153 |  | 5. | 3161 | CIP-005-3a R1.5. | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirement R3; Standard CIP-007-3 Requirements R1 and R3 through R9; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3153 |  | 6. | 3159 | CIP-005-3a R1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3155 | 3167 | 1. | 3171 | CIP-005-3a R2.5.1. | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 251000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3155 | 3167 | 2. | 3172 | CIP-005-3a R2.5.2. | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 252000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3155 | 3167 | 3. | 3170 | CIP-005-3a R2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 253000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3155 | 3167 | 4. | 3169 | CIP-005-3a R2.5.4. | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 254000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3155 |  | 1. | RP-2021-06-17-0000008 | CIP-005-3a R2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3155 |  | 2. | 3168 | CIP-005-3a R2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3155 |  | 3. | 3165 | CIP-005-3a R2.3. | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3155 |  | 4. | RP-2021-06-17-0000009 | CIP-005-3a R2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3155 |  | 5. | 3167 | CIP-005-3a R2.5. | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3155 |  | 6. | 3166 | CIP-005-3a R2.6. | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. (Retirement approved by FERC effective January 21, 2014.) |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3152 |  | 1. | 3174 | CIP-005-3a R3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3152 |  | 2. | RP-2021-06-17-0000010 | CIP-005-3a R3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3154 |  | 1. | 3177 | CIP-005-3a R4.1. | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3154 |  | 2. | 3175 | CIP-005-3a R4.2. | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3154 |  | 3. | 3176 | CIP-005-3a R4.3. | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3154 |  | 4. | 3178 | CIP-005-3a R4.4. | A review of controls for default accounts, passwords, and network management community strings; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3154 |  | 5. | 3179 | CIP-005-3a R4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3156 |  | 1. | 3180 | CIP-005-3a R5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-3 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-3 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3156 |  | 2. | 3181 | CIP-005-3a R5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
244 | 3156 |  | 3. | 3182 | CIP-005-3a R5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
245 | 3183 |  | 1. | 3184 | BAL-002-1 R1.1. | A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a Reserve Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority with respect to monitoring and meeting the requirements of Standard BAL-002. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
245 | 3185 |  | 1. | 3186 | BAL-002-1 R2.1. | The minimum reserve requirement for the group. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
245 | 3185 |  | 2. | 3187 | BAL-002-1 R2.2. | Its allocation among members. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
245 | 3185 |  | 3. | 3188 | BAL-002-1 R2.3. | The permissible mix of Operating Reserve – Spinning and Operating Reserve – Supplemental that may be included in Contingency Reserve. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
245 | 3185 |  | 4. | 3189 | BAL-002-1 R2.4. | The procedure for applying Contingency Reserve in practice. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
245 | 3185 |  | 5. | 3190 | BAL-002-1 R2.5. | The limitations, if any, upon the amount of interruptible load that may be included. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
245 | 3185 |  | 6. | 3191 | BAL-002-1 R2.6. | The same portion of resource capacity (e.g. reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
245 | 3192 |  | 1. | 3193 | BAL-002-1 R3.1. | As a minimum, the Balancing Authority or Reserve Sharing Group shall carry at least enough Contingency Reserve to cover the most severe single contingency. All Balancing Authorities and Reserve Sharing Groups shall review, no less frequently than annually, their probable contingencies to determine their prospective most severe single contingencies. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
245 | 3194 |  | 1. | 3195 | BAL-002-1 R4.1. | A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre-Disturbance value. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
245 | 3194 |  | 2. | 3196 | BAL-002-1 R4.2. | The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
245 | 3197 |  | 1. | 3198 | BAL-002-1 R5.1. | The Reserve Sharing Group reviews group ACE (or equivalent) and demonstrates compliance to the DCS. To be in compliance, the group ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. or |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
245 | 3197 |  | 2. | 3199 | BAL-002-1 R5.2. | The Reserve Sharing Group reviews each member’s ACE in response to the activation of reserves. To be in compliance, a member’s ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
245 | 3200 |  | 1. | 3201 | BAL-002-1 R6.1. | The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
245 | 3200 |  | 2. | 3202 | BAL-002-1 R6.2. | The default Contingency Reserve Restoration Period is 90 minutes. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
246 | 3206 | 3207 | 1. | 3208 | BAL-006-2 R4.1.1. | The hourly values of Net Interchange Schedule. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2018-12-31 |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
246 | 3206 | 3207 | 2. | 3209 | BAL-006-2 R4.1.2. | The hourly integrated megawatt-hour values of Net Actual Interchange. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2018-12-31 |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
246 | 3206 |  | 1. | 3207 | BAL-006-2 R4.1. | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: |  | BA | BA | [21 empty] | 2011-04-01 |  | 2018-12-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
246 | 3206 |  | 2. | 3210 | BAL-006-2 R4.2. | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and Off-Peak hours of the month. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2018-12-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
246 | 3206 |  | 3. | 3211 | BAL-006-2 R4.3. | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). |  | BA | BA | [21 empty] | 2011-04-01 |  | 2018-12-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
247 | 3213 |  | 1. | RP-2021-06-16-0000027 | BAL-502-RFC-02 R1.1. | Calculate a planning reserve margin that will result in the sum of the probabilities for loss of Load for the integrated peak hour for all days of each planning year1 analyzed (per R1.2) being equal to 0.1. (This is comparable to a “one day in 10 year” criterion). |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 110000000 | RF-US |  |  | RF-US
247 | 3213 |  | 1.1. | RP-2021-06-16-0000028 | BAL-502-RFC-02 R1.1.1. | The utilization of Direct Control Load Management or curtailment of Interruptible Demand shall not contribute to the loss of Load probability. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 111000000 | RF-US |  |  | RF-US
247 | 3213 |  | 1.2. | RP-2021-06-16-0000029 | BAL-502-RFC-02 R1.1.2. | The planning reserve margin developed from R1.1 shall be expressed as a percentage of the median2 forecast peak Net Internal Demand (planning reserve margin). Note: The median forecast is expected to have a 50% probability of being too high and 50% probability of being too low (50:50). |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 112000000 | RF-US |  |  | RF-US
247 | 3213 |  | 2. | RP-2021-06-16-0000030 | BAL-502-RFC-02 R1.2. | Be performed or verified separately for each of the following planning years: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 120000000 | RF-US |  |  | RF-US
247 | 3213 |  | 2.1. | RP-2021-06-16-0000031 | BAL-502-RFC-02 R1.2.1. | Perform an analysis for Year One. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 121000000 | RF-US |  |  | RF-US
247 | 3213 |  | 2.2. | RP-2021-06-16-0000032 | BAL-502-RFC-02 R1.2.2. | Perform an analysis or verification at a minimum for one year in the 2 through 5 year period and at a minimum one year in the 6 though 10 year period. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 122000000 | RF-US |  |  | RF-US
247 | 3213 |  | 2.2.1. | RP-2021-06-16-0000033 | BAL-502-RFC-02 R1.2.2.1. | If the analysis is verified, the verification must be supported by current or past studies for the same planning year. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 122100000 | RF-US |  |  | RF-US
247 | 3213 |  | 3. | RP-2021-06-16-0000034 | BAL-502-RFC-02 R1.3. | Include the following subject matter and documentation of its use: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 130000000 | RF-US |  |  | RF-US
247 | 3213 |  | 3.1. | RP-2021-06-16-0000035 | BAL-502-RFC-02 R1.3.1. | Load forecast characteristics: • Median (50:50) forecast peak Load. • Load forecast uncertainty (reflects variability in the Load forecast due to weather and regional economic forecasts). • Load diversity. • Seasonal Load variations. • Daily demand modeling assumptions (firm, interruptible). • Contractual arrangements concerning curtailable/Interruptible Demand. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 131000000 | RF-US |  |  | RF-US
247 | 3213 |  | 3.2. | RP-2021-06-16-0000036 | BAL-502-RFC-02 R1.3.2. | Resource characteristics: • Historic resource performance and any projected changes • Seasonal resource ratings • Modeling assumptions of firm capacity purchases from and sales to entities outside the Planning Coordinator area. • Resource planned outage schedules, deratings, and retirements. • Modeling assumptions of intermittent and energy limited resource such as wind and cogeneration. • Criteria for including planned resource additions in the analysis |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 132000000 | RF-US |  |  | RF-US
247 | 3213 |  | 3.3. | RP-2021-06-16-0000037 | BAL-502-RFC-02 R1.3.3. | Transmission limitations that prevent the delivery of generation reserves |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 133000000 | RF-US |  |  | RF-US
247 | 3213 |  | 3.3.1. | RP-2021-06-16-0000038 | BAL-502-RFC-02 R1.3.3.1. | Criteria for including planned Transmission Facility additions in the analysis |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 133100000 | RF-US |  |  | RF-US
247 | 3213 |  | 3.4. | RP-2021-06-16-0000039 | BAL-502-RFC-02 R1.3.4. | Assistance from other interconnected systems including multi-area assessment considering Transmission limitations into the study area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 134000000 | RF-US |  |  | RF-US
247 | 3213 |  | 4. | RP-2021-06-16-0000040 | BAL-502-RFC-02 R1.4. | Consider the following resource availability characteristics and document how and why they were included in the analysis or why they were not included: • Availability and deliverability of fuel. • Common mode outages that affect resource availability • Environmental or regulatory restrictions of resource availability. • Any other demand (Load) response programs not included in R1.3.1. • Sensitivity to resource outage rates. • Impacts of extreme weather/drought conditions that affect unit availability. • Modeling assumptions for emergency operation procedures used to make reserves available. • Market resources not committed to serving Load (uncommitted resources) within the Planning Coordinator area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 140000000 | RF-US |  |  | RF-US
247 | 3213 |  | 5. | RP-2021-06-16-0000041 | BAL-502-RFC-02 R1.5. | Consider Transmission maintenance outage schedules and document how and why they were included in the Resource Adequacy analysis or why they were not included |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 150000000 | RF-US |  |  | RF-US
247 | 3213 |  | 6. | RP-2021-06-16-0000042 | BAL-502-RFC-02 R1.6. | Document that capacity resources are appropriately accounted for in its Resource Adequacy analysis |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 160000000 | RF-US |  |  | RF-US
247 | 3213 |  | 7. | RP-2021-06-16-0000043 | BAL-502-RFC-02 R1.7. | Document that all Load in the Planning Coordinator area is accounted for in its Resource Adequacy analysis |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 170000000 | RF-US |  |  | RF-US
247 | 3214 |  | 1. | RP-2021-06-16-0000044 | BAL-502-RFC-02 R2.1. | This documentation shall cover each of the years in Year One through ten. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 210000000 | RF-US |  |  | RF-US
247 | 3214 |  | 2. | RP-2021-06-16-0000045 | BAL-502-RFC-02 R2.2. | This documentation shall include the planning reserve margin calculated per requirement R1.1 for each of the three years in the analysis. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 220000000 | RF-US |  |  | RF-US
247 | 3214 |  | 3. | RP-2021-06-16-0000046 | BAL-502-RFC-02 R2.3. | The documentation as specified per requirement R2.1 and R2.2 shall be publicly posted no later than 30 calendar days prior to the beginning of Year One. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  | 230000000 | RF-US |  |  | RF-US
249 | 3218 |  | 1. | 3219 | CIP-003-4 R1.1. | The cyber security policy addresses the requirements in Standards CIP-002-4 through CIP-009-4, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3218 |  | 2. | 3220 | CIP-003-4 R1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3218 |  | 3. | 3221 | CIP-003-4 R1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3222 |  | 1. | 3223 | CIP-003-4 R2.1. | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3222 |  | 2. | 3224 | CIP-003-4 R2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3222 |  | 3. | 3225 | CIP-003-4 R2.3. | Where allowed by Standards CIP-002-4 through CIP-009-4, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3222 |  | 4. | 3226 | CIP-003-4 R2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3227 |  | 1. | 3228 | CIP-003-4 R3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3227 |  | 2. | 3229 | CIP-003-4 R3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3227 |  | 3. | 3230 | CIP-003-4 R3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3231 |  | 1. | 3232 | CIP-003-4 R4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-4, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3231 |  | 2. | 3233 | CIP-003-4 R4.2. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3231 |  | 3. | 3234 | CIP-003-4 R4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3235 | 3236 | 1. | 3237 | CIP-003-4 R5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3235 | 3236 | 2. | 3238 | CIP-003-4 R5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3235 |  | 1. | 3236 | CIP-003-4 R5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3235 |  | 2. | 3239 | CIP-003-4 R5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
249 | 3235 |  | 3. | 3240 | CIP-003-4 R5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
25 | 284 | 286 | 1. | 287 | CIP-004-1 R2.2.1. | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
25 | 284 | 286 | 2. | 288 | CIP-004-1 R2.2.2. | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
25 | 284 | 286 | 3. | 289 | CIP-004-1 R2.2.3. | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
25 | 284 | 286 | 4. | 290 | CIP-004-1 R2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 224000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
25 | 284 |  | 1. | 285 | CIP-004-1 R2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained within ninety calendar days of such authorization. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-04-07 |  | 2010-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
25 | 284 |  | 2. | 286 | CIP-004-1 R2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-04-07 |  | 2010-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
25 | 284 |  | 3. | 291 | CIP-004-1 R2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
25 | 292 |  | 1. | 293 | CIP-004-1 R3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
25 | 292 |  | 2. | 294 | CIP-004-1 R3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
25 | 292 |  | 3. | 295 | CIP-004-1 R3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
25 | 296 |  | 1. | 297 | CIP-004-1 R4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
25 | 296 |  | 2. | 298 | CIP-004-1 R4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-04-07 |  | 2010-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
250 | 3243 | 3245 | 1. | 3246 | CIP-004-4 R2.2.1. | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2012-12-11 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
250 | 3243 | 3245 | 2. | 3247 | CIP-004-4 R2.2.2. | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2012-12-11 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
250 | 3243 | 3245 | 3. | 3248 | CIP-004-4 R2.2.3. | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2012-12-11 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
250 | 3243 | 3245 | 4. | 3249 | CIP-004-4 R2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2012-12-11 |  |  | 224000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
250 | 3243 |  | 1. | 3244 | CIP-004-4 R2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
250 | 3243 |  | 2. | 3245 | CIP-004-4 R2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-4, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
250 | 3243 |  | 3. | 3250 | CIP-004-4 R2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
250 | 3251 |  | 1. | 3252 | CIP-004-4 R3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
250 | 3251 |  | 2. | 3253 | CIP-004-4 R3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
250 | 3251 |  | 3. | 3254 | CIP-004-4 R3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
250 | 3255 |  | 1. | 3256 | CIP-004-4 R4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
250 | 3255 |  | 2. | 3257 | CIP-004-4 R4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3258 |  | 1. | 3259 | CIP-005-4a R1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3258 |  | 2. | 3260 | CIP-005-4a R1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3258 |  | 3. | 3261 | CIP-005-4a R1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3258 |  | 4. | 3262 | CIP-005-4a R1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3258 |  | 5. | 3263 | CIP-005-4a R1.5. | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirement R3; Standard CIP-007-4 Requirements R1 and R3 through R9; Standard CIP-008-4; and Standard CIP-009-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3258 |  | 6. | 3264 | CIP-005-4a R1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3265 | 3270 | 1. | 3271 | CIP-005-4a R2.5.1. | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 251000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3265 | 3270 | 2. | 3272 | CIP-005-4a R2.5.2. | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 252000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3265 | 3270 | 3. | 3273 | CIP-005-4a R2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004-4 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 253000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3265 | 3270 | 4. | 3274 | CIP-005-4a R2.5.4. | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 254000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3265 |  | 1. | RP-2021-06-15-0000005 | CIP-005-4a R2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3265 |  | 2. | 3267 | CIP-005-4a R2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3265 |  | 3. | 3268 | CIP-005-4a R2.3. | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3265 |  | 4. | RP-2021-06-15-0000006 | CIP-005-4a R2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3265 |  | 5. | 3270 | CIP-005-4a R2.5. | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3265 |  | 6. | 3275 | CIP-005-4a R2.6. | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3276 |  | 1. | 3277 | CIP-005-4a R3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3276 |  | 2. | RP-2021-06-15-0000007 | CIP-005-4a R3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3279 |  | 1. | 3280 | CIP-005-4a R4.1. | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3279 |  | 2. | 3281 | CIP-005-4a R4.2. | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3279 |  | 3. | 3282 | CIP-005-4a R4.3. | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3279 |  | 4. | 3283 | CIP-005-4a R4.4. | A review of controls for default accounts, passwords, and network management community strings; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3279 |  | 5. | 3284 | CIP-005-4a R4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3285 |  | 1. | 3286 | CIP-005-4a R5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-4 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-4 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3285 |  | 2. | 3287 | CIP-005-4a R5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
251 | 3285 |  | 3. | 3288 | CIP-005-4a R5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
252 | 3289 | 3295 | 1. | 3296 | CIP-006-4c R1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
252 | 3289 | 3295 | 2. | 3297 | CIP-006-4c R1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
252 | 3289 |  | 1. | 3290 | CIP-006-4c R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
252 | 3289 |  | 2. | 3291 | CIP-006-4c R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
252 | 3289 |  | 3. | 3292 | CIP-006-4c R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
252 | 3289 |  | 4. | 3293 | CIP-006-4c R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
252 | 3289 |  | 5. | 3294 | CIP-006-4c R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-4 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
252 | 3289 |  | 6. | 3295 | CIP-006-4c R1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
252 | 3289 |  | 7 | RP-2021-06-15-0000019 | CIP-006-4c R1.7 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
252 | 3289 |  | 8. | 3299 | CIP-006-4c R1.8. | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
252 | 3300 |  | 1. | 3301 | CIP-006-4c R2.1. | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
252 | 3300 |  | 2. | 3302 | CIP-006-4c R2.2. | Be afforded the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP-009-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
252 | 3308 |  | 1. | 3309 | CIP-006-4c R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
252 | 3308 |  | 2. | 3310 | CIP-006-4c R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
252 | 3308 |  | 3. | 3311 | CIP-006-4c R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3312 |  | 1. | 3313 | CIP-007-4a R1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3312 |  | 2. | 3314 | CIP-007-4a R1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3312 |  | 3. | 3315 | CIP-007-4a R1.3. | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3316 |  | 1. | 3317 | CIP-007-4a R2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3316 |  | 2. | 3318 | CIP-007-4a R2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3316 |  | 3. | 3319 | CIP-007-4a R2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3320 |  | 1. | 3321 | CIP-007-4a R3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3320 |  | 2. | 3322 | CIP-007-4a R3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3323 |  | 1. | 3324 | CIP-007-4a R4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3323 |  | 2. | 3325 | CIP-007-4a R4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3326 | 3327 | 1. | 3328 | CIP-007-4a R5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-4 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3326 | 3327 | 2. | 3329 | CIP-007-4a R5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3326 | 3327 | 3. | 3330 | CIP-007-4a R5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-4 Requirement R5 and Standard CIP-004-4 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3326 | 3331 | 1. | 3332 | CIP-007-4a R5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 521000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3326 | 3331 | 2. | 3333 | CIP-007-4a R5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 522000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3326 | 3331 | 3. | 3334 | CIP-007-4a R5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 523000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3326 | 3335 | 1. | 3336 | CIP-007-4a R5.3.1. | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 531000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3326 | 3335 | 2. | 3337 | CIP-007-4a R5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 532000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3326 | 3335 | 3. | 3338 | CIP-007-4a R5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 533000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3326 |  | 1. | 3327 | CIP-007-4a R5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3326 |  | 2. | 3331 | CIP-007-4a R5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3326 |  | 3. | 3335 | CIP-007-4a R5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3339 |  | 1. | 3340 | CIP-007-4a R6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3339 |  | 2. | 3341 | CIP-007-4a R6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3339 |  | 3. | 3342 | CIP-007-4a R6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3339 |  | 4. | 3343 | CIP-007-4a R6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3339 |  | 5. | 3344 | CIP-007-4a R6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3345 |  | 1. | 3346 | CIP-007-4a R7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3345 |  | 2. | 3347 | CIP-007-4a R7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3345 |  | 3. | 3348 | CIP-007-4a R7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3349 |  | 1. | 3350 | CIP-007-4a R8.1. | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3349 |  | 2. | 3351 | CIP-007-4a R8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3349 |  | 3. | 3352 | CIP-007-4a R8.3. | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
253 | 3349 |  | 4. | 3353 | CIP-007-4a R8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 840000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
254 | 3355 |  | 1. | 3356 | CIP-008-4 R1.1. | Procedures to characterize and classify events as reportable Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
254 | 3355 |  | 2. | 3357 | CIP-008-4 R1.2. | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
254 | 3355 |  | 3. | 3358 | CIP-008-4 R1.3. | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
254 | 3355 |  | 4. | 3359 | CIP-008-4 R1.4. | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
254 | 3355 |  | 5. | 3360 | CIP-008-4 R1.5. | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
254 | 3355 |  | 6. | 3361 | CIP-008-4 R1.6. | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
255 | 3363 |  | 1. | 3364 | CIP-009-4 R1.1. | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
255 | 3363 |  | 2. | 3365 | CIP-009-4 R1.2. | Define the roles and responsibilities of responders. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
256 | 3375 |  | 1. | 3376 | EOP-002-3 R6.1. | Loading all available generating capacity. |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
256 | 3375 |  | 2. | 3377 | EOP-002-3 R6.2. | Deploying all available operating reserve. |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
256 | 3375 |  | 3. | 3378 | EOP-002-3 R6.3. | Interrupting interruptible load and exports. |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
256 | 3375 |  | 4. | 3379 | EOP-002-3 R6.4. | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
256 | 3375 |  | 5. | 3380 | EOP-002-3 R6.5. | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
256 | 3375 |  | 6. | 3381 | EOP-002-3 R6.6. | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | 660000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
256 | 3382 |  | 1. | 3383 | EOP-002-3 R7.1. | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
256 | 3382 |  | 2. | 3384 | EOP-002-3 R7.2. | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
256 | 3386 |  | 1. | 3387 | EOP-002-3 R9.1. | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  | LSE | [7 empty] | LSE | [14 empty] | 2011-01-10 |  | 2012-09-12 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
256 | 3386 |  | 2. | 3388 | EOP-002-3 R9.2. | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  | RC | [11 empty] | RC | [10 empty] | 2011-01-10 |  | 2012-09-12 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
256 | 3386 |  | 3. | 3389 | EOP-002-3 R9.3. | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2011-01-10 |  | 2012-09-12 |  |  | 930000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
256 | 3386 |  | 4. | 3390 | EOP-002-3 R9.4. | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2011-01-10 |  | 2012-09-12 |  |  | 940000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3399 | 6489 | 1. | 6490 | EOP-008-1 R1.2.1. | Tools and applications to ensure that System Operators have situational awareness of the BES. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3399 | 6489 | 2. | 6491 | EOP-008-1 R1.2.2. | Data communications. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3399 | 6489 | 3. | 6492 | EOP-008-1 R1.2.3. | Voice communications. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3399 | 6489 | 4. | 6493 | EOP-008-1 R1.2.4. | Power source(s). |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3399 | 6489 | 5. | 6494 | EOP-008-1 R1.2.5. | Physical and cyber security. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3399 | 6498 | 1. | RP-2021-05-26-0000001 | EOP-008-1 R1.6.1. | A list of all entities to notify when there is a change in operating locations. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3399 | 6498 | 2. | RP-2021-05-26-0000002 | EOP-008-1 R1.6.2. | Actions to manage the risk to the BES during the transition from primary to backup functionality as well as during outages of the primary or backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3399 | 6498 | 3. | RP-2021-05-26-0000003 | EOP-008-1 R1.6.3. | Identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  | 163000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3399 |  | 1. | 6488 | EOP-008-1 R1.1. | The location and method of implementation for providing backup functionality for the time it takes to restore the primary control center functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3399 |  | 2. | 6489 | EOP-008-1 R1.2. | A summary description of the elements required to support the backup functionality. These elements shall include, at a minimum: |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3399 |  | 3. | 6495 | EOP-008-1 R1.3. | An Operating Process for keeping the backup functionality consistent with the primary control center. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3399 |  | 4. | 6496 | EOP-008-1 R1.4. | Operating Procedures, including decision authority, for use in determining when to implement the Operating Plan for backup functionality |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3399 |  | 5. | 6497 | EOP-008-1 R1.5. | A transition period between the loss of primary control center functionality and the time to fully implement the backup functionality that is less than or equal to two hours. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3399 |  | 6. | 6498 | EOP-008-1 R1.6. | An Operating Process describing the actions to be taken during the transition period between the loss of primary control center functionality and the time to fully implement backup functionality elements identified in Requirement R1, Part 1.2. The Operating Process shall include at a minimum: |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3403 |  | 1. | 6502 | EOP-008-1 R5.1. | An update and approval of the Operating Plan for backup functionality shall take place within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3405 |  | 1. | 6503 | EOP-008-1 R7.1. | The transition time between the simulated loss of primary control center functionality and the time to fully implement the backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
258 | 3405 |  | 2. | 6504 | EOP-008-1 R7.2. | The backup functionality for a minimum of two continuous hours. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
259 | 3407 |  | 1. | 3408 | FAC-002-1 R1.1. | Evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [9 empty] | TO |  |  |  |  | 2011-01-10 |  | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
259 | 3407 |  | 2. | 3409 | FAC-002-1 R1.2. | Ensurance of compliance with NERC Reliability Standards and applicable Regional, subregional, Power Pool, and individual system planning criteria and facility connection requirements. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [9 empty] | TO |  |  |  |  | 2011-01-10 |  | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
259 | 3407 |  | 3. | 3410 | FAC-002-1 R1.3. | Evidence that the parties involved in the assessment have coordinated and cooperated on the assessment of the reliability impacts of new facilities on the interconnected transmission systems. While these studies may be performed independently, the results shall be jointly evaluated and coordinated by the entities involved. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [9 empty] | TO |  |  |  |  | 2011-01-10 |  | 2015-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
259 | 3407 |  | 4. | 3411 | FAC-002-1 R1.4. | Evidence that the assessment included steady-state, short-circuit, and dynamics studies as necessary to evaluate system performance under both normal and contingency conditions in accordance with Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [9 empty] | TO |  |  |  |  | 2011-01-10 |  | 2015-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
259 | 3407 |  | 5. | 3412 | FAC-002-1 R1.5. | Documentation that the assessment included study assumptions, system performance, alternatives considered, and jointly coordinated recommendations. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [9 empty] | TO |  |  |  |  | 2011-01-10 |  | 2015-12-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 299 |  | 1. | 300 | CIP-005-1 R1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 299 |  | 2. | 301 | CIP-005-1 R1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 299 |  | 3. | 302 | CIP-005-1 R1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 299 |  | 4. | 303 | CIP-005-1 R1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 299 |  | 5. | 304 | CIP-005-1 R1.5. | Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirements R2 and R3, Standard CIP-007, Requirements R1 and R3 through R9, Standard CIP-008, and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 299 |  | 6. | 305 | CIP-005-1 R1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 306 | 311 | 1. | 312 | CIP-005-1 R2.5.1. | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 251000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 306 | 311 | 2. | 313 | CIP-005-1 R2.5.2. | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 252000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 306 | 311 | 3. | 314 | CIP-005-1 R2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 253000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 306 | 311 | 4. | 315 | CIP-005-1 R2.5.4. | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 254000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 306 |  | 1. | 307 | CIP-005-1 R2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 306 |  | 2. | 308 | CIP-005-1 R2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 306 |  | 3. | 309 | CIP-005-1 R2.3. | The Responsible Entity shall maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 306 |  | 4. | 310 | CIP-005-1 R2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 306 |  | 5. | 311 | CIP-005-1 R2.5. | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 306 |  | 6. | 316 | CIP-005-1 R2.6. | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 317 |  | 1. | 318 | CIP-005-1 R3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 317 |  | 2. | 319 | CIP-005-1 R3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 320 |  | 1. | 321 | CIP-005-1 R4.1. | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 320 |  | 2. | 322 | CIP-005-1 R4.2. | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 320 |  | 3. | 323 | CIP-005-1 R4.3. | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 320 |  | 4. | 324 | CIP-005-1 R4.4. | A review of controls for default accounts, passwords, and network management community strings; and, |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 320 |  | 5. | 325 | CIP-005-1 R4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 326 |  | 1. | 327 | CIP-005-1 R5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 326 |  | 2. | 328 | CIP-005-1 R5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
26 | 326 |  | 3. | 329 | CIP-005-1 R5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3414 | 6570 | 1. | 6691 | FAC-013-2 R1.4.1. | Generation dispatch, including but not limited to long term planned outages, additions and retirements. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3414 | 6570 | 2. | 6692 | FAC-013-2 R1.4.2. | Transmission system topology, including but not limited to long term planned Transmission outages, additions, and retirements. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3414 | 6570 | 3. | 6693 | FAC-013-2 R1.4.3. | System demand. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  | 143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3414 | 6570 | 4. | 6694 | FAC-013-2 R1.4.4. | Current approved and projected Transmission uses. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  | 144000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3414 | 6570 | 5. | 6695 | FAC-013-2 R1.4.5. | Parallel path (loop flow) adjustments. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  | 145000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3414 | 6570 | 6. | 6696 | FAC-013-2 R1.4.6. | Contingencies |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  | 146000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3414 | 6570 | 7. | 6697 | FAC-013-2 R1.4.7. | Monitored Facilities. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  | 147000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3414 |  | 1. | 6567 | FAC-013-2 R1.1. | Criteria for the selection of the transfers to be assessed. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3414 |  | 2. | 6568 | FAC-013-2 R1.2. | A statement that the assessment shall respect known System Operating Limits (SOLs). |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3414 |  | 3. | 6569 | FAC-013-2 R1.3. | A statement that the assumptions and criteria used to perform the assessment are consistent with the Planning Coordinator’s planning practices. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3414 |  | 4. | 6570 | FAC-013-2 R1.4. | A description of how each of the following assumptions and criteria used in performing the assessment are addressed: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3414 |  | 5. | 6571 | FAC-013-2 R1.5. | A description of how simulations of transfers are performed through the adjustment of generation, Load or both. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3415 | 6572 | 1. | 6698 | FAC-013-2 R2.1.1. | Each Planning Coordinator adjacent to the Planning Coordinator’s Planning Coordinator area or overlapping the Planning Coordinator’s area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3415 | 6572 | 2. | 6699 | FAC-013-2 R2.1.2. | Each Transmission Planner within the Planning Coordinator’s Planning Coordinator area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3415 |  | 1. | 6572 | FAC-013-2 R2.1. | Distribute to the following prior to the effectiveness of such revisions: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
260 | 3415 |  | 2. | 6573 | FAC-013-2 R2.2. | Distribute to each functional entity that has a reliability-related need for the Transfer Capability methodology and submits a request for that methodology within 30 calendar days of receiving that written request. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
261 | 3420 |  | 1. | 3421 | IRO-005-2a R1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
261 | 3420 |  | 10. | 3422 | IRO-005-2a R1.10. | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
261 | 3420 |  | 2. | 3423 | IRO-005-2a R1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
261 | 3420 |  | 3. | 3424 | IRO-005-2a R1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
261 | 3420 |  | 4. | 3425 | IRO-005-2a R1.4. | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
261 | 3420 |  | 5. | 3426 | IRO-005-2a R1.5. | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
261 | 3420 |  | 6. | 3427 | IRO-005-2a R1.6. | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
261 | 3420 |  | 7. | 3428 | IRO-005-2a R1.7. | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
261 | 3420 |  | 8. | 3429 | IRO-005-2a R1.8. | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
261 | 3420 |  | 9. | 3430 | IRO-005-2a R1.9. | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
263 | 3449 |  | 1. | 6418 | IRO-006-EAST-1 R2.1. | A list of congestion management actions to be implemented, and |  | RC | [11 empty] | RC | [10 empty] | 2011-04-21 |  | 2016-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US | MRO-US | NPCC-US | RF-US | SERC-US
263 | 3449 |  | 2. | 6419 | IRO-006-EAST-1 R2.2. | One of the following TLR levels: TLR-1, TLR-2, TLR-3A, TLR-3B, TLR-4, TLR-5A, TLR-5B, TLR-6, TLR-0 |  | RC | [11 empty] | RC | [10 empty] | 2011-04-21 |  | 2016-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US | MRO-US | NPCC-US | RF-US | SERC-US
263 | 3450 |  | 1. | 6420 | IRO-006-EAST-1 R3.1. | Notify all Reliability Coordinators in the Eastern Interconnection of the identified TLR level |  | RC | [11 empty] | RC | [10 empty] | 2011-04-21 |  | 2016-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US | MRO-US | NPCC-US | RF-US | SERC-US
263 | 3450 |  | 2. | 6421 | IRO-006-EAST-1 R3.2. | Communicate the list of congestion management actions to be implemented to 1.) all Reliability Coordinators in the Eastern Interconnection, and 2.) those Reliability Coordinators in other Interconnections responsible for curtailing Interchange Transactions crossing Interconnection boundaries identified in the list of congestion management actions. |  | RC | [11 empty] | RC | [10 empty] | 2011-04-21 |  | 2016-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US | MRO-US | NPCC-US | RF-US | SERC-US
263 | 3450 |  | 3. | 6422 | IRO-006-EAST-1 R3.3. | Request that the congestion management actions identified in Requirement R2, Part 2.1 be implemented by: 1.) Each Reliability Coordinator associated with a Sink Balancing Authority for which Interchange Transactions are to be curtailed, 2.) Each Reliability Coordinator associated with a Balancing Authority in the Eastern Interconnection for which Network Integration Transmission Service or Native Load is to be curtailed, and 3.) Each Reliability Coordinator associated with a Balancing Authority in the Eastern Interconnection for which its Market Flow is to be curtailed. |  | RC | [11 empty] | RC | [10 empty] | 2011-04-21 |  | 2016-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US | MRO-US | NPCC-US | RF-US | SERC-US
264 | 3452 | 3455 | 1. | 3456 | TPL-001-1 R1.3.1. | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3452 | 3455 | 2. | 3457 | TPL-001-1 R1.3.2. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-0(i)b_R3. |  |  | 2012-07-06 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3452 | 3455 | 3. | 3458 | TPL-001-1 R1.3.3. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3452 | 3455 | 4. | 3459 | TPL-001-1 R1.3.4. | Have established normal (pre-contingency) operating procedures in place. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3452 | 3455 | 5. | 3460 | TPL-001-1 R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3452 | 3455 | 6. | 3461 | TPL-001-1 R1.3.6. | Be performed for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3452 | 3455 | 7. | 3462 | TPL-001-1 R1.3.7. | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3452 | 3455 | 8. | 3463 | TPL-001-1 R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3452 | 3455 | 9. | 3464 | TPL-001-1 R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  |  | 2012-07-06 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3452 |  | 1. | 3453 | TPL-001-1 R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3452 |  | 2. | 3454 | TPL-001-1 R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3452 |  | 3. | 3455 | TPL-001-1 R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3452 |  | 4. | 3465 | TPL-001-1 R1.4. | Address any planned upgrades needed to meet the performance requirements of Category A. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3466 | 3467 | 1. | 3468 | TPL-001-1 R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3466 | 3467 | 2. | 3469 | TPL-001-1 R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3466 | 3467 | 3. | 3470 | TPL-001-1 R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3466 |  | 1. | 3467 | TPL-001-1 R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
264 | 3466 |  | 2. | 3471 | TPL-001-1 R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 | 3476 | 1. | 3477 | TPL-002-0b R1.3.1. | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 | 3476 | 10. | 3478 | TPL-002-0b R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 1310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 | 3476 | 11. | 3479 | TPL-002-0b R1.3.11. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 1311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 | 3476 | 12. | 3480 | TPL-002-0b R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 1312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 | 3476 | 2. | 3481 | TPL-002-0b R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 | 3476 | 3. | 3482 | TPL-002-0b R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 | 3476 | 4. | 3483 | TPL-002-0b R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 | 3476 | 5. | 3484 | TPL-002-0b R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 | 3476 | 6. | 3485 | TPL-002-0b R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 | 3476 | 7. | 3486 | TPL-002-0b R1.3.7. | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 | 3476 | 8. | 3487 | TPL-002-0b R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 | 3476 | 9. | 3488 | TPL-002-0b R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 |  | 1. | 3474 | TPL-002-0b R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 |  | 2. | 3475 | TPL-002-0b R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 |  | 3. | 3476 | TPL-002-0b R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories,, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 |  | 4. | 3489 | TPL-002-0b R1.4. | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3473 |  | 5. | 3490 | TPL-002-0b R1.5. | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3491 | 3492 | 1. | 3493 | TPL-002-0b R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3491 | 3492 | 2. | 3494 | TPL-002-0b R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3491 | 3492 | 3. | 3495 | TPL-002-0b R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3491 |  | 1. | 3492 | TPL-002-0b R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
265 | 3491 |  | 2. | 3496 | TPL-002-0b R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 | 3501 | 1. | 3502 | TPL-002-1b R1.3.1. | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 | 3501 | 10. | 3503 | TPL-002-1b R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 1310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 | 3501 | 11. | 3504 | TPL-002-1b R1.3.11. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 1311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 | 3501 | 12. | 3505 | TPL-002-1b R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 1312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 | 3501 | 2. | 3506 | TPL-002-1b R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 | 3501 | 3. | 3507 | TPL-002-1b R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 | 3501 | 4. | 3508 | TPL-002-1b R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 | 3501 | 5. | 3509 | TPL-002-1b R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 | 3501 | 6. | 3510 | TPL-002-1b R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 | 3501 | 7. | 3511 | TPL-002-1b R1.3.7. | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 | 3501 | 8. | 3512 | TPL-002-1b R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 | 3501 | 9. | 3513 | TPL-002-1b R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 |  | 1. | 3499 | TPL-002-1b R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 |  | 2. | 3500 | TPL-002-1b R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 |  | 3. | 3501 | TPL-002-1b R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 |  | 4. | 3514 | TPL-002-1b R1.4. | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3498 |  | 5. | 3515 | TPL-002-1b R1.5. | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3516 | 3517 | 1. | 3518 | TPL-002-1b R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3516 | 3517 | 2. | 3519 | TPL-002-1b R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3516 | 3517 | 3. | 3520 | TPL-002-1b R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3516 |  | 1. | 3517 | TPL-002-1b R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
266 | 3516 |  | 2. | 3521 | TPL-002-1b R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 | 3526 | 1. | 3527 | TPL-003-1a R1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 | 3526 | 10. | 3528 | TPL-003-1a R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 1310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 | 3526 | 11. | 3529 | TPL-003-1a R1.3.11. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 1311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 | 3526 | 12. | 3530 | TPL-003-1a R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 1312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 | 3526 | 2. | 3531 | TPL-003-1a R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 | 3526 | 3. | 3532 | TPL-003-1a R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 | 3526 | 4. | 3533 | TPL-003-1a R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 | 3526 | 5. | 3534 | TPL-003-1a R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 | 3526 | 6. | 3535 | TPL-003-1a R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 | 3526 | 7. | 3536 | TPL-003-1a R1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 | 3526 | 8. | 3537 | TPL-003-1a R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 | 3526 | 9. | 3538 | TPL-003-1a R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 |  | 1. | 3524 | TPL-003-1a R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 |  | 2. | 3525 | TPL-003-1a R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 |  | 3. | 3526 | TPL-003-1a R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 |  | 4. | 3539 | TPL-003-1a R1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3523 |  | 5. | 3540 | TPL-003-1a R1.5. | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3541 | 3542 | 1. | 3543 | TPL-003-1a R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3541 | 3542 | 2. | 3544 | TPL-003-1a R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3541 | 3542 | 3. | 3545 | TPL-003-1a R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3541 |  | 1. | 3542 | TPL-003-1a R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
267 | 3541 |  | 2. | 3546 | TPL-003-1a R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
268 | 3548 | 3551 | 1. | 3552 | TPL-004-1 R1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
268 | 3548 | 3551 | 2. | 3553 | TPL-004-1 R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
268 | 3548 | 3551 | 3. | 3554 | TPL-004-1 R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
268 | 3548 | 3551 | 4. | 3555 | TPL-004-1 R1.3.4. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
268 | 3548 | 3551 | 5. | 3556 | TPL-004-1 R1.3.5. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
268 | 3548 | 3551 | 6. | 3557 | TPL-004-1 R1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
268 | 3548 | 3551 | 7. | 3558 | TPL-004-1 R1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
268 | 3548 | 3551 | 8. | 3559 | TPL-004-1 R1.3.8. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
268 | 3548 | 3551 | 9. | 3560 | TPL-004-1 R1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
268 | 3548 |  | 1. | 3549 | TPL-004-1 R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
268 | 3548 |  | 2. | 3550 | TPL-004-1 R1.2. | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
268 | 3548 |  | 3. | 3551 | TPL-004-1 R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
268 | 3548 |  | 4. | 3561 | TPL-004-1 R1.4. | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 330 |  | 1. | 331 | CIP-006-1 R1.1. | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 330 |  | 2. | 332 | CIP-006-1 R1.2. | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 330 |  | 3. | 333 | CIP-006-1 R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 330 |  | 4. | 334 | CIP-006-1 R1.4. | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 330 |  | 5. | 335 | CIP-006-1 R1.5. | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 330 |  | 6. | 336 | CIP-006-1 R1.6. | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 330 |  | 7. | 337 | CIP-006-1 R1.7. | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 330 |  | 8. | 338 | CIP-006-1 R1.8. | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 330 |  | 9. | 339 | CIP-006-1 R1.9. | Process for ensuring that the physical security plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 340 |  | 1. | 341 | CIP-006-1 R2.1. | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 340 |  | 2. | 342 | CIP-006-1 R2.2. | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 340 |  | 3. | 343 | CIP-006-1 R2.3. | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 340 |  | 4. | 344 | CIP-006-1 R2.4. | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 345 |  | 1. | 346 | CIP-006-1 R3.1. | Alarm Systems: Systems that alarm to indicate a door, gate or window has been pened without authorization. These alarms must provide for immediate notificationto personnel responsible for response. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 345 |  | 2. | 347 | CIP-006-1 R3.2. | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 348 |  | 1. | 349 | CIP-006-1 R4.1. | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 348 |  | 2. | RP-2021-06-15-0000008 | CIP-006-1 R4.2. | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 348 |  | 3. | 351 | CIP-006-1 R4.3. | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 353 |  | 1. | 354 | CIP-006-1 R6.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 353 |  | 2. | 355 | CIP-006-1 R6.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
27 | 353 |  | 3. | 356 | CIP-006-1 R6.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
270 | 3566 | 3567 | 1. | 3568 | INT-003-3 R1.1.1. | Interchange Schedule start and end time. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2014-09-30 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
270 | 3566 | 3567 | 2. | 3569 | INT-003-3 R1.1.2. | Energy profile. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2014-09-30 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
270 | 3566 |  | 1. | 3567 | INT-003-3 R1.1. | The Sending Balancing Authority and Receiving Balancing Authority shall agree on Interchange as received from the Interchange Authority, including: |  | BA | BA | [21 empty] | 2011-04-01 |  | 2014-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
270 | 3566 |  | 2. | 3570 | INT-003-3 R1.2. | If a high voltage direct current (HVDC) tie is on the Scheduling Path, then the Sending Balancing Authorities and Receiving Balancing Authorities shall coordinate the Interchange Schedule with the Transmission Operator of the HVDC tie. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2014-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5499 |  | 1. | 6583 | PRC-006-1 E.B.2.1. | Those islands selected by applying the criteria in Requirement E.B.1, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5499 |  | 2. | 6584 | PRC-006-1 E.B.2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5497 | RP-2021-09-01-0000004 | 1. | 6577 | PRC-006-1 E.A.3.3.1. | Individual generating unit greater than 50 MVA (gross nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 331000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5497 | RP-2021-09-01-0000004 | 2. | 6578 | PRC-006-1 E.A.3.3.2. | Generating plants/facilities greater than 50 MVA (gross aggregate nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 332000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5497 | RP-2021-09-01-0000004 | 3. | 6579 | PRC-006-1 E.A.3.3.3. | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 50 MVA gross nameplate rating. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 333000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5497 |  | 1. | RP-2021-09-01-0000002 | PRC-006-1 E.A.3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1A, either for 30 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5497 |  | 2. | RP-2021-09-01-0000003 | PRC-006-1 E.A.3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1A, either for 30 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5497 |  | 3. | RP-2021-09-01-0000004 | PRC-006-1 E.A.3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5500 | 6587 | 1. | 6588 | PRC-006-1 E.B.3.3.1. | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 331000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5500 | 6587 | 2. | 6589 | PRC-006-1 E.B.3.3.2. | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 332000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5500 | 6587 | 3. | 6590 | PRC-006-1 E.B.3.3.3. | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 333000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5500 |  | 1. | 6585 | PRC-006-1 E.B.3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5500 |  | 2. | 6586 | PRC-006-1 E.B.3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5500 |  | 3. | 6587 | PRC-006-1 E.B.3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5496 |  | 1. | RP-2021-09-02-0000001 | PRC-006-1 E.A.4.1. | Underfrequency trip settings of individual generating units that are part of plants/facilities with a capacity of 50 MVA or more individually or cumulatively (gross nameplate rating), directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1A, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5496 |  | 2. | RP-2021-09-02-0000002 | PRC-006-1 E.A.4.2. | Overfrequency trip settings of individual generating units that are part of plants/facilities with a capacity of 50 MVA or more individually or cumulatively (gross nameplate rating), directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 - Attachment 2A, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5496 |  | 3. | RP-2021-09-02-0000003 | PRC-006-1 E.A.4.3. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5501 |  | 1. | 6591 | PRC-006-1 E.B.4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5501 |  | 2. | 6592 | PRC-006-1 E.B.4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5501 |  | 3. | 6593 | PRC-006-1 E.B.4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5501 |  | 4. | 6594 | PRC-006-1 E.B.4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5501 |  | 5. | 6595 | PRC-006-1 E.B.4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5501 |  | 6. | 6596 | PRC-006-1 E.B.4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 460000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5501 |  | 7. | 6597 | PRC-006-1 E.B.4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 470000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5502 |  | 1. | 6598 | PRC-006-1 E.B.11.1. | The performance of the UFLS equipment, E.B. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 5502 |  | 2. | 6599 | PRC-006-1 E.B.11.2. | The effectiveness of the UFLS program |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 1120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3583 |  | 1. | 6546 | PRC-006-1 R2.1. | Those islands selected by applying the criteria in Requirement R1, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-10-01 |  | 2015-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3583 |  | 2. | 6547 | PRC-006-1 R2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3583 |  | 3. | 6548 | PRC-006-1 R2.3. | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3584 | 6551 | 1. | 6552 | PRC-006-1 R3.3.1. | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 331000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3584 | 6551 | 2. | 6553 | PRC-006-1 R3.3.2. | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 332000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3584 | 6551 | 3. | 6554 | PRC-006-1 R3.3.3. | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 333000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3584 |  | 1. | 6549 | PRC-006-1 R3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3584 |  | 2. | 6550 | PRC-006-1 R3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3584 |  | 3. | 6551 | PRC-006-1 R3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3585 |  | 1. | 6555 | PRC-006-1 R4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3585 |  | 2. | 6556 | PRC-006-1 R4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3585 |  | 3. | 6557 | PRC-006-1 R4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3585 |  | 4. | 6558 | PRC-006-1 R4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3585 |  | 5. | 6559 | PRC-006-1 R4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3585 |  | 6. | 6560 | PRC-006-1 R4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 460000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3585 |  | 7. | 6561 | PRC-006-1 R4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 470000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3579 |  | 1. | 7386 | PRC-006-1 R11.1. | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3579 |  | 2. | 7387 | PRC-006-1 R11.2. | The effectiveness of the UFLS program. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3582 |  | 1. | 6562 | PRC-006-1 R14.1. | UFLS program, including a schedule for implementation |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3582 |  | 2. | 6563 | PRC-006-1 R14.2. | UFLS design assessment |  | PCPA | [9 empty] | PCPA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
273 | 3582 |  | 3. | 6564 | PRC-006-1 R14.3. | Format and schedule of UFLS data submittal |  | PCPA | [9 empty] | PCPA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  | 143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
274 | 3591 |  | 1. | 3592 | TOP-005-1.1a R1.1. | Each Reliability Coordinator shall identify the data requirements from the list in Attachment 1-TOP-005-0 “Electric System Reliability Data” and any additional operating information requirements relating to operation of the bulk power system within the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
275 | 3601 |  | 1. | 3602 | VAR-001-2 R3.1. | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2011-01-10 |  | 2013-12-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
275 | 3601 |  | 2. | 3603 | VAR-001-2 R3.2. | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  | TOP | [18 empty] | TOP |  |  |  | 2011-01-10 |  | 2013-12-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
275 | 3606 |  | 1. | RP-2021-06-03-0000003 | VAR-001-2 R6.1. | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2011-10-01 |  | 2013-12-31 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
275 | 3610 |  | 1. | 3611 | VAR-001-2 R9.1. | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  | TOP | [18 empty] | TOP |  |  |  | 2011-01-10 |  | 2013-12-31 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3617 |  | 1. | 3624 | CIP-005-1a R1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3617 |  | 2. | 3626 | CIP-005-1a R1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3617 |  | 3. | 3621 | CIP-005-1a R1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3617 |  | 4. | 3622 | CIP-005-1a R1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3617 |  | 5. | 3625 | CIP-005-1a R1.5. | Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirements R2 and R3, Standard CIP-007, Requirements R1 and R3 through R9, Standard CIP-008, and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3617 |  | 6. | 3623 | CIP-005-1a R1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3619 | 3631 | 1. | 3635 | CIP-005-1a R2.5.1. | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 251000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3619 | 3631 | 2. | 3636 | CIP-005-1a R2.5.2. | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 252000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3619 | 3631 | 3. | 3634 | CIP-005-1a R2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 253000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3619 | 3631 | 4. | 3633 | CIP-005-1a R2.5.4. | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 254000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3619 |  | 1. | 3627 | CIP-005-1a R2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3619 |  | 2. | 3632 | CIP-005-1a R2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3619 |  | 3. | 3629 | CIP-005-1a R2.3. | The Responsible Entity shall maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3619 |  | 4. | 3628 | CIP-005-1a R2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3619 |  | 5. | 3631 | CIP-005-1a R2.5. | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3619 |  | 6. | 3630 | CIP-005-1a R2.6. | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3616 |  | 1. | 3638 | CIP-005-1a R3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3616 |  | 2. | 3637 | CIP-005-1a R3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3618 |  | 1. | 3641 | CIP-005-1a R4.1. | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3618 |  | 2. | 3639 | CIP-005-1a R4.2. | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3618 |  | 3. | 3640 | CIP-005-1a R4.3. | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3618 |  | 4. | 3642 | CIP-005-1a R4.4. | A review of controls for default accounts, passwords, and network management community strings; and, |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3618 |  | 5. | 3643 | CIP-005-1a R4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3620 |  | 1. | 3644 | CIP-005-1a R5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3620 |  | 2. | 3645 | CIP-005-1a R5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
277 | 3620 |  | 3. | 3646 | CIP-005-1a R5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3648 |  | 1. | 3655 | CIP-005-2a R1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3648 |  | 2. | 3657 | CIP-005-2a R1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3648 |  | 3. | 3652 | CIP-005-2a R1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3648 |  | 4. | 3653 | CIP-005-2a R1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3648 |  | 5. | 3656 | CIP-005-2a R1.5. | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirement R3; Standard CIP-007-2 Requirements R1 and R3 through R9; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3648 |  | 6. | 3654 | CIP-005-2a R1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3650 | 3662 | 1. | 3666 | CIP-005-2a R2.5.1. | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 251000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3650 | 3662 | 2. | 3667 | CIP-005-2a R2.5.2. | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 252000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3650 | 3662 | 3. | 3665 | CIP-005-2a R2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 253000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3650 | 3662 | 4. | 3664 | CIP-005-2a R2.5.4. | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 254000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3650 |  | 1. | 3658 | CIP-005-2a R2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3650 |  | 2. | 3663 | CIP-005-2a R2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3650 |  | 3. | 3660 | CIP-005-2a R2.3. | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3650 |  | 4. | 3659 | CIP-005-2a R2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3650 |  | 5. | 3662 | CIP-005-2a R2.5. | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3650 |  | 6. | 3661 | CIP-005-2a R2.6. | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3647 |  | 1. | 3669 | CIP-005-2a R3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3647 |  | 2. | RP-2021-06-15-0000002 | CIP-005-2a R3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3649 |  | 1. | 3672 | CIP-005-2a R4.1. | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3649 |  | 2. | 3670 | CIP-005-2a R4.2. | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3649 |  | 3. | 3671 | CIP-005-2a R4.3. | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3649 |  | 4. | 3673 | CIP-005-2a R4.4. | A review of controls for default accounts, passwords, and network management community strings; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3649 |  | 5. | 3674 | CIP-005-2a R4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3651 |  | 1. | 3675 | CIP-005-2a R5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-2 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-2 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3651 |  | 2. | 3676 | CIP-005-2a R5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
278 | 3651 |  | 3. | 3677 | CIP-005-2a R5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
279 | 3684 |  | 1. | 3697 | BAL-005-0a R1.1. | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
279 | 3684 |  | 2. | 3695 | BAL-005-0a R1.2. | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
279 | 3684 |  | 3. | 3696 | BAL-005-0a R1.3. | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
279 | 3688 |  | 1. | 3701 | BAL-005-0a R8.1. | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
279 | 3693 |  | 1. | 3702 | BAL-005-0a R9.1. | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
279 | 3690 |  | 1. | 3698 | BAL-005-0a R12.1. | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
279 | 3690 |  | 2. | 3699 | BAL-005-0a R12.2. | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
279 | 3690 |  | 3. | 3700 | BAL-005-0a R12.3. | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 357 |  | 1. | 358 | CIP-006-1a R1.1. | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 357 |  | 2. | 359 | CIP-006-1a R1.2. | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 357 |  | 3. | 360 | CIP-006-1a R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 357 |  | 4. | 361 | CIP-006-1a R1.4. | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 357 |  | 5. | 362 | CIP-006-1a R1.5. | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 357 |  | 6. | 363 | CIP-006-1a R1.6. | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 357 |  | 7. | 364 | CIP-006-1a R1.7. | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 357 |  | 8. | 365 | CIP-006-1a R1.8. | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 357 |  | 9. | 366 | CIP-006-1a R1.9. | Process for ensuring that the physical security plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 367 |  | 1. | 368 | CIP-006-1a R2.1. | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 367 |  | 2. | 369 | CIP-006-1a R2.2. | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 367 |  | 3. | 370 | CIP-006-1a R2.3. | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 367 |  | 4. | 371 | CIP-006-1a R2.4. | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 372 |  | 1. | 373 | CIP-006-1a R3.1. | Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 372 |  | 2. | 374 | CIP-006-1a R3.2. | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 375 |  | 1. | 376 | CIP-006-1a R4.1. | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 375 |  | 2. | RP-2021-06-15-0000009 | CIP-006-1a R4.2. | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 375 |  | 3. | 378 | CIP-006-1a R4.3. | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 380 |  | 1. | 381 | CIP-006-1a R6.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 380 |  | 2. | 382 | CIP-006-1a R6.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
28 | 380 |  | 3. | 383 | CIP-006-1a R6.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
280 | 3703 |  | 1. | 3705 | PRC-005-1a R1.1. | Maintenance and testing intervals and their basis. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-09-26 |  | 2012-03-13 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
280 | 3703 |  | 2. | 3706 | PRC-005-1a R1.2. | Summary of maintenance and testing procedures. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-09-26 |  | 2012-03-13 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
280 | 3704 |  | 1. | 3707 | PRC-005-1a R2.1. | Evidence Protection System devices were maintained and tested within the defined intervals. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-09-26 |  | 2012-03-13 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
280 | 3704 |  | 2. | 3708 | PRC-005-1a R2.2. | Date each Protection System device was last tested/maintained. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-09-26 |  | 2012-03-13 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3709 | 6442 | 1. | 6443 | PER-003-1 R1.1.1. | Resource and demand balancing |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3709 | 6442 | 2. | 6444 | PER-003-1 R1.1.2. | Transmission operations |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3709 | 6442 | 3. | 6445 | PER-003-1 R1.1.3. | Emergency preparedness and operations |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3709 | 6442 | 4. | 6446 | PER-003-1 R1.1.4. | System operations |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3709 | 6442 | 5. | 6447 | PER-003-1 R1.1.5. | Protection and control |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3709 | 6442 | 6. | 6448 | PER-003-1 R1.1.6. | Voltage and reactive |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  | 116000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3709 | 6442 | 7. | 6449 | PER-003-1 R1.1.7. | Interchange scheduling and coordination |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  | 117000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3709 | 6442 | 8. | 6450 | PER-003-1 R1.1.8. | Interconnection reliability operations and coordination |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  | 118000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3709 |  | 1. | 6442 | PER-003-1 R1.1. | Areas of Competency |  | RC | [11 empty] | RC | [9 empty] | M1.1 A list of Real-time operating positions. | 2011-09-15 |  | 2019-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3710 | 6451 | 1. | 6452 | PER-003-1 R2.1.1. | Transmission operations |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3710 | 6451 | 2. | 6453 | PER-003-1 R2.1.2. | Emergency preparedness and operations |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3710 | 6451 | 3. | 6454 | PER-003-1 R2.1.3. | System operations |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3710 | 6451 | 4. | 6455 | PER-003-1 R2.1.4. | Protection and control |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3710 | 6451 | 5. | 6456 | PER-003-1 R2.1.5. | Voltage and reactive |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  | 215000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3710 |  | 1. | 6451 | PER-003-1 R2.1. | Areas of Competency |  | TOP | [18 empty] | TOP |  |  |  | 2011-09-15 |  | 2019-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3710 |  | 2. | 6457 | PER-003-1 R2.2. | Certificates: • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator |  | TOP | [18 empty] | TOP |  |  |  | 2011-09-15 |  | 2019-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3711 | 6458 | 1. | 6459 | PER-003-1 R3.1.1. | Resources and demand balancing |  | BA | BA | [21 empty] | 2012-10-01 |  | 2019-06-30 |  |  | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3711 | 6458 | 2. | 6460 | PER-003-1 R3.1.2. | Emergency preparedness and operations |  | BA | BA | [21 empty] | 2012-10-01 |  | 2019-06-30 |  |  | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3711 | 6458 | 3. | 6461 | PER-003-1 R3.1.3. | System operations |  | BA | BA | [21 empty] | 2012-10-01 |  | 2019-06-30 |  |  | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3711 | 6458 | 4. | 6462 | PER-003-1 R3.1.4. | Interchange scheduling and coordination |  | BA | BA | [21 empty] | 2012-10-01 |  | 2019-06-30 |  |  | 314000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3711 |  | 1. | 6458 | PER-003-1 R3.1. | Areas of Competency |  | BA | BA | [21 empty] | 2011-09-15 |  | 2019-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
281 | 3711 |  | 2. | 6464 | PER-003-1 R3.2. | Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator |  | BA | BA | [21 empty] | 2011-09-15 |  | 2019-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
282 | 3714 |  | 1. | 3718 | BAL-003-0.1a R1.1. | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
282 | 3714 |  | 2. | 3719 | BAL-003-0.1a R1.2. | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
282 | 3713 |  | 1. | 3721 | BAL-003-0.1a R2.1. | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
282 | 3713 |  | 2. | 3720 | BAL-003-0.1a R2.2. | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
282 | 3715 |  | 1. | 3723 | BAL-003-0.1a R4.1. | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
282 | 3715 |  | 2. | 3722 | BAL-003-0.1a R4.2. | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
282 | 3712 |  | 1. | 3724 | BAL-003-0.1a R5.1. | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3729 |  | 1. | RP-2021-06-16-0000001 | FAC-008-2 R1.1. | The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. |  | GO |  |  |  |  | GO | [19 empty] | 2011-05-24 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3729 |  | 2. | RP-2021-06-16-0000002 | FAC-008-2 R1.2. | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO |  |  |  |  | GO | [19 empty] | 2011-05-24 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3730 |  | 1. | RP-2021-06-16-0000003 | FAC-008-2 R2.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | GO |  |  |  |  | GO | [19 empty] | 2011-05-24 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3730 |  | 2. | RP-2021-06-16-0000004 | FAC-008-2 R2.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: |  | GO |  |  |  |  | GO | [19 empty] | 2011-05-24 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3730 |  | 2.1. | RP-2021-06-16-0000005 | FAC-008-2 R2.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | GO |  |  |  |  | GO | [19 empty] | 2011-05-24 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3730 |  | 2.2. | RP-2021-06-16-0000006 | FAC-008-2 R2.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | GO |  |  |  |  | GO | [19 empty] | 2011-05-24 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3730 |  | 2.3. | RP-2021-06-16-0000007 | FAC-008-2 R2.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | GO |  |  |  |  | GO | [19 empty] | 2011-05-24 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3730 |  | 2.4. | RP-2021-06-16-0000008 | FAC-008-2 R2.2.4. | Operating limitations. Note: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. |  | GO |  |  |  |  | GO | [19 empty] | 2011-05-24 |  |  | 224000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3730 |  | 3. | RP-2021-06-16-0000009 | FAC-008-2 R2.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO |  |  |  |  | GO | [19 empty] | 2011-05-24 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3730 |  | 4. | RP-2021-06-16-0000010 | FAC-008-2 R2.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | GO |  |  |  |  | GO | [19 empty] | 2011-05-24 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3730 |  | 4.1. | RP-2021-06-16-0000011 | FAC-008-2 R2.4.1. | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO |  |  |  |  | GO | [19 empty] | 2011-05-24 |  |  | 241000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3730 |  | 4.2. | RP-2021-06-16-0000012 | FAC-008-2 R2.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO |  |  |  |  | GO | [19 empty] | 2011-05-24 |  |  | 242000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3731 |  | 1. | RP-2021-06-16-0000013 | FAC-008-2 R3.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | TO | [17 empty] | TO | [6 empty] | 2011-05-24 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3731 |  | 2. | RP-2021-06-16-0000014 | FAC-008-2 R3.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: |  | TO | [17 empty] | TO | [6 empty] | 2011-05-24 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3731 |  | 2.1. | RP-2021-06-16-0000015 | FAC-008-2 R3.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | TO | [17 empty] | TO | [6 empty] | 2011-05-24 |  |  | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3731 |  | 2.2. | RP-2021-06-16-0000016 | FAC-008-2 R3.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | TO | [17 empty] | TO | [6 empty] | 2011-05-24 |  |  | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3731 |  | 2.3. | RP-2021-06-16-0000017 | FAC-008-2 R3.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | TO | [17 empty] | TO | [6 empty] | 2011-05-24 |  |  | 323000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3731 |  | 2.4. | RP-2021-06-16-0000018 | FAC-008-2 R3.2.4. | Operating limitations. Note: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. |  | TO | [17 empty] | TO | [6 empty] | 2011-05-24 |  |  | 324000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3731 |  | 3. | RP-2021-06-16-0000019 | FAC-008-2 R3.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | TO | [17 empty] | TO | [6 empty] | 2011-05-24 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3731 |  | 4. | RP-2021-06-16-0000020 | FAC-008-2 R3.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | TO | [17 empty] | TO | [6 empty] | 2011-05-24 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3731 |  | 4.1. | RP-2021-06-16-0000021 | FAC-008-2 R3.4.1. | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | TO | [17 empty] | TO | [6 empty] | 2011-05-24 |  |  | 341000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
284 | 3731 |  | 4.2. | RP-2021-06-16-0000022 | FAC-008-2 R3.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | TO | [17 empty] | TO | [6 empty] | 2011-05-24 |  |  | 342000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3736 |  | 1. | 6322 | FAC-008-3 R1.1. | The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. |  | GO |  |  |  |  | GO | [17 empty] | 2011-11-17 |  | 2021-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3736 |  | 2. | 6323 | FAC-008-3 R1.2. | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO |  |  |  |  | GO | [17 empty] | 2011-11-17 |  | 2021-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3737 | 6324 | 1. | 6326 | FAC-008-3 R2.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | GO |  |  |  |  | GO | [17 empty] | 2013-01-01 |  | 2021-09-30 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3737 | 6324 | 2. | 6327 | FAC-008-3 R2.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | GO |  |  |  |  | GO | [17 empty] | 2013-01-01 |  | 2021-09-30 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3737 | 6324 | 3. | 6328 | FAC-008-3 R2.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | GO |  |  |  |  | GO | [17 empty] | 2013-01-01 |  | 2021-09-30 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3737 | 6324 | 4. | 6329 | FAC-008-3 R2.2.4. | Operating limitations. (Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice.) |  | GO |  |  |  |  | GO | [17 empty] | 2013-01-01 |  | 2021-09-30 |  |  | 224000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3737 | 6331 | 1. | 6332 | FAC-008-3 R2.4.1. | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO |  |  |  |  | GO | [17 empty] | 2013-01-01 |  | 2021-09-30 |  |  | 241000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3737 | 6331 | 2. | 6333 | FAC-008-3 R2.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO |  |  |  |  | GO | [17 empty] | 2013-01-01 |  | 2021-09-30 |  |  | 242000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3737 |  | 1. | RP-2021-07-01-0000017 | FAC-008-3 R2.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | GO |  |  |  |  | GO | [17 empty] | 2013-01-01 |  | 2021-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3737 |  | 2. | 6324 | FAC-008-3 R2.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: |  | GO |  |  |  |  | GO | [17 empty] | 2011-11-17 |  | 2021-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3737 |  | 3. | 6330 | FAC-008-3 R2.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO |  |  |  |  | GO | [17 empty] | 2011-11-17 |  | 2021-09-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3737 |  | 4. | 6331 | FAC-008-3 R2.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | GO |  |  |  |  | GO | [17 empty] | 2011-11-17 |  | 2021-09-30 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3738 | 6334 | 1. | 6336 | FAC-008-3 R3.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | TO | [17 empty] | TO |  |  |  |  | 2013-01-01 |  | 2021-09-30 |  |  | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3738 | 6334 | 2. | 6337 | FAC-008-3 R3.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | TO | [17 empty] | TO |  |  |  |  | 2013-01-01 |  | 2021-09-30 |  |  | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3738 | 6334 | 3. | 6338 | FAC-008-3 R3.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | TO | [17 empty] | TO |  |  |  |  | 2013-01-01 |  | 2021-09-30 |  |  | 323000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3738 | 6334 | 4. | 6339 | FAC-008-3 R3.2.4. | Operating limitations. (Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice.) |  | TO | [17 empty] | TO |  |  |  |  | 2013-01-01 |  | 2021-09-30 |  |  | 324000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3738 | 6341 | 1. | 6342 | FAC-008-3 R3.4.1. | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | TO | [17 empty] | TO |  |  |  |  | 2013-01-01 |  | 2021-09-30 |  |  | 341000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3738 | 6341 | 2. | 6343 | FAC-008-3 R3.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | TO | [17 empty] | TO |  |  |  |  | 2013-01-01 |  | 2021-09-30 |  |  | 342000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3738 |  | 1. | RP-2021-07-01-0000022 | FAC-008-3 R3.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | TO | [17 empty] | TO |  |  |  |  | 2013-01-01 |  | 2021-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3738 |  | 2. | 6334 | FAC-008-3 R3.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: |  | TO | [17 empty] | TO |  |  |  |  | 2011-11-17 |  | 2021-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3738 |  | 3. | 6340 | FAC-008-3 R3.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | TO | [17 empty] | TO |  |  |  |  | 2011-11-17 |  | 2021-09-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3738 |  | 4. | 6341 | FAC-008-3 R3.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | TO | [17 empty] | TO |  |  |  |  | 2011-11-17 |  | 2021-09-30 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3738 |  | 4.1. DO NOT USE | RP-2021-07-01-0000020 | FAC-008-3 R3.4.1. DO NOT USE | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | TO | [17 empty] | TO |  |  |  |  | 2013-01-01 |  | 2021-09-30 |  |  | 341000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3743 | 6347 | 1. | 6348 | FAC-008-3 R8.2.1. | Identity of the existing next most limiting equipment of the Facility |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-01-01 |  | 2021-09-30 |  |  | 821000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3743 | 6347 | 2. | 6349 | FAC-008-3 R8.2.2. | The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-01-01 |  | 2021-09-30 |  |  | 822000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3743 |  | 1. | RP-2021-07-01-0000023 | FAC-008-3 R8.1. | As scheduled by the requesting entities: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-01-01 |  | 2021-09-30 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3743 |  | 1.1. | 6344 | FAC-008-3 R8.1.1. | Facility Ratings |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-11-17 |  | 2021-09-30 |  |  | 811000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3743 |  | 1.2. | 6345 | FAC-008-3 R8.1.2. | Identity of the most limiting equipment of the Facilities |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-01-01 |  | 2021-09-30 |  |  | 812000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
285 | 3743 |  | 2. | 6347 | FAC-008-3 R8.2. | Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-11-17 |  | 2021-09-30 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
286 | 3744 | 7389 | 1. | 7390 | PRC-002-NPCC-01 R1.2.1. | Transmission and Generator circuit breaker positions |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 121000000 | NPCC-US |  | NPCC-US
286 | 3744 | 7389 | 2. | 7391 | PRC-002-NPCC-01 R1.2.2. | Protective Relay tripping for all Protection Groups that operate to trip circuit breakers identified in 1.2.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 122000000 | NPCC-US |  | NPCC-US
286 | 3744 | 7389 | 3. | 7392 | PRC-002-NPCC-01 R1.2.3. | Teleprotection keying and receive |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 123000000 | NPCC-US |  | NPCC-US
286 | 3744 |  | 1. | 7388 | PRC-002-NPCC-01 R1.1. | Be provided at all substations and at locations where circuit breaker operation affects continuity of service to radial Loads greater than 300MW, or the operation of which drops 50MVA Nameplate Rating or greater of Generation, or the operation of which creates a Generation/Load island. Be provided at generating units above 50MVA Nameplate Rating or series of generating units utilizing a control scheme such that the loss of 1 unit results in a loss of greater than 50MVA Nameplate Capacity, and at Generating Plants above 300MVA Name Plate Capacity. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 110000000 | NPCC-US |  | NPCC-US
286 | 3744 |  | 2. | 7389 | PRC-002-NPCC-01 R1.2. | Monitor the following at each location listed in 1.1: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 120000000 | NPCC-US |  | NPCC-US
286 | 3753 |  | 1. | RP-2021-06-23-0000010 | PRC-002-NPCC-01 R2.1. | All transmission lines. |  | TO | [17 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 210000000 | NPCC-US |  | NPCC-US
286 | 3753 |  | 2. | RP-2021-06-23-0000011 | PRC-002-NPCC-01 R2.2. | Autotransformers or phase-shifters connected to busses. |  | TO | [17 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 220000000 | NPCC-US |  | NPCC-US
286 | 3753 |  | 3. | RP-2021-06-23-0000012 | PRC-002-NPCC-01 R2.3. | Shunt capacitors, shunt reactors. |  | TO | [17 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 230000000 | NPCC-US |  | NPCC-US
286 | 3753 |  | 4. | RP-2021-06-23-0000013 | PRC-002-NPCC-01 R2.4. | Individual generator line interconnections. |  | TO | [17 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 240000000 | NPCC-US |  | NPCC-US
286 | 3753 |  | 5. | RP-2021-06-23-0000014 | PRC-002-NPCC-01 R2.5. | Dynamic VAR Devices. |  | TO | [17 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 250000000 | NPCC-US |  | NPCC-US
286 | 3753 |  | 6. | RP-2021-06-23-0000015 | PRC-002-NPCC-01 R2.6. | HVDC terminals. |  | TO | [17 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 260000000 | NPCC-US |  | NPCC-US
286 | 3756 |  | 1. | RP-2021-06-23-0000016 | PRC-002-NPCC-01 R5.1. | Three phase-to-neutral voltages. (Common bus-side voltages may be used for lines.) |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 510000000 | NPCC-US |  | NPCC-US
286 | 3756 |  | 2. | RP-2021-06-23-0000017 | PRC-002-NPCC-01 R5.2. | Three phase currents and neutral currents. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 520000000 | NPCC-US |  | NPCC-US
286 | 3756 |  | 3. | 7355 | PRC-002-NPCC-01 R5.3. | Polarizing currents and voltages, if used. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 530000000 | NPCC-US |  | NPCC-US
286 | 3756 |  | 4. | 7356 | PRC-002-NPCC-01 R5.4. | Frequency. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 540000000 | NPCC-US |  | NPCC-US
286 | 3756 |  | 5. | 7357 | PRC-002-NPCC-01 R5.5. | Real and reactive power. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 550000000 | NPCC-US |  | NPCC-US
286 | 3757 | 7360 | 1. | 7361 | PRC-002-NPCC-01 R6.3.1. | Monitored phase overcurrents set at 1.5 pu or less of rated CT secondary current or Protective Relay tripping for all Protection Groups. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 631000000 | NPCC-US |  | NPCC-US
286 | 3757 | 7360 | 2. | 7362 | PRC-002-NPCC-01 R6.3.2. | Neutral (residual) overcurrent set at 0.2 pu or less of rated CT secondary current. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 632000000 | NPCC-US |  | NPCC-US
286 | 3757 | 7360 | 3. | 7363 | PRC-002-NPCC-01 R6.3.3. | Monitored phase undervoltage set at 0.85 pu or greater. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 633000000 | NPCC-US |  | NPCC-US
286 | 3757 |  | 1. | 7358 | PRC-002-NPCC-01 R6.1. | Each Fault recorder record duration shall be a minimum of one (1) second. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 610000000 | NPCC-US |  | NPCC-US
286 | 3757 |  | 2. | 7359 | PRC-002-NPCC-01 R6.2. | Each Fault recorder shall have a minimum recording rate of 16 samples per cycle. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 620000000 | NPCC-US |  | NPCC-US
286 | 3757 |  | 3. | 7360 | PRC-002-NPCC-01 R6.3. | Each Fault recorder shall be set to trigger for at least the following: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 630000000 | NPCC-US |  | NPCC-US
286 | 3757 |  | 4. | 7364 | PRC-002-NPCC-01 R6.4. | Document additional triggers and deviations from the settings in 6.3.2 and 6.3.3 when local conditions dictate. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 640000000 | NPCC-US |  | NPCC-US
286 | 3758 | 7366 | 1. | 7367 | PRC-002-NPCC-01 R7.2.1. | Major Load centers. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  | 721000000 | NPCC-US |  | NPCC-US
286 | 3758 | 7366 | 2. | 7402 | PRC-002-NPCC-01 R7.2.2. | Major Generation clusters. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  | 722000000 | NPCC-US |  | NPCC-US
286 | 3758 | 7366 | 3. | 7403 | PRC-002-NPCC-01 R7.2.3. | Major voltage sensitive areas. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  | 723000000 | NPCC-US |  | NPCC-US
286 | 3758 | 7366 | 4. | 7404 | PRC-002-NPCC-01 R7.2.4. | Major transmission interfaces. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  | 724000000 | NPCC-US |  | NPCC-US
286 | 3758 | 7366 | 5. | 7405 | PRC-002-NPCC-01 R7.2.5. | Major transmission junctions. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  | 725000000 | NPCC-US |  | NPCC-US
286 | 3758 | 7366 | 6. | 7406 | PRC-002-NPCC-01 R7.2.6. | Elements associated with Interconnection Reliability Operating Limits (IROLs). |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  | 726000000 | NPCC-US |  | NPCC-US
286 | 3758 | 7366 | 7. | 7407 | PRC-002-NPCC-01 R7.2.7. | Major EHV interconnections between operating areas. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  | 727000000 | NPCC-US |  | NPCC-US
286 | 3758 |  | 1. | 7365 | PRC-002-NPCC-01 R7.1. | Provides a minimum of 1 DDR per 3,000 MW of peak Load. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 710000000 | NPCC-US |  | NPCC-US
286 | 3758 |  | 2. | 7366 | PRC-002-NPCC-01 R7.2. | Records dynamic disturbance information with consideration of the following facilities/locations: |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  | 720000000 | NPCC-US |  | NPCC-US
286 | 3760 | 7410 | 1. | 7411 | PRC-002-NPCC-01 R9.3.1. | Rate of change of Frequency. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  | 931000000 | NPCC-US |  | NPCC-US
286 | 3760 | 7410 | 2. | 7412 | PRC-002-NPCC-01 R9.3.2. | Rate of change of Power. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  | 932000000 | NPCC-US |  | NPCC-US
286 | 3760 | 7410 | 3. | 7413 | PRC-002-NPCC-01 R9.3.3. | Delta Frequency (recommend 20 mHz change). |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  | 933000000 | NPCC-US |  | NPCC-US
286 | 3760 | 7410 | 4. | 7414 | PRC-002-NPCC-01 R9.3.4. | Oscillation of Frequency. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  | 934000000 | NPCC-US |  | NPCC-US
286 | 3760 |  | 1. | 7408 | PRC-002-NPCC-01 R9.1. | A minimum recording time of sixty (60) seconds per trigger event. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  | 910000000 | NPCC-US |  | NPCC-US
286 | 3760 |  | 2. | 7409 | PRC-002-NPCC-01 R9.2. | A minimum data sample rate of 960 samples per second, and a minimum data storage rate for RMS quantities of six (6) data points per second. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  | 920000000 | NPCC-US |  | NPCC-US
286 | 3760 |  | 3. | 7410 | PRC-002-NPCC-01 R9.3. | Each DDR shall be set to trigger for at least one of the following (based on manufacturers’ equipment capabilities): |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  | 930000000 | NPCC-US |  | NPCC-US
286 | 3745 |  | 1. | 7415 | PRC-002-NPCC-01 R10.1. | Line currents for most lines such that normal line maintenance activities do not interfere with DDR functionality. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  | 101000000 | NPCC-US |  | NPCC-US
286 | 3745 |  | 2. | 7416 | PRC-002-NPCC-01 R10.2. | Bus voltages such that normal bus maintenance activities do not interfere with DDR functionality. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  | 102000000 | NPCC-US |  | NPCC-US
286 | 3745 |  | 3. | 7417 | PRC-002-NPCC-01 R10.3. | As a minimum, one phase current per monitored Element and two phase-to-neutral voltages of different Elements. One of the monitored voltages shall be of the same phase as the monitored current. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  | 103000000 | NPCC-US |  | NPCC-US
286 | 3745 |  | 4. | 7418 | PRC-002-NPCC-01 R10.4. | Frequency. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  | 104000000 | NPCC-US |  | NPCC-US
286 | 3745 |  | 5. | 7419 | PRC-002-NPCC-01 R10.5. | Real and reactive power. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  | 105000000 | NPCC-US |  | NPCC-US
286 | 3749 |  | 1. | 7420 | PRC-002-NPCC-01 R14.1. | Maintenance and testing intervals and their basis. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 141000000 | NPCC-US |  | NPCC-US
286 | 3749 |  | 2. | 7421 | PRC-002-NPCC-01 R14.2. | Summary of maintenance and testing procedures. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 142000000 | NPCC-US |  | NPCC-US
286 | 3749 |  | 3. | 7422 | PRC-002-NPCC-01 R14.3. | Monthly verification of communication channels used for accessing records remotely (if the entity relies on remote access and the channel is not monitored to a control center staffed around the clock, 24 hours a day, 7 days a week (24/7)). |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 143000000 | NPCC-US |  | NPCC-US
286 | 3749 |  | 4. | 7423 | PRC-002-NPCC-01 R14.4. | Monthly verification of time synchronization (if the loss of time synchronization is not monitored to a 24/7 control center). |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 144000000 | NPCC-US |  | NPCC-US
286 | 3749 |  | 5. | 7424 | PRC-002-NPCC-01 R14.5. | Monthly verification of active analog quantities. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 145000000 | NPCC-US |  | NPCC-US
286 | 3749 |  | 6. | RP-2021-06-23-0000019 | PRC-002-NPCC-01 R14.6. | Verification of DDR and DFR settings in the software every six (6) years. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 146000000 | NPCC-US |  | NPCC-US
286 | 3749 |  | 7. | 7426 | PRC-002-NPCC-01 R14.7. | A requirement to return failed units to service within 90 days. If a DME device will be out of service for greater than 90 days the owner shall keep a record of efforts aimed at restoring the DME to service. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 147000000 | NPCC-US |  | NPCC-US
286 | 3750 |  | 1. | 7427 | PRC-002-NPCC-01 R15.1. | NERC, Regional Entity, Reliability Coordinator. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 151000000 | NPCC-US |  | NPCC-US
286 | 3750 |  | 2. | 7428 | PRC-002-NPCC-01 R15.2. | Request from other Transmission Owners, Generator Owners within NPCC. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 152000000 | NPCC-US |  | NPCC-US
286 | 3751 |  | 1. | 7429 | PRC-002-NPCC-01 R16.1. | The data files shall be capable of being viewed, read, and analyzed with a generic COMTRADE analysis tool as per the latest revision of IEEE Standard C37.111. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 161000000 | NPCC-US |  | NPCC-US
286 | 3751 |  | 2. | 7430 | PRC-002-NPCC-01 R16.2. | Disturbance Data files shall be named in conformance with the latest revision of IEEE Standard C37.232. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 162000000 | NPCC-US |  | NPCC-US
286 | 3751 |  | 3. | 7431 | PRC-002-NPCC-01 R16.3. | Fault Recorder and DDR Files shall contain all monitored channels. SOE records shall contain station name, date, time resolved to milliseconds, SOE point name, status. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 163000000 | NPCC-US |  | NPCC-US
286 | 3752 |  | 1. | RP-2021-06-23-0000018 | PRC-002-NPCC-01 R17.1. | Type of DME. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  |  | 2013-10-20 |  | 2016-07-01 |  |  | 171000000 | NPCC-US |  | NPCC-US
286 | 3752 |  | 2. | 7433 | PRC-002-NPCC-01 R17.2. | Make and model of equipment. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 172000000 | NPCC-US |  | NPCC-US
286 | 3752 |  | 3. | 7434 | PRC-002-NPCC-01 R17.3. | Installation location. |  | GOP, RC, TOP | [5 empty] | GOP | [5 empty] | RC | [6 empty] | TOP |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 173000000 | NPCC-US |  | NPCC-US
286 | 3752 |  | 4. | 7435 | PRC-002-NPCC-01 R17.4. | Operational Status.Operational Status. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 174000000 | NPCC-US |  | NPCC-US
286 | 3752 |  | 5. | 7436 | PRC-002-NPCC-01 R17.5. | Date last tested. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 175000000 | NPCC-US |  | NPCC-US
286 | 3752 |  | 6. | 7437 | PRC-002-NPCC-01 R17.6. | Monitored Elements. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 176000000 | NPCC-US |  | NPCC-US
286 | 3752 |  | 7. | 7438 | PRC-002-NPCC-01 R17.7. | All identified channels. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 177000000 | NPCC-US |  | NPCC-US
286 | 3752 |  | 8. | 7439 | PRC-002-NPCC-01 R17.8. | Monitored electrical quantities. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  | 178000000 | NPCC-US |  | NPCC-US
287 | 3766 |  | 1. | 6350 | PRC-023-2 R6.1. | Maintain a list of circuits subject to PRC-023-2 per application of Attachment B, including identification of the first calendar year in which any criterion in Attachment B applies. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2014-01-01 |  | 2014-09-30 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
287 | 3766 |  | 2. | RP-2021-06-09-0000003 | PRC-023-2 R6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2014-01-01 |  | 2014-09-30 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
288 | 3780 |  | 1. | 3787 | TOP-002-2b R14.1. | Changes in real output capabilities. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-10-20 |  | 2012-09-12 |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
288 | 3780 |  | 2. | 3786 | TOP-002-2b R14.2. | Automatic Voltage Regulator status and mode setting. (Retired August 1, 2007) |  | GOP | [5 empty] | GOP | [16 empty] | 2011-10-20 |  | 2012-09-12 |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
288 | 3782 |  | 1. | 3789 | TOP-002-2b R16.1. | Changes in transmission facility status. |  | TOP | [18 empty] | TOP |  |  |  | 2011-10-20 |  | 2012-09-12 |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
288 | 3782 |  | 2. | 3788 | TOP-002-2b R16.2. | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP |  |  |  | 2011-10-20 |  | 2012-09-12 |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
289 | 3793 |  | 1. | 3811 | IRO-005-3 R1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
289 | 3793 |  | 10. | 3809 | IRO-005-3 R1.10. | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
289 | 3793 |  | 2. | 3808 | IRO-005-3 R1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
289 | 3793 |  | 3. | 3807 | IRO-005-3 R1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
289 | 3793 |  | 4. | 3810 | IRO-005-3 R1.4. | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
289 | 3793 |  | 5. | 3806 | IRO-005-3 R1.5. | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
289 | 3793 |  | 6. | 3805 | IRO-005-3 R1.6. | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
289 | 3793 |  | 7. | 3804 | IRO-005-3 R1.7. | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
289 | 3793 |  | 8. | 3803 | IRO-005-3 R1.8. | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
289 | 3793 |  | 9. | 3802 | IRO-005-3 R1.9. | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 384 |  | 1. | 385 | CIP-007-1 R1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-04-07 |  | 2010-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 384 |  | 2. | 386 | CIP-007-1 R1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 384 |  | 3. | 387 | CIP-007-1 R1.3. | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 388 |  | 1. | 389 | CIP-007-1 R2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 388 |  | 2. | 390 | CIP-007-1 R2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 388 |  | 3. | 391 | CIP-007-1 R2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure or an acceptance of risk. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 392 |  | 1. | 393 | CIP-007-1 R3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 392 |  | 2. | 394 | CIP-007-1 R3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure or an acceptance of risk. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 395 |  | 1. | 396 | CIP-007-1 R4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure or an acceptance of risk. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 395 |  | 2. | 397 | CIP-007-1 R4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 398 | 399 | 1. | 400 | CIP-007-1 R5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 398 | 399 | 2. | 401 | CIP-007-1 R5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 398 | 399 | 3. | 402 | CIP-007-1 R5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003 Requirement R5 and Standard CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 398 | 403 | 1. | 404 | CIP-007-1 R5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 521000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 398 | 403 | 2. | 405 | CIP-007-1 R5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 522000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 398 | 403 | 3. | 406 | CIP-007-1 R5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 523000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 398 | 407 | 1. | 408 | CIP-007-1 R5.3.1. | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 531000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 398 | 407 | 2. | 409 | CIP-007-1 R5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 532000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 398 | 407 | 3. | 410 | CIP-007-1 R5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 533000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 398 |  | 1. | 399 | CIP-007-1 R5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 398 |  | 2. | 403 | CIP-007-1 R5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 398 |  | 3. | 407 | CIP-007-1 R5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 411 |  | 1. | 412 | CIP-007-1 R6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 411 |  | 2. | 413 | CIP-007-1 R6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 411 |  | 3. | 414 | CIP-007-1 R6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 411 |  | 4. | 415 | CIP-007-1 R6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 411 |  | 5. | 416 | CIP-007-1 R6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 417 |  | 1. | 418 | CIP-007-1 R7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 417 |  | 2. | 419 | CIP-007-1 R7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 417 |  | 3. | 420 | CIP-007-1 R7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 421 |  | 1. | 422 | CIP-007-1 R8.1. | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 421 |  | 2. | 423 | CIP-007-1 R8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 421 |  | 3. | 424 | CIP-007-1 R8.3. | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
29 | 421 |  | 4. | 425 | CIP-007-1 R8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | 840000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
290 | 3818 |  | 1. | 3822 | TOP-001-1a R7.1. | For a generator outage, the Generator Operator shall notify and coordinate with the Transmission Operator. The Transmission Operator shall notify the Reliability Coordinator and other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-11-21 |  | 2017-03-31 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
290 | 3818 |  | 2. | 3820 | TOP-001-1a R7.2. | For a transmission facility, the Transmission Operator shall notify and coordinate with its Reliability Coordinator. The Transmission Operator shall notify other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  | TOP | [18 empty] | TOP |  |  |  | 2011-11-21 |  | 2017-03-31 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
290 | 3818 |  | 3. | RP-2021-06-24-0000028 | TOP-001-1a R7.3. | When time does not permit such notifications and coordination, or when immediate action is required to prevent a hazard to the public, lengthy customer service interruption, or damage to facilities, the Generator Operator shall notify the Transmission Operator, and the Transmission Operator shall notify its Reliability Coordinator and adjacent Transmission Operators, at the earliest possible time. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-11-21 |  | 2017-03-31 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
292 | 3828 |  | 1. | 3836 | EOP-001-0b R3.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
292 | 3828 |  | 2. | 3834 | EOP-001-0b R3.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
292 | 3828 |  | 3. | 3835 | EOP-001-0b R3.3. | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
292 | 3828 |  | 4. | 3833 | EOP-001-0b R3.4. | Develop, maintain, and implement a set of plans for system restoration. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
292 | 3830 |  | 1. | 3840 | EOP-001-0b R4.1. | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
292 | 3830 |  | 2. | 3837 | EOP-001-0b R4.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
292 | 3830 |  | 3. | 3838 | EOP-001-0b R4.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
292 | 3830 |  | 4. | 3839 | EOP-001-0b R4.4. | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
292 | 3829 |  | 1. | 3841 | EOP-001-0b R7.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
292 | 3829 |  | 2. | 3842 | EOP-001-0b R7.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
292 | 3829 |  | 3. | 3843 | EOP-001-0b R7.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
292 | 3829 |  | 4. | 3844 | EOP-001-0b R7.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
293 | 3847 |  | 1. | 3852 | EOP-001-2b R2.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
293 | 3847 |  | 2. | 3851 | EOP-001-2b R2.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
293 | 3847 |  | 3. | 3853 | EOP-001-2b R2.3. | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
293 | 3848 |  | 1. | 3857 | EOP-001-2b R3.1. | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
293 | 3848 |  | 2. | 3854 | EOP-001-2b R3.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
293 | 3848 |  | 3. | 3855 | EOP-001-2b R3.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
293 | 3848 |  | 4. | 3856 | EOP-001-2b R3.4. | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
293 | 3845 |  | 1. | 3858 | EOP-001-2b R6.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
293 | 3845 |  | 2. | 3859 | EOP-001-2b R6.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
293 | 3845 |  | 3. | 3860 | EOP-001-2b R6.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
293 | 3845 |  | 4. | 3861 | EOP-001-2b R6.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
297 | 3874 |  | 1. | 7054 | IRO-014-2 R1.1. | Communications and notifications, including the mutually agreed to conditions under which one Reliability Coordinator notifies other Reliability Coordinators; the process to follow in making those notifications; and the data and information to be exchanged with other Reliability Coordinators. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
297 | 3874 |  | 2. | 7055 | IRO-014-2 R1.2. | Energy and capacity shortages. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
297 | 3874 |  | 3. | 7056 | IRO-014-2 R1.3. | Planned or unplanned outage information. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
297 | 3874 |  | 4. | 7057 | IRO-014-2 R1.4. | Control of voltage, including the coordination of reactive resources. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
297 | 3874 |  | 5. | 7058 | IRO-014-2 R1.5. | Coordination of information exchange to support reliability assessments. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
297 | 3874 |  | 6. | 7059 | IRO-014-2 R1.6. | Authority to act to prevent and mitigate system conditions which could cause Adverse Reliability Impacts to other Reliability Coordinator Areas. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
297 | 3874 |  | 7. | 7060 | IRO-014-2 R1.7. | Weekly conference calls |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
297 | 3875 |  | 1. | 7061 | IRO-014-2 R2.1. | Review and update annually with no more that 15 months between reviews. |  | RC | [11 empty] | RC | [9 empty] | 2.1 Reviewed and updated annually with no more than 15 months between reviews. |  |  | 2016-01-26 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
297 | 3875 |  | 2. | 7062 | IRO-014-2 R2.2. | Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. |  | RC | [11 empty] | RC | [9 empty] | 2.2 Agreed to, in writing, by all the Reliability Coordinators required to take the indicated action(s). |  |  | 2016-01-26 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
297 | 3875 |  | 3. | 7063 | IRO-014-2 R2.3. | Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. |  | RC | [11 empty] | RC | [9 empty] | 2.3 Distributed within 30 days of an update to all Reliability Coordinators that are required to take the indicated action(s). This evidence may include, but is not limited to dated documentation with confirmation of receipt, dated notice of acceptance or agreement to take specified actions, or dated electronic communications with confirmation of receipt and acceptance or agreement to take specified actions. (R2) |  |  | 2016-01-26 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
299 | 3892 |  | 1. | 3902 | CIP-006-2a R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
299 | 3892 |  | 2. | 3903 | CIP-006-2a R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
299 | 3892 |  | 3. | 3904 | CIP-006-2a R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
299 | 3892 |  | 4. | 3901 | CIP-006-2a R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
299 | 3892 |  | 5. | 3900 | CIP-006-2a R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
299 | 3892 |  | 6. | 3898 | CIP-006-2a R1.6. | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
299 | 3892 |  | 7. | RP-2021-06-15-0000013 | CIP-006-2a R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
299 | 3892 |  | 8. | 3899 | CIP-006-2a R1.8. | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
299 | 3894 |  | 1. | 3907 | CIP-006-2a R2.1. | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
299 | 3894 |  | 2. | 3906 | CIP-006-2a R2.2. | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
299 | 3895 |  | 1. | 3908 | CIP-006-2a R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
299 | 3895 |  | 2. | 3909 | CIP-006-2a R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
299 | 3895 |  | 3. | 3910 | CIP-006-2a R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
30 | 427 |  | 1. | 428 | CIP-008-1 R1.1. | Procedures to characterize and classify events as reportable Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
30 | 427 |  | 2. | 429 | CIP-008-1 R1.2. | Response actions, including roles and responsibilities of incident response teams, incident handling procedures, and communication plans. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
30 | 427 |  | 3. | 430 | CIP-008-1 R1.3. | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES ISAC either directly or through an intermediary. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
30 | 427 |  | 4. | 431 | CIP-008-1 R1.4. | Process for updating the Cyber Security Incident response plan within ninety calendar days of any changes. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
30 | 427 |  | 5. | 432 | CIP-008-1 R1.5. | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
30 | 427 |  | 6. | 433 | CIP-008-1 R1.6. | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
300 | 3913 | 3922 | 1. | 3927 | CIP-006-3a R1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-05-18 |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
300 | 3913 | 3922 | 2. | 3928 | CIP-006-3a R1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-05-18 |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
300 | 3913 |  | 1. | 3923 | CIP-006-3a R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
300 | 3913 |  | 2. | 3924 | CIP-006-3a R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
300 | 3913 |  | 3. | 3925 | CIP-006-3a R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
300 | 3913 |  | 4. | 3926 | CIP-006-3a R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
300 | 3913 |  | 5. | 3919 | CIP-006-3a R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
300 | 3913 |  | 6. | 3922 | CIP-006-3a R1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
300 | 3913 |  | 7. | RP-2021-06-15-0000017 | CIP-006-3a R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-05-18 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
300 | 3913 |  | 8. | 3921 | CIP-006-3a R1.8. | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
300 | 3918 |  | 1. | 3929 | CIP-006-3a R2.1. | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
300 | 3918 |  | 2. | 3930 | CIP-006-3a R2.2. | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
300 | 3912 |  | 1. | 3931 | CIP-006-3a R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
300 | 3912 |  | 2. | 3932 | CIP-006-3a R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
300 | 3912 |  | 3. | 3933 | CIP-006-3a R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
302 | 3939 |  | 1. | RP-2021-06-15-0000037 | FAC-003-2 R3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; |  | TO | [17 empty] | TO |  |  |  |  | 2014-07-01 |  | 2013-11-25 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
302 | 3939 |  | 2. | RP-2021-06-15-0000038 | FAC-003-2 R3.2. | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. |  | TO | [17 empty] | TO |  |  |  |  | 2014-07-01 |  | 2013-11-25 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
305 | 3948 |  | 1. | 6600 | PRC-006-SERC-01 R1.1. | A Planning Coordinator may adjust island boundaries to differ from subregional boundaries where necessary for the sole purpose of producing a contiguous subregional island more suitable for simulation. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  | 110000000 | SERC-US |  |  |  | SERC-US
305 | 3949 | 6603 | 1. | 6605 | PRC-006-SERC-01 R2.3.1. | This does not apply to UFLS relays with time delay of one second or longer and a higher frequency setpoint applied to prevent the frequency from stalling at less than 60 Hz when recovering from an underfrequency event. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2014-04-01 |  | 2017-12-31 |  |  | 231000000 | SERC-US |  |  |  | SERC-US
305 | 3949 |  | 1. | 6601 | PRC-006-SERC-01 R2.1. | Have the capability of shedding at least 30 percent of the Peak Demand (MW) served from the Planning Coordinator’s transmission system. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  | 210000000 | SERC-US |  |  |  | SERC-US
305 | 3949 |  | 2. | 6602 | PRC-006-SERC-01 R2.2. | Shed load with a minimum of three frequency set points. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  | 220000000 | SERC-US |  |  |  | SERC-US
305 | 3949 |  | 3. | 6603 | PRC-006-SERC-01 R2.3. | The highest frequency set point for relays used to arrest frequency decline shall be no lower than 59.3 Hz and not higher than 59.5 Hz. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  | 230000000 | SERC-US |  |  |  | SERC-US
305 | 3949 |  | 4. | 6606 | PRC-006-SERC-01 R2.4. | The lowest frequency set point shall be no lower than 58.4 Hz. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  | 240000000 | SERC-US |  |  |  | SERC-US
305 | 3949 |  | 5. | 6607 | PRC-006-SERC-01 R2.5. | The difference between frequency set points shall be at least 0.2 Hz but no greater than 0.5 Hz. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  | 250000000 | SERC-US |  |  |  | SERC-US
305 | 3949 |  | 6. | RP-2021-06-24-0000018 | PRC-006-SERC-01 R2.6. | Time delay (from frequency reaching the set point to the trip signal) shall be at least six cycles. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2014-04-01 |  | 2017-12-31 |  |  | 260000000 | SERC-US |  |  |  | SERC-US
305 | 3951 |  | 1. | 6609 | PRC-006-SERC-01 R4.1. | The percent of load shedding to be implemented shall be based on the actual or estimated distribution substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year actual Peak Demand. |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  |  | 2015-10-01 |  | 2017-12-31 |  |  | 410000000 | SERC-US |  |  |  | SERC-US
305 | 3951 |  | 2. | 6610 | PRC-006-SERC-01 R4.2. | The amount of load in each load shedding step shall be within -1.0 and +3.0 of the percentage specified by the Planning Coordinator (for example, if the specified percentage step load shed is 12%, the allowable range is 11 to 15%). |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  |  | 2015-10-01 |  | 2017-12-31 |  |  | 420000000 | SERC-US |  |  |  | SERC-US
305 | 3951 |  | 3. | 6611 | PRC-006-SERC-01 R4.3. | The amount of total UFLS load of all steps combined shall be within -1.0 and +5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  |  | 2015-10-01 |  | 2017-12-31 |  |  | 430000000 | SERC-US |  |  |  | SERC-US
305 | 3952 |  | 1. | 6612 | PRC-006-SERC-01 R5.1. | The percent of load shedding to be implemented shall be based on the actual or estimated distribution substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year actual Peak Demand. |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  |  | 2015-10-01 |  | 2017-12-31 |  |  | 510000000 | SERC-US |  |  |  | SERC-US
305 | 3952 |  | 2. | 6613 | PRC-006-SERC-01 R5.2. | The amount of total UFLS load shall be within ± 5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  |  | 2015-10-01 |  | 2017-12-31 |  |  | 520000000 | SERC-US |  |  |  | SERC-US
305 | 3954 |  | 1. | RP-2021-06-24-0000020 | PRC-006-SERC-01 R7.1. | Underfrequency trip set points (Hz) |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2014-04-01 |  | 2017-12-31 |  |  | 710000000 | SERC-US |  |  |  | SERC-US
305 | 3954 |  | 2. | RP-2021-06-24-0000021 | PRC-006-SERC-01 R7.2. | Total clearing time associated with each set point (sec). This includes the time from when frequency reaches the set point and ends when the breaker opens. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2014-04-01 |  | 2017-12-31 |  |  | 720000000 | SERC-US |  |  |  | SERC-US
305 | 3954 |  | 3. | 6616 | PRC-006-SERC-01 R7.3. | Amount of previous year actual or estimated load associated with each set point, both in percent and in MW. The percentage and the Load demand (MW) shall be based on the time coincident with the previous year actual Peak Demand. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  | 730000000 | SERC-US |  |  |  | SERC-US
305 | 3955 |  | 1. | 6619 | PRC-006-SERC-01 R8.1. | Generator protection automatic underfrequency and overfrequency trip set points (Hz). |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [17 empty] | 2013-02-25 |  | 2017-12-31 |  |  | 810000000 | SERC-US |  |  |  | SERC-US
305 | 3955 |  | 2. | RP-2021-06-24-0000022 | PRC-006-SERC-01 R8.2. | Total clearing time associated with each set point (sec). This is defined as the time that begins when frequency reaches the set point and ends when the breaker opens. If inverse time underfrequency relays are used, provide the total clearing time at 59.0, 58.5, 58.0, and 57.0 Hz. |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [17 empty] | 2014-04-01 |  | 2017-12-31 |  |  | 820000000 | SERC-US |  |  |  | SERC-US
305 | 3955 |  | 3. | 6621 | PRC-006-SERC-01 R8.3. | Maximum generator net MW that could be tripped automatically due to an underfrequency or overfrequency condition. |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [17 empty] | 2013-02-25 |  | 2017-12-31 |  |  | 830000000 | SERC-US |  |  |  | SERC-US
306 | 3956 |  | 1. | RP-2021-06-21-0000004 | FAC-001-1 R1.1. | Generation Facilities, |  | TO | [17 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3956 |  | 2. | RP-2021-06-21-0000005 | FAC-001-1 R1.2. | Transmission Facilities, and |  | TO | [17 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3956 |  | 3. | RP-2021-06-21-0000006 | FAC-001-1 R1.3. | End-user Facilities |  | TO | [17 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1. | RP-2021-06-21-0000007 | FAC-001-1 R3.1. | Provide a written summary of its plans to achieve the required system performance as described in Requirements R1 or R2 throughout the planning horizon: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.1. | RP-2021-06-21-0000008 | FAC-001-1 R3.1.1. | Procedures for coordinated joint studies of new Facilities and their impacts on the interconnected Transmission systems. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.10. | RP-2021-06-21-0000017 | FAC-001-1 R3.1.10. | Power quality impacts. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.11. | RP-2021-06-21-0000018 | FAC-001-1 R3.1.11. | Equipment Ratings. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 311100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.12. | RP-2021-06-21-0000019 | FAC-001-1 R3.1.12. | Synchronizing of Facilities. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 311200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.13. | RP-2021-06-21-0000020 | FAC-001-1 R3.1.13. | Maintenance coordination. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 311300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.14. | RP-2021-06-21-0000021 | FAC-001-1 R3.1.14. | Operational issues (abnormal frequency and voltages). |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 311400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.15. | RP-2021-06-21-0000022 | FAC-001-1 R3.1.15. | Inspection requirements for existing or new Facilities. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 311500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.16. | RP-2021-06-21-0000023 | FAC-001-1 R3.1.16. | Communications and procedures during normal and emergency operating conditions. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 311600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.2. | RP-2021-06-21-0000009 | FAC-001-1 R3.1.2. | Procedures for notification of new or modified Facilities to others (those responsible for the reliability of the interconnected Transmission systems) as soon as feasible. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.3. | RP-2021-06-21-0000010 | FAC-001-1 R3.1.3. | Voltage level and MW and MVAR capacity or demand at point of connection. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.4. | RP-2021-06-21-0000011 | FAC-001-1 R3.1.4. | Breaker duty and surge protection. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 314000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.5. | RP-2021-06-21-0000012 | FAC-001-1 R3.1.5. | System protection and coordination. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 315000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.6. | RP-2021-06-21-0000013 | FAC-001-1 R3.1.6. | Metering and telecommunications. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 316000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.7. | RP-2021-06-21-0000014 | FAC-001-1 R3.1.7. | Grounding and safety issues. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 317000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.8. | RP-2021-06-21-0000015 | FAC-001-1 R3.1.8. | Insulation and insulation coordination. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 318000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
306 | 3958 |  | 1.9. | RP-2021-06-21-0000016 | FAC-001-1 R3.1.9. | Voltage, Reactive Power, and power factor control. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2015-12-31 |  |  | 319000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3960 | 3965 | 1. | 3966 | MOD-028-2 R1.5.1. | Define if the source used for Available Transfer Capability (ATC) calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | 2013-10-01 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3960 | 3965 | 2. | 3967 | MOD-028-2 R1.5.2. | Define if the sink used for ATC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | 2013-10-01 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3960 | 3965 | 3. | 3968 | MOD-028-2 R1.5.3. | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  | 2013-10-01 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 153000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3960 | 3965 | 4. | 3969 | MOD-028-2 R1.5.4. | If the Transmission Service Provider’s ATC calculation process involves a grouping of generation, the ATCID must identify how these generators participate in the group. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | 2013-10-01 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 154000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3960 |  | 1. | 3961 | MOD-028-2 R1.1. | Information describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Operator, the results of the TTC calculations can be validated. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3960 |  | 2. | 3962 | MOD-028-2 R1.2. | A description of the manner in which the Transmission Operator will account for Interchange Schedules in the calculation of TTC. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3960 |  | 3. | 3963 | MOD-028-2 R1.3. | Any contractual obligations for allocation of TTC. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3960 |  | 4. | 3964 | MOD-028-2 R1.4. | A description of the manner in which Contingencies are identified for use in the TTC process. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3960 |  | 5. | 3965 | MOD-028-2 R1.5. | The following information on how source and sink for transmission service is accounted for in ATC calculations including: |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall provide its current ATCID that has the information described in R1 to show compliance with R1. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3972 |  | 1. | 3973 | MOD-028-2 R2.1. | Modeling data and topology of its Reliability Coordinator’s area of responsibility. Equivalent representation of radial lines and facilities 161 kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall provide evidence including the model used to calculate TTC as well as other evidence (such as Facility Ratings provided by facility owners, written documentation, logs, and data) to show that the modeling requirements in R2 were met. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3972 |  | 2. | 3974 | MOD-028-2 R2.2. | Modeling data and topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination areas. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall provide evidence including the model used to calculate TTC as well as other evidence (such as Facility Ratings provided by facility owners, written documentation, logs, and data) to show that the modeling requirements in R2 were met. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3972 |  | 3. | 3975 | MOD-028-2 R2.3. | Facility Ratings specified by the Generator Owners and Transmission Owners. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall provide evidence including the model used to calculate TTC as well as other evidence (such as Facility Ratings provided by facility owners, written documentation, logs, and data) to show that the modeling requirements in R2 were met. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3976 | 3977 | 1. | 3978 | MOD-028-2 R3.1.1. | Expected generation and Transmission outages, additions, and retirements, included as specified in the ATCID. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall provide evidence, including scheduled outages, facility additions and retirements, (such as written documentation, logs, and data) that the data described in R3 and R4 were included in the determination of TTC as specified in the ATCID. | 2013-10-01 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3976 | 3977 | 2. | 3979 | MOD-028-2 R3.1.2. | A daily or hourly load forecast for TTCs used in current-day and next-day ATC calculations. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall provide evidence, including scheduled outages, facility additions and retirements, (such as written documentation, logs, and data) that the data described in R3 and R4 were included in the determination of TTC as specified in the ATCID. | 2013-10-01 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3976 | 3977 | 3. | 3980 | MOD-028-2 R3.1.3. | A daily load forecast for TTCs used in ATC calculations for days two through 31. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall provide evidence, including scheduled outages, facility additions and retirements, (such as written documentation, logs, and data) that the data described in R3 and R4 were included in the determination of TTC as specified in the ATCID. | 2013-10-01 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3976 | 3977 | 4. | 3981 | MOD-028-2 R3.1.4. | A monthly load forecast for TTCs used in ATC calculations for months two through 13 months TTCs. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall provide evidence, including scheduled outages, facility additions and retirements, (such as written documentation, logs, and data) that the data described in R3 and R4 were included in the determination of TTC as specified in the ATCID. | 2013-10-01 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 314000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3976 | 3977 | 5. | 3982 | MOD-028-2 R3.1.5. | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. |  | TOP | [18 empty] | TOP |  |  |  | 2013-10-01 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 315000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3976 |  | 1. | 3977 | MOD-028-2 R3.1. | For TTCs, use the following (as well as any other values and additional parameters as specified in the ATCID): |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall provide evidence, including scheduled outages, facility additions and retirements, (such as written documentation, logs, and data) that the data described in R3 and R4 were included in the determination of TTC as specified in the ATCID. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3983 |  | 1. | 3984 | MOD-028-2 R4.1. | Use all Contingencies meeting the criteria described in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3983 |  | 2. | 3985 | MOD-028-2 R4.2. | Respect any contractual allocations of TTC. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall provide the contingencies used in determining TTC and the ATCID as evidence to show that the contingencies described in the ATCID were included in the determination of TTC. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3983 |  | 3. | 3986 | MOD-028-2 R4.3. | Include, for each time period, the Firm Transmission Service expected to be scheduled as specified in the ATCID (filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers) for the Transmission Service Provider, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed modeling the source and sink as follows: - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point shall as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can not be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is to be delivered as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is being delivered as the sink. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall provide the contingencies used in determining TTC and the ATCID as evidence to show that the contingencies described in the ATCID were included in the determination of TTC. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3987 |  | 1. | 3988 | MOD-028-2 R5.1. | At least once within the seven calendar days prior to the specified period for TTCs used in hourly and daily ATC calculations. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall provide copies of contracts that contain requirements to allocate TTCs and TTC values to show that any contractual allocations of TTC were respected as required in R4.2. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3987 |  | 2. | 3989 | MOD-028-2 R5.2. | At least once per calendar month for TTCs used in monthly ATC calculations. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall provide copies of contracts that contain requirements to allocate TTCs and TTC values to show that any contractual allocations of TTC were respected as required in R4.2. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3987 |  | 3. | 3990 | MOD-028-2 R5.3. | Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3991 |  | 1. | 3992 | MOD-028-2 R6.1. | Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either: - A System Operating Limit is reached on the Transmission Service Provider’s system, or - A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater . Footnote: The Transmission operator may honor distribution factors less than 5% if desired. |  | TOP | [18 empty] | TOP |  |  | M6. Each Transmission Operator shall provide evidence (such as copies of coordination agreements, reservations, interchange transactions, or other documentation) to show that firm reservations were used to estimate scheduled interchange, the modeling of scheduled interchange was based on the rules described in R4.3, and that estimated scheduled interchange was included in the determination of TTC. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3991 |  | 2. | 3993 | MOD-028-2 R6.2. | If the limit in step R6.1 can not be reached by adjusting any combination of load or generation, then set the incremental Transfer Capability by the results of the case where the maximum adjustments were applied. |  | TOP | [18 empty] | TOP |  |  | M6. Each Transmission Operator shall provide evidence (such as copies of coordination agreements, reservations, interchange transactions, or other documentation) to show that firm reservations were used to estimate scheduled interchange, the modeling of scheduled interchange was based on the rules described in R4.3, and that estimated scheduled interchange was included in the determination of TTC. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3991 |  | 3. | 3994 | MOD-028-2 R6.3. | Use (as the TTC) the lesser of: - The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or - The sum of Facility Ratings of all ties comprising the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3991 |  | 4. | 3995 | MOD-028-2 R6.4. | For ATC Paths whose capacity uses jointly-owned or allocated Facilities, limit TTC for each Transmission Service Provider so the TTC does not exceed each Transmission Service Provider’s contractual rights. |  | TOP | [18 empty] | TOP |  |  | M6. Each Transmission Operator shall provide evidence (such as copies of coordination agreements, reservations, interchange transactions, or other documentation) to show that firm reservations were used to estimate scheduled interchange, the modeling of scheduled interchange was based on the rules described in R4.3, and that estimated scheduled interchange was included in the determination of TTC. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3996 |  | 1. | 3997 | MOD-028-2 R7.1. | One calendar day after its determination for TTCs used in hourly and daily ATC calculations. |  | TOP | [18 empty] | TOP |  |  | M7. Each Transmission Operator shall provide evidence (such as logs and data and dated copies of requests from the Transmission Service Provider to establish TTCs at specific intervals) that TTCs have been established at least once in the calendar week prior to the specified period for TTCs used in hourly and daily ATC calculations, at least once per calendar month for TTCs used in monthly ATC calculations, and within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a autotransformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage; provided such outage is expected to last 24 hours or longer in duration per the specifications in R5. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
307 | 3996 |  | 2. | 3998 | MOD-028-2 R7.2. | Seven calendar days after its determination for TTCs used in monthly ATC calculations. |  | TOP | [18 empty] | TOP |  |  | M7. Each Transmission Operator shall provide evidence (such as logs and data and dated copies of requests from the Transmission Service Provider to establish TTCs at specific intervals) that TTCs have been established at least once in the calendar week prior to the specified period for TTCs used in hourly and daily ATC calculations, at least once per calendar month for TTCs used in monthly ATC calculations, and within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a autotransformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage; provided such outage is expected to last 24 hours or longer in duration per the specifications in R5. | 2013-09-27 |  | 2024-02-01 |  | 4. Applicability: 4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
309 | 4022 |  | 1. | 6525 | PRC-006-NPCC-1 R5.1. | Inform its Planning Coordinator of the need to exceed the stated tolerances or the number of stages as shown in UFLS Attachment C, Table 1 if applicable and |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  |  | 2016-01-01 |  | 2020-03-31 |  |  | 510000000 | NPCC-US |  | NPCC-US
309 | 4022 |  | 2. | 6526 | PRC-006-NPCC-1 R5.2. | Provide its Planning Coordinator with a technical study that demonstrates that the Distribution Providers or Transmission Owners specific deviations from the requirements of UFLS Attachment C, Table 1 will not have a significant adverse impact on the bulk power system. |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  |  | 2016-01-01 |  | 2020-03-31 |  |  | 520000000 | NPCC-US |  | NPCC-US
309 | 4022 |  | 3. | 6527 | PRC-006-NPCC-1 R5.3. | Inform its Planning Coordinator of the need to exceed the stated tolerances of UFLS Attachment C, Table 2 or Table 3, and in the case of Attachment C, Table 2 only, the need to deviate from providing two stages of UFLS, if applicable, and |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  |  | 2020-03-31 |  | 2020-03-31 |  |  | 530000000 | NPCC-US |  | NPCC-US
309 | 4022 |  | 4. | 6528 | PRC-006-NPCC-1 R5.4. | Provide its Planning Coordinator with an analysis demonstrating that no alternative load shedding solution is available that would allow the Distribution Provider or Transmission Owner to comply with UFLS Attachment C Table 2 or Attachment C Table 3. |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  |  | 2016-01-01 |  | 2020-03-31 |  |  | 540000000 | NPCC-US |  | NPCC-US
309 | 4024 |  | 1. | 6529 | PRC-006-NPCC-1 R7.1. | Eastern Interconnection – 100 ms |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  |  | 2016-01-01 |  | 2020-03-31 |  |  | 710000000 | NPCC-US |  | NPCC-US
309 | 4024 |  | 2. | 6542 | PRC-006-NPCC-1 R7.2. | Québec Interconnection – 200 ms |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  |  | 2016-01-01 |  | 2020-03-31 |  |  | 720000000 | NPCC-US |  | NPCC-US
309 | 4010 |  | 1. | 6530 | PRC-006-NPCC-1 R15.1. | Design measures to prevent the generating unit from tripping directly or indirectly for underfrequency conditions above the appropriate generator tripping threshold curve in Figure 1. |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [17 empty] | 2013-04-29 |  | 2020-03-31 |  |  | 151000000 | NPCC-US |  | NPCC-US
309 | 4010 |  | 2. | 6533 | PRC-006-NPCC-1 R15.2. | Design auxiliary system(s) or devices used for the control and protection of auxiliary system(s), necessary for the generating unit operation such that they will not trip the generating unit during underfrequency conditions above the appropriate generator underfrequency trip protection settings threshold curve in Figure 1. |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [17 empty] | 2013-04-29 |  | 2020-03-31 |  |  | 152000000 | NPCC-US |  | NPCC-US
309 | 4011 |  | 1. | 6531 | PRC-006-NPCC-1 R16.1. | Set the underfrequency protection to operate at the lowest frequency allowed by the plant design and licensing limitations. |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [17 empty] | 2013-04-29 |  | 2020-03-31 |  |  | 161000000 | NPCC-US |  | NPCC-US
309 | 4011 |  | 2. | RP-2021-06-24-0000016 | PRC-006-NPCC-1 R16.2. | Transmit the existing underfrequency settings and any changes to the underfrequency settings along with the technical basis for the settings to the Planning Coordinator. |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [17 empty] | 2015-07-01 |  | 2020-03-31 |  |  | 162000000 | NPCC-US |  | NPCC-US
309 | 4011 |  | 3. | 6543 | PRC-006-NPCC-1 R16.3. | Have compensatory load shedding, as provided by a Distribution Provider or Transmission Owner that is adequate to compensate for the loss of their generator due to early tripping. |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [17 empty] | 2013-04-29 |  | 2020-03-31 |  |  | 163000000 | NPCC-US |  | NPCC-US
309 | 4014 |  | 1. | 6534 | PRC-006-NPCC-1 R19.1. | Set the underfrequency protection to operate at as low a frequency as possible in accordance with the plant design and licensing limitations but not greater than 57.8Hz. |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [17 empty] | 2013-04-29 |  | 2020-03-31 |  |  | 191000000 | NPCC-US |  | NPCC-US
309 | 4014 |  | 2. | 6535 | PRC-006-NPCC-1 R19.2. | Set the frequency trip setting upper tolerance to no greater than + 0.1 Hz. |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [17 empty] | 2013-04-29 |  | 2020-03-31 |  |  | 192000000 | NPCC-US |  | NPCC-US
309 | 4014 |  | 3. | RP-2021-06-24-0000017 | PRC-006-NPCC-1 R19.3. | Transmit the initial frequency trip setting and any changes to the setting and the technical basis for the settings to the Planning Coordinator. |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [17 empty] | 2015-07-01 |  | 2020-03-31 |  |  | 193000000 | NPCC-US |  | NPCC-US
309 | 4016 |  | 1. | 6537 | PRC-006-NPCC-1 R20.1. | For each UFLS relay, including those used for compensatory load shedding, the amount and location of load shed at peak, the corresponding frequency threshold and time delay settings. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2013-04-29 |  | 2020-03-31 |  |  | 201000000 | NPCC-US |  | NPCC-US
309 | 4016 |  | 2. | 6538 | PRC-006-NPCC-1 R20.2. | The buses at which the Load is modeled in the NPCC library power flow case. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2013-04-29 |  | 2020-03-31 |  |  | 202000000 | NPCC-US |  | NPCC-US
309 | 4016 |  | 3. | 6539 | PRC-006-NPCC-1 R20.3. | A list of all generating units that may be tripped for underfrequency conditions above the appropriate generator underfrequency trip protection settings threshold curve in Figure 1, including the frequency trip threshold and time delay for each protection system. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2013-04-29 |  | 2020-03-31 |  |  | 203000000 | NPCC-US |  | NPCC-US
309 | 4016 |  | 4. | 6540 | PRC-006-NPCC-1 R20.4. | The location and amount of additional elements to be switched for voltage control that are coordinated with UFLS program tripping. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2013-04-29 |  | 2020-03-31 |  |  | 204000000 | NPCC-US |  | NPCC-US
309 | 4016 |  | 5. | 6541 | PRC-006-NPCC-1 R20.5. | A list of all UFLS relay inhibit functions along with the corresponding settings and locations of these relays. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2013-04-29 |  | 2020-03-31 |  |  | 205000000 | NPCC-US |  | NPCC-US
31 | 435 |  | 1. | 436 | CIP-009-1 R1.1. | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
31 | 435 |  | 2. | 437 | CIP-009-1 R1.2. | Define the roles and responsibilities of responders. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
310 | 4029 | 4039 | 1. | 4049 | CIP-006-3d R1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
310 | 4029 | 4039 | 2. | 4048 | CIP-006-3d R1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
310 | 4029 |  | 1. | 4045 | CIP-006-3d R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
310 | 4029 |  | 2. | 4044 | CIP-006-3d R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
310 | 4029 |  | 3. | 4043 | CIP-006-3d R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
310 | 4029 |  | 4. | 4042 | CIP-006-3d R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
310 | 4029 |  | 5. | 4040 | CIP-006-3d R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
310 | 4029 |  | 6. | 4039 | CIP-006-3d R1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
310 | 4029 |  | 7. | RP-2021-06-15-0000018 | CIP-006-3d R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
310 | 4029 |  | 8. | 4038 | CIP-006-3d R1.8. | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
310 | 4034 |  | 1. | 4047 | CIP-006-3d R2.1. | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
310 | 4034 |  | 2. | 4046 | CIP-006-3d R2.2. | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
310 | 4028 |  | 1. | 4036 | CIP-006-3d R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
310 | 4028 |  | 2. | 4035 | CIP-006-3d R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
310 | 4028 |  | 3. | 4037 | CIP-006-3d R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
311 | 4052 | 4061 | 1. | 4066 | CIP-006-4d R1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
311 | 4052 | 4061 | 2. | 4067 | CIP-006-4d R1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
311 | 4052 |  | 1. | 4062 | CIP-006-4d R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
311 | 4052 |  | 2. | 4063 | CIP-006-4d R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
311 | 4052 |  | 3. | 4064 | CIP-006-4d R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
311 | 4052 |  | 4. | 4065 | CIP-006-4d R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
311 | 4052 |  | 5. | 4058 | CIP-006-4d R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-4 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
311 | 4052 |  | 6. | 4061 | CIP-006-4d R1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
311 | 4052 |  | 7. | RP-2021-06-15-0000020 | CIP-006-4d R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
311 | 4052 |  | 8. | 4060 | CIP-006-4d R1.8. | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
311 | 4057 |  | 1. | 4068 | CIP-006-4d R2.1. | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
311 | 4057 |  | 2. | 4069 | CIP-006-4d R2.2. | Be afforded the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP-009-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
311 | 4051 |  | 1. | 4070 | CIP-006-4d R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
311 | 4051 |  | 2. | 4071 | CIP-006-4d R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
311 | 4051 |  | 3. | 4072 | CIP-006-4d R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
312 | 4073 |  | 1. | 4075 | COM-002-2a R1.1. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators through predetermined communication paths of any condition that could threaten the reliability of its area or when firm load shedding is anticipated. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
313 | 4076 |  | 1. | 4078 | PRC-005-1b R1.1. | Maintenance and testing intervals and their basis. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  |  | 2012-03-14 |  | 2013-11-24 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
313 | 4076 |  | 2. | 4079 | PRC-005-1b R1.2. | Summary of maintenance and testing procedures. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  |  | 2012-03-14 |  | 2013-11-24 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
313 | 4077 |  | 1. | 4080 | PRC-005-1b R2.1. | Evidence Protection System devices were maintained and tested within the defined intervals. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  |  | 2012-03-14 |  | 2013-11-24 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
313 | 4077 |  | 2. | 4081 | PRC-005-1b R2.2. | Date each Protection System device was last tested/maintained. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  |  | 2012-03-14 |  | 2013-11-24 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
314 | 4084 |  | 1. | 4092 | EOP-001-2.1b R2.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
314 | 4084 |  | 2. | 4094 | EOP-001-2.1b R2.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
314 | 4084 |  | 3. | 4093 | EOP-001-2.1b R2.3. | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
314 | 4085 |  | 1. | 4096 | EOP-001-2.1b R3.1. | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
314 | 4085 |  | 2. | 4095 | EOP-001-2.1b R3.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
314 | 4085 |  | 3. | 4097 | EOP-001-2.1b R3.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
314 | 4085 |  | 4. | 4098 | EOP-001-2.1b R3.4. | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
314 | 4082 |  | 1. | 4090 | EOP-001-2.1b R6.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
314 | 4082 |  | 2. | RP-2021-06-21-0000001 | EOP-001-2.1b R6.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2013-07-01 |  | 2017-03-31 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
314 | 4082 |  | 3. | RP-2021-06-21-0000002 | EOP-001-2.1b R6.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2013-07-01 |  | 2017-03-31 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
314 | 4082 |  | 4. | RP-2021-06-21-0000003 | EOP-001-2.1b R6.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2013-07-01 |  | 2017-03-31 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
315 | 4105 |  | 1. | 4118 | BAL-005-0.2b R1.1. | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
315 | 4105 |  | 2. | 4116 | BAL-005-0.2b R1.2. | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
315 | 4105 |  | 3. | 4117 | BAL-005-0.2b R1.3. | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
315 | 4109 |  | 1. | 4122 | BAL-005-0.2b R8.1. | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
315 | 4114 |  | 1. | 4123 | BAL-005-0.2b R9.1. | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
315 | 4111 |  | 1. | 4119 | BAL-005-0.2b R12.1. | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
315 | 4111 |  | 2. | 4120 | BAL-005-0.2b R12.2. | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
315 | 4111 |  | 3. | 4121 | BAL-005-0.2b R12.3. | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
317 | 4125 |  | 1. | 4133 | EOP-001-0.1b R3.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
317 | 4125 |  | 2. | 4135 | EOP-001-0.1b R3.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
317 | 4125 |  | 3. | 4132 | EOP-001-0.1b R3.3. | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
317 | 4125 |  | 4. | 4134 | EOP-001-0.1b R3.4. | Develop, maintain, and implement a set of plans for system restoration. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
317 | 4129 |  | 1. | 4142 | EOP-001-0.1b R4.1. | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
317 | 4129 |  | 2. | 4143 | EOP-001-0.1b R4.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
317 | 4129 |  | 3. | 4140 | EOP-001-0.1b R4.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
317 | 4129 |  | 4. | 4141 | EOP-001-0.1b R4.4. | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
317 | 4128 |  | 1. | 4136 | EOP-001-0.1b R7.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
317 | 4128 |  | 2. | 4139 | EOP-001-0.1b R7.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
317 | 4128 |  | 3. | 4138 | EOP-001-0.1b R7.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
317 | 4128 |  | 4. | 4137 | EOP-001-0.1b R7.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
318 | 4157 |  | 1. | 4163 | TOP-002-2.1b R14.1. | Changes in real output capabilities. |  | GOP | [5 empty] | GOP | [16 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
318 | 4159 |  | 1. | 4165 | TOP-002-2.1b R16.1. | Changes in transmission facility status. |  | TOP | [18 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
318 | 4159 |  | 2. | 4164 | TOP-002-2.1b R16.2. | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
319 | 4169 |  | 1. | 4187 | IRO-005-3.1a R1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
319 | 4169 |  | 10. | 4185 | IRO-005-3.1a R1.10. | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
319 | 4169 |  | 2. | 4184 | IRO-005-3.1a R1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
319 | 4169 |  | 3. | 4183 | IRO-005-3.1a R1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
319 | 4169 |  | 4. | 4186 | IRO-005-3.1a R1.4. | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
319 | 4169 |  | 5. | 4182 | IRO-005-3.1a R1.5. | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
319 | 4169 |  | 6. | 4181 | IRO-005-3.1a R1.6. | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
319 | 4169 |  | 7. | 4180 | IRO-005-3.1a R1.7. | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
319 | 4169 |  | 8. | 4179 | IRO-005-3.1a R1.8. | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
319 | 4169 |  | 9. | 4178 | IRO-005-3.1a R1.9. | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
32 | 442 |  | 1. | 443 | COM-001-1 R1.1. | Internally. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
32 | 442 |  | 2. | 444 | COM-001-1 R1.2. | Between the Reliability Coordinator and its Transmission Operators and Balancing Authorities. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
32 | 442 |  | 3. | RP-2021-06-15-0000026 | COM-001-1 R1.3. | With other Reliability Coordinators, Transmission Operators, and Balancing Authorities as necessary to maintain reliability. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
32 | 442 |  | 4. | RP-2021-06-15-0000027 | COM-001-1 R1.4. | Where applicable, these facilities shall be redundant and diversely routed. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-05-12 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
320 | 4193 |  | 1. | 4197 | EOP-002-3.1 R6.1. | Loading all available generating capacity. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
320 | 4193 |  | 2. | 4202 | EOP-002-3.1 R6.2. | Deploying all available operating reserve. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
320 | 4193 |  | 3. | 4198 | EOP-002-3.1 R6.3. | Interrupting interruptible load and exports. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
320 | 4193 |  | 4. | 4199 | EOP-002-3.1 R6.4. | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
320 | 4193 |  | 5. | 4201 | EOP-002-3.1 R6.5. | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
320 | 4193 |  | 6. | 4200 | EOP-002-3.1 R6.6. | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 660000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
320 | 4196 |  | 1. | 4204 | EOP-002-3.1 R7.1. | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
320 | 4196 |  | 2. | 4203 | EOP-002-3.1 R7.2. | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002 “Energy Emergency Alerts.” |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
320 | 4194 |  | 1. | 4205 | EOP-002-3.1 R9.1. | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002 “Energy Emergency Alerts.” |  | LSE | [7 empty] | LSE | [14 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
320 | 4194 |  | 2. | 4206 | EOP-002-3.1 R9.2. | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
320 | 4194 |  | 3. | 4207 | EOP-002-3.1 R9.3. | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 930000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
320 | 4194 |  | 4. | 4208 | EOP-002-3.1 R9.4. | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | 940000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4209 |  | 1. | 4218 | NUC-001-2.1 R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP | M4.1 The NPIRs have been incorporated into the current operating analysis of the electric system. (Requirement 4.1) | 2013-04-01 |  | 2015-12-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4209 |  | 2. | 4220 | NUC-001-2.1 R4.2. | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP | M4.2 The electric system was operated to meet the NPIRs. (Requirement 4.2) | 2013-04-01 |  | 2015-12-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4209 |  | 3. | 4219 | NUC-001-2.1 R4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP | M4.3 The Transmission Entity informed the Nuclear Plant Generator Operator when it became aware it lost the capability to assess the operation of the electric system affecting the NPIRs. (Requirement 4.3) | 2013-04-01 |  | 2015-12-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4221 | 1. | 4239 | NUC-001-2.1 R9.4.1. | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 941000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4221 | 2. | 4240 | NUC-001-2.1 R9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 942000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4221 | 3. | 4241 | NUC-001-2.1 R9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 943000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4221 | 4. | 4242 | NUC-001-2.1 R9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 944000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4221 | 5. | 4243 | NUC-001-2.1 R9.4.5. | Provisions for personnel training, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 945000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4222 | 1. | 4227 | NUC-001-2.1 R9.1.1. | Definitions of key terms used in the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2014-01-21 |  |  | 911000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4222 | 2. | 4228 | NUC-001-2.1 R9.1.2. | Names of the responsible entities, organizational relationships, and responsibilities related to the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2014-01-21 |  |  | 912000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4222 | 3. | 4225 | NUC-001-2.1 R9.1.3. | A requirement to review the agreement(s) at least every three years. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2014-01-21 |  |  | 913000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4222 | 4. | 4226 | NUC-001-2.1 R9.1.4. | A dispute resolution mechanism. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2014-01-21 |  |  | 914000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4223 | 1. | 4230 | NUC-001-2.1 R9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 921000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4223 | 2. | 4229 | NUC-001-2.1 R9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 922000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4223 | 3. | 4231 | NUC-001-2.1 R9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 923000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4224 | 1. | 4232 | NUC-001-2.1 R9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 931000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4224 | 2. | 4235 | NUC-001-2.1 R9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 932000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4224 | 3. | 4234 | NUC-001-2.1 R9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 933000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4224 | 4. | 4233 | NUC-001-2.1 R9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 934000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4224 | 5. | 4236 | NUC-001-2.1 R9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. . |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 935000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4224 | 6. | 4237 | NUC-001-2.1 R9.3.6. | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 936000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 | 4224 | 7. | 4238 | NUC-001-2.1 R9.3.7. | Coordination of the NPIRs with transmission system Special Protection Systems and underfrequency and undervoltage load shedding programs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 937000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 |  | 1. | 4222 | NUC-001-2.1 R9.1. | Administrative elements: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2014-01-21 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 |  | 2. | 4223 | NUC-001-2.1 R9.2. | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 |  | 3. | 4224 | NUC-001-2.1 R9.3. | Operations and maintenance coordination: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 930000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
321 | 4216 |  | 4. | 4221 | NUC-001-2.1 R9.4. | Communications and training: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | 940000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
323 | 4281 |  | 1. | 4285 | PRC-001-1.1 R2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-04-01 |  | 2015-05-28 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
323 | 4281 |  | 2. | 4286 | PRC-001-1.1 R2.2. | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. |  | TOP | [18 empty] | TOP |  |  |  | 2013-04-01 |  | 2015-05-28 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
323 | 4283 |  | 1. | 4288 | PRC-001-1.1 R3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-04-01 |  | 2015-05-28 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
323 | 4283 |  | 2. | 4287 | PRC-001-1.1 R3.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP |  |  |  | 2013-04-01 |  | 2015-05-28 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
323 | 4284 |  | 1. | 4290 | PRC-001-1.1 R5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-04-01 |  | 2015-05-28 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
323 | 4284 |  | 2. | 4289 | PRC-001-1.1 R5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. |  | TOP | [18 empty] | TOP |  |  |  | 2013-04-01 |  | 2015-05-28 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
324 | 4291 |  | 1. | 4293 | PRC-005-1.1b R1.1. | Maintenance and testing intervals and their basis. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System that affects the reliability of the BES, shall have an associated Protection System maintenance and testing program as defined in Requirement 1. | 2013-11-25 |  | 2027-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
324 | 4291 |  | 2. | 4294 | PRC-005-1.1b R1.2. | Summary of maintenance and testing procedures. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System that affects the reliability of the BES, shall have an associated Protection System maintenance and testing program as defined in Requirement 1. | 2013-11-25 |  | 2027-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
324 | 4292 |  | 1. | 4295 | PRC-005-1.1b R2.1. | Evidence Protection System devices were maintained and tested within the defined intervals. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System that affects the reliability of the BES, shall have evidence it provided documentation of its associated Protection System maintenance and testing program and the implementation of its program as defined in Requirement 2. | 2013-11-25 |  | 2027-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
324 | 4292 |  | 2. | 4296 | PRC-005-1.1b R2.2. | Date each Protection System device was last tested/maintained. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System that affects the reliability of the BES, shall have evidence it provided documentation of its associated Protection System maintenance and testing program and the implementation of its program as defined in Requirement 2. | 2013-11-25 |  | 2027-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
327 | 4299 |  | 1. | 6823 | TOP-003-2 R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses and Real-time monitoring. |  | TOP | [18 empty] | TOP | [5 empty] | 2016-01-26 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
327 | 4299 |  | 2. | 6824 | TOP-003-2 R1.2. | A mutually-agreeable format. |  | TOP | [18 empty] | TOP | [5 empty] | 2016-01-26 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
327 | 4299 |  | 3. | 6825 | TOP-003-2 R1.3. | A periodicity for providing data. |  | TOP | [18 empty] | TOP | [5 empty] | 2016-01-26 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
327 | 4299 |  | 4. | 6826 | TOP-003-2 R1.4. | The deadline by which the respondent is to provide the indicated data. |  | TOP | [18 empty] | TOP | [5 empty] | 2016-01-26 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
327 | 4300 |  | 1. | 6827 | TOP-003-2 R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. |  | BA | BA | [23 empty] | 2016-01-26 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
327 | 4300 |  | 2. | 6828 | TOP-003-2 R2.2. | A mutually-agreeable format. |  | BA | BA | [23 empty] | 2016-01-26 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
327 | 4300 |  | 3. | 6829 | TOP-003-2 R2.3. | A periodicity for providing data. |  | BA | BA | [23 empty] | 2016-01-26 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
327 | 4300 |  | 4. | 6830 | TOP-003-2 R2.4. | The deadline by which the respondent is to provide the indicated data. |  | BA | BA | [23 empty] | 2016-01-26 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
328 | 4318 |  | 1. | 4319 | VAR-001-3 R3.1. | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2013-06-20 |  | 2014-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
328 | 4318 |  | 2. | 4320 | VAR-001-3 R3.2. | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  | TOP | [18 empty] | TOP |  |  |  | 2013-06-20 |  | 2014-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
328 | 4323 |  | 1. | RP-2021-06-03-0000004 | VAR-001-3 R6.1. | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2014-01-01 |  | 2014-09-30 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
328 | 4327 |  | 1. | 4328 | VAR-001-3 R9.1. | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  | TOP | [18 empty] | TOP |  |  |  | 2013-06-20 |  | 2014-09-30 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
329 | 4335 | 4336 | 1. | 4342 | CIP-002-3a R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
329 | 4335 | 4336 | 2. | 4341 | CIP-002-3a R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
329 | 4335 | 4336 | 3. | 4344 | CIP-002-3a R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
329 | 4335 | 4336 | 4. | 4343 | CIP-002-3a R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
329 | 4335 | 4336 | 5. | 4338 | CIP-002-3a R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
329 | 4335 | 4336 | 6. | 4340 | CIP-002-3a R1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
329 | 4335 | 4336 | 7. | 4339 | CIP-002-3a R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 127000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
329 | 4335 |  | 1. | 4337 | CIP-002-3a R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
329 | 4335 |  | 2. | 4336 | CIP-002-3a R1.2. | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
329 | 4334 |  | 1. | 4345 | CIP-002-3a R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
329 | 4334 |  | 2. | 4347 | CIP-002-3a R3.2. | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
329 | 4334 |  | 3. | 4346 | CIP-002-3a R3.3. | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
33 | 452 |  | 1. | 453 | COM-001-1.1 R1.1. | Internally. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2009-05-13 |  | 2015-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
33 | 452 |  | 2. | 454 | COM-001-1.1 R1.2. | Between the Reliability Coordinator and its Transmission Operators and Balancing Authorities. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2009-05-13 |  | 2015-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
33 | 452 |  | 3. | 455 | COM-001-1.1 R1.3. | With other Reliability Coordinators, Transmission Operators, and Balancing Authorities as necessary to maintain reliability. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2009-05-13 |  | 2015-09-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
33 | 452 |  | 4. | 456 | COM-001-1.1 R1.4. | Where applicable, these facilities shall be redundant and diversely routed. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2009-05-13 |  | 2015-09-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
331 | 4353 |  | 1. | 6565 | FAC-003-3 R3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2016-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
331 | 4353 |  | 2. | 6566 | FAC-003-3 R3.2. | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2013-11-25 |  | 2016-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
332 | 4359 |  | 1. | 4360 | PRC-001-2 R2.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  | GOP | [5 empty] | GOP | [18 empty] | 2016-01-26 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
332 | 4359 |  | 2. | 4361 | PRC-001-2 R2.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP | [5 empty] | 2016-01-26 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
333 | 4364 | 4367 | 1. | 4373 | CIP-004-3a R2.2.1. | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
333 | 4364 | 4367 | 2. | 4370 | CIP-004-3a R2.2.2. | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
333 | 4364 | 4367 | 3. | 4371 | CIP-004-3a R2.2.3. | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
333 | 4364 | 4367 | 4. | 4372 | CIP-004-3a R2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 224000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
333 | 4364 |  | 1. | 4368 | CIP-004-3a R2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
333 | 4364 |  | 2. | 4367 | CIP-004-3a R2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-3, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
333 | 4364 |  | 3. | 4369 | CIP-004-3a R2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
333 | 4366 |  | 1. | 4375 | CIP-004-3a R3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
333 | 4366 |  | 2. | 4374 | CIP-004-3a R3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
333 | 4366 |  | 3. | 4376 | CIP-004-3a R3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
333 | 4365 |  | 1. | 4377 | CIP-004-3a R4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
333 | 4365 |  | 2. | 4378 | CIP-004-3a R4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
334 | 4380 | 4383 | 1. | 4389 | CIP-004-4a R2.2.1. | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
334 | 4380 | 4383 | 2. | 4386 | CIP-004-4a R2.2.2. | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
334 | 4380 | 4383 | 3. | 4387 | CIP-004-4a R2.2.3. | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
334 | 4380 | 4383 | 4. | 4388 | CIP-004-4a R2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  | 224000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
334 | 4380 |  | 1. | 4384 | CIP-004-4a R2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
334 | 4380 |  | 2. | 4383 | CIP-004-4a R2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-4, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
334 | 4380 |  | 3. | 4385 | CIP-004-4a R2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
334 | 4382 |  | 1. | 4391 | CIP-004-4a R3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
334 | 4382 |  | 2. | 4390 | CIP-004-4a R3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
334 | 4382 |  | 3. | 4392 | CIP-004-4a R3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
334 | 4381 |  | 1. | 4393 | CIP-004-4a R4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
334 | 4381 |  | 2. | 4394 | CIP-004-4a R4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
336 | 4399 |  | 1. | RP-2021-06-03-0000013 | VAR-002-2b R2.1. | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
336 | 4399 |  | 2. | RP-2021-06-03-0000014 | VAR-002-2b R2.2. | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
336 | 4402 |  | 1. | 4403 | VAR-002-2b R3.1. | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
336 | 4402 |  | 2. | 4404 | VAR-002-2b R3.2. | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
336 | 4405 | 4406 | 1. | 4407 | VAR-002-2b R4.1.1. | Tap settings. |  | GO |  |  |  |  | GO | [17 empty] | 2013-07-01 |  | 2014-09-30 |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
336 | 4405 | 4406 | 2. | 4408 | VAR-002-2b R4.1.2. | Available fixed tap ranges. |  | GO |  |  |  |  | GO | [17 empty] | 2013-07-01 |  | 2014-09-30 |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
336 | 4405 | 4406 | 3. | 4409 | VAR-002-2b R4.1.3. | Impedance data. |  | GO |  |  |  |  | GO | [17 empty] | 2013-07-01 |  | 2014-09-30 |  |  | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
336 | 4405 | 4406 | 4. | 4410 | VAR-002-2b R4.1.4. | The +/- voltage range with step-change in % for load-tap changing transformers. |  | GO |  |  |  |  | GO | [17 empty] | 2013-07-01 |  | 2014-09-30 |  |  | 414000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
336 | 4405 |  | 1. | 4406 | VAR-002-2b R4.1. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO |  |  |  |  | GO | [17 empty] | 2013-07-01 |  | 2014-09-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
336 | 4411 |  | 1. | 4412 | VAR-002-2b R5.1. | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
337 | 4413 |  | 1. | 6544 | PRC-005-2 R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  |  | 2014-02-24 |  | 2015-05-28 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
337 | 4413 |  | 2. | 6545 | PRC-005-2 R1.2. | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  |  | 2014-02-24 |  | 2015-05-28 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
34 | 462 |  | 1. | 463 | COM-002-2 R1.1. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators through predetermined communication paths of any condition that could threaten the reliability of its area or when firm load shedding is anticipated. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4421 |  | 1. | 6714 | COM-001-2 R1.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-06-22 |  | 2015-11-12 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4421 |  | 2. | 6715 | COM-001-2 R1.2. | Each adjacent Reliability Coordinator within the same Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2015-06-22 |  | 2015-11-12 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4422 |  | 1. | 6716 | COM-001-2 R2.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-06-22 |  | 2015-11-12 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4422 |  | 2. | 6717 | COM-001-2 R2.2. | Each adjacent Reliability Coordinator within the same Interconnection. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4423 |  | 1. | 6718 | COM-001-2 R3.1. | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4423 |  | 2. | 6719 | COM-001-2 R3.2. | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4423 |  | 3. | 6720 | COM-001-2 R3.3. | Each Distribution Provider within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4423 |  | 4. | 6721 | COM-001-2 R3.4. | Each Generator Operator within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4423 |  | 5. | 6722 | COM-001-2 R3.5. | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4423 |  | 6. | 6723 | COM-001-2 R3.6. | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  | 360000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4424 |  | 1. | 6724 | COM-001-2 R4.1. | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4424 |  | 2. | 6725 | COM-001-2 R4.2. | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4424 |  | 3. | 6726 | COM-001-2 R4.3. | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4424 |  | 4. | 6727 | COM-001-2 R4.4. | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4425 |  | 1. | 6728 | COM-001-2 R5.1. | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4425 |  | 2. | 6729 | COM-001-2 R5.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4425 |  | 3. | 6730 | COM-001-2 R5.3. | Each Distribution Provider within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4425 |  | 4. | 6731 | COM-001-2 R5.4. | Each Generator Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4425 |  | 5. | 6732 | COM-001-2 R5.5. | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  | 550000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4426 |  | 1. | 6733 | COM-001-2 R6.1. | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4426 |  | 2. | 6734 | COM-001-2 R6.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4426 |  | 3. | 6735 | COM-001-2 R6.3. | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4427 |  | 1. | 6736 | COM-001-2 R7.1. | Its Balancing Authority. |  | DP |  | DP | [20 empty] | 2015-06-22 |  | 2015-11-12 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4427 |  | 2. | 6737 | COM-001-2 R7.2. | Its Transmission Operator. |  | DP |  | DP | [20 empty] | 2015-06-22 |  | 2015-11-12 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4428 |  | 1. | 6738 | COM-001-2 R8.1. | Its Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-06-22 |  | 2015-11-12 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
340 | 4428 |  | 2. | 6739 | COM-001-2 R8.2. | Its Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-06-22 |  | 2015-11-12 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
342 | 4438 |  | 1. | 4443 | BAL-002-1a R1.1. | A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a Reserve Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority with respect to monitoring and meeting the requirements of Standard BAL-002. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
342 | 4439 |  | 1. | 4447 | BAL-002-1a R2.1. | The minimum reserve requirement for the group. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
342 | 4439 |  | 2. | 4448 | BAL-002-1a R2.2. | Its allocation among members. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
342 | 4439 |  | 3. | 4444 | BAL-002-1a R2.3. | The permissible mix of Operating Reserve – Spinning and Operating Reserve – Supplemental that may be included in Contingency Reserve. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
342 | 4439 |  | 4. | 4449 | BAL-002-1a R2.4. | The procedure for applying Contingency Reserve in practice. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
342 | 4439 |  | 5. | 4445 | BAL-002-1a R2.5. | The limitations, if any, upon the amount of interruptible load that may be included. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
342 | 4439 |  | 6. | 4446 | BAL-002-1a R2.6. | The same portion of resource capacity (e.g. reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
342 | 4441 |  | 1. | 4450 | BAL-002-1a R3.1. | As a minimum, the Balancing Authority or Reserve Sharing Group shall carry at least enough Contingency Reserve to cover the most severe single contingency. All Balancing Authorities and Reserve Sharing Groups shall review, no less frequently than annually, their probable contingencies to determine their prospective most severe single contingencies. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
342 | 4440 |  | 1. | 4452 | BAL-002-1a R4.1. | A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre-Disturbance value. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
342 | 4440 |  | 2. | 4451 | BAL-002-1a R4.2. | The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
342 | 4437 |  | 1. | 4453 | BAL-002-1a R5.1. | The Reserve Sharing Group reviews group ACE (or equivalent) and demonstrates compliance to the DCS. To be in compliance, the group ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. or |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
342 | 4437 |  | 2. | 4454 | BAL-002-1a R5.2. | The Reserve Sharing Group reviews each member’s ACE in response to the activation of reserves. To be in compliance, a member’s ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
342 | 4442 |  | 1. | 4455 | BAL-002-1a R6.1. | The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
342 | 4442 |  | 2. | 4456 | BAL-002-1a R6.2. | The default Contingency Reserve Restoration Period is 90 minutes. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
343 | 4457 |  | 1. | 6475 | BAL-002-WECC-2 R1.1. | The greater of either: • The amount of Contingency Reserve equal to the loss of the most severe single contingency; • The amount of Contingency Reserve equal to the sum of three percent of hourly integrated Load plus three percent of hourly integrated generation. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | 1.1 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates its Contingency Reserve was maintained in accordance with the amounts identified in Requirement R1, Part 1.1, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Attachment A is a practical illustration showing how the generation amount may be calculated under Requirement R1. • Where Dynamic Schedules are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1 may include, but is not limited to, documentation showing a reciprocal acknowledgement as to which entity is carrying the reserves. This transfer may be all or some portion of the physical generator and is not limited to the entire physical capability of the generator. • Where Pseudo-Ties are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1, may include, but is not limited to, documentation accounting for the transfers included in the Pseudo-Ties. | 2014-01-28 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 110000000 | WECC-US | [5 empty] | WECC-US
343 | 4457 |  | 2. | 6476 | BAL-002-WECC-2 R1.2. | Comprised of any combination of the reserve types specified below: • Operating Reserve – Spinning • Operating Reserve - Supplemental • Interchange Transactions designated by the Source Balancing Authority as Operating Reserve – Supplemental • Reserve held by other entities by agreement that is deliverable on Firm Transmission Service • A resource, other than generation or load, that can provide energy or reduce energy consumption • Load, including demand response resources, Demand-Side Management resources, Direct Control Load Management, Interruptible Load or Interruptible Demand, or any other Load made available for curtailment by the Balancing Authority or the Reserve Sharing Group via contract or agreement. • All other load, not identified above, once the Reliability Coordinator has declared an energy emergency alert signifying that firm load interruption is imminent or in progress. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | 1.2 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.2. Evidence may include, but is not limited to, documentation that reserves were comprised of the types listed in Requirement R1, Part 1.2 for purposes of meeting the Contingency Reserve obligation of Requirement R1. Additionally, for purposes of the last bullet of Requirement R1, Part 1.2, evidence of compliance may include, but is not limited to, documentation that the reliability coordinator had issued an energy emergency alert, indicating that firm Load interruption was imminent or was in progress. | 2014-01-28 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 120000000 | WECC-US | [5 empty] | WECC-US
343 | 4457 |  | 3. | 6477 | BAL-002-WECC-2 R1.3. | Based on real-time hourly load and generating energy values averaged over each Clock Hour (excluding Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464). |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | 1.3 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.3. Evidence of compliance with Requirement R1, Part 1.3 may include, but is not limited to, documentation that Contingency Reserve amounts are based upon load and generating data averaged over each Clock Hour and excludes Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464. | 2014-01-28 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 130000000 | WECC-US | [5 empty] | WECC-US
343 | 4457 |  | 4. | 6478 | BAL-002-WECC-2 R1.4. | An amount of capacity from a resource that is deployable within ten minutes. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | 1.4 Evidence of compliance with Requirement R1, Part 1.4 may include, but is not limited to, documentation that the reserves maintained to comply with Requirement R1, Part 1.4 are fully deployable within ten minutes. | 2014-01-28 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 140000000 | WECC-US | [5 empty] | WECC-US
343 | 4458 |  | 1. | 6479 | BAL-002-WECC-2 R2.1. | Reserve that is immediately and automatically responsive to frequency deviations through the action of a governor or other control system; |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2014-01-28 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 210000000 | WECC-US | [5 empty] | WECC-US
343 | 4458 |  | 2. | 6480 | BAL-002-WECC-2 R2.2. | Reserve that is capable of fully responding within ten minutes. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2014-01-28 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 220000000 | WECC-US | [5 empty] | WECC-US
344 | 4461 |  | 1. | 4463 | TOP-006-3 R1.1. | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. |  | GOP | [5 empty] | GOP | [18 empty] | 2015-03-18 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
344 | 4461 |  | 2. | 4464 | TOP-006-3 R1.2. | Each Transmission Operator shall inform the Reliability Coordinator and other affected Transmission Operators of all transmission resources available for use. |  | TOP | [18 empty] | TOP | [5 empty] | 2015-03-18 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
344 | 4461 |  | 3. | 4465 | TOP-006-3 R1.3. | Each Balancing Authority shall inform its Reliability Coordinator of all generation resources available for use. |  | BA | BA | [23 empty] | 2015-03-18 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
345 | 4471 |  | 1. | RP-2021-06-08-0000001 | PRC-006-SPP-01 R1.1. | A minimum of 10% shall be shed at each UFLS step in accordance with the table below. See standard for table. |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2013-11-07 |  |  | 110000000 | SPPRE-US
345 | 4471 |  | 2. | RP-2021-06-08-0000002 | PRC-006-SPP-01 R1.2. | The intentional relay time delay for UFLS shall be less than or equal to 30 cycles. |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2013-11-07 |  |  | 120000000 | SPPRE-US
345 | 4471 |  | 3. | RP-2021-06-08-0000003 | PRC-006-SPP-01 R1.3. | Undervoltage inhibit setting shall be less than or equal to 85 percent of nominal voltage. |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2013-11-07 |  |  | 130000000 | SPPRE-US
345 | 4472 |  | 1. | RP-2021-06-08-0000004 | PRC-006-SPP-01 R2.1. | A minimum of one UFLS step with the frequency set point as assigned by the Planning Coordinator. |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2013-11-07 |  |  | 210000000 | SPPRE-US
345 | 4472 |  | 2. | RP-2021-06-08-0000005 | PRC-006-SPP-01 R2.2. | The minimum accumulated Load relief shall be at least 30% of the forecasted peak Load. |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2013-11-07 |  |  | 220000000 | SPPRE-US
345 | 4472 |  | 3. | RP-2021-06-08-0000006 | PRC-006-SPP-01 R2.3. | The intentional relay time delay for UFLS shall be less than or equal to 30 cycles. |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2013-11-07 |  |  | 230000000 | SPPRE-US
345 | 4472 |  | 4. | RP-2021-06-08-0000007 | PRC-006-SPP-01 R2.4. | Undervoltage inhibit setting shall be less than or equal to 85 percent of nominal voltage. |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2013-11-07 |  |  | 240000000 | SPPRE-US
345 | 4475 |  | 1. | RP-2021-06-08-0000008 | PRC-006-SPP-01 R5.1. | Location of installed UFLS equipment |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2013-11-07 |  |  | 510000000 | SPPRE-US
345 | 4475 |  | 2. | RP-2021-06-08-0000009 | PRC-006-SPP-01 R5.2. | Trip frequency(s) for each location |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2013-11-07 |  |  | 520000000 | SPPRE-US
345 | 4475 |  | 3. | RP-2021-06-08-0000010 | PRC-006-SPP-01 R5.3. | Total relay operating time of each location (time required for the relay to reliably sense the frequency + intentional delay time (if any)) |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2013-11-07 |  |  | 530000000 | SPPRE-US
345 | 4475 |  | 4. | RP-2021-06-08-0000011 | PRC-006-SPP-01 R5.4. | Breaker operating time (nameplate) of each location |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2013-11-07 |  |  | 540000000 | SPPRE-US
345 | 4475 |  | 5. | RP-2021-06-08-0000012 | PRC-006-SPP-01 R5.5. | Percentage and/or MW of bus load to be shed at the location |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2013-11-07 |  |  | 550000000 | SPPRE-US
345 | 4475 |  | 6. | RP-2021-06-08-0000013 | PRC-006-SPP-01 R5.6. | Total amount of load shed by each trip frequency and the total forecasted peak Load |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2013-11-07 |  |  | 560000000 | SPPRE-US
345 | 4475 |  | 7. | RP-2021-06-08-0000014 | PRC-006-SPP-01 R5.7. | Tie tripping schemes and the frequency and time delay at which they operate |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2013-11-07 |  |  | 570000000 | SPPRE-US
345 | 4475 |  | 8. | RP-2021-06-08-0000015 | PRC-006-SPP-01 R5.8. | Islanding schemes and the frequency and time delay at which they operate |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2013-11-07 |  |  | 580000000 | SPPRE-US
345 | 4476 |  | 1. | RP-2021-06-08-0000016 | PRC-006-SPP-01 R6.1. | Location of underfrequency and overfrequency equipment |  | GO |  |  |  |  | GO | [19 empty] | 2013-11-07 |  |  | 610000000 | SPPRE-US
345 | 4476 |  | 2. | RP-2021-06-08-0000017 | PRC-006-SPP-01 R6.2. | Trip frequency(s) for each location |  | GO |  |  |  |  | GO | [19 empty] | 2013-11-07 |  |  | 620000000 | SPPRE-US
345 | 4476 |  | 3. | RP-2021-06-08-0000018 | PRC-006-SPP-01 R6.3. | Total relay operating time of each location (time required for the relay to reliably sense the frequency + intentional delay time (if any)) |  | GO |  |  |  |  | GO | [19 empty] | 2013-11-07 |  |  | 630000000 | SPPRE-US
345 | 4476 |  | 4. | RP-2021-06-08-0000019 | PRC-006-SPP-01 R6.4. | Breaker operating time (nameplate) of each location |  | GO |  |  |  |  | GO | [19 empty] | 2013-11-07 |  |  | 640000000 | SPPRE-US
345 | 4476 |  | 5. | RP-2021-06-08-0000020 | PRC-006-SPP-01 R6.5. | MW of generation shed at each location |  | GO |  |  |  |  | GO | [19 empty] | 2013-11-07 |  |  | 650000000 | SPPRE-US
345 | 4477 |  | 1. | RP-2021-06-08-0000021 | PRC-006-SPP-01 R7.1. | For generating units with operating characteristics that limit the unit’s ability to perform in accordance with R7, the Generator Owner shall provide to the Planning Coordinator technical evidence demonstrating that the unit cannot operate within the specified frequency range without causing equipment damage or violating manufacturer’s published equipment ratings. |  | GO |  |  |  |  | GO | [19 empty] | 2013-11-07 |  |  | 710000000 | SPPRE-US
345 | 4478 |  | 1. | RP-2021-06-08-0000022 | PRC-006-SPP-01 R8.1. | The Planning Coordinator shall determine if the UFLS program performance is degraded due to the removal of any generation identified in accordance with R7.1 and verified in accordance with R8. |  | PCPA | [9 empty] | PCPA | [14 empty] | 2013-11-07 |  |  | 810000000 | SPPRE-US
345 | 4478 |  | 1.1. | RP-2021-06-08-0000023 | PRC-006-SPP-01 R8.1.1. | If the Planning Coordinator determines the UFLS program is degraded in accordance with R8.1 and that supplementary load shedding is, therefore, required, the Planning Coordinator shall notify the Generator Owner or UFLS entity(s) in accordance with the following:  Where the Generator Owner is a UFLS Entity and has the required amount of supplementary Load available, the Planning Coordinator shall notify the Generator Owner of Load the entity is required to shed (in addition to that required in accordance with R1 and R2)  Where the Generator Owner is not a UFLS Entity, or does not have the required supplementary Load available for shedding, the Planning Coordinator shall notify any other UFLS Entity(s) within the Planning Coordinator Area of Load the entity(s) is required to shed (in addition to that required in accordance with R1 and R2) |  | PCPA | [9 empty] | PCPA | [14 empty] | 2013-11-07 |  |  | 811000000 | SPPRE-US
346 | 4480 |  | 1. | RP-2021-08-12-0000001 | CIP-002-5 R1.1. | Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2014-02-03 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
346 | 4480 |  | 2. | RP-2021-08-12-0000002 | CIP-002-5 R1.2. | Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2014-02-03 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
346 | 4480 |  | 3. | RP-2021-08-12-0000003 | CIP-002-5 R1.3. | Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2014-02-03 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
346 | 4481 |  | 1. | RP-2021-08-12-0000004 | CIP-002-5 R2.1. | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and |  | BA, GO, GOP, IA, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2014-02-03 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
346 | 4481 |  | 2. | RP-2021-08-12-0000005 | CIP-002-5 R2.2. | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2014-02-03 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
347 | 4482 |  | 1. | 6160 | CIP-003-5 R1.1. | Personnel & training (CIP-004); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
347 | 4482 |  | 2. | 6161 | CIP-003-5 R1.2. | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
347 | 4482 |  | 3. | 6162 | CIP-003-5 R1.3. | Physical security of BES Cyber Systems (CIP-006); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
347 | 4482 |  | 4. | 6163 | CIP-003-5 R1.4. | System security management (CIP-007); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
347 | 4482 |  | 5. | 6164 | CIP-003-5 R1.5. | Incident reporting and response planning (CIP-008); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
347 | 4482 |  | 6. | 6165 | CIP-003-5 R1.6. | Recovery plans for BES Cyber Systems (CIP-009); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
347 | 4482 |  | 7. | 6166 | CIP-003-5 R1.7. | Configuration change management and vulnerability assessments (CIP-010); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
347 | 4482 |  | 8. | 6167 | CIP-003-5 R1.8. | Information protection (CIP-011); and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
347 | 4482 |  | 9. | 6168 | CIP-003-5 R1.9. | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
347 | 4483 |  | 1. | 6169 | CIP-003-5 R2.1. | Cyber security awareness; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2016-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
347 | 4483 |  | 2. | 6170 | CIP-003-5 R2.2. | Physical security controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2016-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
347 | 4483 |  | 3. | 6171 | CIP-003-5 R2.3. | Electronic access controls for external routable protocol connections and Dial-up Connectivity; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2016-06-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
347 | 4483 |  | 4. | 6172 | CIP-003-5 R2.4. | Incident response to a Cyber Security Incident. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2016-06-30 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
349 | 4491 |  | 1. | 6240 | CIP-005-5 R1.1. | All applicable Cyber Assets connected to a network via a routable protocol shall reside within a defined ESP. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1 An example of evidence may include, but is not limited to, a list of all ESPs with all uniquely identifiable applicable Cyber Assets connected via a routable protocol within each ESP. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
349 | 4491 |  | 2. | 6241 | CIP-005-5 R1.2. | All External Routable Connectivity must be through an identified Electronic Access Point (EAP). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. An example of evidence may include, but is not limited to, network diagrams showing all external routable communication paths and the identified EAPs. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
349 | 4491 |  | 3. | 6242 | CIP-005-5 R1.3. | Require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.3. An example of evidence may include, but is not limited to, a list of rules (firewall, access control lists, etc.) that demonstrate that only permitted access is allowed and that each access rule has a documented reason. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
349 | 4491 |  | 4. | RP-2021-06-17-0000011 | CIP-005-5 R1.4. | Where technically feasible, perform authentication when establishing Dial-up Connectivity with applicable Cyber Assets. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
349 | 4491 |  | 5. | 6244 | CIP-005-5 R1.5. | Have one or more methods for detecting known or suspected malicious communications for both inbound and outbound communications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.5. An example of evidence may include, but is not limited to, documentation that malicious communications detection methods (e.g. intrusion detection system, application layer firewall, etc.) are implemented. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
349 | 4492 |  | 1. | 6245 | CIP-005-5 R2.1. | Utilize an Intermediate System such that the Cyber Asset initiating Interactive Remote Access does not directly access an applicable Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1 Examples of evidence may include, but are not limited to, network diagrams or architecture documents. | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
349 | 4492 |  | 2. | 6246 | CIP-005-5 R2.2. | For all Interactive Remote Access sessions, utilize encryption that terminates at an Intermediate System. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. An example of evidence may include, but is not limited to, architecture documents detailing where encryption initiates and terminates. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
349 | 4492 |  | 3. | 6247 | CIP-005-5 R2.3. | Require multi-factor authentication for all Interactive Remote Access sessions. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.3. An example of evidence may include, but is not limited to, architecture documents detailing the authentication factors used. Examples of authenticators may include, but are not limited to, • Something the individual knows such as passwords or PINs. This does not include User ID; • Something the individual has such as tokens, digital certificates, or smart cards; or • Something the individual is such as fingerprints, iris scans, or other biometric characteristics. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
35 | 467 |  | 1. | 468 | EOP-001-0 R3.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
35 | 467 |  | 2. | 469 | EOP-001-0 R3.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
35 | 467 |  | 3. | 470 | EOP-001-0 R3.3. | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
35 | 467 |  | 4. | 471 | EOP-001-0 R3.4. | Develop, maintain, and implement a set of plans for system restoration. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
35 | 472 |  | 1. | 473 | EOP-001-0 R4.1. | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
35 | 472 |  | 2. | 474 | EOP-001-0 R4.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
35 | 472 |  | 3. | 475 | EOP-001-0 R4.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
35 | 472 |  | 4. | 476 | EOP-001-0 R4.4. | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
35 | 479 | 480 | 2 | RP-2021-06-14-0000004 | EOP-001-0 R7.1.2 |  |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | 712000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
35 | 479 |  | 1. | 480 | EOP-001-0 R7.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
35 | 479 |  | 2. | 481 | EOP-001-0 R7.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
35 | 479 |  | 3. | 482 | EOP-001-0 R7.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
35 | 479 |  | 4. | 483 | EOP-001-0 R7.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
350 | 4493 |  | 1. | 6248 | CIP-006-5 R1.1. | Define operational or procedural controls to restrict physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.1 An example of evidence may include, but is not limited to, documentation that operational or procedural controls exist. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
350 | 4493 |  | 2. | RP-2021-06-17-0000014 | CIP-006-5 R1.2. | Utilize at least one physical access control to allow unescorted physical access into each applicable Physical Security Perimeter to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
350 | 4493 |  | 3. | RP-2021-06-17-0000015 | CIP-006-5 R1.3. | Where technically feasible, utilize two or more different physical access controls (this does not require two completely independent physical access control systems) to collectively allow unescorted physical access into Physical Security Perimeters to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
350 | 4493 |  | 4. | 6251 | CIP-006-5 R1.4. | Monitor for unauthorized access through a physical access point into a Physical Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.4 An example of evidence may include, but is not limited to, documentation of controls that monitor for unauthorized access through a physical access point into a Physical Security Perimeter. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
350 | 4493 |  | 5. | 6252 | CIP-006-5 R1.5. | Issue an alarm or alert in response to detected unauthorized access through a physical access point into a Physical Security Perimeter to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of detection. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.5 An example of evidence may include, but is not limited to, language in the physical security plan that describes the issuance of an alarm or alert in response to unauthorized access through a physical access control into a Physical Security Perimeter and additional evidence that the alarm or alert was issued and communicated as identified in the BES Cyber Security Incident Response Plan, such as manual or electronic alarm or alert logs, cell phone or pager logs, or other evidence that documents that the alarm or alert was generated and communicated. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
350 | 4493 |  | 6. | 6253 | CIP-006-5 R1.6. | Monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control System. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.6 An example of evidence may include, but is not limited to, documentation of controls that monitor for unauthorized physical access to a PACS. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
350 | 4493 |  | 7. | 6254 | CIP-006-5 R1.7. | Issue an alarm or alert in response to detected unauthorized physical access to a Physical Access Control System to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of the detection. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.7 An example of evidence may include, but is not limited to, language in the physical security plan that describes the issuance of an alarm or alert in response to unauthorized physical access to Physical Access Control Systems and additional evidence that the alarm or alerts was issued and communicated as identified in the BES Cyber Security Incident Response Plan, such as alarm or alert logs, cell phone or pager logs, or other evidence that the alarm or alert was generated and communicated. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
350 | 4493 |  | 8. | 6255 | CIP-006-5 R1.8. | Log (through automated means or by personnel who control entry) entry of each individual with authorized unescorted physical access into each Physical Security Perimeter, with information to identify the individual and date and time of entry. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.8 An example of evidence may include, but is not limited to, language in the physical security plan that describes logging and recording of physical entry into each Physical Security Perimeter and additional evidence to demonstrate that this logging has been implemented, such as logs of physical access into Physical Security Perimeters that show the individual and the date and time of entry into Physical Security Perimeter. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
350 | 4493 |  | 9. | 6256 | CIP-006-5 R1.9. | Retain physical access logs of entry of individuals with authorized unescorted physical access into each Physical Security Perimeter for at least ninety calendar days. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.9 An example of evidence may include, but is not limited to, dated documentation such as logs of physical access into Physical Security Perimeters that show the date and time of entry into Physical Security Perimeter. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
350 | 4494 |  | 1. | 6257 | CIP-006-5 R2.1. | Require continuous escorted access of visitors (individuals who are provided access but are not authorized for unescorted physical access) within each Physical Security Perimeter, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 2.1 An example of evidence may include, but is not limited to, language in a visitor control program that requires continuous escorted access of visitors within Physical Security Perimeters and additional evidence to demonstrate that the process was implemented, such as visitor logs. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
350 | 4494 |  | 2. | 6258 | CIP-006-5 R2.2. | Require manual or automated logging of visitor entry into and exit from the Physical Security Perimeter that includes date and time of the initial entry and last exit, the visitor’s name, and the name of an individual point of contact responsible for the visitor, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 2.2 An example of evidence may include, but is not limited to, language in a visitor control program that requires continuous escorted access of visitors within Physical Security Perimeters and additional evidence to demonstrate that the process was implemented, such as dated visitor logs that include the required information. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
350 | 4494 |  | 3. | 6259 | CIP-006-5 R2.3. | Retain visitor logs for at least ninety calendar days. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 2.3 An example of evidence may include, but is not limited to, documentation showing logs have been retained for at least ninety calendar days. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
350 | 4495 |  | 1. | 6260 | CIP-006-5 R3.1. | Maintenance and testing of each Physical Access Control System and locally mounted hardware or devices at the Physical Security Perimeter at least once every 24 calendar months to ensure they function properly. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 3.1 An example of evidence may include, but is not limited to, a maintenance and testing program that provides for testing each Physical Access Control System and locally mounted hardware or devices associated with each applicable Physical Security Perimeter at least once every 24 calendar months and additional evidence to demonstrate that this testing was done, such as dated maintenance records, or other documentation showing testing and maintenance has been performed on each applicable device or system at least once every 24 calendar months. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4496 |  | 1. | RP-2021-06-18-0000001 | CIP-007-5 R1.1. | Where technically feasible, enable only logical network accessible ports that have been determined to be needed by the Responsible Entity, including port ranges or services where needed to handle dynamic ports. If a device has no provision for disabling or restricting logical ports on the device then those ports that are open are deemed needed. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4496 |  | 2. | 6188 | CIP-007-5 R1.2. | Protect against the use of unnecessary physical input/output ports used for network connectivity, console commands, or removable media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4497 |  | 1. | 6189 | CIP-007-5 R2.1. | A patch management process for tracking, evaluating, and installing cyber security patches for applicable Cyber Assets. The tracking portion shall include the identification of a source or sources that the Responsible Entity tracks for the release of cyber security patches for applicable Cyber Assets that are updateable and for which a patching source exists. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4497 |  | 2. | 6190 | CIP-007-5 R2.2. | At least once every 35 calendar days, evaluate security patches for applicability that have been released since the last evaluation from the source or sources identified in Part 2.1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4497 |  | 3. | 6191 | CIP-007-5 R2.3. | For applicable patches identified in Part 2.2, within 35 calendar days of the evaluation completion, take one of the following actions: • Apply the applicable patches; or • Create a dated mitigation plan; or • Revise an existing mitigation plan. Mitigation plans shall include the Responsible Entity’s planned actions to mitigate the vulnerabilities addressed by each security patch and a timeframe to complete these mitigations. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4497 |  | 4. | 6192 | CIP-007-5 R2.4. | For each mitigation plan created or revised in Part 2.3, implement the plan within the timeframe specified in the plan, unless a revision to the plan or an extension to the timeframe specified in Part 2.3 is approved by the CIP Senior Manager or delegate. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4498 |  | 1. | 6193 | CIP-007-5 R3.1. | Deploy method(s) to deter, detect, or prevent malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4498 |  | 2. | 6194 | CIP-007-5 R3.2. | Mitigate the threat of detected malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4498 |  | 3. | 6195 | CIP-007-5 R3.3. | For those methods identified in Part 3.1 that use signatures or patterns, have a process for the update of the signatures or patterns. The process must address testing and installing the signatures or patterns. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4499 | 6196 | 1. | 7784 | CIP-007-5 R4.1.1. | Detected successful login attempts; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4499 | 6196 | 2. | 6208 | CIP-007-5 R4.1.2. | Detected failed access attempts and failed login attempts; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4499 | 6196 | 3. | 6209 | CIP-007-5 R4.1.3. | Detected malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4499 | 6197 | 1. | 6210 | CIP-007-5 R4.2.1. | Detected malicious code from Part 4.1; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 421000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4499 | 6197 | 2. | 6211 | CIP-007-5 R4.2.2. | Detected failure of Part 4.1 event logging. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 422000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4499 |  | 1. | 6196 | CIP-007-5 R4.1. | Log events at the BES Cyber System level (per BES Cyber System capability) or at the Cyber Asset level (per Cyber Asset capability) for identification of, and after-the-fact investigations of, Cyber Security Incidents that includes, as a minimum, each of the following types of events: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4499 |  | 2. | 6197 | CIP-007-5 R4.2. | Generate alerts for security events that the Responsible Entity determines necessitates an alert, that includes, as a minimum, each of the following types of events (per Cyber Asset or BES Cyber System capability): |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4499 |  | 3. | RP-2021-06-18-0000002 | CIP-007-5 R4.3. | Where technically feasible, retain applicable event logs identified in Part 4.1 for at least the last 90 consecutive calendar days except under CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4499 |  | 4. | 6199 | CIP-007-5 R4.4. | Review a summarization or sampling of logged events as determined by the Responsible Entity at intervals no greater than 15 calendar days to identify undetected Cyber Security Incidents. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4500 | 6204 | 1. | 6212 | CIP-007-5 R5.5.1. | Password length that is, at least, the lesser of eight characters or the maximum length supported by the Cyber Asset; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 551000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4500 | 6204 | 2. | 6213 | CIP-007-5 R5.5.2. | Minimum password complexity that is the lesser of three or more different types of characters (e.g., uppercase alphabetic, lowercase alphabetic, numeric, non-alphanumeric) or the maximum complexity supported by the Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 552000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4500 |  | 1. | 6200 | CIP-007-5 R5.1. | Have a method(s) to enforce authentication of interactive user access, where technically feasible. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4500 |  | 2. | 6201 | CIP-007-5 R5.2. | Identify and inventory all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4500 |  | 3. | 6202 | CIP-007-5 R5.3. | Identify individuals who have authorized access to shared accounts. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4500 |  | 4. | 6203 | CIP-007-5 R5.4. | Change known default passwords, per Cyber Asset capability |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4500 |  | 5. | 6204 | CIP-007-5 R5.5. | For password-only authentication for interactive user access, either technically or procedurally enforce the following password parameters: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 550000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4500 |  | 6. | 6205 | CIP-007-5 R5.6. | Where technically feasible, for password-only authentication for interactive user access, either technically or procedurally enforce password changes or an obligation to change the password at least once every 15 calendar months. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 560000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
351 | 4500 |  | 7. | 6206 | CIP-007-5 R5.7. | Where technically feasible, either: • Limit the number of unsuccessful authentication attempts; or • Generate alerts after a threshold of unsuccessful authentication attempts. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 570000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
352 | 4501 |  | 1. | 6173 | CIP-008-5 R1.1. | One or more processes to identify, classify, and respond to Cyber Security Incidents. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. An example of evidence may include, but is not limited to, dated documentation of Cyber Security Incident response plan(s) that include the process to identify, classify, and respond to Cyber Security Incidents. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
352 | 4501 |  | 2. | 6174 | CIP-008-5 R1.2. | One or more processes to determine if an identified Cyber Security Incident is a Reportable Cyber Security Incident and notify the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), unless prohibited by law. Initial notification to the ES-ISAC, which may be only a preliminary notice, shall not exceed one hour from the determination of a Reportable Cyber Security Incident. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. Examples of evidence may include, but are not limited to, dated documentation of Cyber Security Incident response plan(s) that provide guidance or thresholds for determining which Cyber Security Incidents are also Reportable Cyber Security Incidents and documentation of initial notices to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
352 | 4501 |  | 3. | 6175 | CIP-008-5 R1.3. | The roles and responsibilities of Cyber Security Incident response groups or individuals. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.3. An example of evidence may include, but is not limited to, dated Cyber Security Incident response process(es) or procedure(s) that define roles and responsibilities (e.g., monitoring, reporting, initiating, documenting, etc.) of Cyber Security Incident response groups or individuals. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
352 | 4501 |  | 4. | 6176 | CIP-008-5 R1.4. | Incident handling procedures for Cyber Security Incidents. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.4. An example of evidence may include, but is not limited to, dated Cyber Security Incident response process(es) or procedure(s) that address incident handling (e.g., containment, eradication, recovery/incident resolution). | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
352 | 4502 |  | 1. | 6177 | CIP-008-5 R2.1. | Test each Cyber Security Incident response plan(s) at least once every 15 calendar months: • By responding to an actual Reportable Cyber Security Incident; • With a paper drill or tabletop exercise of a Reportable Cyber Security Incident; or • With an operational exercise of a Reportable Cyber Security Incident. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. Examples of evidence may include, but are not limited to, dated evidence of a lessons-learned report that includes a summary of the test or a compilation of notes, logs, and communication resulting from the test. Types of exercises may include discussion or operations based exercises. | 2017-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
352 | 4502 |  | 2. | RP-2021-06-18-0000003 | CIP-008-5 R2.2. | Use the Cyber Security Incident response plan(s) under Requirement R1 when responding to a Reportable Cyber Security Incident or performing an exercise of a Reportable Cyber Security Incident. Document deviations from the plan(s) taken during the response to the incident or exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 1.2 High Impact BES Cyber Systems and their associated: • EACMS Medium Impact BES Cyber Systems and their associated: • EACMS | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
352 | 4502 |  | 3. | 6179 | CIP-008-5 R2.3. | Retain records related to Reportable Cyber Security Incidents. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.3. An example of evidence may include, but is not limited to, dated documentation, such as security logs, police reports, emails, response forms or checklists, forensic analysis results, restoration records, and post-incident review notes related to Reportable Cyber Security Incidents. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
352 | 4503 | 6180 | 1. | 6181 | CIP-008-5 R3.1.1. | 3.1.1. Document any lessons learned or document the absence of any lessons learned; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
352 | 4503 | 6180 | 2. | 6182 | CIP-008-5 R3.1.2. | Update the Cyber Security Incident response plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
352 | 4503 | 6180 | 3. | 6183 | CIP-008-5 R3.1.3. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates to the Cyber Security Incident response plan based on any documented lessons learned. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
352 | 4503 | 6184 | 1. | 6185 | CIP-008-5 R3.2.1. | Update the Cyber Security Incident response plan(s); and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
352 | 4503 | 6184 | 2. | 6186 | CIP-008-5 R3.2.2. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
352 | 4503 |  | 1. | 6180 | CIP-008-5 R3.1. | No later than 90 calendar days after completion of a Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.1. An example of evidence may include, but is not limited to, all of the following: 1. Dated documentation of post incident(s) review meeting notes or follow-up report showing lessons learned associated with the Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response or dated documentation stating there were no lessons learned; 2. Dated and revised Cyber Security Incident response plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
352 | 4503 |  | 2. | 6184 | CIP-008-5 R3.2. | No later than 60 calendar days after a change to the roles or responsibilities, Cyber Security Incident response groups or individuals, or technology that the Responsible Entity determines would impact the ability to execute the plan: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.2. An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
353 | 4504 |  | 1. | 6261 | CIP-009-5 R1.1. | Conditions for activation of the recovery plan(s). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
353 | 4504 |  | 2. | 6262 | CIP-009-5 R1.2. | Roles and responsibilities of responders. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
353 | 4504 |  | 3. | 6263 | CIP-009-5 R1.3. | One or more processes for the backup and storage of information required to recover BES Cyber System functionality. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
353 | 4504 |  | 4. | 6264 | CIP-009-5 R1.4. | One or more processes to verify the successful completion of the backup processes in Part 1.3 and to address any backup failures. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
353 | 4504 |  | 5. | 6265 | CIP-009-5 R1.5. | One or more processes to preserve data, per Cyber Asset capability, for determining the cause of a Cyber Security Incident that triggers activation of the recovery plan(s). Data preservation should not impede or restrict recovery. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
353 | 4505 |  | 1. | 6266 | CIP-009-5 R2.1. | Test each of the recovery plans referenced in Requirement R1 at least once every 15 calendar months: • By recovering from an actual incident; • With a paper drill or tabletop exercise; or • With an operational exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
353 | 4505 |  | 2. | 6267 | CIP-009-5 R2.2. | Test a representative sample of information used to recover BES Cyber System functionality at least once every 15 calendar months to ensure that the information is useable and is compatible with current configurations. An actual recovery that incorporates the information used to recover BES Cyber System functionality substitutes for this test. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
353 | 4505 |  | 3. | 6268 | CIP-009-5 R2.3. | Test each of the recovery plans referenced in Requirement R1 at least once every 36 calendar months through an operational exercise of the recovery plans in an environment representative of the production environment. An actual recovery response may substitute for an operational exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
353 | 4506 | 6269 | 1. | 6270 | CIP-009-5 R3.1.1. | Document any lessons learned associated with a recovery plan test or actual recovery or document the absence of any lessons learned; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
353 | 4506 | 6269 | 2. | 6271 | CIP-009-5 R3.1.2. | Update the recovery plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
353 | 4506 | 6269 | 3. | 6272 | CIP-009-5 R3.1.3. | Notify each person or group with a defined role in the recovery plan of the updates to the recovery plan based on any documented lessons learned. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
353 | 4506 | 6273 | 1. | 6274 | CIP-009-5 R3.2.1. | Update the recovery plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
353 | 4506 | 6273 | 2. | 6275 | CIP-009-5 R3.2.2. | Notify each person or group with a defined role in the recovery plan of the updates. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
353 | 4506 |  | 1. | 6269 | CIP-009-5 R3.1. | No later than 90 calendar days after completion of a recovery plan test or actual recovery: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
353 | 4506 |  | 2. | 6273 | CIP-009-5 R3.2. | No later than 60 calendar days after a change to the roles or responsibilities, responders, or technology that the Responsible Entity determines would impact the ability to execute the recovery plan: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4507 | 6218 | 1. | 6219 | CIP-010-1 R1.1.1. | Operating system(s) (including version) or firmware where no independent operating system exists; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4507 | 6218 | 2. | 6220 | CIP-010-1 R1.1.2. | Any commercially available or open-source application software (including version) intentionally installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4507 | 6218 | 3. | 6221 | CIP-010-1 R1.1.3. | Any custom software installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4507 | 6218 | 4. | 6222 | CIP-010-1 R1.1.4. | Any logical network accessible ports; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4507 | 6218 | 5. | 6223 | CIP-010-1 R1.1.5. | Any security patches applied. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4507 | 6226 | 1. | 6227 | CIP-010-1 R1.4.1. | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4507 | 6226 | 2. | 6228 | CIP-010-1 R1.4.2. | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4507 | 6226 | 3. | 6229 | CIP-010-1 R1.4.3. | Document the results of the verification. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4507 | 6230 | 1. | 6231 | CIP-010-1 R1.5.1. | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4507 | 6230 | 2. | 6232 | CIP-010-1 R1.5.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4507 |  | 1. | 6218 | CIP-010-1 R1.1. | Develop a baseline configuration, individually or by group, which shall include the following items: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4507 |  | 2. | 6224 | CIP-010-1 R1.2. | Authorize and document changes that deviate from the existing baseline configuration. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4507 |  | 3. | 6225 | CIP-010-1 R1.3. | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4507 |  | 4. | 6226 | CIP-010-1 R1.4. | For a change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4507 |  | 5. | 6230 | CIP-010-1 R1.5. | Where technically feasible, for each change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4508 |  | 1. | 6233 | CIP-010-1 R2.1. | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4509 | 6235 | 1. | 6236 | CIP-010-1 R3.2.1. | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4509 | 6235 | 2. | 6237 | CIP-010-1 R3.2.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4509 |  | 1. | 6234 | CIP-010-1 R3.1. | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4509 |  | 2. | 6235 | CIP-010-1 R3.2. | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4509 |  | 3. | 6238 | CIP-010-1 R3.3. | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
354 | 4509 |  | 4. | 6239 | CIP-010-1 R3.4. | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
355 | 4510 |  | 1. | 6214 | CIP-011-1 R1.1. | Method(s) to identify information that meets the definition of BES Cyber System Information. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
355 | 4510 |  | 2. | 6215 | CIP-011-1 R1.2. | Procedure(s) for protecting and securely handling BES Cyber System Information, including storage, transit, and use. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
355 | 4511 |  | 1. | 6216 | CIP-011-1 R2.1. | Prior to the release for reuse of applicable Cyber Assets that contain BES Cyber System Information (except for reuse within other systems identified in the “Applicable Systems” column), the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset data storage media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
355 | 4511 |  | 2. | 6217 | CIP-011-1 R2.2. | Prior to the disposal of applicable Cyber Assets that contain BES Cyber System Information, the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset or destroy the data storage media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
357 | 4519 |  | 1. | 6483 | BAL-004-WECC-02 R1.1. | For load-serving Balancing Authorities, 150% of the previous calendar year’s integrated hourly Peak Demand, |  | BA | BA | [21 empty] | 2013-10-16 |  | 2018-09-30 |  |  | 110000000 | WECC-US | [5 empty] | WECC-US
357 | 4519 |  | 2. | 6484 | BAL-004-WECC-02 R1.2. | For generation-only Balancing Authorities, 150% of the previous calendar year’s integrated hourly peak generation. |  | BA | BA | [21 empty] | 2013-10-16 |  | 2018-09-30 |  |  | 120000000 | WECC-US | [5 empty] | WECC-US
357 | 4522 |  | 1. | 6485 | BAL-004-WECC-02 R4.1. | PIIhourly, |  | BA | BA | [21 empty] | 2013-10-16 |  | 2018-09-30 |  |  | 410000000 | WECC-US | [5 empty] | WECC-US
357 | 4522 |  | 2. | 6486 | BAL-004-WECC-02 R4.2. | PIIaccum, |  | BA | BA | [21 empty] | 2013-10-16 |  | 2018-09-30 |  |  | 420000000 | WECC-US | [5 empty] | WECC-US
357 | 4522 |  | 3. | 6487 | BAL-004-WECC-02 R4.3. | Automatic Time Error Correction term (IATEC). |  | BA | BA | [21 empty] | 2013-10-16 |  | 2018-09-30 |  |  | 430000000 | WECC-US | [5 empty] | WECC-US
358 | 4533 |  | 1. | 6481 | BAL-003-1 R3.1. | Less than zero at all times, and |  | BA, FRSG | BA |  |  | FRSG | [18 empty] | 2014-03-24 |  | 2015-11-12 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
358 | 4533 |  | 2. | 6482 | BAL-003-1 R3.2. | Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. |  | BA, FRSG | BA |  |  | FRSG | [18 empty] | 2014-03-24 |  | 2015-11-12 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
359 | 4535 |  | 1 . | RP-2021-07-06-0000006 | MOD-025-2 R1.1 . | Verify the Real Power capability of its generating units in accordance with Attachment 1. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have evidence that it performed the verification, such as a completed Attachment 2 or the Generator Owner form with the same information or dated information collected and used to complete attachments, and will have evidence that it submitted the information within 90 days to its Transmission Planner; such as dated electronic mail messages or mail receipts in accordance with Requirement R1. | 2016-07-01 |  |  | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following: 4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
359 | 4535 |  | 2. | 6770 | MOD-025-2 R1.2. | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have evidence that it performed the verification, such as a completed Attachment 2 or the Generator Owner form with the same information or dated information collected and used to complete attachments, and will have evidence that it submitted the information within 90 days to its Transmission Planner; such as dated electronic mail messages or mail receipts in accordance with Requirement R1. | 2014-05-27 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following: 4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
359 | 4536 |  | 1 . | RP-2021-07-06-0000007 | MOD-025-2 R2.1 . | Verify, in accordance with Attachment 1, (i) the Reactive Power capability of its generating units and (ii) the Reactive Power capability of its synchronous condenser units. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have evidence that it performed the verification, such as a completed Attachment 2 or the Generator Owner form with the same information, or dated information collected and used to complete attachments and will have evidence that it submitted the information within 90 days to its Transmission Planner; such as dated electronic mail messages or mail receipts in accordance with Requirement R2. | 2016-07-01 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following: 4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
359 | 4536 |  | 2. | 6772 | MOD-025-2 R2.2. | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have evidence that it performed the verification, such as a completed Attachment 2 or the Generator Owner form with the same information, or dated information collected and used to complete attachments and will have evidence that it submitted the information within 90 days to its Transmission Planner; such as dated electronic mail messages or mail receipts in accordance with Requirement R2. | 2014-05-27 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following: 4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
359 | 4537 |  | 1. | RP-2021-07-06-0000008 | MOD-025-2 R3.1. | Verify, in accordance with Attachment 1, the Reactive Power capability of its synchronous condenser units. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner will have evidence that it performed the verification, such as a completed Attachment 2 or the Transmission Owner form with equivalent information or dated information collected and used to complete attachments, and will have evidence that it submitted the information within 90 days to its Transmission Planner; such as dated electronic mail messages or mail receipts in accordance with Requirement R3. | 2016-07-01 |  |  | In those jurisdictions where regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following Board of Trustees adoption. • Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. • Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following: 4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
359 | 4537 |  | 2. | 6774 | MOD-025-2 R3.2. | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner will have evidence that it performed the verification, such as a completed Attachment 2 or the Transmission Owner form with equivalent information or dated information collected and used to complete attachments, and will have evidence that it submitted the information within 90 days to its Transmission Planner; such as dated electronic mail messages or mail receipts in accordance with Requirement R3. | 2014-05-27 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following: 4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
36 | 485 |  | 1. | 486 | EOP-001-1 R2.1. | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
36 | 485 |  | 2. | 487 | EOP-001-1 R2.2. | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
36 | 485 |  | 3. | 488 | EOP-001-1 R2.3. | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
36 | 485 |  | 4. | 489 | EOP-001-1 R2.4. | Develop, maintain, and implement a set of plans for system restoration. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
36 | 490 |  | 1. | 491 | EOP-001-1 R3.1. | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
36 | 490 |  | 2. | 492 | EOP-001-1 R3.2. | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
36 | 490 |  | 3. | 493 | EOP-001-1 R3.3. | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
36 | 490 |  | 4. | 494 | EOP-001-1 R3.4. | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
36 | 497 |  | 1. | 498 | EOP-001-1 R6.1. | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
36 | 497 |  | 2. | 499 | EOP-001-1 R6.2. | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
36 | 497 |  | 3. | 500 | EOP-001-1 R6.3. | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
36 | 497 |  | 4. | 501 | EOP-001-1 R6.4. | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
360 | 4539 | 6423 | 1. | 6424 | MOD-026-1 R2.1.1. | Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance, |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner must have and provide dated evidence it verified each generator excitation control system or plant volt/var control function model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | 2018-07-01 |  |  |  | 4.2. Facilities: For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.4 For all Interconnections: • A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
360 | 4539 | 6423 | 2. | 6425 | MOD-026-1 R2.1.2. | Manufacturer, model number (if available), and type of the excitation control system including, but not limited to static, AC brushless, DC rotating, and/or the plant volt/var control function (if installed), |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner must have and provide dated evidence it verified each generator excitation control system or plant volt/var control function model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | 2018-07-01 |  |  |  | 4.2. Facilities: For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.4 For all Interconnections: • A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
360 | 4539 | 6423 | 3. | 6426 | MOD-026-1 R2.1.3. | Model structure and data including, but not limited to reactance, time constants, saturation factors, total rotational inertia, or equivalent data for the generator, |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner must have and provide dated evidence it verified each generator excitation control system or plant volt/var control function model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | 2018-07-01 |  |  |  | 4.2. Facilities: For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.4 For all Interconnections: • A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
360 | 4539 | 6423 | 4. | 6427 | MOD-026-1 R2.1.4. | Model structure and data for the excitation control system, including the closed loop voltage regulator if a closed loop voltage regulator is installed or the model structure and data for the plant volt/var control function system, |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner must have and provide dated evidence it verified each generator excitation control system or plant volt/var control function model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | 2018-07-01 |  |  |  | 4.2. Facilities: For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.4 For all Interconnections: • A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
360 | 4539 | 6423 | 5. | 6428 | MOD-026-1 R2.1.5. | Compensation settings (such as droop, line drop, differential compensation), if used, and |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner must have and provide dated evidence it verified each generator excitation control system or plant volt/var control function model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | 2018-07-01 |  |  |  | 4.2. Facilities: For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.4 For all Interconnections: • A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. | 215000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
360 | 4539 | 6423 | 6. | 6429 | MOD-026-1 R2.1.6. | Model structure and data for power system stabilizer, if so equipped. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner must have and provide dated evidence it verified each generator excitation control system or plant volt/var control function model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | 2018-07-01 |  |  |  | 4.2. Facilities: For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.4 For all Interconnections: • A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. | 216000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
360 | 4539 |  | 1. | 6423 | MOD-026-1 R2.1. | Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s), or both. Each verification shall include the following: |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner must have and provide dated evidence it verified each generator excitation control system or plant volt/var control function model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | 2018-07-01 |  |  |  | 4.2. Facilities: For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.4 For all Interconnections: • A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
360 | 4543 |  | 1. | 6430 | MOD-026-1 R6.1. | The excitation control system or plant volt/var control function model initializes to compute modeling data without error, |  | TP | [19 empty] | TP |  | Evidence of Requirement R6 must include, for each model received, the dated response indicating the model was usable or not usable according to the criteria specified in Parts 6.1 through 6.3 and for a model that is not usable, a technical description; and dated evidence of transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) that the Generator Owner was notified within 90 calendar days of receipt of model information. | 2014-05-26 |  |  |  | 4.2. Facilities: For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.4 For all Interconnections: • A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
360 | 4543 |  | 2. | 6431 | MOD-026-1 R6.2. | A no-disturbance simulation results in negligible transients, and |  | TP | [19 empty] | TP |  | Evidence of Requirement R6 must include, for each model received, the dated response indicating the model was usable or not usable according to the criteria specified in Parts 6.1 through 6.3 and for a model that is not usable, a technical description; and dated evidence of transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) that the Generator Owner was notified within 90 calendar days of receipt of model information. | 2014-05-26 |  |  |  | 4.2. Facilities: For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.4 For all Interconnections: • A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
360 | 4543 |  | 3. | 6432 | MOD-026-1 R6.3. | For an otherwise stable simulation, a disturbance simulation results in the excitation control and plant volt/var control function model exhibiting positive damping. |  | TP | [19 empty] | TP |  | Evidence of Requirement R6 must include, for each model received, the dated response indicating the model was usable or not usable according to the criteria specified in Parts 6.1 through 6.3 and for a model that is not usable, a technical description; and dated evidence of transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) that the Generator Owner was notified within 90 calendar days of receipt of model information. | 2014-05-26 |  |  |  | 4.2. Facilities: For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.4 For all Interconnections: • A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
361 | 4545 | 6433 | 1. | 6434 | MOD-027-1 R2.1.1. | Documentation comparing the applicable unit’s MW model response to the recorded MW response for either: ? A frequency excursion from a system disturbance that meets MOD-027 Attachment 1 Note 1 with the applicable unit on-line, ? A speed governor reference change with the applicable unit online, or ? A partial load rejection test, Footnote: Differences between the control mode tested and the final simulation model must be identified, particularly when analyzing load rejection data. Most controls change gains or have a set point runback which takes effect when the breaker opens. Load or set point controls will also not be in effect once the breaker opens. Some method of accounting for these differences must be presented if the final model is not validated from on-line data under the normal operating conditions under which the model is expected to apply. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner must have and provide dated evidence it verified each generator turbine/governor and load control or active power/frequency control model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | 2014-07-01 |  |  |  | 4.2. Facilities For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
361 | 4545 | 6433 | 2. | 6435 | MOD-027-1 R2.1.2. | Type of governor and load control or active power control/frequency control equipment, Footnote: Turbine/governor and load control or active power/frequency control: |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner must have and provide dated evidence it verified each generator turbine/governor and load control or active power/frequency control model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | 2014-07-01 |  |  |  | 4.2. Facilities For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
361 | 4545 | 6433 | 3. | 6436 | MOD-027-1 R2.1.3. | A description of the turbine (e.g. for hydro turbine - Kaplan, Francis, or Pelton; for steam turbine - boiler type, normal fuel type, and turbine type; for gas turbine - the type and manufacturer; for variable energy plant - type and manufacturer), |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner must have and provide dated evidence it verified each generator turbine/governor and load control or active power/frequency control model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | 2014-07-01 |  |  |  | 4.2. Facilities For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
361 | 4545 | 6433 | 4. | 6437 | MOD-027-1 R2.1.4. | Model structure and data for turbine/governor and load control or active power/frequency control, and |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner must have and provide dated evidence it verified each generator turbine/governor and load control or active power/frequency control model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | 2014-07-01 |  |  |  | 4.2. Facilities For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
361 | 4545 | 6433 | 5. | 6438 | MOD-027-1 R2.1.5. | Representation of the real power response effects of outer loop controls such as operator set point controls, and load control but excluding AGC control) that would override the governor response (including blocked or nonfunctioning governors or modes of operation that limit Frequency Response), if applicable. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner must have and provide dated evidence it verified each generator turbine/governor and load control or active power/frequency control model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | 2018-07-01 |  |  |  | 4.2. Facilities For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). | 215000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
361 | 4545 |  | 1. | 6433 | MOD-027-1 R2.1. | Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units rated less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s) or both. Each verification shall include the following: |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner must have and provide dated evidence it verified each generator turbine/governor and load control or active power/frequency control model according to Part 2.1 for each applicable unit and a dated transmittal (e.g., electronic mail message, postal receipt, or confirmation of facsimile) as evidence it provided the model, documentation, and data to its Transmission Planner, in accordance with Requirement R2. | 2014-07-01 |  |  |  | 4.2. Facilities For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
361 | 4548 |  | 1 . | RP-2021-07-06-0000009 | MOD-027-1 R5.1 . | The turbine/governor and load control or active power/frequency control function model initializes to compute modeling data without error, |  | TP | [19 empty] | TP |  | Evidence of Requirement R5 must include, for each model received, the dated response indicating the model was usable or not usable according to the criteria specified in Parts 5.1 through 5.3 and for a model that is not useable, a technical description is the model is not usable, and dated evidence of transmittal (e.g., electronic mail messages, postal receipts, or confirmation of facsimile) that the Generator Owner was notified within 90 calendar days of receipt of model information in accordance with Requirement R5. | 2014-07-01 |  |  | In those jurisdictions where regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. In those jurisdictions where no regulatory approval is required: • Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following Board of Trustees adoption. | 4.2. Facilities For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
361 | 4548 |  | 2. | 6440 | MOD-027-1 R5.2. | A no-disturbance simulation results in negligible transients, and |  | TP | [19 empty] | TP |  | Evidence of Requirement R5 must include, for each model received, the dated response indicating the model was usable or not usable according to the criteria specified in Parts 5.1 through 5.3 and for a model that is not useable, a technical description is the model is not usable, and dated evidence of transmittal (e.g., electronic mail messages, postal receipts, or confirmation of facsimile) that the Generator Owner was notified within 90 calendar days of receipt of model information in accordance with Requirement R5. | 2014-05-26 |  |  |  | 4.2. Facilities For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
361 | 4548 |  | 3. | 6441 | MOD-027-1 R5.3. | For an otherwise stable simulation, a disturbance simulation results in the turbine/governor and load control or active power/frequency control model exhibiting positive damping. |  | TP | [19 empty] | TP |  | Evidence of Requirement R5 must include, for each model received, the dated response indicating the model was usable or not usable according to the criteria specified in Parts 5.1 through 5.3 and for a model that is not useable, a technical description is the model is not usable, and dated evidence of transmittal (e.g., electronic mail messages, postal receipts, or confirmation of facsimile) that the Generator Owner was notified within 90 calendar days of receipt of model information in accordance with Requirement R5. | 2014-05-26 |  |  |  | 4.2. Facilities For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following: 4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating). 4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating). 4.2.2 Generation in the Western Interconnection with the following characteristics: 4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating). 4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3 Generation in the ERCOT Interconnection with the following characteristics: 4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating). 4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
362 | 4549 | 6955 | 1. | 6956 | PRC-019-1 R1.1.1. | The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2016-07-01 |  | 2016-06-30 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
362 | 4549 | 6955 | 2. | 6957 | PRC-019-1 R1.1.2. | The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2016-07-01 |  | 2016-06-30 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
362 | 4549 |  | 1. | 6955 | PRC-019-1 R1.1. | Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2014-05-27 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
364 | 4554 | 4561 | 1. | 4565 | CIP-002-3b R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
364 | 4554 | 4561 | 2. | 4568 | CIP-002-3b R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
364 | 4554 | 4561 | 3. | 4567 | CIP-002-3b R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
364 | 4554 | 4561 | 4. | 4564 | CIP-002-3b R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
364 | 4554 | 4561 | 5. | 4566 | CIP-002-3b R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
364 | 4554 | 4561 | 6. | 4563 | CIP-002-3b R1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
364 | 4554 | 4561 | 7. | 4562 | CIP-002-3b R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 127000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
364 | 4554 |  | 1. | 4560 | CIP-002-3b R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
364 | 4554 |  | 2. | 4561 | CIP-002-3b R1.2. | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
364 | 4553 |  | 1. | 4559 | CIP-002-3b R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
364 | 4553 |  | 2. | 4558 | CIP-002-3b R3.2. | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
364 | 4553 |  | 3. | 4557 | CIP-002-3b R3.3. | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4572 | 6622 | 1.1. | 6623 | TPL-001-4 R1.1.1.1. | Existing Facilities |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2015-01-01 |  |  |  |  | 1111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4572 | 6622 | 2. | 6624 | TPL-001-4 R1.1.2. | Known outage(s) of generation or Transmission Facility(ies) with a duration of at least six months. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2015-01-01 |  |  |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4572 | 6622 | 3. | 6625 | TPL-001-4 R1.1.3. | New planned Facilities and changes to existing Facilities |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2015-01-01 |  |  |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4572 | 6622 | 4. | 6626 | TPL-001-4 R1.1.4. | Real and reactive Load forecasts |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2015-01-01 |  |  |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4572 | 6622 | 5. | 6627 | TPL-001-4 R1.1.5. | Known commitments for Firm Transmission Service and Interchange |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2015-01-01 |  |  |  |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4572 | 6622 | 6. | 6628 | TPL-001-4 R1.1.6. | Resources (supply or demand side) required for Load |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2015-01-01 |  |  |  |  | 116000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4572 |  | 1. | 6622 | TPL-001-4 R1.1. | System models shall represent: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within their respective area, using data consistent with MOD-010 and MOD-012, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2013-12-23 |  | 2023-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6629 | 1. | 6630 | TPL-001-4 R2.1.1. | System peak Load for either Year One or year two, and for year five. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6629 | 2. | 6631 | TPL-001-4 R2.1.2. | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6629 | 3. | 6632 | TPL-001-4 R2.1.3. | P1 events in Table 1, with known outages modeled as in Requirement R1, Part 1.1.2, under those System peak or Off-Peak conditions when known outages are scheduled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6629 | 4. | 6633 | TPL-001-4 R2.1.4. | For each of the studies described in Requirement R2, Parts 2.1.1 and 2.1.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in System response : -Real and reactive forecasted Load. -Expected transfers. -Expected in service dates of new or modified Transmission Facilities. -Generation additions, retirements, or other dispatch scenarios. -Controllable Loads and Demand Side Management. -Duration or timing of known Transmission outages. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6629 | 5. | 6634 | TPL-001-4 R2.1.5. | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be studied. The studies shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-01 |  |  |  |  | 215000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6635 | 1. | 6636 | TPL-001-4 R2.2.1. | A current study assessing expected System peak Load conditions for one of the years in the Long-Term Transmission Planning Horizon and the rationale for why that year was selected. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6638 | 1. | 6648 | TPL-001-4 R2.4.1. | System peak Load for one of the five years. System peak Load levels shall include a Load model which represents the expected dynamic behavior of Loads that could impact the study area, considering the behavior of induction motor Loads. An aggregate System Load model which represents the overall dynamic behavior of the Load is acceptable. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 241000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6638 | 2. | 6649 | TPL-001-4 R2.4.2. | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 242000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6638 | 3. | 6650 | TPL-001-4 R2.4.3. | For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in performance: • Load level, Load forecast, or dynamic Load model assumptions. • Expected transfers. • Expected in service dates of new or modified Transmission Facilities. • Reactive resource capability. • Generation additions, retirements, or other dispatch scenarios. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 243000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6652 | 1. | 6653 | TPL-001-4 R2.6.1. | For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 261000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6652 | 2. | 6654 | TPL-001-4 R2.6.2. | For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 262000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6655 | 1. | 6656 | TPL-001-4 R2.7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Special Protection Systems • Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations. • Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations. • Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan. • Use of rate applications, DSM, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 271000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6655 | 2. | 6657 | TPL-001-4 R2.7.2. | Include actions to resolve performance deficiencies identified in multiple sensitivity studies or provide a rationale for why actions were not necessary. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 272000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6655 | 3. | 6658 | TPL-001-4 R2.7.3. | If situations arise that are beyond the control of the Transmission Planner or Planning Coordinator that prevent the implementation of a Corrective Action Plan in the required timeframe, then the Transmission Planner or Planning Coordinator is permitted to utilize Non-Consequential Load Loss and curtailment of Firm Transmission Service to correct the situation that would normally not be permitted in Table 1, provided that the Transmission Planner or Planning Coordinator documents that they are taking actions to resolve the situation. The Transmission Planner or Planning Coordinator shall document the situation causing the problem, alternatives evaluated, and the use of Non-Consequential Load Loss or curtailment of Firm Transmission Service. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 273000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6655 | 4. | 6659 | TPL-001-4 R2.7.4. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 274000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6660 | 1. | 6661 | TPL-001-4 R2.8.1. | List System deficiencies and the associated actions needed to achieve required System performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 281000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 | 6660 | 2. | 6662 | TPL-001-4 R2.8.2. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  |  |  |  | 282000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 |  | 1. | 6629 | TPL-001-4 R2.1. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  | 2023-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 |  | 2. | 6635 | TPL-001-4 R2.2. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  | 2023-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 |  | 3 . | RP-2021-09-07-0000009 | TPL-001-4 R2.3 . | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  | 2023-06-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 |  | 4. | 6638 | TPL-001-4 R2.4. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  | 2023-06-30 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 |  | 5. | 6651 | TPL-001-4 R2.5. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6 and shall include documentation to support the technical rationale for determining material changes. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  | 2023-06-30 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 |  | 6. | 6652 | TPL-001-4 R2.6. | Past studies may be used to support the Planning Assessment if they meet the following requirements: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  | 2023-06-30 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 |  | 7. | 6655 | TPL-001-4 R2.7. | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.4 and 2.4.3. The Corrective Action Plan(s) shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  | 2023-06-30 |  |  | 270000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4573 |  | 8. | 6660 | TPL-001-4 R2.8. | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2016-01-01 |  | 2023-06-30 |  |  | 280000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4574 | 6665 | 1. | 6666 | TPL-001-4 R3.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2016-01-01 |  |  |  |  | 331000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4574 | 6665 | 2. | 6667 | TPL-001-4 R3.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide steady state control of electrical system quantities when such devices impact the study area. These devices may include equipment such as phase-shifting transformers, load tap changing transformers, and switched capacitors and inductors. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2016-01-01 |  |  |  |  | 332000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4574 | 6666 | 1. | 6668 | TPL-001-4 R3.3.1.1. | Tripping of generators where simulations show generator bus voltages or high side of the generation step up (GSU) voltages are less than known or assumed minimum generator steady state or ride through voltage limitations. Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-01 |  |  |  |  | 331100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4574 | 6666 | 2. | 6669 | TPL-001-4 R3.3.1.2. | Tripping of Transmission elements where relay loadability limits are exceeded. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-01 |  |  |  |  | 331200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4574 | RP-2021-07-09-0000052 | 1. | 6671 | TPL-001-4 R3.4 .1. | The Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2016-01-01 |  |  |  |  | 341000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4574 |  | 1. | 6663 | TPL-001-4 R3.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2016-01-01 |  | 2023-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4574 |  | 2. | 6664 | TPL-001-4 R3.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2016-01-01 |  | 2023-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4574 |  | 3. | 6665 | TPL-001-4 R3.3. | Contingency analyses for Requirement R3, Parts 3.1 & 3.2 shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2016-01-01 |  | 2023-06-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4574 |  | 4 . | RP-2021-07-09-0000052 | TPL-001-4 R3.4 . | Those planning events in Table 1, that are expected to produce more severe System impacts on its portion of the BES, shall be identified and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2016-01-01 |  | 2023-06-30 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4574 |  | 5 . | RP-2021-07-09-0000053 | TPL-001-4 R3.5 . | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2016-01-01 |  | 2023-06-30 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4575 | 6673 | 1. | 6674 | TPL-001-4 R4.1.1. | For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Special Protection System is not considered pulling out of synchronism. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2016-01-01 |  |  |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4575 | 6673 | 2. | 6675 | TPL-001-4 R4.1.2. | For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2016-01-01 |  |  |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4575 | 6673 | 3. | 6676 | TPL-001-4 R4.1.3. | For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2016-01-01 |  |  |  |  | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4575 | 6678 | 1. | 6679 | TPL-001-4 R4.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2016-01-01 |  |  |  |  | 431000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4575 | 6678 | 2. | 6683 | TPL-001-4 R4.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2016-01-01 |  |  |  |  | 432000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4575 | 6679 | 1. | 6680 | TPL-001-4 R4.3.1.1. | Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2016-01-01 |  |  |  |  | 43110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4575 | 6679 | 2. | 6681 | TPL-001-4 R4.3.1.2. | Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-01 |  |  |  |  | 431200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4575 | 6679 | 3. | 6682 | TPL-001-4 R4.3.1.3. | Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-01 |  |  |  |  | 431300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4575 | RP-2021-07-09-0000056 | 1. | 6685 | TPL-001-4 R4.4 .1. | Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2016-01-01 |  |  |  |  | 441000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4575 |  | 1. | 6673 | TPL-001-4 R4.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2016-01-01 |  | 2023-06-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4575 |  | 2. | 6677 | TPL-001-4 R4.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2016-01-01 |  | 2023-06-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4575 |  | 3. | 6678 | TPL-001-4 R4.3. | Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4575 |  | 4 . | RP-2021-07-09-0000056 | TPL-001-4 R4.4 . | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2016-01-01 |  | 2023-06-30 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4575 |  | 5 . | RP-2021-07-09-0000057 | TPL-001-4 R4.5 . | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2016-01-01 |  | 2023-06-30 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
366 | 4579 |  | 1. | 6688 | TPL-001-4 R8.1. | If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Planning Coordinator and Transmission Planner shall provide evidence, such as email notices, documentation of updated web pages, postal receipts showing recipient and date; or a demonstration of a public posting, that it has distributed its Planning Assessment results to adjacent Planning Coordinators and adjacent Transmission Planners within 90 days of having completed its Planning Assessment, and to any functional entity who has indicated a reliability need within 30 days of a written request and that the Planning Coordinator or Transmission Planner has provided a documented response to comments received on Planning Assessment results within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2016-01-01 |  | 2023-06-30 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4580 | 4584 | 1. | 4588 | TPL-001-3 R1.3.1. | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4580 | 4584 | 2. | 4591 | TPL-001-3 R1.3.2. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4580 | 4584 | 3. | 4594 | TPL-001-3 R1.3.3. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4580 | 4584 | 4. | 4589 | TPL-001-3 R1.3.4. | Have established normal (pre-contingency) operating procedures in place. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4580 | 4584 | 5. | 4590 | TPL-001-3 R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4580 | 4584 | 6. | 4587 | TPL-001-3 R1.3.6. | Be performed for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4580 | 4584 | 7. | 4593 | TPL-001-3 R1.3.7. | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4580 | 4584 | 8. | 4592 | TPL-001-3 R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4580 | 4584 | 9. | 4595 | TPL-001-3 R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4580 |  | 1. | 4586 | TPL-001-3 R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-1_R3. |  |  | 2014-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4580 |  | 2. | 4583 | TPL-001-3 R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4580 |  | 3. | 4584 | TPL-001-3 R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4580 |  | 4. | 4585 | TPL-001-3 R1.4. | Address any planned upgrades needed to meet the performance requirements of Category A. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4581 | 4596 | 1. | 4600 | TPL-001-3 R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4581 | 4596 | 2. | 4599 | TPL-001-3 R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4581 | 4596 | 3. | 4598 | TPL-001-3 R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4581 |  | 1. | 4596 | TPL-001-3 R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
367 | 4581 |  | 2. | 4597 | TPL-001-3 R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 | 4625 | 1. | 4632 | TPL-002-2b R1.3.1. | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 | 4625 | 10. | 4637 | TPL-002-2b R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 1310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 | 4625 | 11. | 4641 | TPL-002-2b R1.3.11. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 1311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 | 4625 | 12. | 4636 | TPL-002-2b R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 1312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 | 4625 | 2. | 4631 | TPL-002-2b R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 | 4625 | 3. | 4640 | TPL-002-2b R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 | 4625 | 4. | 4639 | TPL-002-2b R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 | 4625 | 5. | 4634 | TPL-002-2b R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 | 4625 | 6. | 4633 | TPL-002-2b R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 | 4625 | 7. | 4630 | TPL-002-2b R1.3.7. | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 | 4625 | 8. | 4635 | TPL-002-2b R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 | 4625 | 9. | 4638 | TPL-002-2b R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 |  | 1. | 4628 | TPL-002-2b R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 |  | 2. | 4626 | TPL-002-2b R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 |  | 3. | 4625 | TPL-002-2b R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories,, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 |  | 4. | 4627 | TPL-002-2b R1.4. | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4622 |  | 5. | 4629 | TPL-002-2b R1.5. | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4623 | 4642 | 1. | 4646 | TPL-002-2b R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4623 | 4642 | 2. | 4645 | TPL-002-2b R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4623 | 4642 | 3. | 4644 | TPL-002-2b R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4623 |  | 1. | 4642 | TPL-002-2b R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
369 | 4623 |  | 2. | 4643 | TPL-002-2b R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
37 | 507 |  | 1. | 508 | EOP-002-2 R6.1. | Loading all available generating capacity. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
37 | 507 |  | 2. | 509 | EOP-002-2 R6.2. | Deploying all available operating reserve. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
37 | 507 |  | 3. | 510 | EOP-002-2 R6.3. | Interrupting interruptible load and exports. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
37 | 507 |  | 4. | 511 | EOP-002-2 R6.4. | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
37 | 507 |  | 5. | 512 | EOP-002-2 R6.5. | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
37 | 507 |  | 6. | 513 | EOP-002-2 R6.6. | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 660000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
37 | 514 |  | 1. | 515 | EOP-002-2 R7.1. | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
37 | 514 |  | 2. | 516 | EOP-002-2 R7.2. | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
37 | 518 |  | 1. | 519 | EOP-002-2 R9.1. | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  | LSE | [7 empty] | LSE | [14 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
37 | 518 |  | 2. | 520 | EOP-002-2 R9.2. | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
37 | 518 |  | 3. | 521 | EOP-002-2 R9.3. | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 930000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
37 | 518 |  | 4. | 522 | EOP-002-2 R9.4. | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-05-12 |  |  | 940000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 | 4650 | 1. | 4657 | TPL-003-2a R1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 | 4650 | 10. | 4662 | TPL-003-2a R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 1310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 | 4650 | 11. | 4666 | TPL-003-2a R1.3.11. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 1311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 | 4650 | 12. | 4661 | TPL-003-2a R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 1312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 | 4650 | 2. | 4656 | TPL-003-2a R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 | 4650 | 3. | 4665 | TPL-003-2a R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 | 4650 | 4. | 4664 | TPL-003-2a R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 | 4650 | 5. | 4659 | TPL-003-2a R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 | 4650 | 6. | 4658 | TPL-003-2a R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 | 4650 | 7. | 4655 | TPL-003-2a R1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 | 4650 | 8. | 4660 | TPL-003-2a R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 | 4650 | 9. | 4663 | TPL-003-2a R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 |  | 1. | 4653 | TPL-003-2a R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 |  | 2. | 4651 | TPL-003-2a R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 |  | 3. | 4650 | TPL-003-2a R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 |  | 4. | 4652 | TPL-003-2a R1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4647 |  | 5. | 4654 | TPL-003-2a R1.5. | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4648 | 4667 | 1. | 4671 | TPL-003-2a R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4648 | 4667 | 2. | 4670 | TPL-003-2a R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4648 | 4667 | 3. | 4669 | TPL-003-2a R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4648 |  | 1. | 4667 | TPL-003-2a R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
370 | 4648 |  | 2. | 4668 | TPL-003-2a R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
371 | 4672 | 4674 | 1. | 4679 | TPL-004-2 R1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
371 | 4672 | 4674 | 2. | 4682 | TPL-004-2 R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
371 | 4672 | 4674 | 3. | 4678 | TPL-004-2 R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
371 | 4672 | 4674 | 4. | 4686 | TPL-004-2 R1.3.4. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
371 | 4672 | 4674 | 5. | 4680 | TPL-004-2 R1.3.5. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
371 | 4672 | 4674 | 6. | 4681 | TPL-004-2 R1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
371 | 4672 | 4674 | 7. | 4684 | TPL-004-2 R1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
371 | 4672 | 4674 | 8. | 4683 | TPL-004-2 R1.3.8. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
371 | 4672 | 4674 | 9. | 4685 | TPL-004-2 R1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
371 | 4672 |  | 1. | 4676 | TPL-004-2 R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
371 | 4672 |  | 2. | 4675 | TPL-004-2 R1.2. | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
371 | 4672 |  | 3. | 4674 | TPL-004-2 R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
371 | 4672 |  | 4. | 4677 | TPL-004-2 R1.4. | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 | 4690 | 1. | 4697 | TPL-003-0b R1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 | 4690 | 10. | 4702 | TPL-003-0b R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 1310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 | 4690 | 11. | 4706 | TPL-003-0b R1.3.11. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 1311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 | 4690 | 12. | 4701 | TPL-003-0b R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 1312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 | 4690 | 2. | 4696 | TPL-003-0b R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 | 4690 | 3. | 4705 | TPL-003-0b R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 | 4690 | 4. | 4704 | TPL-003-0b R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 | 4690 | 5. | 4699 | TPL-003-0b R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 | 4690 | 6. | 4698 | TPL-003-0b R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 | 4690 | 7. | 4695 | TPL-003-0b R1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 | 4690 | 8. | 4700 | TPL-003-0b R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 | 4690 | 9. | 4703 | TPL-003-0b R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 |  | 1. | 4693 | TPL-003-0b R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 |  | 2. | 4691 | TPL-003-0b R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 |  | 3. | 4690 | TPL-003-0b R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 |  | 4. | 4692 | TPL-003-0b R1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4687 |  | 5. | 4694 | TPL-003-0b R1.5. | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4688 | 4707 | 1. | 4711 | TPL-003-0b R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4688 | 4707 | 2. | 4710 | TPL-003-0b R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4688 | 4707 | 3. | 4709 | TPL-003-0b R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4688 |  | 1. | 4707 | TPL-003-0b R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
372 | 4688 |  | 2. | 4708 | TPL-003-0b R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 | 4719 | 1. | 4728 | TPL-003-2b R1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 | 4719 | 10. | 4725 | TPL-003-2b R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 1310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 | 4719 | 11. | 4723 | TPL-003-2b R1.3.11. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 1311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 | 4719 | 12. | 4724 | TPL-003-2b R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 1312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 | 4719 | 2. | 4729 | TPL-003-2b R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 | 4719 | 3. | 4726 | TPL-003-2b R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 | 4719 | 4. | 4727 | TPL-003-2b R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 | 4719 | 5. | 4732 | TPL-003-2b R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 | 4719 | 6. | 4733 | TPL-003-2b R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 | 4719 | 7. | 4731 | TPL-003-2b R1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 | 4719 | 8. | 4730 | TPL-003-2b R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 | 4719 | 9. | 4722 | TPL-003-2b R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 |  | 1. | 4717 | TPL-003-2b R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 |  | 2. | 4716 | TPL-003-2b R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 |  | 3. | 4719 | TPL-003-2b R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 |  | 4. | 4718 | TPL-003-2b R1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4714 |  | 5. | 4715 | TPL-003-2b R1.5. | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4713 | 4720 | 1. | 4735 | TPL-003-2b R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4713 | 4720 | 2. | 4734 | TPL-003-2b R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4713 | 4720 | 3. | 4736 | TPL-003-2b R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4713 |  | 1. | 4720 | TPL-003-2b R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
373 | 4713 |  | 2. | 4721 | TPL-003-2b R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
374 | 4737 | 4739 | 1. | 4744 | TPL-004-0a R1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
374 | 4737 | 4739 | 2. | 4747 | TPL-004-0a R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
374 | 4737 | 4739 | 3. | 4743 | TPL-004-0a R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
374 | 4737 | 4739 | 4. | 4751 | TPL-004-0a R1.3.4. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
374 | 4737 | 4739 | 5. | 4745 | TPL-004-0a R1.3.5. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
374 | 4737 | 4739 | 6. | 4746 | TPL-004-0a R1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
374 | 4737 | 4739 | 7. | 4749 | TPL-004-0a R1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
374 | 4737 | 4739 | 8. | 4748 | TPL-004-0a R1.3.8. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
374 | 4737 | 4739 | 9. | 4750 | TPL-004-0a R1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
374 | 4737 |  | 1. | 4741 | TPL-004-0a R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
374 | 4737 |  | 2. | 4740 | TPL-004-0a R1.2. | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
374 | 4737 |  | 3. | 4739 | TPL-004-0a R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
374 | 4737 |  | 4. | 4742 | TPL-004-0a R1.4. | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
375 | 4753 | 4756 | 1. | 4763 | TPL-004-2a R1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
375 | 4753 | 4756 | 2. | 4762 | TPL-004-2a R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
375 | 4753 | 4756 | 3. | 4764 | TPL-004-2a R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
375 | 4753 | 4756 | 4. | 4760 | TPL-004-2a R1.3.4. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
375 | 4753 | 4756 | 5. | 4766 | TPL-004-2a R1.3.5. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
375 | 4753 | 4756 | 6. | 4765 | TPL-004-2a R1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
375 | 4753 | 4756 | 7. | 4758 | TPL-004-2a R1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
375 | 4753 | 4756 | 8. | 4759 | TPL-004-2a R1.3.8. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
375 | 4753 | 4756 | 9. | 4761 | TPL-004-2a R1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
375 | 4753 |  | 1. | 4754 | TPL-004-2a R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
375 | 4753 |  | 2. | 4757 | TPL-004-2a R1.2. | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
375 | 4753 |  | 3. | 4756 | TPL-004-2a R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
375 | 4753 |  | 4. | 4755 | TPL-004-2a R1.4. | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
376 | 4769 |  | 1. | 6958 | PRC-024-1 R3.1. | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. |  | GO |  |  |  |  | GO | [17 empty] | 2014-05-27 |  | 2016-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
38 | 528 |  | 1. | 529 | EOP-002-2.1 R6.1. | Loading all available generating capacity. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
38 | 528 |  | 2. | 530 | EOP-002-2.1 R6.2. | Deploying all available operating reserve. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
38 | 528 |  | 3. | 531 | EOP-002-2.1 R6.3. | Interrupting interruptible load and exports. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
38 | 528 |  | 4. | 532 | EOP-002-2.1 R6.4. | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
38 | 528 |  | 5. | 533 | EOP-002-2.1 R6.5. | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
38 | 528 |  | 6. | 534 | EOP-002-2.1 R6.6. | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | 660000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
38 | 535 |  | 1. | 536 | EOP-002-2.1 R7.1. | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
38 | 535 |  | 2. | 537 | EOP-002-2.1 R7.2. | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
38 | 539 |  | 1. | 540 | EOP-002-2.1 R9.1. | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  | LSE | [7 empty] | LSE | [14 empty] | 2009-05-13 |  | 2011-09-30 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
38 | 539 |  | 2. | 541 | EOP-002-2.1 R9.2. | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  | RC | [11 empty] | RC | [10 empty] | 2009-05-13 |  | 2011-09-30 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
38 | 539 |  | 3. | 542 | EOP-002-2.1 R9.3. | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2009-05-13 |  | 2011-09-30 |  |  | 930000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
38 | 539 |  | 4. | 543 | EOP-002-2.1 R9.4. | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2009-05-13 |  | 2011-09-30 |  |  | 940000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
380 | 4785 |  | 1. | 6368 | BAL-001-TRE-1 R2.1. | The performance of a combined cycle facility will be determined using an expected performance droop of 5.78%. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | The BA shall have evidence it calculated and reported the rolling average initial and sustained Primary Frequency Response performance of each generating unit/generating facility monthly as required in Requirement R2. | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. | 210000000 | TXRE-US |  |  |  |  | TXRE-US
380 | 4785 |  | 2. | 6369 | BAL-001-TRE-1 R2.2. | The calculation results shall be submitted to the Compliance Enforcement Authority and made available to the GO by the end of the month in which they were completed. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | The BA shall have evidence it calculated and reported the rolling average initial and sustained Primary Frequency Response performance of each generating unit/generating facility monthly as required in Requirement R2. | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. | 220000000 | TXRE-US |  |  |  |  | TXRE-US
380 | 4785 |  | 3. | 6370 | BAL-001-TRE-1 R2.3. | If a generating unit/generating facility has not participated in a minimum of (8) eight FMEs in a 12-month period, its performance shall be based on a rolling eight FME average response. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | The BA shall have evidence it calculated and reported the rolling average initial and sustained Primary Frequency Response performance of each generating unit/generating facility monthly as required in Requirement R2. | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. | 230000000 | TXRE-US |  |  |  |  | TXRE-US
380 | 4789 |  | 1. | 6465 | BAL-001-TRE-1 R6.1. | Limit Governor deadbands within those listed in Table 6.1, unless directed otherwise by the BA. (see standard for table) | See Standard for calculations | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Each GO shall have evidence that it set its Governor parameters in accordance with Requirement R6. Examples of evidence include but are not limited to: • Governor test reports • Governor setting sheets • Performance monitoring reports | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. | 610000000 | TXRE-US |  |  |  |  | TXRE-US
380 | 4789 |  | 2. | 6466 | BAL-001-TRE-1 R6.2. | Limit Governor droop settings such that they do not exceed those listed in Table 6.2, unless directed otherwise by the BA. (see standard for table) | See Standard for table | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Each GO shall have evidence that it set its Governor parameters in accordance with Requirement R6. Examples of evidence include but are not limited to: • Governor test reports • Governor setting sheets • Performance monitoring reports | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. | 620000000 | TXRE-US |  |  |  |  | TXRE-US
380 | 4789 |  | 3. | 6467 | BAL-001-TRE-1 R6.3. | For digital and electronic Governors, once frequency deviation has exceeded the Governor deadband from 60.000 Hz, the Governor setting shall follow the slope derived from the formula below.(see standard for formula) where MWGCS is the maximum megawatt control range of the Governor control system. For mechanical Governors, droop will be proportional from the deadband by design. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Each GO shall have evidence that it set its Governor parameters in accordance with Requirement R6. Examples of evidence include but are not limited to: • Governor test reports • Governor setting sheets • Performance monitoring reports | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. | 630000000 | TXRE-US |  |  |  |  | TXRE-US
380 | 4792 |  | 1. | 6468 | BAL-001-TRE-1 R9.1. | The initial Primary Frequency Response performance shall be the ratio of the Actual Primary Frequency Response to the Expected Primary Frequency Response during the initial measurement period following the FME. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Each GO shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of initial Primary Frequency Response performance level of at least 0.75 as described in Requirement R9. Each GO shall have documented evidence of any FMEs where the generating unit performance should be excluded from the rolling average calculation. | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. | 910000000 | TXRE-US |  |  |  |  | TXRE-US
380 | 4792 |  | 2. | 6469 | BAL-001-TRE-1 R9.2. | If a generating unit/generating facility has not participated in a minimum of eight FMEs in a 12-month period, performance shall be based on a rolling eight-FME average. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Each GO shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of initial Primary Frequency Response performance level of at least 0.75 as described in Requirement R9. Each GO shall have documented evidence of any FMEs where the generating unit performance should be excluded from the rolling average calculation. | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. | 920000000 | TXRE-US |  |  |  |  | TXRE-US
380 | 4793 |  | 1. | 6472 | BAL-001-TRE-1 R10.1. | The sustained Primary Frequency Response performance shall be the ratio of the Actual Primary Frequency Response to the Expected Primary Frequency Response during the sustained measurement period following the FME. |  | GO |  |  |  |  | GO | [17 empty] | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. | 101000000 | TXRE-US |  |  |  |  | TXRE-US
380 | 4793 |  | 2. | 6473 | BAL-001-TRE-1 R10.2. | If a generating unit/generating facility has not participated in a minimum of eight FMEs in a 12-month period, performance shall be based on a rolling eight- FME average. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Each GO shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of sustained Primary Frequency Response performance of at least 0.75 as described in Requirement R10. Each GO shall have documented evidence of any Frequency Measurable Events where generating unit performance should be excluded from the rolling average calculation. | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. | 102000000 | TXRE-US |  |  |  |  | TXRE-US
380 | 4793 |  | 3. | 6474 | BAL-001-TRE-1 R10.3. | A generating unit/generating facility’s sustained Primary Frequency Response performance during an FME may be excluded from the rolling average calculation due to a legitimate operating condition that prevented normal Primary Frequency Response performance. Examples of legitimate operating conditions that may support exclusion of FMEs include: Operation at or near auxiliary equipment operating limits (such as boiler feed pumps, condensate pumps, pulverizers, and forced draft fans); Data telemetry failure. The Compliance Enforcement Authority may request raw data from the GO as a substitute. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [15 empty] | Each GO shall have evidence that each of its generating units/generating facilities achieved a minimum rolling average of sustained Primary Frequency Response performance of at least 0.75 as described in Requirement R10. Each GO shall have documented evidence of any Frequency Measurable Events where generating unit performance should be excluded from the rolling average calculation. | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. | 103000000 | TXRE-US |  |  |  |  | TXRE-US
381 | 4797 | 4798 | 1. | 4799 | BAL-006-0 R4.1.1. | The hourly values of Net Interchange Schedule. |  | BA | BA | [23 empty] | 2006-05-01 |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
381 | 4797 | 4798 | 2. | 4800 | BAL-006-0 R4.1.2. | The hourly integrated megawatt-hour values of Net Actual Interchange. |  | BA | BA | [23 empty] | 2006-05-01 |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
381 | 4797 |  | 1. | 4798 | BAL-006-0 R4.1. | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: |  | BA | BA | [23 empty] | 2006-05-01 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
381 | 4797 |  | 2. | 4801 | BAL-006-0 R4.2. | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and OffPeak hours of the month. |  | BA | BA | [23 empty] | 2006-05-01 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
381 | 4797 |  | 3. | 4802 | BAL-006-0 R4.3. | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). |  | BA | BA | [23 empty] | 2006-05-01 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
383 | 4808 |  | 1. | 4809 | COM-001-0 R1.1. | Internally. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
383 | 4808 |  | 2. | 4810 | COM-001-0 R1.2. | Between the Reliability Coordinator and its Transmission Operators and Balancing Authorities. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
383 | 4808 |  | 3. | 4811 | COM-001-0 R1.3. | With other Reliability Coordinators, Transmission Operators, and Balancing Authorities as necessary to maintain reliability. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
383 | 4808 |  | 4. | 4812 | COM-001-0 R1.4. | Where applicable, these facilities shall be redundant and diversely routed. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
384 | 4819 |  | 1. | 4820 | COM-002-0 R2.1. | The Balancing Authority is unable to purchase capacity or energy to meet its demand and reserve requirements on a day-ahead or hour-by-hour basis. |  | BA | BA | [23 empty] | 2006-11-01 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
384 | 4819 |  | 2. | 4821 | COM-002-0 R2.2. | The Transmission Operator recognizes that potential or actual line loadings, and voltage or reactive levels are such that a single Contingency could threaten the reliability of the Interconnection. (Once a single Contingency occurs, the Transmission Operator must prepare for the next Contingency.) |  | TOP | [18 empty] | TOP | [5 empty] | 2006-11-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
384 | 4819 |  | 3. | 4822 | COM-002-0 R2.3. | The Transmission Operator anticipates initiating a 3% or greater voltage reduction, public appeals for load curtailments, or firm load shedding for other than local problems. |  | TOP | [18 empty] | TOP | [5 empty] | 2006-11-01 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
385 | 4824 |  | 1. | 4825 | COM-002-1 R1.1. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators through predetermined communication paths of any condition that could threaten the reliability of its area or when firm load shedding is anticipated. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
386 | 4837 |  | 1. | 4838 | EOP-002-0 R7.1. | Loading all available generating capacity. |  | BA | BA | [23 empty] | 2006-11-01 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
386 | 4837 |  | 2. | 4839 | EOP-002-0 R7.2. | Deploying all available operating reserve. |  | BA | BA | [23 empty] | 2006-11-01 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
386 | 4837 |  | 3. | 4840 | EOP-002-0 R7.3. | Interrupting interruptible load and exports. |  | BA | BA | [23 empty] | 2006-11-01 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
386 | 4837 |  | 4. | 4841 | EOP-002-0 R7.4. | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [23 empty] | 2006-11-01 |  |  | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
386 | 4837 |  | 5. | 4842 | EOP-002-0 R7.5. | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [23 empty] | 2006-11-01 |  |  | 750000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
386 | 4837 |  | 6. | 4843 | EOP-002-0 R7.6. | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  | BA | BA | [23 empty] | 2006-11-01 |  |  | 760000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
386 | 4844 |  | 1. | 4845 | EOP-002-0 R8.1. | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [23 empty] | 2006-11-01 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
386 | 4844 |  | 2. | 4846 | EOP-002-0 R8.2. | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
386 | 4828 |  | 1. | 4829 | EOP-002-0 R10.1. | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
386 | 4828 |  | 2. | 4830 | EOP-002-0 R10.2. | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
386 | 4828 |  | 3. | 4831 | EOP-002-0 R10.3. | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
386 | 4828 |  | 4. | 4848 | EOP-002-0 R10.4. | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
387 | 4854 |  | 1. | 4855 | EOP-002-1 R6.1. | Loading all available generating capacity. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
387 | 4854 |  | 2. | 4856 | EOP-002-1 R6.2. | Deploying all available operating reserve. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
387 | 4854 |  | 3. | 4857 | EOP-002-1 R6.3. | Interrupting interruptible load and exports. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
387 | 4854 |  | 4. | 4858 | EOP-002-1 R6.4. | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
387 | 4854 |  | 5. | 4859 | EOP-002-1 R6.5. | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
387 | 4854 |  | 6. | 4860 | EOP-002-1 R6.6. | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 660000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
387 | 4861 |  | 1. | 4862 | EOP-002-1 R7.1. | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
387 | 4861 |  | 2. | 4863 | EOP-002-1 R7.2. | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  | BA, RC | BA | [10 empty] | RC | [12 empty] | 2007-01-01 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
387 | 4865 |  | 1. | 4866 | EOP-002-1 R9.1. | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  | RC | [11 empty] | RC | [12 empty] | 2007-01-01 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
387 | 4865 |  | 2. | 4867 | EOP-002-1 R9.2. | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  | RC | [11 empty] | RC | [12 empty] | 2007-01-01 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
387 | 4865 |  | 3. | 4868 | EOP-002-1 R9.3. | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [12 empty] | 2007-01-01 |  |  | 930000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
387 | 4865 |  | 4. | 4869 | EOP-002-1 R9.4. | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [12 empty] | 2007-01-01 |  |  | 940000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
389 | 4886 | 4891 | 1. | 4892 | EOP-005-0 R9.5.1. | Voltage, frequency, and phase angle permit. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  | 951000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
389 | 4886 | 4891 | 2. | 4893 | EOP-005-0 R9.5.2. | The size of the area being reconnected and the capacity of the transmission lines effecting the reconnection and the number of synchronizing points across the system are considered. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  | 952000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
389 | 4886 | 4891 | 3. | 4894 | EOP-005-0 R9.5.3. | Reliability Coordinator(s) and adjacent areas are notified and Reliability Coordinator approval is given. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  | 953000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
389 | 4886 | 4891 | 4. | 4895 | EOP-005-0 R9.5.4. | Load is shed in neighboring areas, if required, to permit successful interconnected system restoration. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  | 954000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
389 | 4886 |  | 1. | 4887 | EOP-005-0 R9.1. | The affected Transmission Operators and Balancing Authorities shall work in conjunction with their Reliability Coordinator(s) to determine the extent and condition of the isolated area(s). |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2007-05-02 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
389 | 4886 |  | 2. | 4888 | EOP-005-0 R9.2. | The affected Transmission Operators and Balancing Authorities shall take the necessary actions to restore Bulk Electric System frequency to normal, including adjusting generation, placing additional generators online, or load shedding. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2007-05-02 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
389 | 4886 |  | 3. | 4889 | EOP-005-0 R9.3. | The affected Balancing Authorities, working with their Reliability Coordinator(s), shall immediately review the Interchange Schedules between those Balancing Authority Areas or fragments of those Balancing Authority Areas within the separated area and make adjustments as needed to facilitate the restoration. The affected Balancing Authorities shall make all attempts to maintain the adjusted Interchange Schedules, whether generation control is manual or automatic. |  | BA | BA | [23 empty] | 2007-05-02 |  |  | 930000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
389 | 4886 |  | 4. | 4890 | EOP-005-0 R9.4. | The affected Transmission Operators shall give high priority to restoration of off-site power to nuclear stations. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  | 940000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
389 | 4886 |  | 5. | 4891 | EOP-005-0 R9.5. | The affected Transmission Operators may resynchronize the isolated area(s) with the surrounding area(s) when the following conditions are met: |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  | 950000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
391 | 4902 |  | 1. | 4903 | FAC-003-0 R1.1. | Inspection requirements. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-04-07 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
391 | 4902 |  | 2. | 4904 | FAC-003-0 R1.2. | Trimming clearances. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-04-07 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
391 | 4902 |  | 3. | 4905 | FAC-003-0 R1.3. | Annual work plan. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-04-07 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
392 | 4907 | 4908 | 1. | 4909 | FAC-004-0 R1.1.1. | Transmission circuits. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-08-01 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
392 | 4907 | 4908 | 2. | 4910 | FAC-004-0 R1.1.2. | Transformers. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-08-01 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
392 | 4907 | 4908 | 3. | 4911 | FAC-004-0 R1.1.3. | Series and shunt reactive elements |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-08-01 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
392 | 4907 | 4908 | 4. | 4912 | FAC-004-0 R1.1.4. | Terminal equipment (e.g., switches, breakers, current transformers, etc) |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-08-01 |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
392 | 4907 | 4908 | 5. | 4913 | FAC-004-0 R1.1.5. | VAR compensators. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-08-01 |  |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
392 | 4907 | 4908 | 6. | 4914 | FAC-004-0 R1.1.6. | High voltage direct current converters. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-08-01 |  |  | 116000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
392 | 4907 | 4908 | 7. | 4915 | FAC-004-0 R1.1.7. | Any other device listed as a Limiting Element |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-08-01 |  |  | 117000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
392 | 4907 |  | 1. | 4908 | FAC-004-0 R1.1. | The methodology(ies) used to determine equipment and Facility Rating of the items listed for both normal and emergency conditions: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-08-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
392 | 4907 |  | 2. | 4916 | FAC-004-0 R1.2. | The Rating of a facility shall not exceed the Rating(s) of the most Limiting Element(s) in the circuit, including terminal connections and associated equipment. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-08-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
392 | 4907 |  | 3. | 4917 | FAC-004-0 R1.3. | In cases where protection systems and control settings constitute a loading limit on a facility, this limit shall become the Rating for that facility. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-08-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
392 | 4907 |  | 4. | 4918 | FAC-004-0 R1.4. | Ratings of jointly-owned and jointly-operated facilities shall be coordinated among the joint owners and joint operators resulting in a single set of Ratings. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-08-01 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
392 | 4907 |  | 5. | 4919 | FAC-004-0 R1.5. | The documentation shall identify the assumptions used to determine each of the equipment and Facility Ratings, including references to industry Rating practices and standards (e.g., ANSI, IEEE, etc.). Seasonal Ratings and variations in assumptions shall be included. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-08-01 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
393 | 4921 |  | 1. | 4922 | FAC-005-0 R1.1. | The Ratings shall be consistent with the entity’s methodology(ies) for determining Facility Ratings and shall be updated as facility changes occur. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO | [6 empty] | 2006-10-07 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
394 | 4924 |  | 1. | 4925 | INT-001-0 R1.1. | All Interchange Transactions that are between Balancing Authority Areas |  | BA, PSE | BA | [9 empty] | PSE | [13 empty] | 2007-01-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
394 | 4924 |  | 2. | 4926 | INT-001-0 R1.2. | All transfers that are entirely within a Balancing Authority Area using Point-to-Point Transmission Service (including all grandfathered and “non-Order 888” Point-to-Point Transmission Service). |  | BA, PSE | BA | [9 empty] | PSE | [13 empty] | 2007-01-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
394 | 4924 |  | 3. | 4927 | INT-001-0 R1.3. | All Dynamic Schedules at the expected average MW profile for each hour. |  | BA, PSE | BA | [9 empty] | PSE | [13 empty] | 2007-01-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
394 | 4928 |  | 1. | 4929 | INT-001-0 R2.1. | If a Purchasing-Selling Entity is not involved in the Transaction, such as delivery from a jointly owned generator. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
394 | 4928 |  | 2. | 4930 | INT-001-0 R2.2. | To replace unexpected generation loss, such as through prearranged reserve sharing agreements or other arrangements. If the duration of the Emergency Transaction to replace the generation loss is less than 60 minutes, then the Transaction shall be exempt from Tagging. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
394 | 4928 |  | 3. | 4931 | INT-001-0 R2.3. | All bilateral inadvertent interchange payback. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
395 | 4935 |  | 1. | 4936 | INT-001-1 R1.1. | All Dynamic Schedules at the expected average MW profile for each hour. |  | PSE | [10 empty] | PSE | [13 empty] | 2006-11-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
395 | 4937 |  | 1. | 4938 | INT-001-1 R2.1. | If a Purchasing-Selling Entity is not involved in the Interchange, such as delivery from a jointly owned generator. |  | BA, PSE | BA | [9 empty] | PSE | [13 empty] | 2006-11-01 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
395 | 4937 |  | 2. | 4939 | INT-001-1 R2.2. | For each bilateral Inadvertent Interchange payback. |  | BA | BA | [23 empty] | 2006-11-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
396 | 4940 |  | 1. | 4941 | INT-002-0 R1.1. | Sink and Source Balancing Authority for the Transaction. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
396 | 4940 |  | 2. | 4942 | INT-002-0 R1.2. | Intermediate Balancing Authorities on the Schedule Path. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
396 | 4940 |  | 3. | 4943 | INT-002-0 R1.3. | Transmission Service Provider(s) on the Schedule Path |  | BA, TSP | BA | [19 empty] | TSP |  |  |  | 2007-01-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
396 | 4940 |  | 4. | 4944 | INT-002-0 R1.4. | Reliability analysis services (IDC or other regional reliability tools). |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
396 | 4940 |  | 5. | 4945 | INT-002-0 R1.5. | Transmission Operators and Reliability Coordinators who may receive the information through Reliability analysis services. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
396 | 4946 |  | 1. | 4947 | INT-002-0 R2.1. | Valid OASIS reservation number or transmission contract identifier. |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
396 | 4946 |  | 2. | 4948 | INT-002-0 R2.2. | Transmission priority matches reservation |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
396 | 4946 |  | 3. | 4949 | INT-002-0 R2.3. | Energy profile fits within OASIS reservation. |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
396 | 4946 |  | 4. | 4950 | INT-002-0 R2.4. | OASIS reservation accommodates all Interchange Transactions. |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
396 | 4946 |  | 5. | 4951 | INT-002-0 R2.5. | Connectivity of adjacent Transmission Service Providers. |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
396 | 4946 |  | 6. | 4952 | INT-002-0 R2.6. | Loss accounting. |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
396 | 4953 |  | 1. | 4954 | INT-002-0 R3.1. | Transaction start and end time. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
396 | 4953 |  | 2. | 4955 | INT-002-0 R3.2. | Energy profile (ability to support the magnitude of the transaction). |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
396 | 4953 |  | 3. | 4956 | INT-002-0 R3.3. | Ramp (ability of generation maneuverability to accommodate). |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
396 | 4953 |  | 4. | 4957 | INT-002-0 R3.4. | Scheduling path (proper connectivity of adjacent Balancing Authorities). |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
397 | 4960 | 4961 | 1. | 4962 | INT-003-0 R1.1.1. | Interchange Schedule start and end time. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
397 | 4960 | 4961 | 2. | 4963 | INT-003-0 R1.1.2. | Energy profile. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
397 | 4960 | 4961 | 3. | 4964 | INT-003-0 R1.1.3. | Ramp start time and duration (Balancing Authorities shall use the Ramp duration established for their Interconnection unless they agree to an alternative Ramp duration.) Default Ramps durations are as follows: • Default Ramp duration for the Eastern Interconnection shall be 10 minutes equally across the Interchange Schedule start and end times. • Default Ramp duration for the Western Interconnection shall be 20 minutes equally across the Interchange Schedule start and end times. • Ramp durations for Interchange Schedules implemented for compliance with NERC’s Disturbance Control Standard (recovery from a disturbance condition) and Interchange Transaction curtailment in response to line loading relief procedures may be shorter than the above defaults, but must be identical for the Sending Balancing Authority and Receiving Balancing Authority. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
397 | 4960 |  | 1. | 4961 | INT-003-0 R1.1. | The Sending Balancing Authority and Receiving Balancing Authority shall agree on: |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
397 | 4960 |  | 2. | 4965 | INT-003-0 R1.2. | If a high voltage direct current (HVDC) tie is on the Scheduling Path, then the Sending Balancing Authorities and Receiving Balancing Authorities shall coordinate the Interchange Schedule with the Transmission Operator of the HVDC tie. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
397 | 4960 |  | 3. | 4966 | INT-003-0 R1.3. | Balancing Authorities that implement Interchange Schedules that cross an Interconnection boundary shall use the same start time and Ramp durations. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
397 | 4971 |  | 1. | 4972 | INT-003-0 R6.1. | The total capacity of both the owned and arranged-for transmission facilities in service for any Transmission Service Provider along the path, or |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
397 | 4971 |  | 2. | 4973 | INT-003-0 R6.2. | The established network Total Transfer Capability between Balancing Authorities, which considers other transmission facilities available to them under specific arrangements, and the overall physical constraints of the transmission network. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
398 | 4974 | 4975 | 1. | 4976 | INT-003-1 R1.1.1. | Interchange Schedule start and end time. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
398 | 4974 | 4975 | 2. | 4977 | INT-003-1 R1.1.2. | Energy profile. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
398 | 4974 |  | 1. | 4975 | INT-003-1 R1.1. | The Sending Balancing Authority and Receiving Balancing Authority shall agree on Interchange as received from the Interchange Authority, including: |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
398 | 4974 |  | 2. | 4978 | INT-003-1 R1.2. | If a high voltage direct current (HVDC) tie is on the Scheduling Path, then the Sending Balancing Authorities and Receiving Balancing Authorities shall coordinate the Interchange Schedule with the Transmission Operator of the HVDC tie. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
399 | 4979 |  | 1. | 4980 | INT-004-0 R1.1. | Transmission Loading Relief procedure curtailment — Eastern Interconnection. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
399 | 4979 |  | 2. | 4981 | INT-004-0 R1.2. | Interconnection, regional, or local overload relief or congestion management procedures. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
399 | 4979 |  | 3. | 4982 | INT-004-0 R1.3. | SOL or IROL potential or actual limit violation. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
399 | 4979 |  | 4. | 4983 | INT-004-0 R1.4. | Loss of generation. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
399 | 4979 |  | 5. | 4984 | INT-004-0 R1.5. | Loss of Load. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
399 | 4985 |  | 1. | 4986 | INT-004-0 R2.1. | When a loss of generation necessitates curtailing Interchange Transactions, the Source Balancing Authority shall coordinate the modifications to the appropriate tags. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
399 | 4985 |  | 2. | 4987 | INT-004-0 R2.2. | When a loss of Load necessitates curtailing Interchange Transactions, the Sink Balancing Authority shall coordinate the modifications to the appropriate tags. |  | BA | BA | [23 empty] | 2007-01-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
399 | 4990 |  | 1. | 4991 | INT-004-0 R5.1. | The average energy profile in an hour is greater than 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +10%. |  | PSE | [10 empty] | PSE | [13 empty] | 2007-01-01 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
399 | 4990 |  | 2. | 4992 | INT-004-0 R5.2. | The average energy profile in an hour is less than or equal to 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +25 megawatt-hours. |  | PSE | [10 empty] | PSE | [13 empty] | 2007-01-01 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
399 | 4990 |  | 3. | 4993 | INT-004-0 R5.3. | A Reliability Coordinator or Transmission Operator determines the deviation, regardless of magnitude, to be a reliability concern and notifies the Purchasing-Selling Entity of that determination and the reasons. |  | PSE, RC, TOP | [10 empty] | PSE | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
40 | 554 |  | 1. | 555 | EOP-004-1 R3.1. | The affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load-Serving Entity shall submit within 24 hours of the disturbance or unusual occurrence either a copy of the report submitted to DOE, or, if no DOE report is required, a copy of the NERC Interconnection Reliability Operating Limit and Preliminary Disturbance Report form. Events that are not identified until some time after they occur shall be reported within 24 hours of being recognized. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-12-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
40 | 554 |  | 2. | 556 | EOP-004-1 R3.2. | Applicable reporting forms are provided in Attachments 1-EOP-004 and 2-EOP-004. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-12-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
40 | 554 |  | 3. | 557 | EOP-004-1 R3.3. | Under certain adverse conditions, e.g., severe weather, it may not be possible to assess the damage caused by a disturbance and issue a written Interconnection Reliability Operating Limit and Preliminary Disturbance Report within 24 hours. In such cases, the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity shall promptly notify its Regional Reliability Organization(s) and NERC, and verbally provide as much information as is available at that time. The affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity shall then provide timely, periodic verbal updates until adequate information is available to issue a written Preliminary Disturbance Report. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-12-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
40 | 554 |  | 4. | 558 | EOP-004-1 R3.4. | If, in the judgment of the Regional Reliability Organization, after consultation with the Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity in which a disturbance occurred, a final report is required, the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity shall prepare this report within 60 days. As a minimum, the final report shall have a discussion of the events and its cause, the conclusions reached, and recommendations to prevent recurrence of this type of event. The report shall be subject to Regional Reliability Organization approval. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-12-31 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
405 | 5025 |  | 1. | 5026 | IRO-005-0 R1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
405 | 5025 |  | 10. | 5027 | IRO-005-0 R1.10. | Contingency events. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
405 | 5025 |  | 2. | 5028 | IRO-005-0 R1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
405 | 5025 |  | 3. | 5029 | IRO-005-0 R1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
405 | 5025 |  | 4. | 5030 | IRO-005-0 R1.4. | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
405 | 5025 |  | 5. | 5031 | IRO-005-0 R1.5. | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
405 | 5025 |  | 6. | 5032 | IRO-005-0 R1.6. | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
405 | 5025 |  | 7. | 5033 | IRO-005-0 R1.7. | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
405 | 5025 |  | 8. | 5034 | IRO-005-0 R1.8. | Planned generation dispatches. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
405 | 5025 |  | 9. | 5035 | IRO-005-0 R1.9. | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
406 | 5053 |  | 1. | 5054 | IRO-006-0 R2.1. | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection is provided in Attachment 1-IRO-006-0. |  | RC | [11 empty] | RC | [12 empty] | 2005-08-08 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
406 | 5053 |  | 2. | 5055 | IRO-006-0 R2.2. | The equivalent Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is the “WSCC Unscheduled Flow Mitigation Plan,” provided at: http://www.wecc.biz/documents/library/UFAS/UFAS_mitigation_plan_rev_2001- clean_8-8-03.pdf. |  | RC | [11 empty] | RC | [12 empty] | 2005-08-08 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
406 | 5053 |  | 3. | 5056 | IRO-006-0 R2.3. | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: http://www.ercot.com/tac/retailisoadhoccommittee/protocols/keydocs/draftercotprotoc ols.htm. |  | RC | [11 empty] | RC | [12 empty] | 2005-08-08 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
407 | 5062 |  | 1. | 5063 | IRO-006-1 R2.1. | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection is provided in Attachment 1-IRO-006-0. |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
407 | 5062 |  | 2. | 5064 | IRO-006-1 R2.2. | The equivalent Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is the “WSCC Unscheduled Flow Mitigation Plan,” provided at: http://www.wecc.biz/documents/library/UFAS/UFAS_mitigation_plan_rev_2001- clean_8-8-03.pdf. |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
407 | 5062 |  | 3. | 5065 | IRO-006-1 R2.3. | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: http://www.ercot.com/tac/retailisoadhoccommittee/protocols/keydocs/draftercotprotoc ols.htm. |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
408 | 5071 |  | 1. | 5072 | IRO-006-2 R2.1. | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection is provided in Attachment 1-IRO-006-0. |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
408 | 5071 |  | 2. | 5073 | IRO-006-2 R2.2. | The equivalent Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is the “WSCC Unscheduled Flow Mitigation Plan,” provided at: http://www.wecc.biz/documents/library/UFAS/UFAS_mitigation_plan_rev_2001 -clean_8-8-03.pdf. |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
408 | 5071 |  | 3. | 5074 | IRO-006-2 R2.3. | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: http://www.ercot.com/tac/retailisoadhoccommittee/protocols/keydocs/draftercotp rotocols.htm. |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
409 | 5079 | 5080 | 1. | 5081 | MOD-013-0 R1.1.1. | Estimated or typical manufacturer’s dynamics data, based on units of similar design and characteristics, may be submitted when unit-specific dynamics data cannot be obtained. In no case shall other than unit-specific data be reported for generator units installed after 1990. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
409 | 5079 | 5080 | 2. | 5082 | MOD-013-0 R1.1.2. | The Interconnection-wide requirements shall specify unit size thresholds for permitting: − The use of non-detailed vs. detailed models, − The netting of small generating units with bus load, and − The combining of multiple generating units at one plant. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
409 | 5079 |  | 1. | 5080 | MOD-013-0 R1.1. | Unit-specific dynamics data shall be reported for generators and synchronous condensers (including, as appropriate to the model, items such as inertia constant, damping coefficient, saturation parameters, and direct and quadrature axes reactances and time constants), excitation systems, voltage regulators, turbine-governor systems, power system stabilizers, and other associated generation equipment. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
409 | 5079 |  | 2. | 5083 | MOD-013-0 R1.2. | Device specific dynamics data shall be reported for dynamic devices, including, among others, static VAR controllers, high voltage direct current systems, flexible AC transmission systems, and static compensators. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
409 | 5079 |  | 3. | 5084 | MOD-013-0 R1.3. | Dynamics data representing electrical demand characteristics as a function of frequency and voltage. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
409 | 5079 |  | 4. | 5085 | MOD-013-0 R1.4. | Dynamics data shall be consistent with the reported steady-state (power flow) data supplied per Reliability Standard MOD-010-0_R1. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
41 | 562 |  | 1. | 563 | EOP-005-1 R10.1. | The Transmission Operator shall perform this simulation or testing at least once every five years. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
41 | 564 | 569 | 1 | RP-2021-06-15-0000028 | EOP-005-1 R11.5.1 | Voltage, frequency, and phase angle permit. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 1151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
41 | 564 | 569 | 2. | 571 | EOP-005-1 R11.5.2. | The size of the area being reconnected and the capacity of the transmission lines effecting the reconnection and the number of synchronizing points across the system are considered. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 115200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
41 | 564 | 569 | 3. | 572 | EOP-005-1 R11.5.3. | Reliability Coordinator(s) and adjacent areas are notified and Reliability Coordinator approval is given. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 1153000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
41 | 564 | 569 | 4. | 573 | EOP-005-1 R11.5.4. | Load is shed in neighboring areas, if required, to permit successful interconnected system restoration. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 1154000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
41 | 564 |  | 1. | 565 | EOP-005-1 R11.1. | The affected Transmission Operators and Balancing Authorities shall work in conjunction with their Reliability Coordinator(s) to determine the extent and condition of the isolated area(s). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
41 | 564 |  | 2. | 566 | EOP-005-1 R11.2. | The affected Transmission Operators and Balancing Authorities shall take the necessary actions to restore Bulk Electric System frequency to normal, including adjusting generation, placing additional generators on line, or load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
41 | 564 |  | 3. | 567 | EOP-005-1 R11.3. | The affected Balancing Authorities, working with their Reliability Coordinator(s), shall immediately review the Interchange Schedules between those Balancing Authority Areas or fragments of those Balancing Authority Areas within the separated area and make adjustments as needed to facilitate the restoration. The affected Balancing Authorities shall make all attempts to maintain the adjusted Interchange Schedules, whether generation control is manual or automatic. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2013-06-30 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
41 | 564 |  | 4. | 568 | EOP-005-1 R11.4. | The affected Transmission Operators shall give high priority to restoration of off-site power to nuclear stations. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
41 | 564 |  | 5. | 569 | EOP-005-1 R11.5. | The affected Transmission Operators may resynchronize the isolated area(s) with the surrounding area(s) when the following conditions are met: |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
410 | 5087 |  | 1. | 5088 | MOD-016-0 R1.1. | The aggregated and dispersed data submittal requirements shall ensure that consistent data is supplied for Reliability Standards TPL-005-0, TPL-006-0, MOD-010-0, MOD011-0, MOD-012-0, MOD-013-0, MOD-014-0, MOD-015-0, MOD-016, MOD-017- 0, MOD-018-0, MOD-019-0, MOD-020-0, and MOD-021-0. |  | PCPA, RRO | [9 empty] | PCPA |  |  |  |  | RRO | [9 empty] | 2006-11-02 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
412 | 5096 |  | 1. | 5097 | PRC-001-0 R2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
412 | 5096 |  | 2. | 5098 | PRC-001-0 R2.2. | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
412 | 5099 |  | 1. | 5100 | PRC-001-0 R3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
412 | 5099 |  | 2. | 5101 | PRC-001-0 R3.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
412 | 5103 |  | 1. | 5104 | PRC-001-0 R5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s protection systems. |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
412 | 5103 |  | 2. | 5105 | PRC-001-0 R5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ protection systems. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 | 5109 | 1. | 5110 | PRC-002-0 R1.2.1. | Recording duration requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 | 5109 | 2. | 5111 | PRC-002-0 R1.2.2. | Time synchronization requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 | 5109 | 3. | 5112 | PRC-002-0 R1.2.3. | Data format requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 | 5109 | 4. | 5113 | PRC-002-0 R1.2.4. | Event triggering requirements |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 | 5114 | 1. | 5115 | PRC-002-0 R1.3.1. | Voltage. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 | 5114 | 2. | 5116 | PRC-002-0 R1.3.2. | Current. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 | 5114 | 3. | 5117 | PRC-002-0 R1.3.3. | Frequency. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 | 5114 | 4. | 5118 | PRC-002-0 R1.3.4. | MW and/or MVAR, as appropriate. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 | 5121 | 1. | 5122 | PRC-002-0 R1.6.1. | Substations. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 | 5121 | 2. | 5123 | PRC-002-0 R1.6.2. | Transmission lines. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 | 5121 | 3. | 5124 | PRC-002-0 R1.6.3. | Generators. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 163000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 |  | 1. | 5108 | PRC-002-0 R1.1. | Type of data recording capability (e.g., sequence-of-event, Fault recording, dynamic Disturbance recording). |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 |  | 2. | 5109 | PRC-002-0 R1.2. | Equipment characteristics including but not limited to: |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 |  | 3. | 5114 | PRC-002-0 R1.3. | Monitoring, recording, and reporting capabilities of the equipment. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 |  | 4. | 5119 | PRC-002-0 R1.4. | Data retention capabilities (e.g., length of time data is to be available for retrieval). |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 |  | 5. | 5120 | PRC-002-0 R1.5. | Regional coverage requirements (e.g., by voltage, geographic area, electric area or subarea). |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 |  | 6. | 5121 | PRC-002-0 R1.6. | Installation requirements: |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 |  | 7. | 5125 | PRC-002-0 R1.7. | Responsibility for maintenance and testing. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
413 | 5107 |  | 8. | 5126 | PRC-002-0 R1.8. | Requirements for periodic (at least every five years) updating, review, and approval of the Regional requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
414 | 5128 |  | 1. | 5129 | PRC-003-0 R1.1. | Requirements for monitoring and analysis of all transmission protective device misoperations. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-05-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
414 | 5128 |  | 2. | 5130 | PRC-003-0 R1.2. | Description of the data reporting requirements (periodicity and format) for those misoperations that adversely affects the reliability of the Bulk Electric Systems as specified by the Regional Reliability Organization. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-05-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
414 | 5128 |  | 3. | 5131 | PRC-003-0 R1.3. | Process for review, follow up, and documentation of corrective action plans for misoperations. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-05-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
414 | 5128 |  | 4. | 5132 | PRC-003-0 R1.4. | Identification of the Regional Reliability Organization group responsible for the procedure and the process for Regional Reliability Organization approval of the procedure. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-05-01 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
414 | 5128 |  | 5. | 5133 | PRC-003-0 R1.5. | Regional Reliability Organization definition of misoperations. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-05-01 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
416 | 5137 | 5138 | 1. | 5139 | PRC-005-0 R1.1.1. | Relays. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO | [6 empty] | 2006-05-01 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
416 | 5137 | 5138 | 2. | 5140 | PRC-005-0 R1.1.2. | Instrument transformers. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO | [6 empty] | 2006-05-01 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
416 | 5137 | 5138 | 3. | 5141 | PRC-005-0 R1.1.3. | Communications systems, where appropriate. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO | [6 empty] | 2006-05-01 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
416 | 5137 | 5138 | 4. | 5142 | PRC-005-0 R1.1.4. | Batteries. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO | [6 empty] | 2006-05-01 |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
416 | 5137 |  | 1. | 5138 | PRC-005-0 R1.1. | Transmission protection system identification shall include but are not limited to: |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO | [6 empty] | 2006-05-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
416 | 5137 |  | 2. | 5143 | PRC-005-0 R1.2. | Documentation of maintenance and testing intervals and their basis. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO | [6 empty] | 2006-05-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
416 | 5137 |  | 3. | 5144 | PRC-005-0 R1.3. | Summary of testing procedure. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO | [6 empty] | 2006-05-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
416 | 5137 |  | 4. | 5145 | PRC-005-0 R1.4. | Schedule for system testing. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO | [6 empty] | 2006-05-01 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
416 | 5137 |  | 5. | 5146 | PRC-005-0 R1.5. | Schedule for system maintenance. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO | [6 empty] | 2006-05-01 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
416 | 5137 |  | 6. | 5147 | PRC-005-0 R1.6. | Date last tested/maintained. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO | [6 empty] | 2006-05-01 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
417 | RQ-2021-06-09-0000001 |  | 1. | RP-2021-06-09-0000004 | TOP-001-0 R7.1. | For a generator outage, the Generator Operator shall notify and coordinate with the Transmission Operator. The Transmission Operator shall notify the Reliability Coordinator and other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
417 | RQ-2021-06-09-0000001 |  | 2. | RP-2021-06-09-0000005 | TOP-001-0 R7.2. | For a transmission facility, the Transmission Operator shall notify and coordinate with its Reliability Coordinator. The Transmission Operator shall notify other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
417 | RQ-2021-06-09-0000001 |  | 3. | RP-2021-06-09-0000006 | TOP-001-0 R7.3. | When time does not permit such notifications and coordination, or when immediate action is required to prevent a hazard to the public, lengthy customer service interruption, or damage to facilities, the Generator Operator shall notify the Transmission Operator, and the Transmission Operator shall notify its Reliability Coordinator and adjacent Transmission Operators, at the earliest possible time. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
418 | 5160 |  | 1. | 5161 | TOP-002-0 R14.1. | Changes in real and reactive output capabilities. |  | GOP | [5 empty] | GOP | [18 empty] | 2007-08-07 |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
418 | 5160 |  | 2. | 5162 | TOP-002-0 R14.2. | Automatic Voltage Regulator status and mode setting. |  | GOP | [5 empty] | GOP | [18 empty] | 2007-08-07 |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
418 | 5164 |  | 1. | 5165 | TOP-002-0 R16.1. | Changes in transmission facility status |  | TOP | [18 empty] | TOP | [5 empty] | 2007-08-07 |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
418 | 5164 |  | 2. | 5166 | TOP-002-0 R16.2. | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-08-07 |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
419 | 5183 |  | 1. | 5184 | TOP-002-1 R14.1. | Changes in real output capabilities |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
419 | 5186 |  | 1. | 5187 | TOP-002-1 R16.1. | Changes in transmission facility status. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
419 | 5186 |  | 2. | 5188 | TOP-002-1 R16.2. | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
420 | 5205 |  | 1. | 5206 | TOP-004-0 R6.1. | Equipment ratings. |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
420 | 5205 |  | 2. | 5207 | TOP-004-0 R6.2. | Monitoring and controlling voltage levels and real and reactive power flows. |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
420 | 5205 |  | 3. | 5208 | TOP-004-0 R6.3. | Switching transmission elements. |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
420 | 5205 |  | 4. | 5209 | TOP-004-0 R6.4. | Planned outages of transmission elements. |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
420 | 5205 |  | 5. | 5210 | TOP-004-0 R6.5. | Development of IROLs and SOLs. |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
420 | 5205 |  | 6. | 5211 | TOP-004-0 R6.6. | Responding to IROL and SOL violations. |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  | 660000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
421 | 5212 |  | 1. | 5213 | TOP-005-0 R1.1. | Each Reliability Coordinator shall identify the data requirements from the list in Attachment 1-TOP-005-0 “Electric System Reliability Data” and any additional operating information requirements relating to operation of the bulk power system within the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
422 | 5218 |  | 1. | 5219 | TOP-006-0 R1.1. | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
422 | 5218 |  | 2. | 5220 | TOP-006-0 R1.2. | Each Transmission Operator and Balancing Authority shall inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
424 | 5237 |  | 1. | 5238 | VAR-001-0 R7.1. | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
424 | 5240 |  | 1. | 5241 | VAR-001-0 R9.1. | When a generator’s voltage regulator is out of service, the Generator Operator shall maintain the generator field excitation at a level to maintain Interconnection and generator stability. |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
425 | 5243 |  | 1. | 6317 | CIP-002-5.1 R1.1. | Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-12-26 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
425 | 5243 |  | 2. | 6318 | CIP-002-5.1 R1.2. | Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-12-26 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
425 | 5243 |  | 3. | 6319 | CIP-002-5.1 R1.3. | Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-12-26 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
425 | 5244 |  | 1. | 6320 | CIP-002-5.1 R2.1. | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-12-26 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
425 | 5244 |  | 2. | 6321 | CIP-002-5.1 R2.2. | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. |  | BA, DP, DP-UFLS, GO, GOP, IA, RC, TO, TOP | BA | DP | DP-UFLS |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-12-26 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5245 |  | 1. | 6276 | CIP-004-5.1 R1.1. | Security awareness that, at least once each calendar quarter, reinforces cyber security practices (which may include associated physical security practices) for the Responsible Entity’s personnel who have authorized electronic or authorized unescorted physical access to BES Cyber Systems. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation that the quarterly reinforcement has been provided. Examples of evidence of reinforcement may include, but are not limited to, dated copies of information used to reinforce security awareness, as well as evidence of distribution, such as: • direct communications (for example, e-mails, memos, computer-based training); or • indirect communications (for example, posters, intranet, or brochures); or • management support and reinforcement (for example, presentations or meetings). | 2014-02-03 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5246 |  | 1. | 6287 | CIP-004-5.1 R2.1. | Training content on: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2014-02-03 |  | 2016-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5246 |  | 1.1. | 6277 | CIP-004-5.1 R2.1.1. | Cyber security policies; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5246 |  | 1.2. | 6278 | CIP-004-5.1 R2.1.2. | Physical access controls; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5246 |  | 1.3. | 6279 | CIP-004-5.1 R2.1.3. | Electronic access controls; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5246 |  | 1.4. | RP-2021-06-17-0000003 | CIP-004-5.1 R2.1.4. | The visitor control program; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5246 |  | 1.5. | RP-2021-06-17-0000004 | CIP-004-5.1 R2.1.5. | Handling of BES Cyber System Information and its storage; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 215000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5246 |  | 1.6. | 6282 | CIP-004-5.1 R2.1.6. | Identification of a Cyber Security Incident and initial notifications in accordance with the entity’s incident response plan; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  | 216000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5246 |  | 1.7. | 6283 | CIP-004-5.1 R2.1.7. | Recovery plans for BES Cyber Systems; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  | 217000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5246 |  | 1.8. | 6284 | CIP-004-5.1 R2.1.8. | Response to Cyber Security Incidents; and | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  | 218000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5246 |  | 1.9. | 6285 | CIP-004-5.1 R2.1.9. | Cyber security risks associated with a BES Cyber System’s electronic interconnectivity and interoperability with other Cyber Assets. | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  | 219000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5246 |  | 2. | 6286 | CIP-004-5.1 R2.2. | Require completion of the training specified in Part 2.1 prior to granting authorized electronic access and authorized unescorted physical access to applicable Cyber Assets, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training records and documentation of when CIP Exceptional Circumstances were invoked. | 2014-02-03 |  | 2016-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5246 |  | 3. | 6297 | CIP-004-5.1 R2.3. | Require completion of the training specified in Part 2.1 at least once every 15 calendar months. | [23 empty] | Examples of evidence may include, but are not limited to, dated individual training records. |  |  | 2016-06-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5246 |  | 4. | 6280 | CIP-004-5.1 R2.4. | The visitor control program; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5246 |  | 5. | 6281 | CIP-004-5.1 R2.5. | The visitor control program; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5247 | 6299 | 1. | 6300 | CIP-004-5.1 R3.2.1. | current residence, regardless of duration; and | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. |  |  | 2016-06-30 |  |  | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5247 | 6299 | 2. | 6301 | CIP-004-5.1 R3.2.2. | other locations where, during the seven years immediately prior to the date of the criminal history records check, the subject has resided for six consecutive months or more. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. |  |  | 2016-06-30 |  |  | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5247 |  | 1. | 6298 | CIP-004-5.1 R3.1. | Process to confirm identity. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to confirm identity. |  |  | 2016-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5247 |  | 2. | 6299 | CIP-004-5.1 R3.2. | Process to perform a seven year criminal history records check as part of each personnel risk assessment that includes: | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. |  |  | 2016-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5247 |  | 3. | 6302 | CIP-004-5.1 R3.3. | Criteria or process to evaluate criminal history records checks for authorizing access. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to evaluate criminal history records checks. |  |  | 2016-06-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5247 |  | 4. | 6303 | CIP-004-5.1 R3.4. | Criteria or process for verifying that personnel risk assessments performed for contractors or service vendors are conducted according to Parts 3.1 through 3.3. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s criteria or process for verifying contractors or service vendors personnel risk assessments. |  |  | 2016-06-30 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5247 |  | 5. | 6304 | CIP-004-5.1 R3.5. | Process to ensure that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed according to Parts 3.1 to 3.4 within the last seven years. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process for ensuring that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed within the last seven years. |  |  | 2016-06-30 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5248 | 6305 | 1. | 6306 | CIP-004-5.1 R4.1.1. | Electronic access; | [23 empty] | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. |  |  | 2016-06-30 |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5248 | 6305 | 2. | 6307 | CIP-004-5.1 R4.1.2. | Unescorted physical access into a Physical Security Perimeter; and | [23 empty] | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. |  |  | 2016-06-30 |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5248 | 6305 | 3. | 6308 | CIP-004-5.1 R4.1.3. | Access to designated storage locations, whether physical or electronic, for BES Cyber System Information. | [23 empty] | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. |  |  | 2016-06-30 |  |  | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5248 |  | 1. | 6305 | CIP-004-5.1 R4.1. | Process to authorize based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: | [23 empty] | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. |  |  | 2016-06-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5248 |  | 2. | RP-2021-06-17-0000006 | CIP-004-5.1 R4.2. | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5248 |  | 3. | 6310 | CIP-004-5.1 R4.3. | For electronic access, verify at least once every 15 calendar months that all user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and are those that the Responsible Entity determines are necessary. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the review that includes all of the following: 1. A dated listing of all accounts/account groups or roles within the system; 2. A summary description of privileges associated with each group or role; 3. Accounts assigned to the group or role; and 4. Dated evidence showing verification of the privileges for the group are authorized and appropriate to the work function performed by people assigned to each account. |  |  | 2016-06-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5248 |  | 4. | RP-2021-06-17-0000007 | CIP-004-5.1 R4.4. | Verify at least once every 15 calendar months that access to the designated storage locations for BES Cyber System Information, whether physical or electronic, are correct and are those that the Responsible Entity determines are necessary for performing assigned work functions. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5249 |  | 1. | 6312 | CIP-004-5.1 R5.1. | A process to initiate removal of an individual’s ability for unescorted physical access and Interactive Remote Access upon a termination action, and complete the removals within 24 hours of the termination action (Removal of the ability for access may be different than deletion, disabling, revocation, or removal of all access rights). | [23 empty] | An example of evidence may include, but is not limited to, documentation of all of the following: 1. Dated workflow or sign-off form verifying access removal associated with the termination action; and 2. Logs or other demonstration showing such persons no longer have access. |  |  | 2016-06-30 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5249 |  | 2. | 6313 | CIP-004-5.1 R5.2. | For reassignments or transfers, revoke the individual’s authorized electronic access to individual accounts and authorized unescorted physical access that the Responsible Entity determines are not necessary by the end of the next calendar day following the date that the Responsible Entity determines that the individual no longer requires retention of that access. | [23 empty] | An example of evidence may include, but is not limited to, documentation of all of the following: 1. Dated workflow or sign-off form showing a review of logical and physical access; and 2. Logs or other demonstration showing such persons no longer have access that the Responsible Entity determines is not necessary. |  |  | 2016-06-30 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5249 |  | 3. | 6314 | CIP-004-5.1 R5.3. | For termination actions, revoke the individual’s access to the designated storage locations for BES Cyber System Information, whether physical or electronic (unless already revoked according to Requirement R5.1), by the end of the next calendar day following the effective date of the termination action. | [23 empty] | An example of evidence may include, but is not limited to, workflow or sign-off form verifying access removal to designated physical areas or cyber systems containing BES Cyber System Information associated with the terminations and dated within the next calendar day of the termination action. |  |  | 2016-06-30 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5249 |  | 4. | 6315 | CIP-004-5.1 R5.4. | For termination actions, revoke the individual’s non-shared user accounts (unless already revoked according to Parts 5.1 or 5.3) within 30 calendar days of the effective date of the termination action. | [23 empty] | An example of evidence may include, but is not limited to, workflow or sign-off form showing access removal for any individual BES Cyber Assets and software applications as determined necessary to completing the revocation of access and dated within thirty calendar days of the termination actions. |  |  | 2016-06-30 |  |  | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
426 | 5249 |  | 5. | 6316 | CIP-004-5.1 R5.5. | For termination actions, change passwords for shared account(s) known to the user within 30 calendar days of the termination action. For reassignments or transfers, change passwords for shared account(s) known to the user within 30 calendar days following the date that the Responsible Entity determines that the individual no longer requires retention of that access. If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances. | [23 empty] | Examples of evidence may include, but are not limited to: • Workflow or sign-off form showing password reset within 30 calendar days of the termination; • Workflow or sign-off form showing password reset within 30 calendar days of the reassignments or transfers; or • Documentation of the extenuating operating circumstance and workflow or sign-off form showing password reset within 10 calendar days following the end of the operating circumstance. |  |  | 2016-06-30 |  |  | 550000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
427 | 5250 |  | 1. | 6505 | EOP-010-1 R1.1. | A description of activities designed to mitigate the effects of GMD events on the reliable operation of the interconnected transmission system within the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have a current GMD Operating Plan meeting all the provisions of Requirement R1; evidence such as a review or revision history to indicate that the GMD Operating Plan has been maintained; and evidence to show that the plan was implemented as called for in its GMD Operating Plan, such as dated operator logs, voice recordings, or voice transcripts. | 2015-04-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
427 | 5250 |  | 2. | 6506 | EOP-010-1 R1.2. | A process for the Reliability Coordinator to review the GMD Operating Procedures or Operating Processes of Transmission Operators within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have a current GMD Operating Plan meeting all the provisions of Requirement R1; evidence such as a review or revision history to indicate that the GMD Operating Plan has been maintained; and evidence to show that the plan was implemented as called for in its GMD Operating Plan, such as dated operator logs, voice recordings, or voice transcripts. | 2015-04-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
427 | 5252 |  | 1. | 6507 | EOP-010-1 R3.1. | Steps or tasks to receive space weather information. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have a GMD Operating Procedure or Operating Process meeting all the provisions of Requirement R3; evidence such as a review or revision history to indicate that the GMD Operating Procedure or Operating Process has been maintained; and evidence to show that the Operating Procedure or Operating Process was implemented as called for in its GMD Operating Procedure or Operating Process, such as dated operator logs, voice recordings, or voice transcripts. | 2015-04-01 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
427 | 5252 |  | 2. | 6508 | EOP-010-1 R3.2. | System Operator actions to be initiated based on predetermined conditions. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have a GMD Operating Procedure or Operating Process meeting all the provisions of Requirement R3; evidence such as a review or revision history to indicate that the GMD Operating Procedure or Operating Process has been maintained; and evidence to show that the Operating Procedure or Operating Process was implemented as called for in its GMD Operating Procedure or Operating Process, such as dated operator logs, voice recordings, or voice transcripts. | 2015-04-01 |  |  |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
427 | 5252 |  | 3. | 6509 | EOP-010-1 R3.3. | The conditions for terminating the Operating Procedure or Operating Process. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have a GMD Operating Procedure or Operating Process meeting all the provisions of Requirement R3; evidence such as a review or revision history to indicate that the GMD Operating Procedure or Operating Process has been maintained; and evidence to show that the Operating Procedure or Operating Process was implemented as called for in its GMD Operating Procedure or Operating Process, such as dated operator logs, voice recordings, or voice transcripts. | 2015-04-01 |  |  |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
428 | 5253 |  | 1. | 6973 | PRC-005-3 R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO | [6 empty] | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
428 | 5253 |  | 2. | 6974 | PRC-005-3 R1.2. | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO | [6 empty] | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
429 | 5263 |  | 1. | 6617 | PRC-023-3 R6.1. | Maintain a list of circuits subject to PRC-023-3 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-3, Attachment B applies. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2014-09-22 |  | 2017-03-31 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
429 | 5263 |  | 2. | 6618 | PRC-023-3 R6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2014-09-22 |  | 2017-03-31 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
43 | 588 |  | 1. | 589 | EOP-007-0 R1.1. | A requirement to have a database that contains all blackstart generators1 designated for use in an SRP within the respective areas. This database shall be updated on an annual basis. The database shall include the name, location, megawatt capacity, type of unit, latest date of test, and starting method. |  | RRO | [14 empty] | RRO | [7 empty] | 2011-05-23 |  | 2011-05-23 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
43 | 588 |  | 2. | 590 | EOP-007-0 R1.2. | A requirement to demonstrate that blackstart units perform their intended functions as required in the Regional SRP. This requirement can be met through either simulation or testing. The BCP must consider the availability of designated BCP units and initial transmission switching requirements. |  | RRO | [14 empty] | RRO | [7 empty] | 2011-05-23 |  | 2011-05-23 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
43 | 588 |  | 4. | 595 | EOP-007-0 R1.4. | A requirement to review and update the Regional BCP at least every five years. |  | RRO | [14 empty] | RRO | [7 empty] | 2011-05-23 |  | 2011-05-23 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5266 |  | 1. | 5272 | CIP-003-3a R1.1. | The cyber security policy addresses the requirements in Standards CIP-002-3 through CIP-009-3, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5266 |  | 2. | 5271 | CIP-003-3a R1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5266 |  | 3. | 5270 | CIP-003-3a R1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5265 |  | 1. | 5275 | CIP-003-3a R2.1. | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5265 |  | 2. | 5276 | CIP-003-3a R2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5265 |  | 3. | 5274 | CIP-003-3a R2.3. | Where allowed by Standards CIP-002-3 through CIP-009-3, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5265 |  | 4. | 5273 | CIP-003-3a R2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5268 |  | 1. | 5278 | CIP-003-3a R3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5268 |  | 2. | 5279 | CIP-003-3a R3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5268 |  | 3. | 5277 | CIP-003-3a R3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5264 |  | 1. | 5282 | CIP-003-3a R4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-3, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5264 |  | 2. | 5281 | CIP-003-3a R4.2. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5264 |  | 3. | 5280 | CIP-003-3a R4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5269 | 5283 | 1. | 5286 | CIP-003-3a R5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5269 | 5283 | 2. | 5287 | CIP-003-3a R5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5269 |  | 1. | 5283 | CIP-003-3a R5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5269 |  | 2. | 5285 | CIP-003-3a R5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
430 | 5269 |  | 3. | 5284 | CIP-003-3a R5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3: 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission. 4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5290 |  | 1. | 5296 | CIP-003-4a R1.1. | The cyber security policy addresses the requirements in Standards CIP-002-4 through CIP-009-4, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5290 |  | 2. | 5295 | CIP-003-4a R1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5290 |  | 3. | 5294 | CIP-003-4a R1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5289 |  | 1. | 5299 | CIP-003-4a R2.1. | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5289 |  | 2. | 5300 | CIP-003-4a R2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5289 |  | 3. | 5298 | CIP-003-4a R2.3. | Where allowed by Standards CIP-002-4 through CIP-009-4, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5289 |  | 4. | 5297 | CIP-003-4a R2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5292 |  | 1. | 5302 | CIP-003-4a R3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5292 |  | 2. | 5303 | CIP-003-4a R3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5292 |  | 3. | 5301 | CIP-003-4a R3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5288 |  | 1. | 5306 | CIP-003-4a R4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-4, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5288 |  | 2. | 5305 | CIP-003-4a R4.2. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5288 |  | 3. | 5304 | CIP-003-4a R4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5293 | 5307 | 1. | 5310 | CIP-003-4a R5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5293 | 5307 | 2. | 5311 | CIP-003-4a R5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5293 |  | 1. | 5307 | CIP-003-4a R5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5293 |  | 2. | 5309 | CIP-003-4a R5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
431 | 5293 |  | 3. | 5308 | CIP-003-4a R5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5315 |  | 1. | 5322 | CIP-007-3b R1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5315 |  | 2. | 5323 | CIP-007-3b R1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5315 |  | 3. | 5321 | CIP-007-3b R1.3. | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5314 |  | 1. | 5325 | CIP-007-3b R2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5314 |  | 2. | 5324 | CIP-007-3b R2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5314 |  | 3. | 5326 | CIP-007-3b R2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5320 |  | 1. | 5327 | CIP-007-3b R3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5320 |  | 2. | 5328 | CIP-007-3b R3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5317 |  | 1. | 5330 | CIP-007-3b R4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5317 |  | 2. | 5329 | CIP-007-3b R4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5318 | 5331 | 1. | 5338 | CIP-007-3b R5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 521000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5318 | 5331 | 2. | 5339 | CIP-007-3b R5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 522000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5318 | 5331 | 3. | 5337 | CIP-007-3b R5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 523000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5318 | 5332 | 1. | 5335 | CIP-007-3b R5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5318 | 5332 | 2. | 5334 | CIP-007-3b R5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5318 | 5332 | 3. | 5336 | CIP-007-3b R5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5318 | 5333 | 1. | 5341 | CIP-007-3b R5.3.1. | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 531000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5318 | 5333 | 2. | 5342 | CIP-007-3b R5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 532000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5318 | 5333 | 3. | 5340 | CIP-007-3b R5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 533000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5318 |  | 1. | 5332 | CIP-007-3b R5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5318 |  | 2. | 5331 | CIP-007-3b R5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5318 |  | 3. | 5333 | CIP-007-3b R5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5312 |  | 1. | 5347 | CIP-007-3b R6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5312 |  | 2. | 5345 | CIP-007-3b R6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5312 |  | 3. | 5346 | CIP-007-3b R6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5312 |  | 4. | 5344 | CIP-007-3b R6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5312 |  | 5. | 5343 | CIP-007-3b R6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5313 |  | 1. | 5349 | CIP-007-3b R7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5313 |  | 2. | 5348 | CIP-007-3b R7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5313 |  | 3. | 5350 | CIP-007-3b R7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5316 |  | 1. | 5354 | CIP-007-3b R8.1. | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5316 |  | 2. | 5351 | CIP-007-3b R8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5316 |  | 3. | 5352 | CIP-007-3b R8.3. | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
432 | 5316 |  | 4. | 5353 | CIP-007-3b R8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | 840000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5358 |  | 1. | 5365 | CIP-007-4b R1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5358 |  | 2. | 5366 | CIP-007-4b R1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5358 |  | 3. | 5364 | CIP-007-4b R1.3. | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5357 |  | 1. | 5368 | CIP-007-4b R2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5357 |  | 2. | 5367 | CIP-007-4b R2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5357 |  | 3. | 5369 | CIP-007-4b R2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5363 |  | 1. | 5370 | CIP-007-4b R3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5363 |  | 2. | 5371 | CIP-007-4b R3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5360 |  | 1. | 5373 | CIP-007-4b R4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5360 |  | 2. | 5372 | CIP-007-4b R4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5361 | 5374 | 1. | 5381 | CIP-007-4b R5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 521000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5361 | 5374 | 2. | 5382 | CIP-007-4b R5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 522000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5361 | 5374 | 3. | 5380 | CIP-007-4b R5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 523000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5361 | 5375 | 1. | 5378 | CIP-007-4b R5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-4 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5361 | 5375 | 2. | 5377 | CIP-007-4b R5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5361 | 5375 | 3. | 5379 | CIP-007-4b R5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-4 Requirement R5 and Standard CIP-004-4 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5361 | 5376 | 1. | 5384 | CIP-007-4b R5.3.1. | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 531000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5361 | 5376 | 2. | 5385 | CIP-007-4b R5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 532000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5361 | 5376 | 3. | 5383 | CIP-007-4b R5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 533000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5361 |  | 1. | 5375 | CIP-007-4b R5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5361 |  | 2. | 5374 | CIP-007-4b R5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5361 |  | 3. | 5376 | CIP-007-4b R5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5355 |  | 1. | 5390 | CIP-007-4b R6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5355 |  | 2. | 5388 | CIP-007-4b R6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5355 |  | 3. | 5389 | CIP-007-4b R6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5355 |  | 4. | 5387 | CIP-007-4b R6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5355 |  | 5. | 5386 | CIP-007-4b R6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5356 |  | 1. | 5392 | CIP-007-4b R7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5356 |  | 2. | 5391 | CIP-007-4b R7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5356 |  | 3. | 5393 | CIP-007-4b R7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5359 |  | 1. | 5397 | CIP-007-4b R8.1. | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5359 |  | 2. | 5394 | CIP-007-4b R8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5359 |  | 3. | 5395 | CIP-007-4b R8.3. | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
433 | 5359 |  | 4. | 5396 | CIP-007-4b R8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | 840000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
435 | 5401 |  | 1. | 6703 | INT-006-4 R1.1. | Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
435 | 5401 |  | 2. | 6704 | INT-006-4 R1.2. | Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
435 | 5402 |  | 1. | 6705 | INT-006-4 R2.1. | Each Transmission Service Provider shall deny the Arranged Interchange or curtail Confirmed Interchange if the transmission path (proper connectivity of adjacent Transmission Service Providers) between it and its adjacent Transmission Service Providers is invalid. |  | TSP | [20 empty] | TSP |  | 2014-06-30 |  | 2021-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
435 | 5403 |  | 1. | 6706 | INT-006-4 R3.1. | If a Balancing Authority denies a Reliability Adjustment Arranged Interchange, the Balancing Authority must communicate that fact to its Reliability Coordinator no more than 10 minutes after the denial. |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
435 | 5405 |  | 1. | 6707 | INT-006-4 R5.1. | The Source Balancing Authority, |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
435 | 5405 |  | 2. | 6708 | INT-006-4 R5.2. | Each Intermediate Balancing Authority, |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
435 | 5405 |  | 3. | 6709 | INT-006-4 R5.3. | Each Reliability Coordinator associated with each Balancing Authority included in the Arranged Interchange, |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
435 | 5405 |  | 4. | 6710 | INT-006-4 R5.4. | Each Transmission Service Provider included in the Arranged Interchange, and |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
435 | 5405 |  | 5. | 6711 | INT-006-4 R5.5. | Each Purchasing Selling Entity included in the Arranged Interchange. |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  | 550000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
439 | 5413 | 6959 | 1. | 6960 | PER-005-2 R1.1.1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall review, and update if necessary, its list of BES companyspecific Real-time reliability-related tasks identified in part 1.1 each calendar year. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence of using a systematic approach to develop and implement a training program for its System Operators, as specified in Requirement R1. M1.1 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection its methodology and its BES company-specific Real-time reliability-related task list, with the date of the last review, as specified in Requirement R1 part 1.1 and part 1.1.1. M1.2 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection training materials, as specified in Requirement R1 part 1.2. M1.3 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection System Operator training records showing the names of the people trained, the title of the training delivered, and the dates of delivery to show that it delivered the training, as specified in Requirement R1 part 1.3. M1.4 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internal audit results) that it performed an evaluation of its training program each calendar year, as specified in Requirement R1 part 1.4. | 2016-07-01 |  |  |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
439 | 5413 |  | 1. | 6959 | PER-005-2 R1.1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall create a list of Bulk Electric System (BES) company-specific Real-time reliability-related tasks based on a defined and documented methodology. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection its methodology and its BES companyspecific Real-time reliability-related task list, with the date of the last review, as specified in Requirement R1 part 1.1 and part 1.1.1. | 2014-06-19 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
439 | 5413 |  | 2. | 6961 | PER-005-2 R1.2. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliability-related task list created in part 1.1. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.2 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection training materials, as specified in Requirement R1 part 1.2. | 2014-06-19 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
439 | 5413 |  | 3. | 6962 | PER-005-2 R1.3. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall deliver training to its System Operators according to its training program. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.3 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection System Operator training records showing the names of the people trained, the title of the training delivered, and the dates of delivery to show that it delivered the training, as specified in Requirement R1 part 1.3. | 2014-06-19 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
439 | 5413 |  | 4. | 6963 | PER-005-2 R1.4. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training program established in Requirement R1 to identify any needed changes to the training program and shall implement the changes identified. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.4 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internal audit results) that it performed an evaluation of its training program each calendar year, as specified in Requirement R1 part 1.4. | 2014-06-19 |  |  |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
439 | 5414 | 6964 | 1. | 6965 | PER-005-2 R2.1.1. | Each Transmission Owner shall review, and update if necessary, its list of BES company-specific Real-time reliability-related tasks identified in part 2.1 each calendar year. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have available for inspection its methodology and its BES company-specific Real-time reliability-related task list, with the date of the last review, as specified in Requirement R2 part 2.1. | 2016-07-01 |  |  |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
439 | 5414 |  | 1. | 6964 | PER-005-2 R2.1. | Each Transmission Owner shall create a list of BES company-specific Real-time reliability-related tasks based on a defined and documented methodology. |  | TO | [17 empty] | TO |  |  |  | M2.1 Each Transmission Owner shall have available for inspection its methodology and its BES company-specific Real-time reliability-related task list, with the date of the last review, as specified in Requirement R2 part 2.1. | 2014-06-19 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
439 | 5414 |  | 2. | 6966 | PER-005-2 R2.2. | Each Transmission Owner shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliabilityrelated task list created in part 2.1. |  | TO | [17 empty] | TO |  |  |  | M2.2 Each Transmission Owner shall have available for inspection training materials, as specified in Requirement R2 part 2.2. | 2014-06-19 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
439 | 5414 |  | 3. | 6967 | PER-005-2 R2.3. | Each Transmission Owner shall deliver training to its personnel identified in Applicability Section 4.1.4.1 of this standard according to its training program. |  | TO | [17 empty] | TO |  |  |  | M2.3 Each Transmission Owner shall have available for inspection training records showing the names of the people trained, the title of the training delivered, and the dates of delivery to show that it delivered the training, as specified in Requirement R2 part 2.3. | 2014-06-19 |  |  |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
439 | 5414 |  | 4. | 6968 | PER-005-2 R2.4. | Each Transmission Owner shall conduct an evaluation each calendar year of the training program established in Requirement R2 to identify any needed changes to the training program and shall implement the changes identified. |  | TO | [17 empty] | TO |  |  |  | M2.4 Each Transmission Owner shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internal audit results) that it performed an evaluation of its training program each calendar year, as specified in Requirement R2 part 2.4. | 2014-06-19 |  |  |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
439 | 5415 |  | 1 . | RP-2021-07-08-0000001 | PER-005-2 R3.1 . | Within six months of a modification or addition of a BES company-specific Realtime reliability-related task, each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify the capabilities of each of its personnel identified in Requirement R1 or Requirement R2 to perform the new or modified BES company-specific Real-time reliability-related tasks identified in Requirement R1 part 1.1 or Requirement R2 part 2.1. |  | BA, RC, TO, TOP | BA | [10 empty] | RC | [5 empty] | TO | TOP |  |  | M3.1 Each Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner shall present evidence that it verified the capabilities of applicable personnel to perform new or modified BES company-specific Realtime reliability-related tasks within 6 months of a modification or addition of a BES company-specific Real-time reliability-related task. | 2016-07-01 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
439 | 5416 |  | 1. | 6970 | PER-005-2 R4.1. | A Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner that did not previously meet the criteria of Requirement R4, shall comply with Requirement R4 within 12 months of meeting the criteria. |  | BA, RC, TO, TOP | BA | [10 empty] | RC | [5 empty] | TO | TOP |  |  | M4.1 Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall have available for inspection training records that provide evidence that personnel identified in Requirement R1 or Requirement R2 completed training that included the use of simulation technology, as specified in Requirement R4, within 12 months of meeting the criteria of Requirement R4. | 2014-06-19 |  |  |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
439 | 5417 |  | 1. | 6971 | PER-005-2 R5.1. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training established in Requirement R5 to identify and implement changes to the training. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M5.1 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internal audit results) that it performed an evaluation each calendar year, as specified in Requirement R5 part 5.1. | 2014-06-19 |  |  |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
439 | 5418 |  | 1. | 6972 | PER-005-2 R6.1. | Each Generator Operator shall conduct an evaluation each calendar year of the training established in Requirement R6 to identify and implement changes to the training. |  | GOP | [5 empty] | GOP | [15 empty] | M6.1 Each Generator Operator shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internal audit results) that it performed an evaluation each calendar year, as specified in Requirement R6 part 6.1. | 2014-06-19 |  |  |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
44 | 597 |  | 1. | 598 | EOP-008-0 R1.1. | The contingency plan shall not rely on data or voice communication from the primary control facility to be viable. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
44 | 597 |  | 2. | 599 | EOP-008-0 R1.2. | The plan shall include procedures and responsibilities for providing basic tie line control and procedures and for maintaining the status of all inter-area schedules, such that there is an hourly accounting of all schedules. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
44 | 597 |  | 3. | 600 | EOP-008-0 R1.3. | The contingency plan must address monitoring and control of critical transmission facilities, generation control, voltage control, time and frequency control, control of critical substation devices, and logging of significant power system events. The plan shall list the critical facilities. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
44 | 597 |  | 4. | 601 | EOP-008-0 R1.4. | The plan shall include procedures and responsibilities for maintaining basic voice communication capabilities with other areas. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
44 | 597 |  | 5. | 602 | EOP-008-0 R1.5. | The plan shall include procedures and responsibilities for conducting periodic tests, at least annually, to ensure viability of the plan. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
44 | 597 |  | 6. | 603 | EOP-008-0 R1.6. | The plan shall include procedures and responsibilities for providing annual training to ensure that operating personnel are able to implement the contingency plans. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
44 | 597 |  | 7. | 604 | EOP-008-0 R1.7. | The plan shall be reviewed and updated annually. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
44 | 597 |  | 8. | 605 | EOP-008-0 R1.8. | Interim provisions must be included if it is expected to take more than one hour to implement the contingency plan for loss of primary control facility. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 | 7064 | 1. | 7065 | MOD-001-2 R1.1.1. | Facility ratings; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 | 7064 | 2. | 7066 | MOD-001-2 R1.1.2. | System voltage limits; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 | 7064 | 3. | 7067 | MOD-001-2 R1.1.3. | Transient stability limits; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 | 7064 | 4. | 7068 | MOD-001-2 R1.1.4. | Voltage stability limits; and |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 | 7064 | 5. | 7069 | MOD-001-2 R1.1.5. | Other System Operating Limits (SOLs). |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 | 7070 | 1. | 7071 | MOD-001-2 R1.2.1. | The simulation of transfers performed through the adjustment of generation, Load, or both; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 | 7070 | 2. | 7072 | MOD-001-2 R1.2.2. | Transmission topology, including, but not limited to, additions and retirements; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 | 7070 | 3. | 7073 | MOD-001-2 R1.2.3. | Expected transmission uses; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 | 7070 | 4. | 7074 | MOD-001-2 R1.2.4. | Planned outages; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 | 7070 | 5. | 7075 | MOD-001-2 R1.2.5. | Parallel path (loop flow) adjustments; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 | 7070 | 6. | 7076 | MOD-001-2 R1.2.6. | Load forecast; and |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 | 7070 | 7. | 7077 | MOD-001-2 R1.2.7. | Generator dispatch, including, but not limited to, additions and retirements. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 127000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 | 7078 | 1. | 7079 | MOD-001-2 R1.3.1. | Each Transmission Operator that uses the Flowgate Methodology shall include in its methodology an impact test process for including requested constraints. If a generator to Load transfer in a registered entity’s area or a transfer to a neighboring registered entity impacts the requested constraint by five percent or greater, the requested constraint shall be included in the TFC determination, otherwise the requested constraint is not required to be included. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 | 7078 | 2. | 7080 | MOD-001-2 R1.3.2. | Each Transmission Operator that uses the Area Interchange or Rated System Path Methodology shall describe in its methodology the process it uses to account for requested constraints that have a five percent or greater distribution factor for a transfer between areas in the TTC determination; otherwise the requested constraint is not required to be included. When testing transfers involving the requesting Transmission Operator’s area, the requested constraint may be excluded. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 | 7078 | 3. | 7081 | MOD-001-2 R1.3.3. | A different method for determining whether requested constraints need to be included in the TFC or TTC determination may be used if agreed to by the Transmission Operators. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 |  | 1. | 7064 | MOD-001-2 R1.1. | Each methodology shall describe the method used to account for the following limitations in both the pre- and post-contingency state: |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 |  | 2. | 7070 | MOD-001-2 R1.2. | Each methodology shall describe the method used to account for each of the following elements, provided such elements impact the determination of TFC or TTC: |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5419 |  | 3. | 7078 | MOD-001-2 R1.3. | Each methodology shall describe the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, provided that (1) the request references this specific requirement, and (2) the requesting Transmission Operator includes those constraints in its TFC or TTC determination. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5420 | 7082 | 1. | 7083 | MOD-001-2 R2.1.1. | The simulation of transfers performed through the adjustment of generation, Load, or both; |  | TSP | [20 empty] | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5420 | 7082 | 2. | 7084 | MOD-001-2 R2.1.2. | Transmission topology, including, but not limited to, additions and retirements; |  | TSP | [20 empty] | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5420 | 7082 | 3. | 7085 | MOD-001-2 R2.1.3. | Expected transmission uses; |  | TSP | [20 empty] | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5420 | 7082 | 4. | 7086 | MOD-001-2 R2.1.4. | Planned outages; |  | TSP | [20 empty] | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5420 | 7082 | 5. | 7087 | MOD-001-2 R2.1.5. | Parallel path (loop flow) adjustments; |  | TSP | [20 empty] | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 215000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5420 | 7082 | 6. | 7088 | MOD-001-2 R2.1.6. | Load forecast; and |  | TSP | [20 empty] | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 216000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5420 | 7082 | 7. | 7089 | MOD-001-2 R2.1.7. | Generator dispatch, including, but not limited to, additions and retirements. |  | TSP | [20 empty] | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 217000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5420 |  | 1. | 7082 | MOD-001-2 R2.1. | Each methodology shall describe the method used to account for the following elements, provided such elements impact the determination of AFC or ATC: |  | TSP | [20 empty] | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5420 |  | 2. | 7090 | MOD-001-2 R2.2. | Each Transmission Service Provider that uses the Flowgate Methodology shall, for reliability-related constraints identified in part 1.3, use the AFC determined by the Transmission Service Provider for that constraint. |  | TSP | [20 empty] | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5423 | 7092 | 1. | 7093 | MOD-001-2 R5.2.1. | TRMID; and |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 521000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5423 | 7092 | 2. | 7094 | MOD-001-2 R5.2.2. | TFC or TTC methodology. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 522000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5423 | 7095 | 1. | 7096 | MOD-001-2 R5.3.1. | ATCID; and |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 531000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5423 | 7095 | 2. | 7097 | MOD-001-2 R5.3.2. | CBMID. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 532000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5423 |  | 1. | 7091 | MOD-001-2 R5.1. | A written response to any request for clarification of its TFC or TTC methodology, ATCID, CBMID, or TRMID. If the request for clarification is contrary to the Transmission Operator’s or Transmission Service Provider’s confidentiality, regulatory, or security requirements then a written response shall be provided explaining the clarifications not provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory, or security concerns. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5423 |  | 2. | 7092 | MOD-001-2 R5.2. | If not publicly posted on OASIS or its company website, the Transmission Operator’s effective: |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5423 |  | 3. | 7095 | MOD-001-2 R5.3. | If not publicly posted on OASIS or its company website, the Transmission Service Provider’s effective: |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5424 | 7098 | 1. | 7101 | MOD-001-2 R6.1.1. | Alter the format in which it maintains or uses the data; or |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 611000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5424 | 7098 | 2. | 7102 | MOD-001-2 R6.1.2. | Make available the requested data on a more frequent basis than it produces the data and in no event shall it be required to provide the data more frequently than once an hour. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 612000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5424 |  | 1. | 7098 | MOD-001-2 R6.1. | In responding to a written request for data on an ongoing basis, the Transmission Service Provider or Transmission Operator shall make available its data on an ongoing basis no later than 45 calendar days from receipt of the written request. Unless otherwise agreed upon, the Transmission Operator or Transmission Service Provider is not required to: |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5424 |  | 2. | 7099 | MOD-001-2 R6.2. | In responding to all other data requests, each Transmission Operator or Transmission Service Provider shall make available the requested data within 45 calendar days of receipt of the written request. Unless otherwise agreed upon, the Transmission Operator or Transmission Service Provider is not required to alter the format in which it maintains or uses the data. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
440 | 5424 |  | 3. | 7100 | MOD-001-2 R6.3. | If making available any requested data under parts 6.1 or 6.2 of this requirement is contrary to the Transmission Operator’s or Transmission Service Provider’s confidentiality, regulatory, or security requirements, the Transmission Operator or Transmission Service Provider shall not be required to make available that data; provided that, within 45 calendar days of the written request, it responds to the requesting registered entity specifying the data that is not being provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory or security concerns. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  |  | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2. 4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
441 | 5425 | 6797 | 1. | 6798 | MOD-032-1 R1.2.1. | Data format; |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
441 | 5425 | 6797 | 2. | 6799 | MOD-032-1 R1.2.2. | Level of detail to which equipment shall be modeled; |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
441 | 5425 | 6797 | 3. | 6800 | MOD-032-1 R1.2.3. | Case types or scenarios to be modeled; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
441 | 5425 | 6797 | 4. | 6801 | MOD-032-1 R1.2.4. | A schedule for submission of data at least once every 13 calendar months. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
441 | 5425 |  | 1. | 6796 | MOD-032-1 R1.1. | The data listed in Attachment 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
441 | 5425 |  | 2. | 6797 | MOD-032-1 R1.2. | Specifications of the following items consistent with procedures for building the Interconnection-wide case(s): |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
441 | 5425 |  | 3. | 6802 | MOD-032-1 R1.3. | Specifications for distribution or posting of the data requirements and reporting procedures so that they are available to those entities responsible for providing the data. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Planning Coordinator and Transmission Planner shall provide evidence that it has jointly developed the required modeling data requirements and reporting procedures specified in Requirement R1. | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
441 | 5427 |  | 1. | 6803 | MOD-032-1 R3.1. | Provide either updated data or an explanation with a technical basis for maintaining the current data; |  | BA, GO, LSE, RP, TO, TSP | BA |  |  |  | GO |  |  | LSE | [5 empty] | RP |  |  |  | TO |  |  | TSP | Each registered entity identified in Requirement R3 that has received written notification from its Planning Coordinator or Transmission Planner regarding technical concerns with the data submitted under Requirement R2 shall provide evidence, such as email records or postal receipts showing recipient and date, that it has provided either updated data or an explanation with a technical basis for maintaining the current data to its Planning Coordinator or Transmission Planner within 90 calendar days of receipt (or within the longer time period agreed upon by the notifying Planning Coordinator or Transmission Planner), or a statement that it has not received written notification regarding technical concerns with the data submitted. | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
441 | 5427 |  | 2. | 6804 | MOD-032-1 R3.2. | Provide the response within 90 calendar days of receipt, unless a longer time period is agreed upon by the notifying Planning Coordinator or Transmission Planner. |  | BA, GO, LSE, RP, TO, TSP | BA |  |  |  | GO |  |  | LSE | [5 empty] | RP |  |  |  | TO |  |  | TSP | Each registered entity identified in Requirement R3 that has received written notification from its Planning Coordinator or Transmission Planner regarding technical concerns with the data submitted under Requirement R2 shall provide evidence, such as email records or postal receipts showing recipient and date, that it has provided either updated data or an explanation with a technical basis for maintaining the current data to its Planning Coordinator or Transmission Planner within 90 calendar days of receipt (or within the longer time period agreed upon by the notifying Planning Coordinator or Transmission Planner), or a statement that it has not received written notification regarding technical concerns with the data submitted. | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
442 | 5429 |  | 1. | 6805 | MOD-033-1 R1.1. | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning power flow model to actual system behavior, represented by a state estimator case or other Real-time data sources, at least once every 24 calendar months through simulation; |  | PCPA | [9 empty] | PCPA | [12 empty] | 2014-05-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
442 | 5429 |  | 2. | 6806 | MOD-033-1 R1.2. | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning dynamic model to actual system response, through simulation of a dynamic local event, at least once every 24 calendar months (use a dynamic local event that occurs within 24 calendar months of the last dynamic local event used in comparison, and complete each comparison within 24 calendar months of the dynamic local event). If no dynamic local event occurs within the 24 calendar months, use the next dynamic local event that occurs; |  | PCPA | [9 empty] | PCPA | [12 empty] | 2014-05-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
442 | 5429 |  | 3. | 6807 | MOD-033-1 R1.3. | Guidelines the Planning Coordinator will use to determine unacceptable differences in performance under Part 1.1 or 1.2; and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2014-05-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
442 | 5429 |  | 4. | 6808 | MOD-033-1 R1.4. | Guidelines to resolve the unacceptable differences in performance identified under Part 1.3. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2014-05-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
443 | 5445 |  | 1. | 7444 | VAR-001-4 E.A.181. | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-08-01 |  | 2015-11-12 |  |  | 1810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
443 | 5445 |  | 2. | 7445 | VAR-001-4 E.A.182. | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-08-01 |  | 2015-11-12 |  |  | 1820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
443 | 5431 |  | 1. | 6647 | VAR-001-4 R1.1. | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP |  |  |  | 2014-08-01 |  | 2015-11-12 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
443 | 5434 |  | 1. | 8391 | VAR-001-4 R4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2014-08-01 |  | 2015-11-12 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
443 | 5435 |  | 1. | RP-2021-06-24-0000060 | VAR-001-4 R5.1. | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | 2014-10-01 |  | 2015-11-12 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
443 | 5435 |  | 2. | RP-2021-06-24-0000061 | VAR-001-4 R5.2. | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  |  | 2014-10-01 |  | 2015-11-12 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
443 | 5435 |  | 3. | RP-2021-06-24-0000062 | VAR-001-4 R5.3. | The Transmission Operator shall provide the criteria used to develop voltage schedules Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  |  | 2014-10-01 |  | 2015-11-12 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
444 | 5438 |  | 1. | 5439 | TOP-007-WECC-1a R2.1. | If the path SOL decreases within 20 minutes before the start of the hour, the Transmission Operator shall adjust the Net Scheduled Interchange within 30 minutes to the new SOL value. Net Scheduled Interchange exceeding the new SOL during this 30-minute period will not be a violation of R2. |  | TOP | [18 empty] | TOP |  |  | M2.1. Evidence that Net Scheduled Interchange was at or below the new SOL within 30-minutes of when the SOL decreased. | 2014-06-18 |  | 2017-03-10 |  |  | 210000000 | WECC-US | [5 empty] | WECC-US
445 | 5447 |  | 1. | RP-2021-06-24-0000072 | VAR-002-3 R2.1. | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-10-01 |  | 2015-05-28 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
445 | 5447 |  | 2. | RP-2021-06-24-0000073 | VAR-002-3 R2.2. | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-10-01 |  | 2015-05-28 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
445 | 5447 |  | 3. | 6641 | VAR-002-3 R2.3. | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-08-01 |  | 2015-05-28 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
445 | 5450 | 6642 | 1. | 6643 | VAR-002-3 R5.1.1. | Tap settings. |  | GO |  |  |  |  | GO | [17 empty] | 2014-10-01 |  | 2015-05-28 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
445 | 5450 | 6642 | 2. | 6644 | VAR-002-3 R5.1.2. | Available fixed tap ranges. |  | GO |  |  |  |  | GO | [17 empty] | 2014-10-01 |  | 2015-05-28 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
445 | 5450 | 6642 | 3. | 6645 | VAR-002-3 R5.1.3. | Impedance data. |  | GO |  |  |  |  | GO | [17 empty] | 2014-10-01 |  | 2015-05-28 |  |  | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
445 | 5450 |  | 1. | 6642 | VAR-002-3 R5.1. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO |  |  |  |  | GO | [17 empty] | 2014-08-01 |  | 2015-05-28 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
445 | 5451 |  | 1. | 6646 | VAR-002-3 R6.1. | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. |  | GO |  |  |  |  | GO | [17 empty] | 2014-08-01 |  | 2015-05-28 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 | 6777 | 1. | 6778 | MOD-031-1 R1.3.1. | Integrated hourly Demands in megawatts for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 | 6777 | 2. | 6779 | MOD-031-1 R1.3.2. | Monthly and annual integrated peak hour Demands in megawatts for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 | 6777 | 3. | 6781 | MOD-031-1 R1.3.3. | Monthly and annual Net Energy for Load in gigawatthours for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 | 6777 | 4. | 6782 | MOD-031-1 R1.3.4. | Monthly and annual peak hour controllable and dispatchable Demand Side Management under the control or supervision of the System Operator in megawatts for the prior calendar year. Three values shall be reported for each hour: 1) the committed megawatts (the amount under control or supervision), 2) the dispatched megawatts (the amount, if any, activated for use by the System Operator), and 3) the realized megawatts (the amount of actual demand reduction). |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 | 6779 | 1. | 6780 | MOD-031-1 R1.3.2.1. | If the annual peak hour actual Demand varies due to weather-related conditions (e.g., temperature, humidity or wind speed), the Applicable Entity shall also provide the weather normalized annual peak hour actual Demand for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  | 13210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 | 6783 | 1. | 6784 | MOD-031-1 R1.4.1. | Monthly peak hour forecast Total Internal Demands in megawatts for the next two calendar years. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 | 6783 | 2. | 6785 | MOD-031-1 R1.4.2. | Monthly forecast Net Energy for Load in gigawatthours for the next two calendar years. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 | 6783 | 3. | 6786 | MOD-031-1 R1.4.3. | Peak hour forecast Total Internal Demands (summer and winter) in megawatts for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  | 143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 | 6783 | 4. | 6787 | MOD-031-1 R1.4.4. | Annual forecast Net Energy for Load in gigawatthours for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  | 144000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 | 6783 | 5. | 6788 | MOD-031-1 R1.4.5. | Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  | 145000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 | 6789 | 1. | 6790 | MOD-031-1 R1.5.1. | The assumptions and methods used in the development of aggregated Peak Demand and Net Energy for Load forecasts. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 | 6789 | 2. | 6791 | MOD-031-1 R1.5.2. | The Demand and energy effects of controllable and dispatchable Demand Side Management under the control or supervision of the System Operator. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 | 6789 | 3. | 6792 | MOD-031-1 R1.5.3. | How Demand Side Management is addressed in the forecasts of its Peak Demand and annual Net Energy for Load. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  | 153000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 | 6789 | 4. | 6793 | MOD-031-1 R1.5.4. | How the controllable and dispatchable Demand Side Management forecast compares to actual controllable and dispatchable Demand Side Management for the prior calendar year and, if applicable, how the assumptions and methods for future forecasts were adjusted. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  | 154000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 | 6789 | 5. | 6794 | MOD-031-1 R1.5.5. | How the peak Demand forecast compares to actual Demand for the prior calendar year with due regard to any relevant weather-related variations (e.g., temperature, humidity, or wind speed) and, if applicable, how the assumptions and methods for future forecasts were adjusted. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  | 155000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 |  | 1. | 6775 | MOD-031-1 R1.1. | A list of Transmission Planners, Balancing Authorities, Load Serving Entities, and Distribution Providers that are required to provide the data (“Applicable Entities”). |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 |  | 2. | 6776 | MOD-031-1 R1.2. | A timetable for providing the data. (A minimum of 30 calendar days must be allowed for responding to the request). |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 |  | 3. | 6777 | MOD-031-1 R1.3. | A request to provide any or all of the following actual data, as necessary: |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 |  | 4. | 6783 | MOD-031-1 R1.4. | A request to provide any or all of the following forecast data, as necessary: |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5452 |  | 5. | 6789 | MOD-031-1 R1.5. | A request to provide any or all of the following summary explanations, as necessary,: |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
446 | 5455 |  | 1. | 6795 | MOD-031-1 R4.1. | If the Applicable Entity does not provide data requested under this requirement because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
447 | 5456 |  | 1. | 7776 | COM-002-4 R1.1. | Require its operating personnel that issue and receive an oral or written Operating Instruction to use the English language, unless agreed to otherwise. An alternate language may be used for internal operations. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its documented communications protocols developed for Requirement R1. | 2015-06-22 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
447 | 5456 |  | 2. | 7777 | COM-002-4 R1.2. | Require its operating personnel that issue an oral two-party, person-to-person Operating Instruction to take one of the following actions: • Confirm the receiver’s response if the repeated information is correct. • Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver. • Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its documented communications protocols developed for Requirement R1. | 2015-06-22 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
447 | 5456 |  | 3. | 7778 | COM-002-4 R1.3. | Require its operating personnel that receive an oral two-party, person-to-person Operating Instruction to take one of the following actions: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct. • Request that the issuer reissue the Operating Instruction. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its documented communications protocols developed for Requirement R1. | 2015-06-22 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
447 | 5456 |  | 4. | 7779 | COM-002-4 R1.4. | Require its operating personnel that issue a written or oral single-party to multiple-party burst Operating Instruction to confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its documented communications protocols developed for Requirement R1. | 2015-06-22 |  |  |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
447 | 5456 |  | 5. | 7780 | COM-002-4 R1.5. | Specify the instances that require time identification when issuing an oral or written Operating Instruction and the format for that time identification. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its documented communications protocols developed for Requirement R1. | 2015-06-22 |  |  |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
447 | 5456 |  | 6. | 7781 | COM-002-4 R1.6. | Specify the nomenclature for Transmission interface Elements and Transmission interface Facilities when issuing an oral or written Operating Instruction. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide its documented communications protocols developed for Requirement R1. | 2015-06-22 |  |  |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
447 | 5459 |  | 1. | 7782 | COM-002-4 R4.1. | Assess adherence to the documented communications protocols in Requirement R1 by its operating personnel that issue and receive Operating Instructions, provide feedback to those operating personnel and take corrective action, as deemed appropriate by the entity, to address deviations from the documented protocols. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide evidence of its assessments, including spreadsheets, logs or other evidence of feedback, findings of effectiveness and any changes made to its documented communications protocols developed for Requirement R1 in fulfillment of Requirement R4. The entity shall provide, as part of its assessment, evidence of any corrective actions taken where an operating personnel’s non-adherence to the protocols developed in Requirement R1 is the sole or partial cause of an Emergency and for all other instances where the entity determined that it was appropriate to take a corrective action to address deviations from the documented protocols developed in Requirement R1. | 2015-06-22 |  |  |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
447 | 5459 |  | 2. | 7783 | COM-002-4 R4.2. | Assess the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions and modify its documented communication protocols, as necessary. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall provide evidence of its assessments, including spreadsheets, logs or other evidence of feedback, findings of effectiveness and any changes made to its documented communications protocols developed for Requirement R1 in fulfillment of Requirement R4. The entity shall provide, as part of its assessment, evidence of any corrective actions taken where an operating personnel’s non-adherence to the protocols developed in Requirement R1 is the sole or partial cause of an Emergency and for all other instances where the entity determined that it was appropriate to take a corrective action to address deviations from the documented protocols developed in Requirement R1. | 2015-06-22 |  |  |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5463 |  | 1. | 6740 | CIP-014-1 R1.1. | Subsequent risk assessments shall be performed: • At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection; or • At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection. |  | TO | [17 empty] | TO |  |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5463 |  | 2. | RP-2021-06-18-0000013 | CIP-014-1 R1.2. | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. |  | TO | [17 empty] | TO |  |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5464 |  | 1. | 6742 | CIP-014-1 R2.1. | Each Transmission Owner shall select an unaffiliated verifying entity that is either: • A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or • An entity that has transmission planning or analysis experience. |  | TO | [17 empty] | TO |  |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5464 |  | 2. | RP-2021-06-18-0000014 | CIP-014-1 R2.2. | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. |  | TO | [17 empty] | TO |  |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5464 |  | 3. | 6744 | CIP-014-1 R2.3. | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation: • Modify its identification under Requirement R1 consistent with the recommendation; or • Document the technical basis for not modifying the identification in accordance with the recommendation. |  | TO | [17 empty] | TO |  |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5464 |  | 4. | 6745 | CIP-014-1 R2.4. | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO | [17 empty] | TO |  |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5465 |  | 1. | 6746 | CIP-014-1 R3.1. | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. |  | TO | [17 empty] | TO |  |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5466 |  | 1. | RP-2021-06-18-0000015 | CIP-014-1 R4.1. | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5466 |  | 2. | 6748 | CIP-014-1 R4.2. | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5466 |  | 3. | 6749 | CIP-014-1 R4.3. | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5467 |  | 1. | 6750 | CIP-014-1 R5.1. | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5467 |  | 2. | 6751 | CIP-014-1 R5.2. | Law enforcement contact and coordination information. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5467 |  | 3. | 6752 | CIP-014-1 R5.3. | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5467 |  | 4. | 6753 | CIP-014-1 R5.4. | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5468 |  | 1. | 6754 | CIP-014-1 R6.1. | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following: • An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification. • An entity or organization approved by the ERO. • A governmental agency with physical security expertise. • An entity or organization with demonstrated law enforcement, government, or military physical security expertise. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5468 |  | 2. | RP-2021-06-18-0000016 | CIP-014-1 R6.2. | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5468 |  | 3. | 6756 | CIP-014-1 R6.3. | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation: • Modify its evaluation or security plan(s) consistent with the recommendation; or • Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
448 | 5468 |  | 4. | 6757 | CIP-014-1 R6.4. | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
449 | 8605 |  | 1. | 8606 | CIP-007-3 R1.1. | The Responsible Entity shall create, implement, and maintain cyber security testprocedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. | [5 empty] | 110000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8605 |  | 2. | RP-2021-08-31-0000002 | CIP-007-3 R1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. | [5 empty] | 120000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8605 |  | 3. | RP-2021-08-31-0000003 | CIP-007-3 R1.3. | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation of its security test procedures as specified in Requirement R1. | [5 empty] | 130000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8609 |  | 1. | RP-2021-08-31-0000004 | CIP-007-3 R2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation as specified in Requirement R2. | [5 empty] | 210000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8609 |  | 2. | RP-2021-09-03-0000002 | CIP-007-3 R2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation as specified in Requirement R2. | [5 empty] | 220000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8609 |  | 3. | 8612 | CIP-007-3 R2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation as specified in Requirement R2. | [5 empty] | 230000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8613 |  | 1. | RP-2021-08-31-0000005 | CIP-007-3 R3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. | [5 empty] | 310000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8613 |  | 2. | RP-2021-08-31-0000006 | CIP-007-3 R3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its security patch management program, as specified in Requirement R3. | [5 empty] | 320000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8616 |  | 1. | RP-2021-09-06-0000001 | CIP-007-3 R4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. | [5 empty] | 410000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8616 |  | 2. | 8618 | CIP-007-3 R4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its malicious software prevention program as specified in Requirement R4. | [5 empty] | 420000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8619 | 8620 | 1. | 8621 | CIP-007-3 R5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | 511000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8619 | 8620 | 2. | 8622 | CIP-007-3 R5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | 512000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8619 | 8620 | 3. | 8623 | CIP-007-3 R5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | 513000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8619 | 8624 | 1. | 8625 | CIP-007-3 R5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. | [5 empty] | 521000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8619 | 8624 | 2. | 8626 | CIP-007-3 R5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | 522000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8619 | 8624 | 3. | 8627 | CIP-007-3 R5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | 523000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8619 | 8628 | 1. | 8629 | CIP-007-3 R5.3.1. | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. | [5 empty] | 531000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8619 | 8628 | 2. | 8630 | CIP-007-3 R5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. | [5 empty] | 532000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8619 | 8628 | 3. | 8631 | CIP-007-3 R5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. | [5 empty] | 533000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8619 |  | 1. | 8620 | CIP-007-3 R5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | 510000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8619 |  | 2. | 8624 | CIP-007-3 R5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [6 empty] | 520000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8619 |  | 3. | 8628 | CIP-007-3 R5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its account management program as specified in Requirement R5. | [5 empty] | 530000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8632 |  | 1. | RP-2021-09-06-0000009 | CIP-007-3 R6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. | [5 empty] | 610000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8632 |  | 2. | RP-2021-09-06-0000010 | CIP-007-3 R6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. | [5 empty] | 620000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8632 |  | 3. | RP-2021-09-06-0000011 | CIP-007-3 R6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP008-3. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. | [5 empty] | 630000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8632 |  | 4. | RP-2021-09-06-0000012 | CIP-007-3 R6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. | [5 empty] | 640000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8632 |  | 5. | RP-2021-09-06-0000013 | CIP-007-3 R6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its security status monitoring program as specified in Requirement R6. | [5 empty] | 650000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
449 | 8638 |  | 1. | 8639 | CIP-007-3 R7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. | [5 empty] | 710000000 | MRO-MB
449 | 8638 |  | 2. | 8640 | CIP-007-3 R7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. | [5 empty] | 720000000 | MRO-MB
449 | 8638 |  | 3. | RP-2021-09-03-0000003 | CIP-007-3 R7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its program for the disposal or redeployment of Cyber Assets as specified in Requirement R7. | [5 empty] | 730000000 | MRO-MB
449 | 8642 |  | 1. | 8643 | CIP-007-3 R8.1. | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. | [5 empty] | 810000000 | MRO-MB
449 | 8642 |  | 2. | 8644 | CIP-007-3 R8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. | [5 empty] | 820000000 | MRO-MB
449 | 8642 |  | 3. | 8645 | CIP-007-3 R8.3. | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. | [5 empty] | 830000000 | MRO-MB
449 | 8642 |  | 4. | 8646 | CIP-007-3 R8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | The Responsible Entity shall make available documentation and records of its annual vulnerability assessment of all Cyber Assets within the Electronic Security Perimeters(s) as specified in Requirement R8. | [5 empty] | 840000000 | MRO-MB
450 | 5469 |  | 1. | 6758 | FAC-001-2 R1.1. | generation Facilities; |  | TO | [17 empty] | TO |  |  |  | M1. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | 2014-11-06 |  | 2018-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
450 | 5469 |  | 2. | RP-2021-06-21-0000024 | FAC-001-2 R1.2. | transmission Facilities; and |  | TO | [17 empty] | TO |  |  |  |  | 2016-01-01 |  | 2018-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
450 | 5469 |  | 3. | 6760 | FAC-001-2 R1.3. | end-user Facilities. |  | TO | [17 empty] | TO |  |  |  |  | 2014-11-06 |  | 2018-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
450 | 5471 |  | 1. | 6761 | FAC-001-2 R3.1. | Procedures for coordinated studies of new or materially modified existing interconnections and their impacts on affected system(s). |  | TO | [17 empty] | TO |  |  |  |  | 2014-11-06 |  | 2018-12-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
450 | 5471 |  | 2. | 6762 | FAC-001-2 R3.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new or materially modified existing interconnections. |  | TO | [17 empty] | TO |  |  |  |  | 2014-11-06 |  | 2018-12-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
450 | 5472 |  | 1. | 6763 | FAC-001-2 R4.1. | Procedures for coordinated studies of new interconnections and their impacts on affected system(s). |  | GO |  |  |  |  | GO | [17 empty] | 2014-11-06 |  | 2018-12-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
450 | 5472 |  | 2. | 6764 | FAC-001-2 R4.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. |  | GO |  |  |  |  | GO | [17 empty] | 2014-11-06 |  | 2018-12-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
451 | 5473 |  | 1. | 6765 | FAC-002-2 R1.1. | The reliability impact of the new interconnection, or materially modified existing interconnection, on affected system(s); |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2014-11-06 |  | 2021-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
451 | 5473 |  | 2. | 6766 | FAC-002-2 R1.2. | Adherence to applicable NERC Reliability Standards; regional and Transmission Owner planning criteria; and Facility interconnection requirements; |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2014-11-06 |  | 2021-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
451 | 5473 |  | 3. | 6767 | FAC-002-2 R1.3. | Steady-state, short-circuit, and dynamics studies, as necessary, to evaluate system performance under both normal and contingency conditions; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2014-11-06 |  | 2021-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
451 | 5473 |  | 4. | 6768 | FAC-002-2 R1.4. | Study assumptions, system performance, alternatives considered, and coordinated recommendations. While these studies may be performed independently, the results shall be evaluated and coordinated by the entities involved. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2014-11-06 |  | 2021-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
457 | 5481 |  | 1. | 7141 | PRC-004-3 R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-05-13 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
457 | 5481 |  | 2. | 7142 | PRC-004-3 R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-05-13 |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
457 | 5481 |  | 3. | 7143 | PRC-004-3 R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-05-13 |  | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
457 | 5482 | 7144 | 1. | 7145 | PRC-004-3 R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2016-07-01 |  | 2016-06-30 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
457 | 5482 | 7144 | 2. | 7146 | PRC-004-3 R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2016-07-01 |  | 2016-06-30 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
457 | 5482 | 7144 | 3. | 7147 | PRC-004-3 R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2016-07-01 |  | 2016-06-30 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
457 | 5482 |  | 1. | 7144 | PRC-004-3 R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-05-13 |  | 2016-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
457 | 5482 |  | 2. | 7148 | PRC-004-3 R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-05-13 |  | 2016-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5490 |  | 1. | 6891 | NUC-001-3 R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5490 |  | 2. | 6892 | NUC-001-3 R4.2. | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5490 |  | 3. | 6897 | NUC-001-3 R4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 | 6899 | 1. | 6900 | NUC-001-3 R9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the Agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  | 921000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 | 6899 | 2. | 6901 | NUC-001-3 R9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  | 922000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 | 6899 | 3. | 6902 | NUC-001-3 R9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  | 923000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 | 6903 | 1. | 6904 | NUC-001-3 R9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  | 931000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 | 6903 | 2. | 6905 | NUC-001-3 R9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  | 932000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 | 6903 | 3. | 6906 | NUC-001-3 R9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  | 933000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 | 6903 | 4. | 6907 | NUC-001-3 R9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  | 934000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 | 6903 | 5. | 6908 | NUC-001-3 R9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  | 935000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 | 6903 | 6. | 6909 | NUC-001-3 R9.3.6. | Coordination of physical and cyber security protection at the nuclear plant interface to ensure each asset is covered under at least one entity’s pla |  | BA, DP, GO, GOP, LSE, PCPA, RSG, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA | [6 empty] | RSG | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  | 936000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 | 6903 | 7. | 6910 | NUC-001-3 R9.3.7. | Coordination of the NPIRs with transmission system Remedial Action Schemes and any programs that reduce or shed load based on underfrequency or undervoltage. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  | 937000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 | 6911 | 1. | 6913 | NUC-001-3 R9.4.1. | Provisions for communications affecting the NPIRs between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of applicable unique terms |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  | 941000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 | 6911 | 2. | 6914 | NUC-001-3 R9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  | 942000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 | 6911 | 3. | 6915 | NUC-001-3 R9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  | 943000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 | 6911 | 4. | 6916 | NUC-001-3 R9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  | 944000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 | 6911 | 5. | 6917 | NUC-001-3 R9.4.5. | Provisions for personnel training, as related to NPIRs |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  | 945000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 |  | 1. | 6898 | NUC-001-3 R9.1. | Retired. [Note: Part 9.1 was retired under the Paragraph 81 project. The NUC SDT proposes to leave this Part blank to avoid renumbering Requirement parts that would impact existing agreements throughout the industry.] |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 |  | 2. | 6899 | NUC-001-3 R9.2. | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 |  | 3. | 6903 | NUC-001-3 R9.3. | Operations and maintenance coordination |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  | 930000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
458 | 5495 |  | 4. | 6911 | NUC-001-3 R9.4. | Communications and training Administrative elements: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  | 940000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5507 |  | 1. | 7163 | PRC-002-2 R1.1. | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-2, Attachment 1. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-2, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. | 2015-11-24 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5507 |  | 2. | 7164 | PRC-002-2 R1.2. | Notify other owners of BES Elements connected to those BES buses, if any, within 90-calendar days of completion of Part 1.1, that those BES Elements require SER data and/or FR data. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-2, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. | 2015-11-24 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5507 |  | 3. | 7165 | PRC-002-2 R1.3. | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners, if any, in accordance with Part 1.2, and implement the re-evaluated list of BES buses as per the Implementation Plan. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-2, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. | 2015-11-24 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5509 | 7167 | 1. | 7168 | PRC-002-2 R3.2.1. | Transformers that have a low-side operating voltage of 100kV or above. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5509 | 7167 | 2. | 7169 | PRC-002-2 R3.2.2. | Transmission Lines. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5509 |  | 1. | 7166 | PRC-002-2 R3.1. | Phase-to-neutral voltage for each phase of each specified BES bus. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5509 |  | 2. | 7167 | PRC-002-2 R3.2. | Each phase current and the residual or neutral current for the following BES Elements: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5510 | RP-2021-07-08-0000004 | 1. | 7173 | PRC-002-2 R4.3 . 1. | Neutral (residual) overcurrent. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 431000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5510 | RP-2021-07-08-0000004 | 2. | 7174 | PRC-002-2 R4.3 . 2. | Phase undervoltage or overcurrent. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 432000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5510 |  | 1. | 7170 | PRC-002-2 R4.1. | A single record or multiple records that include: • A pre-trigger record length of at least two cycles and a total record length of at least 30-cycles for the same trigger point, or • At least two cycles of the pre-trigger data, the first three cycles of the post-trigger data, and the final cycle of the fault as seen by the fault recorder. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5510 |  | 2. | 7171 | PRC-002-2 R4.2. | A minimum recording rate of 16 samples per cycle. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5510 |  | 3 . | RP-2021-07-08-0000004 | PRC-002-2 R4.3 . | Trigger settings for at least the following: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | 2021-01-01 |  | 2024-03-31 | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5511 | 7175 | 1. | 7176 | PRC-002-2 R5.1.1. | Generating resource(s) with: |  | PCPA, RC | [9 empty] | PCPA |  | RC | [9 empty] | The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2016-07-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5511 | 7175 | 2. | 7179 | PRC-002-2 R5.1.2. | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). |  | PCPA, RC | [9 empty] | PCPA |  | RC | [9 empty] | The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2016-07-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5511 | 7175 | 3. | 7180 | PRC-002-2 R5.1.3. | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter. |  | PCPA, RC | [9 empty] | PCPA |  | RC | [9 empty] | The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2016-07-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5511 | 7175 | 4. | 7181 | PRC-002-2 R5.1.4. | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). |  | PCPA, RC | [9 empty] | PCPA |  | RC | [10 empty] | 2016-07-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 514000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5511 | 7175 | 5. | 7182 | PRC-002-2 R5.1.5. | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. |  | PCPA, RC | [9 empty] | PCPA |  | RC | [9 empty] | The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2016-07-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 515000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5511 | 7176 | 1. | 7177 | PRC-002-2 R5.1.1.1. | Gross individual nameplate rating greater than or equal to 500 MVA. |  | PCPA, RC | [9 empty] | PCPA |  | RC | [9 empty] | The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2016-07-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 51110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5511 | 7176 | 2. | 7178 | PRC-002-2 R5.1.1.2. | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. |  | PCPA, RC | [9 empty] | PCPA |  | RC | [9 empty] | The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2016-07-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 51120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5511 | 7183 | 1. | 7184 | PRC-002-2 R5.2.1. | One BES Element; and |  | PCPA, RC | [9 empty] | PCPA |  | RC | [9 empty] | The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2016-07-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 521000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5511 | 7183 | 2. | 7185 | PRC-002-2 R5.2.2. | One BES Element per 3,000 MW of the Responsible Entity’s historical simultaneous peak System Demand. |  | PCPA, RC | [9 empty] | PCPA |  | RC | [9 empty] | The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2016-07-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 522000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5511 |  | 1. | 7175 | PRC-002-2 R5.1. | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: |  | PCPA, RC | [9 empty] | PCPA |  | RC | [9 empty] | The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2015-11-24 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5511 |  | 2. | 7183 | PRC-002-2 R5.2. | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: |  | PCPA, RC | [9 empty] | PCPA |  | RC | [9 empty] | The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2015-11-24 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5511 |  | 3. | 7186 | PRC-002-2 R5.3. | Notify all owners of identified BES Elements, within 90-calendar days of completion of Part 5.1, that their respective BES Elements require DDR data when requested. |  | PCPA, RC | [9 empty] | PCPA |  | RC | [9 empty] | The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2015-11-24 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5511 |  | 4. | 7187 | PRC-002-2 R5.4. | Re-evaluate all BES Elements at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3 to implement the re-evaluated list of BES Elements as per the Implementation Plan. |  | PCPA, RC | [9 empty] | PCPA |  | RC | [9 empty] | The Responsible Entity has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Responsible Entity has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2015-11-24 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5512 |  | 1. | 7188 | PRC-002-2 R6.1. | One phase-to-neutral or positive sequence voltage. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5512 |  | 2. | 7189 | PRC-002-2 R6.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5512 |  | 3. | 7190 | PRC-002-2 R6.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5512 |  | 4. | 7191 | PRC-002-2 R6.4. | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5513 |  | 1. | 7192 | PRC-002-2 R7.1. | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5513 |  | 2. | 7193 | PRC-002-2 R7.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. |  | GO |  |  |  |  | GO | [17 empty] | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5513 |  | 3. | 7194 | PRC-002-2 R7.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5513 |  | 4. | 7195 | PRC-002-2 R7.4. | Frequency of at least one of the voltages in Requirement R7, Part 7.1. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5514 |  | 1. | RP-2021-07-08-0000005 | PRC-002-2 R8.1. | Triggered record lengths of at least three minutes. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | 2021-01-01 |  | 2024-03-31 | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date. Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date. Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5514 |  | 2. | 7197 | PRC-002-2 R8.2. | At least one of the following three triggers: • Off nominal frequency trigger set at: Low High o Eastern Interconnection <59.75 Hz >61.0 Hz o Western Interconnection <59.55 Hz >61.0 Hz o ERCOT Interconnection <59.35 Hz >61.0 Hz o Hydro-Quebec Interconnection <58.55 Hz >61.5 Hz • Rate of change of frequency trigger set at: o Eastern Interconnection < -0.03125 Hz/sec > 0.125 Hz/sec o Western Interconnection < -0.05625 Hz/sec > 0.125 Hz/sec o ERCOT Interconnection < -0.08125 Hz/sec > 0.125 Hz/sec o Hydro-Quebec Interconnection < -0.18125 Hz/sec > 0.1875 Hz/sec • Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5515 |  | 1. | 7198 | PRC-002-2 R9.1. | Input sampling rate of at least 960 samples per second. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5515 |  | 2. | 7199 | PRC-002-2 R9.2. | Output recording rate of electrical quantities of at least 30 times per second. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5516 |  | 1. | 7200 | PRC-002-2 R10.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5516 |  | 2. | 7201 | PRC-002-2 R10.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5517 |  | 1. | 7202 | PRC-002-2 R11.1. | Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5517 |  | 2. | 7203 | PRC-002-2 R11.2. | Data subject to Part 11.1 will be provided within 30-calendar days of a request unless an extension is granted by the requestor. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5517 |  | 3. | 7204 | PRC-002-2 R11.3. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5517 |  | 4. | 7205 | PRC-002-2 R11.4. | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
459 | 5517 |  | 5. | 7206 | PRC-002-2 R11.5. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | 2021-01-01 |  | 2024-03-31 |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator 4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator 4.1.3 Western Interconnection – Reliability Coordinator 4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 608 |  | 1. | 609 | FAC-001-0 R1.1. | Generation facilities, |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 608 |  | 2. | 610 | FAC-001-0 R1.2. | Transmission facilities, and |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 608 |  | 3. | 611 | FAC-001-0 R1.3. | End-user facilities. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 1. | 614 | FAC-001-0 R2.1.1. | Procedures for coordinated joint studies of new facilities and their impacts on the interconnected transmission systems. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 10. | 615 | FAC-001-0 R2.1.10. | Power quality impacts. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 2110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 11. | 616 | FAC-001-0 R2.1.11. | Equipment Ratings. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 2111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 12. | 617 | FAC-001-0 R2.1.12. | Synchronizing of facilities. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 2112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 13. | 618 | FAC-001-0 R2.1.13. | Maintenance coordination. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 2113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 14. | 619 | FAC-001-0 R2.1.14. | Operational issues (abnormal frequency and voltages). |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 2114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 15. | 620 | FAC-001-0 R2.1.15. | Inspection requirements for existing or new facilities. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 2115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 16. | 621 | FAC-001-0 R2.1.16. | Communications and procedures during normal and emergency operating conditions. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 2116000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 2. | 622 | FAC-001-0 R2.1.2. | Procedures for notification of new or modified facilities to others (those responsible for the reliability of the interconnected transmission systems) as soon as feasible. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 3. | 623 | FAC-001-0 R2.1.3. | Voltage level and MW and MVAR capacity or demand at point of connection. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 4. | 624 | FAC-001-0 R2.1.4. | Breaker duty and surge protection. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 5. | 625 | FAC-001-0 R2.1.5. | System protection and coordination. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 215000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 6. | 626 | FAC-001-0 R2.1.6. | Metering and telecommunications. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 216000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 7. | 627 | FAC-001-0 R2.1.7. | Grounding and safety issues. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 217000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 8. | 628 | FAC-001-0 R2.1.8. | Insulation and insulation coordination. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 218000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 | 613 | 9. | 629 | FAC-001-0 R2.1.9. | Voltage, Reactive Power, and power factor control. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 219000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
46 | 612 |  | 1. | 613 | FAC-001-0 R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2013-11-24 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7683 |  | 1. | 7684 | PRC-006-2 D.B.2.1. | Those islands selected by applying the criteria in Requirement D.B.1, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7683 |  | 2. | 7685 | PRC-006-2 D.B.2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7686 | 7689 | 1. | 7690 | PRC-006-2 D.B.3.3.1. | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  | 331000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7686 | 7689 | 2. | 7691 | PRC-006-2 D.B.3.3.2. | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  | 332000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7686 | 7689 | 3. | 7692 | PRC-006-2 D.B.3.3.3. | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  | 333000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7686 |  | 1. | 7687 | PRC-006-2 D.B.3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7686 |  | 2. | 7688 | PRC-006-2 D.B.3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7686 |  | 3. | 7689 | PRC-006-2 D.B.3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7693 |  | 1. | 7694 | PRC-006-2 D.B.4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7693 |  | 2. | 7695 | PRC-006-2 D.B.4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7693 |  | 3. | 7696 | PRC-006-2 D.B.4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7693 |  | 4. | 7697 | PRC-006-2 D.B.4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7693 |  | 5. | 7698 | PRC-006-2 D.B.4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7693 |  | 6. | 7699 | PRC-006-2 D.B.4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 460000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7693 |  | 7. | 7700 | PRC-006-2 D.B.4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 470000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7701 |  | 1. | 7702 | PRC-006-2 D.B.11.1. | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 1110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 7701 |  | 2. | 7703 | PRC-006-2 D.B.11.2. | The effectiveness of the UFLS program |  | PCPA | [9 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 1120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 5520 |  | 1. | RP-2021-06-23-0000040 | PRC-006-2 R2.1. | Those islands selected by applying the criteria in Requirement R1, and |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 5520 |  | 2. | 6933 | PRC-006-2 R2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 5520 |  | 3. | 6934 | PRC-006-2 R2.3. | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 5521 |  | 1. | 6935 | PRC-006-2 R3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, an |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 5521 |  | 2. | 6936 | PRC-006-2 R3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 5521 |  | 3. | 6937 | PRC-006-2 R3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: • Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES • Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES • Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 5522 |  | 1. | RP-2021-06-23-0000041 | PRC-006-2 R4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 5522 |  | 2. | RP-2021-06-23-0000042 | PRC-006-2 R4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 5522 |  | 3. | RP-2021-06-23-0000043 | PRC-006-2 R4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 5522 |  | 4. | 6941 | PRC-006-2 R4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 5522 |  | 5. | 6942 | PRC-006-2 R4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 5522 |  | 6. | 6943 | PRC-006-2 R4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 460000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 5522 |  | 7. | 6944 | PRC-006-2 R4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessmen |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 470000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 5529 |  | 1. | 6945 | PRC-006-2 R11.1. | The performance of the UFLS equipment, |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 5529 |  | 2. | 6946 | PRC-006-2 R11.2. | The effectiveness of the UFLS program. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 6948 |  | 1. | RP-2021-06-23-0000044 | PRC-006-2 R14.1. | UFLS program, including a schedule for implementation |  | DP, DP-UFLS, PCPA, TO |  | DP | DP-UFLS | [6 empty] | PCPA | [7 empty] | TO |  |  |  |  | 2015-10-01 |  | 2017-09-30 |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 6948 |  | 2. | RP-2021-06-23-0000045 | PRC-006-2 R14.2. | UFLS design assessment |  | DP, DP-UFLS, PCPA, TO |  | DP | DP-UFLS | [6 empty] | PCPA | [7 empty] | TO |  |  |  |  | 2015-10-01 |  | 2017-09-30 |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 6948 |  | 3. | 6951 | PRC-006-2 R14.3. | Format and schedule of UFLS data submittal |  | DP, DP-UFLS, PCPA, TO |  | DP | DP-UFLS | [6 empty] | PCPA | [7 empty] | TO |  |  |  |  | 2015-03-04 |  | 2017-09-30 |  |  | 143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 6952 |  | 1. | 6953 | PRC-006-2 R15.1. | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
460 | 6952 |  | 2. | 6954 | PRC-006-2 R15.2. | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
461 | 5531 |  | 1. | RP-2021-06-25-0000001 | VAR-002-WECC-2 R1.1. | The synchronous generator or synchronous condenser operates for less than five percent of all hours during any calendar quarter. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-04-01 |  | 2018-09-05 |  |  | 110000000 | WECC-US | [5 empty] | WECC-US
461 | 5531 |  | 10. | 7723 | VAR-002-WECC-2 R1.10. | If AVR exhibits instability due to operation of a Load Tap Changer (LTC) transformer in the area, the Transmission Operator may authorize the Generator Operator to operate the excitation system in modes other than automatic voltage control until the system configuration changes. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  | 110000000 | WECC-US | [5 empty] | WECC-US
461 | 5531 |  | 2. | 7715 | VAR-002-WECC-2 R1.2. | Performing maintenance and testing up to a maximum of seven calendar days per calendar quarter. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  | 120000000 | WECC-US | [5 empty] | WECC-US
461 | 5531 |  | 3. | 7716 | VAR-002-WECC-2 R1.3. | AVR exhibits instability due to abnormal system configuration. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  | 130000000 | WECC-US | [5 empty] | WECC-US
461 | 5531 |  | 4. | 7717 | VAR-002-WECC-2 R1.4. | Due to component failure, the AVR may be out of service up to 60 consecutive days for repair per incident. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  | 140000000 | WECC-US | [5 empty] | WECC-US
461 | 5531 |  | 5. | 7718 | VAR-002-WECC-2 R1.5. | Due to a component failure, the AVR may be out of service up to one year provided the Generator Operator or Transmission Operator submits documentation identifying the need for time to obtain replacement parts and if required to schedule an outage. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  | 150000000 | WECC-US | [5 empty] | WECC-US
461 | 5531 |  | 6. | 7719 | VAR-002-WECC-2 R1.6. | Due to a component failure, the AVR may be out of service up to 24 months provided the Generator Operator or Transmission Operator submits documentation identifying the need for time for excitation system replacement (replace the AVR, limiters, and controls but not necessarily the power source and power bridge) and to schedule an outage. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  | 160000000 | WECC-US | [5 empty] | WECC-US
461 | 5531 |  | 7. | RP-2021-06-25-0000002 | VAR-002-WECC-2 R1.7. | The synchronous generator or synchronous condenser has not achieved Commercial Operation. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-04-01 |  | 2018-09-05 |  |  | 170000000 | WECC-US | [5 empty] | WECC-US
461 | 5531 |  | 8. | RP-2021-06-25-0000003 | VAR-002-WECC-2 R1.8. | The Transmission Operator directs the Generator Operator to operate the synchronous generator, and the AVR is unavailable for service. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-04-01 |  | 2018-09-05 |  |  | 180000000 | WECC-US | [5 empty] | WECC-US
461 | 5531 |  | 9. | 7722 | VAR-002-WECC-2 R1.9. | The Reliability Coordinator directs Transmission Operator to operate the synchronous condenser, and the AVR is unavailable for service. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  | 190000000 | WECC-US | [5 empty] | WECC-US
463 | 5533 |  | 1. | RP-2021-06-25-0000009 | VAR-501-WECC-2 R1.1. | The synchronous generator operates for less than five percent of all hours during any calendar quarter. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  | 110000000 | WECC-US | [5 empty] | WECC-US
463 | 5533 |  | 10. | 7837 | VAR-501-WECC-2 R1.10. | Due to a component failure, the PSS may be out of service up to 24 months provided the Generator Operator submits documentation identifying the need for time for PSS replacement and to schedule an outage. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  | 110000000 | WECC-US | [5 empty] | WECC-US
463 | 5533 |  | 11. | 7839 | VAR-501-WECC-2 R1.11. | The synchronous generator has not achieved Commercial Operation. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  | 111000000 | WECC-US | [5 empty] | WECC-US
463 | 5533 |  | 12. | 7840 | VAR-501-WECC-2 R1.12. | The Transmission Operator directs the Generator Operator to operate the synchronous generator, and the PSS is unavailable for service. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  | 112000000 | WECC-US | [5 empty] | WECC-US
463 | 5533 |  | 2. | 7829 | VAR-501-WECC-2 R1.2. | Performing maintenance and testing up to a maximum of seven calendar days per calendar quarter. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  | 120000000 | WECC-US | [5 empty] | WECC-US
463 | 5533 |  | 3. | 7830 | VAR-501-WECC-2 R1.3. | PSS exhibits instability due to abnormal system configuration. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  | 130000000 | WECC-US | [5 empty] | WECC-US
463 | 5533 |  | 4. | 7831 | VAR-501-WECC-2 R1.4. | Unit is operating in the synchronous condenser mode (very near zero real power level). |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  | 140000000 | WECC-US | [5 empty] | WECC-US
463 | 5533 |  | 5. | 7832 | VAR-501-WECC-2 R1.5. | Unit is generating less power than its design limit for effective PSS operation. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  | 150000000 | WECC-US | [5 empty] | WECC-US
463 | 5533 |  | 6. | 7833 | VAR-501-WECC-2 R1.6. | Unit is passing through a range of output that is a known “rough zone” (range in which a hydro unit is experiencing excessive vibration). |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  | 160000000 | WECC-US | [5 empty] | WECC-US
463 | 5533 |  | 7. | 7834 | VAR-501-WECC-2 R1.7. | The generator AVR is not in service. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  | 170000000 | WECC-US | [5 empty] | WECC-US
463 | 5533 |  | 8. | 7835 | VAR-501-WECC-2 R1.8. | Due to component failure, the PSS may be out of service up to 60 consecutive days for repair per incident. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  | 180000000 | WECC-US | [5 empty] | WECC-US
463 | 5533 |  | 9. | 7836 | VAR-501-WECC-2 R1.9. | Due to a component failure, the PSS may be out of service up to one year provided the Generator Operator submits documentation identifying the need for time to obtain replacement parts and if required to schedule an outage. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  | 190000000 | WECC-US | [5 empty] | WECC-US
464 | 5534 |  | 1. | 6881 | PRC-005-4 R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO | [6 empty] | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
464 | 5534 |  | 2. | 6882 | PRC-005-4 R1.2. | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO | [6 empty] | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5539 | 6851 | 1. | 6852 | EOP-011-1 R1.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | 2017-04-01 |  | 2023-03-31 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5539 | 6851 | 2. | RP-2021-07-01-0000005 | EOP-011-1 R1.2.2. | Cancellation or recall of Transmission and generation outages; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | 2017-04-01 |  | 2023-03-31 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5539 | 6851 | 3. | 6853 | EOP-011-1 R1.2.3. | Transmission system reconfiguration; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | 2017-04-01 |  | 2023-03-31 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5539 | 6851 | 4. | 6855 | EOP-011-1 R1.2.4. | Redispatch of generation request; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | 2017-04-01 |  | 2023-03-31 |  |  | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5539 | 6851 | 5. | 6856 | EOP-011-1 R1.2.5. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | 2017-04-01 |  | 2023-03-31 |  |  | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5539 | 6851 | 6. | 6857 | EOP-011-1 R1.2.6. | Reliability impacts of extreme weather conditions. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | 2017-04-01 |  | 2023-03-31 |  |  | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5539 |  | 1. | 6850 | EOP-011-1 R1.1. | Roles and responsibilities for activating the Operating Plan(s); |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | 2016-01-25 |  | 2023-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5539 |  | 2. | 6851 | EOP-011-1 R1.2. | Processes to prepare for and mitigate Emergencies including: |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | 2016-01-25 |  | 2023-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5540 | 6859 | 1. | 6860 | EOP-011-1 R2.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | 2017-04-01 |  | 2023-03-31 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5540 | 6859 | 2. | 6861 | EOP-011-1 R2.2.2. | Requesting an Energy Emergency Alert, per Attachment 1; |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | 2017-04-01 |  | 2023-03-31 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5540 | 6859 | 3. | 6862 | EOP-011-1 R2.2.3. | Managing generating resources in its Balancing Authority Area to address: |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | 2017-04-01 |  | 2023-03-31 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5540 | 6859 | 4. | 6867 | EOP-011-1 R2.2.4. | Public appeals for voluntary Load reductions; |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | 2017-04-01 |  | 2023-03-31 |  |  | 224000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5540 | 6859 | 5. | 6868 | EOP-011-1 R2.2.5. | Requests to government agencies to implement their programs to achieve necessary energy reductions; |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | 2017-04-01 |  | 2023-03-31 |  |  | 225000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5540 | 6859 | 6. | 6869 | EOP-011-1 R2.2.6. | Reduction of internal utility energy use; |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | 2017-04-01 |  | 2023-03-31 |  |  | 226000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5540 | 6859 | 7. | 6870 | EOP-011-1 R2.2.7. | Use of Interruptible Load, curtailable Load and demand response; |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | 2017-04-01 |  | 2023-03-31 |  |  | 227000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5540 | 6859 | 8. | 6871 | EOP-011-1 R2.2.8. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | 2017-04-01 |  | 2023-03-31 |  |  | 228000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5540 | 6859 | 9. | 6872 | EOP-011-1 R2.2.9. | Reliability impacts of extreme weather conditions. |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | 2017-04-01 |  | 2023-03-31 |  |  | 229000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5540 | 6862 | 1. | 6863 | EOP-011-1 R2.2.3.1. | capability and availability; |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | 2017-04-01 |  | 2023-03-31 |  |  | 22310000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5540 | 6862 | 2. | 6864 | EOP-011-1 R2.2.3.2. | fuel supply and inventory concerns; |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | 2017-04-01 |  | 2023-03-31 |  |  | 22320000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5540 | 6862 | 3. | 6865 | EOP-011-1 R2.2.3.3. | fuel switching capabilities; and |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | 2017-04-01 |  | 2023-03-31 |  |  | 22330000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5540 | 6862 | 4. | 6866 | EOP-011-1 R2.2.3.4. | environmental constraints. |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | 2017-04-01 |  | 2023-03-31 |  |  | 22340000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5540 |  | 1. | 6858 | EOP-011-1 R2.1. | Roles and responsibilities for activating the Operating Plan(s); |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | 2016-01-25 |  | 2023-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5540 |  | 2. | 6859 | EOP-011-1 R2.2. | Processes to prepare for and mitigate Emergencies including: |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | 2016-01-25 |  | 2023-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5541 | 6873 | 1. | 6874 | EOP-011-1 R3.1.1. | Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator will have documentation, such as dated e-mails or other correspondences that it reviewed Transmission Operator and Balancing Authority Operating Plans within 30 calendar days of submittal in accordance with Requirement R3. | 2017-04-01 |  | 2023-03-31 |  |  | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5541 | 6873 | 2. | 6875 | EOP-011-1 R3.1.2. | Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator will have documentation, such as dated e-mails or other correspondences that it reviewed Transmission Operator and Balancing Authority Operating Plans within 30 calendar days of submittal in accordance with Requirement R3. | 2017-04-01 |  | 2023-03-31 |  |  | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5541 | 6873 | 3. | 6876 | EOP-011-1 R3.1.3. | Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator will have documentation, such as dated e-mails or other correspondences that it reviewed Transmission Operator and Balancing Authority Operating Plans within 30 calendar days of submittal in accordance with Requirement R3. | 2017-04-01 |  | 2023-03-31 |  |  | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
466 | 5541 |  | 1. | 6873 | EOP-011-1 R3.1. | Within 30 calendar days of receipt, the Reliability Coordinator shall: |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator will have documentation, such as dated e-mails or other correspondences that it reviewed Transmission Operator and Balancing Authority Operating Plans within 30 calendar days of submittal in accordance with Requirement R3. | 2016-01-25 |  | 2023-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
467 | 5546 |  | 1 . | RP-2021-07-09-0000045 | PRC-026-1 R2.1 . | Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-1 – Attachment B criteria has not been performed in the last five calendar years. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Generator Owner and Transmission Owner shall have dated evidence that demonstrates the evaluation was performed according to Requirement R2. Evidence may include, but is not limited to, the following documentation: apparent impedance characteristic plots, email, design drawings, facsimiles, R-X plots, software output, records, reports, transmittals, lists, settings sheets, or spreadsheets. | 2020-01-01 |  | 2024-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
467 | 5546 |  | 2 . | RP-2021-07-09-0000046 | PRC-026-1 R2.2 . | Within 12 full calendar months of becoming aware3 of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable4 power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Generator Owner and Transmission Owner shall have dated evidence that demonstrates the evaluation was performed according to Requirement R2. Evidence may include, but is not limited to, the following documentation: apparent impedance characteristic plots, email, design drawings, facsimiles, R-X plots, software output, records, reports, transmittals, lists, settings sheets, or spreadsheets. | 2020-01-01 |  | 2024-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5552 | 7111 | 1. | 7112 | TPL-007-1 R4.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5552 | 7111 | 2. | 7113 | TPL-007-1 R4.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5552 | 7115 | 1. | 7116 | TPL-007-1 R4.3.1. | If a recipient of the GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 431000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5552 |  | 1. | 7111 | TPL-007-1 R4.1. | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5552 |  | 2. | RP-2021-09-07-0000008 | TPL-007-1 R4.2. | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5552 |  | 3. | 7115 | TPL-007-1 R4.3. | The GMD Vulnerability Assessment shall be provided within 90 calendar days of completion to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners, and to any functional entity that submits a written request and has a reliability-related need. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5553 |  | 1. | 7117 | TPL-007-1 R5.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2019-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5553 |  | 2. | 7118 | TPL-007-1 R5.2. | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2019-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5554 |  | 1. | 7129 | TPL-007-1 R6.1. | Be based on the effective GIC flow information provided in Requirement R5; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2021-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5554 |  | 2. | 7130 | TPL-007-1 R6.2. | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2021-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5554 |  | 3. | 7131 | TPL-007-1 R6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2021-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5554 |  | 4. | 7132 | TPL-007-1 R6.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2021-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5555 | 7135 | 1. | 7136 | TPL-007-1 R7.3.1. | If a recipient of the Corrective Action Plan provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 731000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5555 |  | 1. | 7133 | TPL-007-1 R7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Special Protection Systems. • Use of Operating Procedures, specifying how long they will be needed as part of the Corrective Action Plan. • Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5555 |  | 2. | 7134 | TPL-007-1 R7.2. | Be reviewed in subsequent GMD Vulnerability Assessments until it is determined that the System meets the performance requirements contained in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
468 | 5555 |  | 3. | 7135 | TPL-007-1 R7.3. | Be provided within 90 calendar days of completion to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), functional entities referenced in the Corrective Action Plan, and any functional entity that submits a written request and has a reliability-related need. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities: 4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
469 | 5565 | 5752 | 1. | 5753 | CIP-002-3(i) R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
469 | 5565 | 5752 | 2. | 5754 | CIP-002-3(i) R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
469 | 5565 | 5752 | 3. | 5755 | CIP-002-3(i) R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
469 | 5565 | 5752 | 4. | 5756 | CIP-002-3(i) R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
469 | 5565 | 5752 | 5. | 5757 | CIP-002-3(i) R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
469 | 5565 | 5752 | 6. | 5758 | CIP-002-3(i) R1.2.6. | Remedial Action Schemes that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
469 | 5565 | 5752 | 7. | 5759 | CIP-002-3(i) R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 127000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
469 | 5565 |  | 1. | 5751 | CIP-002-3(i) R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
469 | 5565 |  | 2. | 5752 | CIP-002-3(i) R1.2. | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
469 | 5567 |  | 1. | 5760 | CIP-002-3(i) R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
469 | 5567 |  | 2. | 5761 | CIP-002-3(i) R3.2. | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
469 | 5567 |  | 3. | 5762 | CIP-002-3(i) R3.3. | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
47 | 631 |  | 1. | 632 | FAC-002-0 R1.1. | Evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [9 empty] | TO |  |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
47 | 631 |  | 2. | 633 | FAC-002-0 R1.2. | Ensurance of compliance with NERC Reliability Standards and applicable Regional, subregional, Power Pool, and individual system planning criteria and facility connection requirements. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [9 empty] | TO |  |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
47 | 631 |  | 3. | 634 | FAC-002-0 R1.3. | Evidence that the parties involved in the assessment have coordinated and cooperated on the assessment of the reliability impacts of new facilities on the interconnected transmission systems. While these studies may be performed independently, the results shall be jointly evaluated and coordinated by the entities involved. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [9 empty] | TO |  |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
47 | 631 |  | 4. | 635 | FAC-002-0 R1.4. | Evidence that the assessment included steady-state, short-circuit, and dynamics studies as necessary to evaluate system performance in accordance with Reliability Standard TPL-001-0. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [9 empty] | TO |  |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
47 | 631 |  | 5. | 636 | FAC-002-0 R1.5. | Documentation that the assessment included study assumptions, system performance, alternatives considered, and jointly coordinated recommendations. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [9 empty] | TO |  |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
470 | 5570 |  | 1. | 6700 | INT-004-3.1 R2.1. | For Confirmed Interchange greater than 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 10% for that hour and that deviation is expected to persist. |  | PSE | [10 empty] | PSE | [11 empty] | 2014-11-26 |  | 2020-12-14 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
470 | 5570 |  | 2. | 6701 | INT-004-3.1 R2.2. | For Confirmed Interchange less than or equal to 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 25 MW for that hour and that deviation is expected to persist. |  | PSE | [10 empty] | PSE | [11 empty] | 2014-11-26 |  | 2020-12-14 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
470 | 5570 |  | 3. | 6702 | INT-004-3.1 R2.3. | The Purchasing-Selling Entity receives notification from a Reliability Coordinator or Transmission Operator to update the Confirmed Interchange. |  | PSE | [10 empty] | PSE | [11 empty] | 2014-11-26 |  | 2020-12-14 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
471 | 5572 |  | 1. | 6712 | INT-009-2.1 R1.1. | Identical in magnitude to that of the Adjacent Balancing Authority, and |  | BA | BA | [21 empty] | 2014-11-26 |  | 2021-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
471 | 5572 |  | 2. | 6713 | INT-009-2.1 R1.2. | Opposite in sign or direction to that of the Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2014-11-26 |  | 2021-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
474 | 5579 | 5764 | 1. | 5765 | CIP-002-3(i)b R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
474 | 5579 | 5764 | 2. | 5766 | CIP-002-3(i)b R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
474 | 5579 | 5764 | 3. | 5767 | CIP-002-3(i)b R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
474 | 5579 | 5764 | 4. | 5768 | CIP-002-3(i)b R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
474 | 5579 | 5764 | 5. | 5769 | CIP-002-3(i)b R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
474 | 5579 | 5764 | 6. | 5770 | CIP-002-3(i)b R1.2.6. | Remedial Action Schemes that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
474 | 5579 | 5764 | 7. | 5771 | CIP-002-3(i)b R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 127000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
474 | 5579 |  | 1. | 5763 | CIP-002-3(i)b R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
474 | 5579 |  | 2. | 5764 | CIP-002-3(i)b R1.2. | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
474 | 5581 |  | 1. | 5772 | CIP-002-3(i)b R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
474 | 5581 |  | 2. | 5773 | CIP-002-3(i)b R3.2. | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
474 | 5581 |  | 3. | 5774 | CIP-002-3(i)b R3.3. | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5598 |  | 1. | 5599 | FAC-010-3 R1.1. | Be applicable for developing SOLs used in the planning horizon. |  | PCPA | [9 empty] | PCPA | [11 empty] | The Planning Authority’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. | 2016-01-25 |  | 2024-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5598 |  | 2. | 5600 | FAC-010-3 R1.2. | State that SOLs shall not exceed associated Facility Ratings. |  | PCPA | [9 empty] | PCPA | [11 empty] | The Planning Authority’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. | 2016-01-25 |  | 2024-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5598 |  | 3. | 5601 | FAC-010-3 R1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | PCPA | [9 empty] | PCPA | [11 empty] | The Planning Authority’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. | 2016-01-25 |  | 2024-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5602 | 5614 | 1. | 5615 | FAC-010-3 R2.6.1. | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-04-01 |  |  |  |  | 26100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5602 |  | 1. | RP-2021-07-01-0000010 | FAC-010-3 R2.1. | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5602 |  | 2. | 5603 | FAC-010-3 R2.2. | Following the single Contingencies1 identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5602 |  | 2.1. | 5604 | FAC-010-3 R2.2.1. | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5602 |  | 2.2. | RP-2021-07-01-0000011 | FAC-010-3 R2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5602 |  | 2.3. | RP-2021-07-01-0000012 | FAC-010-3 R2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5602 |  | 3. | RP-2021-07-01-0000013 | FAC-010-3 R2.3. | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5602 |  | 3.1. | 5608 | FAC-010-3 R2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 231000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5602 |  | 3.2. | RP-2021-07-01-0000014 | FAC-010-3 R2.3.2. | System reconfiguration through manual or automatic control or protection actions. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 232000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5602 |  | 4. | 5612 | FAC-010-3 R2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5602 |  | 5. | 5613 | FAC-010-3 R2.5. | Starting with all Facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5602 |  | 6. | 5614 | FAC-010-3 R2.6. | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5617 |  | 1. | 5618 | FAC-010-3 R3.1. | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5617 |  | 2. | 5619 | FAC-010-3 R3.2. | Selection of applicable Contingencies |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5617 |  | 3. | 5620 | FAC-010-3 R3.3. | Level of detail of system models used to determine SOLs. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5617 |  | 4. | 5621 | FAC-010-3 R3.4. | Allowed uses of Remedial Action Schemes. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5617 |  | 5. | 5622 | FAC-010-3 R3.5. | Anticipated transmission system configuration, generation dispatch and Load level. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5617 |  | 6. | 5623 | FAC-010-3 R3.6. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 360000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5624 |  | 1. | 5625 | FAC-010-3 R4.1. | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5624 |  | 2. | 5626 | FAC-010-3 R4.2. | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
477 | 5624 |  | 3. | 5627 | FAC-010-3 R4.3. | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5629 |  | 1. | 5630 | FAC-011-3 R1.1. | Be applicable for developing SOLs used in the operations horizon. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. | 2016-01-25 |  | 2024-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5629 |  | 2. | 5631 | FAC-011-3 R1.2. | State that SOLs shall not exceed associated Facility Ratings. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. | 2016-01-25 |  | 2024-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5629 |  | 3. | 5632 | FAC-011-3 R1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator’s SOL Methodology shall address all of the items listed in Requirement 1 through Requirement 3. | 2016-01-25 |  | 2024-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5633 | 5634 | 1. | 5635 | FAC-011-3 R2.2.1. | Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. | 2016-01-25 |  | 2024-03-31 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5633 | 5634 | 2. | 5636 | FAC-011-3 R2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. | 2017-04-01 |  | 2024-03-31 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5633 | 5634 | 3. | 5637 | FAC-011-3 R2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. | 2017-04-01 |  | 2024-03-31 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5633 | 5638 | 1. | 5639 | FAC-011-3 R2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. | 2016-01-25 |  | 2024-03-31 |  |  | 231000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5633 | 5638 | 2. | 5641 | FAC-011-3 R2.3.2. | Interruption of other network customers, (a) only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or (b) if the real-time operating conditions are more adverse than anticipated in the corresponding studies |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. | 2017-04-01 |  | 2024-03-31 |  |  | 232000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5633 | 5638 | 3. | 5642 | FAC-011-3 R2.3.3. | System reconfiguration through manual or automatic control or protection actions. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. | 2017-04-01 |  | 2024-03-31 |  |  | 233000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5633 |  | 1. | RP-2021-07-02-0000001 | FAC-011-3 R2.1. | In the pre-contingency state, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect current or expected system conditions and shall reflect changes to system topology such as Facility outages. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. | 2017-04-01 |  | 2024-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5633 |  | 2. | 5634 | FAC-011-3 R2.2. | Following the single Contingencies1 identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. | 2016-01-25 |  | 2024-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5633 |  | 3. | 5638 | FAC-011-3 R2.3. | In determining the system’s response to a single Contingency, the following shall be acceptable: |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. | 2017-04-01 |  | 2024-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5633 |  | 4. | 5644 | FAC-011-3 R2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator shall have evidence it issued its SOL Methodology, and any changes to that methodology, including the date they were issued, in accordance with Requirement 4. | 2016-01-25 |  | 2024-03-31 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5645 | 5648 | 1. | 5649 | FAC-011-3 R3.3.1. | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 |  | 2024-03-31 |  |  | 331000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5645 |  | 1. | 5646 | FAC-011-3 R3.1. | Study model (must include at least the entire Reliability Coordinator Area as well as the critical modeling details from other Reliability Coordinator Areas that would impact the Facility or Facilities under study.) |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5645 |  | 2. | 5647 | FAC-011-3 R3.2. | Selection of applicable Contingencies |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5645 |  | 3. | 5648 | FAC-011-3 R3.3. | A process for determining which of the stability limits associated with the list of multiple contingencies (provided by the Planning Authority in accordance with FAC-014 Requirement 6) are applicable for use in the operating horizon given the actual or expected system conditions. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5645 |  | 4. | 5650 | FAC-011-3 R3.4. | Level of detail of system models used to determine SOLs. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5645 |  | 5. | 5651 | FAC-011-3 R3.5. | Allowed uses of Remedial Action Schemes. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5645 |  | 6. | 5652 | FAC-011-3 R3.6. | Anticipated transmission system configuration, generation dispatch and Load level |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 360000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5645 |  | 7. | 5653 | FAC-011-3 R3.7. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 370000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5654 |  | 1. | 5655 | FAC-011-3 R4.1. | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 |  | 2024-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5654 |  | 2. | 5657 | FAC-011-3 R4.2. | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | 2016-01-25 |  | 2024-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
478 | 5654 |  | 3. | 5658 | FAC-011-3 R4.3. | Each Transmission Operator that operates in the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 |  | 2024-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
479 | 5660 |  | 1. | 5661 | IRO-005-3.1(i)a R1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Remedial Action Schemes) and system loading. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
479 | 5660 |  | 10. | 5670 | IRO-005-3.1(i)a R1.10. | Contingency events. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
479 | 5660 |  | 2. | 5662 | IRO-005-3.1(i)a R1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
479 | 5660 |  | 3. | 5663 | IRO-005-3.1(i)a R1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
479 | 5660 |  | 4. | 5664 | IRO-005-3.1(i)a R1.4. | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
479 | 5660 |  | 5. | 5665 | IRO-005-3.1(i)a R1.5. | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
479 | 5660 |  | 6. | 5666 | IRO-005-3.1(i)a R1.6. | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
479 | 5660 |  | 7. | 5667 | IRO-005-3.1(i)a R1.7. | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
479 | 5660 |  | 8. | 5668 | IRO-005-3.1(i)a R1.8. | Planned generation dispatches. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
479 | 5660 |  | 9. | 5669 | IRO-005-3.1(i)a R1.9. | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 638 | 642 | 1. | 643 | FAC-003-1 R1.2.2.1. | Where transmission system transient overvoltage factors are not known, clearances shall be derived from Table 5, IEEE 516-2003, phase-to-ground distances, with appropriate altitude correction factors applied. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 12210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 638 | 642 | 2. | 644 | FAC-003-1 R1.2.2.2. | Where transmission system transient overvoltage factors are known, clearances shall be derived from Table 7, IEEE 516-2003, phase-to-phase voltages, with appropriate altitude correction factors applied. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 12220000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 638 | RP-2021-06-15-0000035 | 1. | 641 | FAC-003-1 R1.2.1. | Clearance 1 — The Transmission Owner shall determine and document appropriate clearance distances to be achieved at the time of transmission vegetation management work based upon local conditions and the expected time frame in which the Transmission Owner plans to return for future vegetation management work. Local conditions may include, but are not limited to: operating voltage, appropriate vegetation management techniques, fire risk, reasonably anticipated tree and conductor movement, species types and growth rates, species failure characteristics, local climate and rainfall patterns, line terrain and elevation, location of the vegetation within the span, and worker approach distance requirements. Clearance 1 distances shall be greater than those defined by Clearance 2 below. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 638 | RP-2021-06-15-0000035 | 2. | 642 | FAC-003-1 R1.2.2. | Clearance 2 — The Transmission Owner shall determine and document specific radial clearances to be maintained between vegetation and conductors under all rated electrical operating conditions. These minimum clearance distances are necessary to prevent flashover between vegetation and conductors and will vary due to such factors as altitude and operating voltage. These Transmission Owner-specific minimum clearance distances shall be no less than those set forth in the Institute of Electrical and Electronics Engineers (IEEE) Standard 516-2003 (Guide for Maintenance Methods on Energized Power Lines) and as specified in its Section 4.2.2.3, Minimum Air Insulation Distances without Tools in the Air Gap. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 638 |  | 1. | 639 | FAC-003-1 R1.1. | The TVMP shall define a schedule for and the type (aerial, ground) of ROW vegetation inspections. This schedule should be flexible enough to adjust for changing conditions. The inspection schedule shall be based on the anticipated growth of vegetation and any other environmental or operational factors that could impact the relationship of vegetation to the Transmission Owner’s transmission lines. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 638 |  | 2. | RP-2021-06-15-0000035 | FAC-003-1 R1.2. | The Transmission Owner, in the TVMP, shall identify and document clearances between vegetation and any overhead, ungrounded supply conductors, taking into consideration transmission line voltage, the effects of ambient temperature on conductor sag under maximum design loading, and the effects of wind velocities on conductor sway. Specifically, the Transmission Owner shall establish clearances to be achieved at the time of vegetation management work identified herein as Clearance 1, and shall also establish and maintain a set of clearances identified herein as Clearance 2 to prevent flashover between vegetation and overhead ungrounded supply conductors. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 638 |  | 3. | 645 | FAC-003-1 R1.3. | All personnel directly involved in the design and implementation of the TVMP shall hold appropriate qualifications and training, as defined by the Transmission Owner, to perform their duties. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 638 |  | 4. | 646 | FAC-003-1 R1.4. | Each Transmission Owner shall develop mitigation measures to achieve sufficient clearances for the protection of the transmission facilities when it identifies locations on the ROW where the Transmission Owner is restricted from attaining the clearances specified in Requirement 1.2.1. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 638 |  | 5. | 647 | FAC-003-1 R1.5. | Each Transmission Owner shall establish and document a process for the immediate communication of vegetation conditions that present an imminent threat of a transmission line outage. This is so that action (temporary reduction in line rating, switching line out of service, etc.) may be taken until the threat is relieved. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 649 | 653 | 1. | 654 | FAC-003-1 R3.4.1. | Category 1 — Grow-ins: Outages caused by vegetation growing into lines from vegetation inside and/or outside of the ROW; |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 341000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 649 | 653 | 2. | 655 | FAC-003-1 R3.4.2. | Category 2 — Fall-ins: Outages caused by vegetation falling into lines from inside the ROW; |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 342000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 649 | 653 | 3. | 656 | FAC-003-1 R3.4.3. | Category 3 — Fall-ins: Outages caused by vegetation falling into lines from outside the ROW. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 343000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 649 |  | 1. | 650 | FAC-003-1 R3.1. | Multiple sustained outages on an individual line, if caused by the same vegetation, shall be reported as one outage regardless of the actual number of outages within a 24-hour period. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 649 |  | 2. | RP-2021-06-15-0000036 | FAC-003-1 R3.2. | The Transmission Owner is not required to report to the RRO, or the RRO’s designee, certain sustained transmission line outages caused by vegetation: (1) Vegetationrelated outages that result from vegetation falling into lines from outside the ROW that result from natural disasters shall not be considered reportable (examples of disasters that could create non-reportable outages include, but are not limited to, earthquakes, fires, tornados, hurricanes, landslides, wind shear, major storms as defined either by the Transmission Owner or an applicable regulatory body, ice storms, and floods), and (2) Vegetation-related outages due to human or animal activity shall not be considered reportable (examples of human or animal activity that could cause a non-reportable outage include, but are not limited to, logging, animal severing tree, vehicle contact with tree, arboricultural activities or horticultural or agricultural activities, or removal or digging of vegetation). |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 649 |  | 3. | 652 | FAC-003-1 R3.3. | The outage information provided by the Transmission Owner to the RRO, or the RRO’s designee, shall include at a minimum: the name of the circuit(s) outaged, the date, time and duration of the outage; a description of the cause of the outage; other pertinent comments; and any countermeasures taken by the Transmission Owner. |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
48 | 649 |  | 4. | 653 | FAC-003-1 R3.4. | An outage shall be categorized as one of the following: |  | TO | [17 empty] | TO |  |  |  |  | 2007-06-18 |  | 2014-06-30 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5682 | 5684 | 1. | 5685 | MOD-030-3 R1.2.1. | Define if the source used for AFC calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | 2017-04-01 |  | 2024-02-01 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5682 | 5684 | 2. | 5686 | MOD-030-3 R1.2.2. | Define if the sink used for AFC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | 2017-04-01 |  | 2024-02-01 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5682 | 5684 | 3. | 5687 | MOD-030-3 R1.2.3. | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  | 2017-04-01 |  | 2024-02-01 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5682 | 5684 | 4. | 5688 | MOD-030-3 R1.2.4. | If the Transmission Service Provider’s AFC calculation process involves a grouping of generators, the ATCID must identify how these generators participate in the group. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | 2017-04-01 |  | 2024-02-01 |  |  | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5682 |  | 1. | 5683 | MOD-030-3 R1.1. | The criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates that are to be considered in Available Flowgate Capability (AFC) calculations. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | 2016-01-25 |  | 2024-02-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5682 |  | 2. | 5684 | MOD-030-3 R1.2. | The following information on how source and sink for transmission service is accounted for in AFC calculations including: |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | 2016-01-25 |  | 2024-02-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5682 |  | 2.3. DO NOT USE | RP-2021-07-07-0000018 | MOD-030-3 R1.2.3. DO NOT USE | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall provide its ATCID and other evidence (such as written documentation) to show that its ATCID contains the criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates and information on how sources and sinks are accounted for in AFC calculations. (R1) | 2017-04-01 |  | 2024-02-01 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 | 5690 | 1. | 5691 | MOD-030-3 R2.1.1. | Results of a first Contingency transfer analysis for ATC Paths internal to a Transmission Operator’s system up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an OTDF of at least 5% and within the Transmission Operator’s system are included as Flowgates. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2017-04-01 |  | 2024-02-01 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 | 5690 | 2. | 5695 | MOD-030-3 R2.1.2. | Results of a first Contingency transfer analysis from all adjacent Balancing Authority source and sink (as defined in the ATCID) combinations up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an Outage Transfer Distribution Factor (OTDF) of at least 5% and within the Transmission Operator’s system are included as Flowgates unless the interface between such adjacent Balancing Authorities is accounted for using another ATC methodology. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2017-04-01 |  | 2024-02-01 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 | 5690 | 2.2. | 5697 | MOD-030-3 R2.1.2.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2017-04-01 |  | 2024-02-01 |  |  | 2122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 | 5690 | 3. | 5700 | MOD-030-3 R2.1.3. | Any limiting Element/Contingency combination at least within its Reliability Coordinator’s Area that has been subjected to an Interconnection-wide congestion management procedure within the last 12 months, unless the limiting Element/Contingency combination is accounted for using another ATC methodology or was created to address temporary operating conditions. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2017-04-01 |  | 2024-02-01 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 | 5690 | 4. | 5701 | MOD-030-3 R2.1.4. | Any limiting Element/Contingency combination within the Transmission model that has been requested to be included by any other Transmission Service Provider using the Flowgate Methodology or Area Interchange Methodology, where: |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2017-04-01 |  | 2024-02-01 |  |  | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 | 5691 | 1. | 5692 | MOD-030-3 R2.1.1.1. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Remedial Action Schemes. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 |  | 2024-02-01 |  |  | 21110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 | 5691 | 2. | 5693 | MOD-030-3 R2.1.1.2. | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2017-04-01 |  | 2024-02-01 |  |  | 21120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 | 5691 | 3. | 5694 | MOD-030-3 R2.1.1.3. | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2017-04-01 |  | 2024-02-01 |  |  | 21130000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 | 5695 | 1. | 5696 | MOD-030-3 R2.1.2.1. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Remedial Action Schemes. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 |  | 2024-02-01 |  |  | 21210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 | 5695 | 3. | 5699 | MOD-030-3 R2.1.2.3. | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2017-04-01 |  | 2024-02-01 |  |  | 21230000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 | 5701 | 1. | 5702 | MOD-030-3 R2.1.4.1. | The coordination of the limiting Element/Contingency combination is not already addressed through a different methodology, and - Any generator within the Transmission Service Provider’s area has at least a 5% Power Transfer Distribution Factor (PTDF) or Outage Transfer Distribution Factor (OTDF) impact on the Flowgate when delivered to the aggregate load of its own area, or - A transfer from any Balancing Area within the Transmission Service Provider’s area to a Balancing Area adjacent has at least a 5% PTDF or OTDF impact on the Flowgate. - The Transmission Operator may utilize distribution factors less than 5% if desired. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2017-04-01 |  | 2024-02-01 |  |  | 21410000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 | 5701 | 2. | 5703 | MOD-030-3 R2.1.4.2. | The limiting Element/Contingency combination is included in the requesting Transmission Service Provider’s methodology. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2017-04-01 |  | 2024-02-01 |  |  | 21420000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 | 5707 | 1. | 5708 | MOD-030-3 R2.5.1. | If notified of a change in the Rating by the Transmission Owner that would affect the TFC of a flowgate used in the AFC process, the TFC should be updated within seven calendar days of the notification. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2017-04-01 |  | 2024-02-01 |  |  | 251000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 |  | 1. | 5690 | MOD-030-3 R2.1. | Include Flowgates used in the AFC process based, at a minimum, on the following criteria |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2016-01-25 |  | 2024-02-01 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 |  | 1.1.1. DO NOT USE | RP-2021-07-07-0000019 | MOD-030-3 R2.1.1.1. DO NOT USE | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Remedial Action Schemes. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2017-04-01 |  | 2024-02-01 |  |  | 211100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 |  | 1.2.1. DO NOT USE | RP-2021-07-07-0000020 | MOD-030-3 R2.1.2.1. DO NOT USE | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Remedial Action Schemes. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2017-04-01 |  | 2024-02-01 |  |  | 212100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 |  | 1.2.2. DO NOT USE | RP-2021-07-07-0000021 | MOD-030-3 R2.1.2.2. DO NOT USE | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2017-04-01 |  | 2024-02-01 |  |  | 212200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 |  | 2. | 5704 | MOD-030-3 R2.2. | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgate definitions at least once per calendar year. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2016-01-25 |  | 2024-02-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 |  | 3. | 5705 | MOD-030-3 R2.3. | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgates that have been requested as part of R2.1.4 within thirty calendar days from the request. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2016-01-25 |  | 2024-02-01 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 |  | 4. | 5706 | MOD-030-3 R2.4. | Establish the TFC of each of the defined Flowgates as equal to: - For thermal limits, the System Operating Limit (SOL) of the Flowgate. - For voltage or stability limits, the flow that will respect the SOL of the Flowgate |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2016-01-25 |  | 2024-02-01 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 |  | 5. | 5707 | MOD-030-3 R2.5. | At a minimum, establish the TFC once per calendar year. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2016-01-25 |  | 2024-02-01 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5689 |  | 6. | 5709 | MOD-030-3 R2.6. | Provide the Transmission Service Provider with the TFCs within seven calendar days of their establishment. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as studies and working papers) that all Flowgates that meet the criteria described in R2.1 are considered in its AFC calculations.(R2.1) | 2016-01-25 |  | 2024-02-01 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5710 |  | 1. | 5711 | MOD-030-3 R3.1. | Contains generation Facility Ratings, such as generation maximum and minimum output levels, specified by the Generator Owners of the Facilities within the model. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | 2016-01-25 |  | 2024-02-01 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5710 |  | 2. | 5712 | MOD-030-3 R3.2. | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 |  | 2024-02-01 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5710 |  | 2. DO NOT USE | RP-2021-07-07-0000022 | MOD-030-3 R3.2. DO NOT USE | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | 2017-04-01 |  | 2024-02-01 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5710 |  | 3. | 5713 | MOD-030-3 R3.3. | Updated at least once per month for AFC calculations for months two through 13. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 |  | 2024-02-01 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5710 |  | 3. DO NOT USE | RP-2021-07-07-0000023 | MOD-030-3 R3.3. DO NOT USE | Updated at least once per month for AFC calculations for months two through 13. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | 2017-04-01 |  | 2024-02-01 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5710 |  | 4. | 5714 | MOD-030-3 R3.4. | Contains modeling data and system topology for the Facilities within its Reliability Coordinator’s Area. Equivalent representation of radial lines and Facilities161kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | 2016-01-25 |  | 2024-02-01 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5710 |  | 5. | 5715 | MOD-030-3 R3.5. | Contains modeling data and system topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination Areas. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall provide evidence (such as logs) that it updated its list of Flowgates at least once per calendar year. (R2.2) | 2016-01-25 |  | 2024-02-01 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5717 |  | 1. | 5718 | MOD-030-3 R5.1. | Use the models provided by the Transmission Operator. |  | TSP | [20 empty] | TSP |  | 2016-01-25 |  | 2024-02-01 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5717 |  | 1. DO NOT USE | RP-2021-07-07-0000024 | MOD-030-3 R5.1. DO NOT USE | Use the models provided by the Transmission Operator. |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as data or models) that it determined the TFC for each Flowgate as defined in R2.4. (R2.4) | 2017-04-01 |  | 2024-02-01 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5717 |  | 2. | 5719 | MOD-030-3 R5.2. | Include in the transmission model expected generation and Transmission outages, additions, and retirements within the scope of the model as specified in the ATCID and in effect during the applicable period of the AFC calculation for the Transmission Service Provider’s area, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as data or models) that it determined the TFC for each Flowgate as defined in R2.4. (R2.4) | 2016-01-25 |  | 2024-02-01 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5717 |  | 3. | 5720 | MOD-030-3 R5.3. | For external Flowgates, identified in R2.1.4, use the AFC provided by the Transmission Service Provider that calculates AFC for that Flowgate. |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as data or models) that it determined the TFC for each Flowgate as defined in R2.4. (R2.4) | 2016-01-25 |  | 2024-02-01 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5721 | 5722 | 1. | 5723 | MOD-030-3 R6.1.1. | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | 2017-04-01 |  | 2024-02-01 |  |  | 611000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5721 | 5722 | 2. | 5724 | MOD-030-3 R6.1.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  | 2017-04-01 |  | 2024-02-01 |  |  | 612000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5721 | 5725 | 1. | 5726 | MOD-030-3 R6.2.1. | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | 2017-04-01 |  | 2024-02-01 |  |  | 621000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5721 | 5725 | 2. | 5727 | MOD-030-3 R6.2.2. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  | 2017-04-01 |  | 2024-02-01 |  |  | 622000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5721 |  | 1. | 5722 | MOD-030-3 R6.1. | The impact of firm Network Integration Transmission Service, including the impacts of generation to load, in the model referenced in R5.2 for the Transmission Service Provider’s area, based on: |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | 2016-01-25 |  | 2024-02-01 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5721 |  | 1.2. DO NOT USE | RP-2021-07-07-0000025 | MOD-030-3 R6.1.2. DO NOT USE | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | 2017-04-01 |  | 2024-02-01 |  |  | 612000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5721 |  | 2. | 5725 | MOD-030-3 R6.2. | The impact of any firm Network Integration Transmission Service, including the impacts of generation to load in the model referenced in R5.2 and has a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed based on: (Footnote:A percentage less than that used in the Interconnection-wide congestion management procedure may be utilized.) |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | 2016-01-25 |  | 2024-02-01 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5721 |  | 2.2. DO NOT USE | RP-2021-07-07-0000026 | MOD-030-3 R6.2.2. DO NOT USE | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | 2017-04-01 |  | 2024-02-01 |  |  | 622000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5721 |  | 3. | 5728 | MOD-030-3 R6.3. | The impact of all confirmed firm Point-to-Point Transmission Service expected to be scheduled, including roll-over rights for Firm Transmission Service contracts, for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | 2016-01-25 |  | 2024-02-01 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5721 |  | 4. | 5729 | MOD-030-3 R6.4. | The impact of any confirmed firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, including roll-over rights for Firm Transmission Service contracts having a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. (Footnote: A percentage less than that used in the Interconnection-wide congestion management procedure may be utilized.) |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | 2016-01-25 |  | 2024-02-01 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5721 |  | 5. | 5730 | MOD-030-3 R6.5. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | 2016-01-25 |  | 2024-02-01 |  |  | 650000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5721 |  | 6. | 5731 | MOD-030-3 R6.6. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. (Footnote: A percentage less than that used in the Interconnection-wide congestion management procedure may be utilized.) |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | 2016-01-25 |  | 2024-02-01 |  |  | 660000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5721 |  | 7. | 5732 | MOD-030-3 R6.7. | The impact of other firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs) that it established the TFCs for each Flowgate in accordance with the timing defined in R2.5. (R2.5) | 2016-01-25 |  | 2024-02-01 |  |  | 670000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5733 |  | 1. | 5734 | MOD-030-3 R7.1. | The impact of all confirmed non-firm Point-to-Point Transmission Service expected to be scheduled for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | 2016-01-25 |  | 2024-02-01 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5733 |  | 2. | 5735 | MOD-030-3 R7.2. | The impact of any confirmed non-firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | 2016-01-25 |  | 2024-02-01 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5733 |  | 3. | 5736 | MOD-030-3 R7.3. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | 2016-01-25 |  | 2024-02-01 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5733 |  | 4. | 5737 | MOD-030-3 R7.4. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | 2016-01-25 |  | 2024-02-01 |  |  | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5733 |  | 5. | 5738 | MOD-030-3 R7.5. | The impact of non-firm Network Integration Transmission Service serving Load within the Transmission Service Provider’s area (i.e., secondary service), to include load growth, and losses not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | 2016-01-25 |  | 2024-02-01 |  |  | 750000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5733 |  | 6. | 5739 | MOD-030-3 R7.6. | The impact of any non-firm Network Integration Transmission Service (secondary service) with a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | 2016-01-25 |  | 2024-02-01 |  |  | 760000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5733 |  | 7. | 5740 | MOD-030-3 R7.7. | The impact of other non-firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP | The Transmission Operator shall provide evidence (such as logs and electronic communication) that it provided the Transmission Service Provider with updated TFCs within seven calendar days of their determination. (R2.6) | 2016-01-25 |  | 2024-02-01 |  |  | 770000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5743 |  | 1. | 5744 | MOD-030-3 R10.1. | For hourly AFC, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the AFC equation. |  | TSP | [20 empty] | TSP | The Transmission Service Provider shall provide evidence including the models received from Transmission Operators and other evidence (such as documentation and data) to show that it used the Transmission Operator’s models in calculating AFC. (R5.1) | 2016-01-25 |  | 2024-02-01 |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5743 |  | 2. | 5745 | MOD-030-3 R10.2. | For daily AFC, once per day. |  | TSP | [20 empty] | TSP | The Transmission Service Provider shall provide evidence including the models received from Transmission Operators and other evidence (such as documentation and data) to show that it used the Transmission Operator’s models in calculating AFC. (R5.1) | 2016-01-25 |  | 2024-02-01 |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
480 | 5743 |  | 3. | 5746 | MOD-030-3 R10.3. | For monthly AFC, once per week. |  | TSP | [20 empty] | TSP | The Transmission Service Provider shall provide evidence including the models received from Transmission Operators and other evidence (such as documentation and data) to show that it used the Transmission Operator’s models in calculating AFC. (R5.1) | 2016-01-25 |  | 2024-02-01 |  |  | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5779 |  | 1. | 5780 | NUC-001-2.1(i) R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5779 |  | 2. | 5781 | NUC-001-2.1(i) R4.2. | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5779 |  | 3. | 5782 | NUC-001-2.1(i) R4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5788 | 1. | 5789 | NUC-001-2.1(i) R9.1.1. | Definitions of key terms used in the agreement. (Retirement approved by FERC effective January 21, 2014.) |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 911000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5788 | 2. | 5790 | NUC-001-2.1(i) R9.1.2. | Names of the responsible entities, organizational relationships, and responsibilities related to the NPIRs. (Retirement approved by FERC effective January 21, 2014.) |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 912000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5788 | 3. | 5791 | NUC-001-2.1(i) R9.1.3. | A requirement to review the agreement(s) at least every three years. (Retirement approved by FERC effective January 21, 2014.) |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 913000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5788 | 4. | 5792 | NUC-001-2.1(i) R9.1.4. | A dispute resolution mechanism. (Retirement approved by FERC effective January 21, 2014.) |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 914000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5793 | 1. | 5794 | NUC-001-2.1(i) R9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 921000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5793 | 2. | 5795 | NUC-001-2.1(i) R9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 922000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5793 | 3. | 5796 | NUC-001-2.1(i) R9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 923000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5797 | 1. | 5798 | NUC-001-2.1(i) R9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 931000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5797 | 2. | 5799 | NUC-001-2.1(i) R9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 932000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5797 | 3. | 5800 | NUC-001-2.1(i) R9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 933000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5797 | 4. | 5801 | NUC-001-2.1(i) R9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 934000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5797 | 5. | 5802 | NUC-001-2.1(i) R9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 935000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5797 | 6. | 5803 | NUC-001-2.1(i) R9.3.6. | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 936000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5797 | 7. | 5804 | NUC-001-2.1(i) R9.3.7. | Coordination of the NPIRs with transmission system Remedial Action Schemes and underfrequency and undervoltage load shedding programs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 937000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5805 | 1. | 5806 | NUC-001-2.1(i) R9.4.1. | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  | 941000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5805 | 2. | 5807 | NUC-001-2.1(i) R9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 942000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5805 | 3. | 5808 | NUC-001-2.1(i) R9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 943000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5805 | 4. | 5809 | NUC-001-2.1(i) R9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 944000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 | 5805 | 5. | 5810 | NUC-001-2.1(i) R9.4.5. | Provisions for personnel training, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 945000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 |  | 1. | 5788 | NUC-001-2.1(i) R9.1. | Administrative elements: (Retirement approved by FERC effective January 21, 2014.) | [26 empty] | 2014-11-13 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 |  | 2. | 5793 | NUC-001-2.1(i) R9.2. | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 |  | 3. | 5797 | NUC-001-2.1(i) R9.3. | Operations and maintenance coordination: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 930000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
482 | 5787 |  | 4. | 5805 | NUC-001-2.1(i) R9.4. | Communications and training: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PCPA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  | 940000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5811 | 5814 | 1. | 5815 | TPL-001-0.1(i) R1.3.1. | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5811 | 5814 | 2. | 5816 | TPL-001-0.1(i) R1.3.2. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5811 | 5814 | 3. | 5817 | TPL-001-0.1(i) R1.3.3. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5811 | 5814 | 4. | 5818 | TPL-001-0.1(i) R1.3.4. | Have established normal (pre-contingency) operating procedures in place. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5811 | 5814 | 5. | 5819 | TPL-001-0.1(i) R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5811 | 5814 | 6. | 5820 | TPL-001-0.1(i) R1.3.6. | Be performed for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5811 | 5814 | 7. | 5821 | TPL-001-0.1(i) R1.3.7. | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5811 | 5814 | 8. | 5822 | TPL-001-0.1(i) R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5811 | 5814 | 9. | 5823 | TPL-001-0.1(i) R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5811 |  | 1. | 5812 | TPL-001-0.1(i) R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5811 |  | 2. | 5813 | TPL-001-0.1(i) R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5811 |  | 3. | 5814 | TPL-001-0.1(i) R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5811 |  | 4. | 5824 | TPL-001-0.1(i) R1.4. | Address any planned upgrades needed to meet the performance requirements of Category A. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5825 | 5826 | 1. | 5827 | TPL-001-0.1(i) R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5825 | 5826 | 2. | 5828 | TPL-001-0.1(i) R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5825 | 5826 | 3. | 5829 | TPL-001-0.1(i) R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5825 |  | 1. | 5826 | TPL-001-0.1(i) R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
483 | 5825 |  | 2. | 5830 | TPL-001-0.1(i) R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 | 5835 | 1. | 5836 | TPL-002-0(i)b R1.3.1. | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 | 5835 | 10. | 5845 | TPL-002-0(i)b R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 1310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 | 5835 | 11. | 5846 | TPL-002-0(i)b R1.3.11. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 1311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 | 5835 | 12. | 5847 | TPL-002-0(i)b R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 1312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 | 5835 | 2. | 5837 | TPL-002-0(i)b R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 | 5835 | 3. | 5838 | TPL-002-0(i)b R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 | 5835 | 4. | 5839 | TPL-002-0(i)b R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 | 5835 | 5. | 5840 | TPL-002-0(i)b R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 | 5835 | 6. | 5841 | TPL-002-0(i)b R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 | 5835 | 7. | 5842 | TPL-002-0(i)b R1.3.7. | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 | 5835 | 8. | 5843 | TPL-002-0(i)b R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 | 5835 | 9. | 5844 | TPL-002-0(i)b R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 |  | 1. | 5833 | TPL-002-0(i)b R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 |  | 2. | 5834 | TPL-002-0(i)b R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 |  | 3. | 5835 | TPL-002-0(i)b R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 |  | 4. | 5848 | TPL-002-0(i)b R1.4. | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5832 |  | 5. | 5849 | TPL-002-0(i)b R1.5. | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5850 | 5851 | 1. | 5852 | TPL-002-0(i)b R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5850 | 5851 | 2. | 5853 | TPL-002-0(i)b R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5850 | 5851 | 3. | 5854 | TPL-002-0(i)b R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5850 |  | 1. | 5851 | TPL-002-0(i)b R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
484 | 5850 |  | 2. | 5855 | TPL-002-0(i)b R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 | 5860 | 1. | 5861 | TPL-003-0(i)b R1.3.1. | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 | 5860 | 10. | 5870 | TPL-003-0(i)b R1.3.10. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 1310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 | 5860 | 11. | 5871 | TPL-003-0(i)b R1.3.11. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 1311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 | 5860 | 12. | 5872 | TPL-003-0(i)b R1.3.12. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 1312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 | 5860 | 2. | 5862 | TPL-003-0(i)b R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 | 5860 | 3. | 5863 | TPL-003-0(i)b R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 | 5860 | 4. | 5864 | TPL-003-0(i)b R1.3.4. | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 | 5860 | 5. | 5865 | TPL-003-0(i)b R1.3.5. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 | 5860 | 6. | 5866 | TPL-003-0(i)b R1.3.6. | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 | 5860 | 7. | 5867 | TPL-003-0(i)b R1.3.7. | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 | 5860 | 8. | 5868 | TPL-003-0(i)b R1.3.8. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 | 5860 | 9. | 5869 | TPL-003-0(i)b R1.3.9. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 |  | 1. | 5858 | TPL-003-0(i)b R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 |  | 2. | 5859 | TPL-003-0(i)b R1.2. | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 |  | 3. | 5860 | TPL-003-0(i)b R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 |  | 4. | 5873 | TPL-003-0(i)b R1.4. | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5857 |  | 5. | 5874 | TPL-003-0(i)b R1.5. | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5875 | 5876 | 1. | 5877 | TPL-003-0(i)b R2.1.1. | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5875 | 5876 | 2. | 5878 | TPL-003-0(i)b R2.1.2. | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5875 | 5876 | 3. | 5879 | TPL-003-0(i)b R2.1.3. | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5875 |  | 1. | 5876 | TPL-003-0(i)b R2.1. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
485 | 5875 |  | 2. | 5880 | TPL-003-0(i)b R2.2. | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
486 | 5882 | 5885 | 1. | 5886 | TPL-004-0(i)a R1.3.1. | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
486 | 5882 | 5885 | 2. | 5887 | TPL-004-0(i)a R1.3.2. | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
486 | 5882 | 5885 | 3. | 5888 | TPL-004-0(i)a R1.3.3. | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
486 | 5882 | 5885 | 4. | 5889 | TPL-004-0(i)a R1.3.4. | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
486 | 5882 | 5885 | 5. | 5890 | TPL-004-0(i)a R1.3.5. | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
486 | 5882 | 5885 | 6. | 5891 | TPL-004-0(i)a R1.3.6. | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 136000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
486 | 5882 | 5885 | 7. | 5892 | TPL-004-0(i)a R1.3.7. | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 137000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
486 | 5882 | 5885 | 8. | 5893 | TPL-004-0(i)a R1.3.8. | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 138000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
486 | 5882 | 5885 | 9. | 5894 | TPL-004-0(i)a R1.3.9. | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  | 139000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
486 | 5882 |  | 1. | 5883 | TPL-004-0(i)a R1.1. | Be made annually. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
486 | 5882 |  | 2. | 5884 | TPL-004-0(i)a R1.2. | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
486 | 5882 |  | 3. | 5885 | TPL-004-0(i)a R1.3. | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
486 | 5882 |  | 4. | 5895 | TPL-004-0(i)a R1.4. | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
487 | 5897 | 5899 | 3. | 5900 | PRC-012-1 R1.2.3. | Requirements to demonstrate that the RAS shall be designed so that a single RAS component failure, when the RAS was intended to operate, does not prevent the interconnected transmission system from meeting the performance requirements defined in Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
487 | 5897 |  | 1. | 5898 | PRC-012-1 R1.1. | Description of the process for submitting a proposed RAS for Regional Reliability Organization review. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
487 | 5897 |  | 2. | 5899 | PRC-012-1 R1.2. | Requirements to provide data that describes design, operation, and modeling of a RAS. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
487 | 5897 |  | 3. | 5901 | PRC-012-1 R1.3. | Requirements to demonstrate that the RAS shall be designed so that a single RAS component failure, when the RAS was intended to operate, does not prevent the interconnected transmission system from meeting the performance requirements defined in Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
487 | 5897 |  | 4. | 5902 | PRC-012-1 R1.4. | Requirements to demonstrate that the inadvertent operation of a RAS shall meet the same performance requirement (TPL-001-0, TPL-002-0, and TPL-003-0) as that required of the contingency for which it was designed, and not exceed TPL-003-0. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
487 | 5897 |  | 5. | 5903 | PRC-012-1 R1.5. | Requirements to demonstrate the proposed RAS will coordinate with other protection and control systems and applicable Regional Reliability Organization Emergency procedures. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
487 | 5897 |  | 6. | 5904 | PRC-012-1 R1.6. | Regional Reliability Organization definition of misoperation. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
487 | 5897 |  | 7. | 5905 | PRC-012-1 R1.7. | Requirements for analysis and documentation of corrective action plans for all RAS misoperations. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
487 | 5897 |  | 8. | 5906 | PRC-012-1 R1.8. | Identification of the Regional Reliability Organization group responsible for the Regional Reliability Organization’s review procedure and the process for Regional Reliability Organization approval of the procedure. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
487 | 5897 |  | 9. | 5907 | PRC-012-1 R1.9. | Determination, as appropriate, of maintenance and testing requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
489 | 5916 |  | 1. | 5917 | PRC-014-1 R3.1. | Identification of group conducting the assessment and the date the assessment was performed. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
489 | 5916 |  | 2. | 5918 | PRC-014-1 R3.2. | Study years, system conditions, and contingencies analyzed in the technical studies on which the assessment is based and when those technical studies were performed. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
489 | 5916 |  | 3. | 5919 | PRC-014-1 R3.3. | Identification of RAS that were found not to comply with NERC standards and Regional Reliability Organization criteria. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
489 | 5916 |  | 4. | 5920 | PRC-014-1 R3.4. | Discussion of any coordination problems found between a RAS and other protection and control systems. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
489 | 5916 |  | 5. | 5921 | PRC-014-1 R3.5. | Provide corrective action plans for non-compliant RAS. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
490 | 5922 |  | 1. | 5923 | PRC-013-1 R1.1. | Design Objectives — Contingencies and system conditions for which the RAS was designed, |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
490 | 5922 |  | 2. | 5924 | PRC-013-1 R1.2. | Operation — The actions taken by the RAS in response to Disturbance conditions, and |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
490 | 5922 |  | 3. | 5925 | PRC-013-1 R1.3. | Modeling — Information on detection logic or relay settings that control operation of the RAS. |  | RRO | [14 empty] | RRO | [9 empty] | 2020-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
493 | 5933 | 5934 | 1. | 5935 | PRC-017-1 R1.1.1. | Relays. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | 2017-04-01 |  | 2027-03-31 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
493 | 5933 | 5934 | 2. | 5936 | PRC-017-1 R1.1.2. | Instrument transformers. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2017-04-01 |  | 2027-03-31 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
493 | 5933 | 5934 | 3. | 5940 | PRC-017-1 R1.1.3. | Summary of testing procedure. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | 2017-04-01 |  | 2027-03-31 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
493 | 5933 | 5934 | 4. | 5938 | PRC-017-1 R1.1.4. | Batteries. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | 2017-04-01 |  | 2027-03-31 |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
493 | 5933 |  | 1. | 5934 | PRC-017-1 R1.1. | RAS identification shall include but is not limited to: |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | 2016-01-25 |  | 2027-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
493 | 5933 |  | 2. | 5939 | PRC-017-1 R1.2. | Documentation of maintenance and testing intervals and their basis. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | 2016-01-25 |  | 2027-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
493 | 5933 |  | 3. | 5941 | PRC-017-1 R1.3. | Summary of testing procedure. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | 2016-01-25 |  | 2027-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
493 | 5933 |  | 4. | 5942 | PRC-017-1 R1.4. | Schedule for system testing. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | 2016-01-25 |  | 2027-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
493 | 5933 |  | 5. | 5943 | PRC-017-1 R1.5. | Schedule for system maintenance. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | 2016-01-25 |  | 2027-03-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
493 | 5933 |  | 6. | 5944 | PRC-017-1 R1.6. | Date last tested/maintained. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place that includes all items in Reliability Standard PRC-017-1_R1. | 2016-01-25 |  | 2027-03-31 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
494 | 5946 |  | 1. | 5947 | PRC-020-2 R1.1. | Owner and operator of the UVLS program. | [26 empty] | 2014-11-13 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
494 | 5946 |  | 2. | 5948 | PRC-020-2 R1.2. | Size and location of customer load, or percent of connected load, to be interrupted. | [26 empty] | 2014-11-13 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
494 | 5946 |  | 3. | 5949 | PRC-020-2 R1.3. | Corresponding voltage set points and overall scheme clearing times. | [26 empty] | 2014-11-13 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
494 | 5946 |  | 4. | RP-2021-06-08-0000024 | PRC-020-2 R1.4. | Time delay from initiation to trip signal | [26 empty] | 2014-11-13 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
494 | 5946 |  | 5. | 5951 | PRC-020-2 R1.5. | Breaker operating times. | [26 empty] | 2014-11-13 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
494 | 5946 |  | 6. | 5952 | PRC-020-2 R1.6. | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Remedial Action Schemes. | [26 empty] | 2014-11-13 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
495 | 5954 |  | 1. | 5955 | PRC-021-2 R1.1. | Size and location of customer load, or percent of connected load, to be interrupted. | [26 empty] | 2014-11-13 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
495 | 5954 |  | 2. | 5956 | PRC-021-2 R1.2. | Corresponding voltage set points and overall scheme clearing times. | [26 empty] | 2014-11-13 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
495 | 5954 |  | 3. | 5957 | PRC-021-2 R1.3. | Time delay from initiation to trip signal. |  | DP, TO |  | DP | [15 empty] | TO | [6 empty] | 2014-11-13 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
495 | 5954 |  | 4. | 5958 | PRC-021-2 R1.4. | Breaker operating times. | [26 empty] | 2014-11-13 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
495 | 5954 |  | 5. | 5959 | PRC-021-2 R1.5. | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Remedial Action Schemes. | [26 empty] | 2014-11-13 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
496 | 5962 |  | 1. | 5963 | PRC-001-1.1(i) R2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | GOP | [5 empty] | GOP | [16 empty] | 2016-01-25 |  | 2015-05-28 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
496 | 5962 |  | 2. | 5964 | PRC-001-1.1(i) R2.2. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 |  | 2015-05-28 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
496 | 5965 |  | 1. | 5966 | PRC-001-1.1(i) R3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2016-01-25 |  | 2015-05-28 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
496 | 5965 |  | 2. | 5967 | PRC-001-1.1(i) R3.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 |  | 2015-05-28 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
496 | 5969 |  | 1. | 5970 | PRC-001-1.1(i) R5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. |  | GOP | [5 empty] | GOP | [16 empty] | 2016-01-25 |  | 2015-05-28 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
496 | 5969 |  | 2. | 5985 | PRC-001-1.1(i) R5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. |  | TO | [17 empty] | TO |  |  |  |  | 2016-01-25 |  | 2015-05-28 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
497 | 5973 |  | 1. | 5986 | PRC-004-WECC-2 R1.1. | System Operators shall review all tripping of transmission elements and RAS operations to identify apparent Misoperations within 24 hours. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M1.1 Transmission Owners and Generation Owners shall have evidence that System Operating personnel reviewed all operations of Protection System and RAS within 24 hours. | 2016-01-25 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf.. 4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. | 110000000 | WECC-US | [5 empty] | WECC-US
497 | 5973 |  | 2. | 5987 | PRC-004-WECC-2 R1.2. | System Protection personnel shall analyze all operations of Protection Systems and RAS within 20 business days for correctness to characterize whether a Misoperation has occurred that may not have been identified by System Operators. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M1.2 Transmission Owners and Generation Owners shall have evidence that System Protection personnel analyzed all operations of Protection System and RAS for correctness within 20 business days. | 2016-01-25 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf.. 4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. | 120000000 | WECC-US | [5 empty] | WECC-US
497 | 5974 | 5988 | 1. | 5976 | PRC-004-WECC-2 R2.2.1. | Following identification of the Protection System or RAS Misoperation, Transmission Owners and Generator Owners shall remove from service within 22 hours for repair or modification the Protection System or RAS that misoperated. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf.. 4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. | 221000000 | WECC-US | [5 empty] | WECC-US
497 | 5974 | 5988 | 2. | RP-2021-09-02-0000009 | PRC-004-WECC-2 R2.2.2. | The Transmission Owner or Generator Owner shall repair or replace any Protection System or RAS that misoperated with a FEPS or FERAS within 20 business days of the date of removal. The Transmission Owner or Generator Owner shall remove the Element from service or disable the RAS if repair or replacement is not completed within 20 business days. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf.. 4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. | 222000000 | WECC-US | [5 empty] | WECC-US
497 | 5974 | 5991 | 1. | 5992 | PRC-004-WECC-2 R2.3.1. | When a FEPS is not available, the Transmission Owners shall remove the associated Element from service. |  | TO | [17 empty] | TO |  |  |  | M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf.. 4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. | 231000000 | WECC-US | [5 empty] | WECC-US
497 | 5974 | 5991 | 2. | 5993 | PRC-004-WECC-2 R2.3.2. | When FERAS is not available, then | [23 empty] | M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf.. 4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. | 232000000 | WECC-US | [5 empty] | WECC-US
497 | 5974 | 5993 | 1. | 7841 | PRC-004-WECC-2 R2.3.2.1. | The Generator Owners shall adjust generation to a reliable operating level, or |  | GO |  |  |  |  | GO | [17 empty] | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf.. 4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. | 23210000 | WECC-US | [5 empty] | WECC-US
497 | 5974 | 5993 | 2. | 7842 | PRC-004-WECC-2 R2.3.2.2. | Transmission Operators shall adjust the SOL and operate the facilities within established limits. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf.. 4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. | 23220000 | WECC-US | [5 empty] | WECC-US
497 | 5974 | 5994 | 1. | 5995 | PRC-004-WECC-2 R2.4.1. | If the Protection System or RAS has a Dependability-Based Misoperation but has one or more FEPS or FERAS that operated correctly, the associated Element or transmission path may remain in service without removing from service the Protection System or RAS |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf.. 4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. | 241000000 | WECC-US | [5 empty] | WECC-US
497 | 5974 | 5994 | 2. | 5996 | PRC-004-WECC-2 R2.4.2. | Transmission Owners or Generator Owners shall remove from service the associated Element or RAS. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf.. 4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. | 242000000 | WECC-US | [5 empty] | WECC-US
497 | 5974 |  | 1. | 5975 | PRC-004-WECC-2 R2.1. | If the Protection System or RAS has a Security-Based Misoperation and two or more Functionally Equivalent Protection Systems (FEPS) or Functionally Equivalent RAS (FERAS) remain in service to ensure Bulk Electric System (BES) reliability, the Transmission Owners or Generator Owners shall remove from service the Protection System or RAS that misoperated within 22 hours following identification of the Misoperation. Repair or replacement of the failed Protection System or RAS is at the Transmission Owners’ and Generator Owners’ discretion. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. | 2016-01-25 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf.. 4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. | 210000000 | WECC-US | [5 empty] | WECC-US
497 | 5974 |  | 2. | 5988 | PRC-004-WECC-2 R2.2. | If the Protection System or RAS has a Security-Based Misoperation and only one FEPS or FERAS remains in service to ensure BES reliability, the Transmission Owner or Generator Owner shall perform the following. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2016-01-25 |  | 2021-01-01 |  |  | 220000000 | WECC-US | [5 empty] | WECC-US
497 | 5974 |  | 3. | 5991 | PRC-004-WECC-2 R2.3. | If the Protection System or RAS has a Security-Based or Dependability-Based Misoperation and a FEPS and FERAS is not in service to ensure BES reliability, Transmission Owners or Generator Owners shall repair and place back in service within 22 hours the Protection System or RAS that misoperated. If this cannot be done, then Transmission Owners and Generator Owners shall perform the following. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. | 2016-01-25 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf.. 4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. | 230000000 | WECC-US | [5 empty] | WECC-US
497 | 5974 |  | 4. | 5994 | PRC-004-WECC-2 R2.4. | If the Protection System or RAS has a Dependability-Based Misoperation but has one or more FEPS or FERAS that operated correctly, the associated Element or transmission path may remain in service without removing from service the Protection System or RAS | [23 empty] | M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf.. 4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. | 240000000 | WECC-US | [5 empty] | WECC-US
497 | 5997 |  | 1. | 5998 | PRC-004-WECC-2 R3.1. | Identification of a Misoperation of a Protection System and/or RAS, | [23 empty] | M3.1 Identification of all Protection System and RAS Misoperations and corrective actions taken or planned. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf.. 4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. | 310000000 | WECC-US | [5 empty] | WECC-US
497 | 5997 |  | 2. | 5999 | PRC-004-WECC-2 R3.2. | Completion of repairs or the replacement of Protection System and/or RAS that misoperated. | [23 empty] | M3.2 Completion of repair or replacement of Protection System and/or RAS that misoperated. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf.. 4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. | 320000000 | WECC-US | [5 empty] | WECC-US
498 | 5977 |  | 1. | 6883 | PRC-010-1 R1.1. | The implementation of the UVLS Program resolves the identified undervoltage issues that led to its development and design. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2016-01-25 |  | 2017-04-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
498 | 5977 |  | 2. | RP-2021-06-24-0000023 | PRC-010-1 R1.2. | The UVLS Program isintegrated through coordination with generator voltage ride‐through capabilities and other protection and controlsystems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2017-04-01 |  | 2017-04-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
498 | 5979 |  | 1. | RP-2021-06-24-0000024 | PRC-010-1 R3.1. | The UVLS Program resolvesthe identified undervoltage issuesfor which the UVLS Program is designed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2017-04-01 |  | 2017-04-01 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
498 | 5979 |  | 2. | RP-2021-06-24-0000025 | PRC-010-1 R3.2. | The UVLS Program isintegrated through coordination with generator voltage ride‐through capabilities and other protection and controlsystems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage‐based load shedding programs. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2017-04-01 |  | 2017-04-01 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
499 | 6000 |  | 1. | 7159 | PRC-005-2(ii) R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
499 | 6000 |  | 2. | 7161 | PRC-005-2(ii) R1.2. | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5 | 17 |  | 1. | 18 | BAL-002-0 R1.1. | A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a Reserve Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority with respect to monitoring and meeting the requirements of Standard BAL-002. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5 | 19 |  | 1. | 20 | BAL-002-0 R2.1. | The minimum reserve requirement for the group. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5 | 19 |  | 2. | 21 | BAL-002-0 R2.2. | Its allocation among members. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5 | 19 |  | 3. | 22 | BAL-002-0 R2.3. | The permissible mix of Operating Reserve - Spinning and Operating Reserve - Supplemental that may be included in Contingency Reserve. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5 | 19 |  | 4. | 23 | BAL-002-0 R2.4. | The procedure for applying Contingency Reserve in practice. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5 | 19 |  | 5. | 24 | BAL-002-0 R2.5. | The limitations, if any, upon the amount of interruptible load that may be included. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5 | 19 |  | 6. | 25 | BAL-002-0 R2.6. | The same portion of resource capacity (e.g., reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5 | 26 |  | 1. | 27 | BAL-002-0 R3.1. | As a minimum, the Balancing Authority or Reserve Sharing Group shall carry at least enough Contingency Reserve to cover the most severe single contingency. All Balancing Authorities and Reserve Sharing Groups shall review, no less frequently than annually, their probable contingencies to determine their prospective most severe single contingencies. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5 | 28 |  | 1. | 29 | BAL-002-0 R4.1. | A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre-Disturbance value. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5 | 28 |  | 2. | 30 | BAL-002-0 R4.2. | The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. This period may be adjusted to better suit the needs of an Interconnection based on analysis approved by the NERC Operating Committee. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5 | 31 |  | 1. | 32 | BAL-002-0 R5.1. | The Reserve Sharing Group reviews group ACE (or equivalent) and demonstrates compliance to the DCS. To be in compliance, the group ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. Or |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5 | 31 |  | 2. | 33 | BAL-002-0 R5.2. | The Reserve Sharing Group reviews each member’s ACE in response to the activation of reserves. To be in compliance, a member’s ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5 | 34 |  | 1. | 35 | BAL-002-0 R6.1. | The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5 | 34 |  | 2. | 36 | BAL-002-0 R6.2. | The default Contingency Reserve Restoration Period is 90 minutes. This period may be adjusted to better suit the reliability targets of the Interconnection based on analysis approved by the NERC Operating Committee. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
50 | 685 | 687 | 1. | 688 | FAC-008-1 R1.2.1. | The scope of equipment addressed shall include, but not be limited to, generators, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2012-12-31 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
50 | 685 | 687 | 2. | 689 | FAC-008-1 R1.2.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2012-12-31 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
50 | 685 | 690 | 1. | 691 | FAC-008-1 R1.3.1. | Ratings provided by equipment manufacturers. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2012-12-31 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
50 | 685 | 690 | 2. | 692 | FAC-008-1 R1.3.2. | Design criteria (e.g., including applicable references to industry Rating practices such as manufacturer’s warranty, IEEE, ANSI or other standards). |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2012-12-31 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
50 | 685 | 690 | 3. | 693 | FAC-008-1 R1.3.3. | Ambient conditions. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2012-12-31 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
50 | 685 | 690 | 4. | 694 | FAC-008-1 R1.3.4. | Operating limitations. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2012-12-31 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
50 | 685 | 690 | 5. | 695 | FAC-008-1 R1.3.5. | Other assumptions. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2012-12-31 |  |  | 135000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
50 | 685 |  | 1. | 686 | FAC-008-1 R1.1. | A statement that a Facility Rating shall equal the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2012-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
50 | 685 |  | 2. | 687 | FAC-008-1 R1.2. | The method by which the Rating (of major BES equipment that comprises a Facility) is determined. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2012-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
50 | 685 |  | 3. | 690 | FAC-008-1 R1.3. | Consideration of the following: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2007-06-18 |  | 2012-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
500 | 6005 |  | 1. | 6879 | PRC-005-3(ii) R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
500 | 6005 |  | 2. | 6880 | PRC-005-3(ii) R1.2. | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  |  | 2016-01-25 |  | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
501 | 6010 |  | 1. | 6831 | TOP-003-3 R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2021-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
501 | 6010 |  | 2. | 6832 | TOP-003-3 R1.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2021-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
501 | 6010 |  | 3. | 6833 | TOP-003-3 R1.3. | A periodicity for providing data. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2021-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
501 | 6010 |  | 4. | 6834 | TOP-003-3 R1.4. | The deadline by which the respondent is to provide the indicated data. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2021-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
501 | 6011 |  | 1. | 6835 | TOP-003-3 R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. |  | BA | BA | [21 empty] | 2016-01-26 |  | 2021-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
501 | 6011 |  | 2. | 6836 | TOP-003-3 R2.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | BA | BA | [21 empty] | 2016-01-26 |  | 2021-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
501 | 6011 |  | 3. | 6837 | TOP-003-3 R2.3. | A periodicity for providing data. |  | BA | BA | [21 empty] | 2016-01-26 |  | 2021-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
501 | 6011 |  | 4. | 6838 | TOP-003-3 R2.4. | The deadline by which the respondent is to provide the indicated data. |  | BA | BA | [21 empty] | 2016-01-26 |  | 2021-03-31 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
501 | 6014 |  | 1. | 6839 | TOP-003-3 R5.1. | A mutually agreeable format |  | BA, DP, GO, GOP, LSE, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
501 | 6014 |  | 2. | 6840 | TOP-003-3 R5.2. | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, LSE, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
501 | 6014 |  | 3. | 6841 | TOP-003-3 R5.3. | A mutually agreeable security protocol |  | BA, DP, GO, GOP, LSE, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 | 6023 | 1. | 6024 | MOD-029-2a R1.1.1. | Includes at least: |  | TOP | [18 empty] | TOP |  |  | Production shall be in the same form and format used by the Transmission Operator to calculate the TTC, as required in R1. (R1) | 2017-04-01 |  | 2024-02-01 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 | 6023 | 10. | 6040 | MOD-029-2a R1.1.10. | Includes any other modeling requirements or criteria specified in the ATCID. |  | TOP | [18 empty] | TOP |  |  | Production shall be in the same form and format used by the Transmission Operator to calculate the TTC, as required in R1. (R1) | 2017-04-01 |  | 2024-02-01 |  |  | 1110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 | 6023 | 2. | 6028 | MOD-029-2a R1.1.2. | Models all system Elements as in-service for the assumed initial conditions. |  | TOP | [18 empty] | TOP |  |  | Production shall be in the same form and format used by the Transmission Operator to calculate the TTC, as required in R1. (R1) | 2017-04-01 |  | 2024-02-01 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 | 6023 | 5. | 6035 | MOD-029-2a R1.1.5. | Uses Load forecast by Balancing Authority. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 |  | 2024-02-01 |  |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 | 6023 | 6. | 6036 | MOD-029-2a R1.1.6. | Uses Transmission Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 |  | 2024-02-01 |  |  | 116000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 | 6023 | 7. | 6037 | MOD-029-2a R1.1.7. | Uses Generation Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 |  | 2024-02-01 |  |  | 117000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 | 6023 | 8. | 6038 | MOD-029-2a R1.1.8. | Uses Remedial Action Scheme (RAS) models where currently existing or projected for implementation within the studied time horizon. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 |  | 2024-02-01 |  |  | 118000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 | 6023 | 9. | 6039 | MOD-029-2a R1.1.9. | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP |  |  | Production shall be in the same form and format used by the Transmission Operator to calculate the TTC, as required in R1. (R1) | 2017-04-01 |  | 2024-02-01 |  |  | 119000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 | 6024 | 1. | 6025 | MOD-029-2a R1.1.1.1. | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 |  | 2024-02-01 |  |  | 11110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 | 6024 | 2. | 6026 | MOD-029-2a R1.1.1.2. | All Transmission Operator areas contiguous with its own Transmission Operator area. (Equivalent representation is allowed.) |  | TOP | [18 empty] | TOP |  |  | Production shall be in the same form and format used by the Transmission Operator to calculate the TTC, as required in R1. (R1) | 2017-04-01 |  | 2024-02-01 |  |  | 11120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 | 6024 | 3. | 6027 | MOD-029-2a R1.1.1.3. | Any other Transmission Operator area linked to the Transmission Operator’s area by joint operating agreement. (Equivalent representation is allowed.) |  | TOP | [18 empty] | TOP |  |  | Production shall be in the same form and format used by the Transmission Operator to calculate the TTC, as required in R1. (R1) | 2017-04-01 |  | 2024-02-01 |  |  | 11130000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 |  | 1. | 6023 | MOD-029-2a R1.1. | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: |  | TOP | [18 empty] | TOP |  |  | M1.1. Production shall be in the same form and format used by the Transmission Operator to calculate the TTC, as required in R1. (R1) | 2016-01-25 |  | 2024-02-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 |  | 1.3. | 6029 | MOD-029-2a R1.1.3. | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. |  | TOP | [18 empty] | TOP |  |  | Production shall be in the same form and format used by the Transmission Operator to calculate the TTC, as required in R1. (R1) | 2017-04-01 |  | 2024-02-01 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 |  | 1.4. | 6030 | MOD-029-2a R1.1.4. | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). |  | TOP | [18 empty] | TOP |  |  | Production shall be in the same form and format used by the Transmission Operator to calculate the TTC, as required in R1. (R1) | 2017-04-01 |  | 2024-02-01 |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 |  | 2. | 6041 | MOD-029-2a R1.2. | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner |  | TOP | [18 empty] | TOP |  |  | M1.2. The Transmission model produced must include the areas listed in R1.1.1 (or an equivalent representation, as described in the requirement) (R1.1) M1.3. The Transmission model produced must show the use of the modeling parameters stated in R1.1.2 through R1.1.10; except that, no evidence shall be required to prove: 1) utilization of a Remedial Action Scheme where none was included in the model or 2) that no additions or retirements to the generation or Transmission system occurred. (R1.1.2 through R1.1.10) M1.4. The Transmission Operator must provide evidence that the models used to determine TTC included Facility Ratings as provided by the Transmission Owner and Generator Owner. (R1.2) | 2016-01-25 |  | 2024-02-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6015 |  | 2. DO NOT USE | RP-2021-07-07-0000011 | MOD-029-2a R1.2. DO NOT USE | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner |  | TOP | [18 empty] | TOP |  |  | The Transmission model produced must include the areas listed in R1.1.1 (or an equivalent representation, as described in the requirement) (R1.1) | 2017-04-01 |  | 2024-02-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6016 | 6042 | 1. | 7665 | MOD-029-2a R2.1.1. | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 |  | 2024-02-01 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6016 | 6042 | 2. | 7666 | MOD-029-2a R2.1.2. | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 |  | 2024-02-01 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6016 | 6042 | 3. | 7667 | MOD-029-2a R2.1.3. | Uncontrolled separation shall not occur. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 |  | 2024-02-01 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6016 |  | 1. | 6042 | MOD-029-2a R2.1. | Except where otherwise specified within MOD-029-2, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | 2016-01-25 |  | 2024-02-01 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6016 |  | 2. | 7668 | MOD-029-2a R2.2. | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependent on a Remedial Action Scheme (RAS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a RAS. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 |  | 2024-02-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6016 |  | 2. DO NOT USE | RP-2021-07-07-0000012 | MOD-029-2a R2.2. DO NOT USE | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependent on a Remedial Action Scheme (RAS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a RAS. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | 2017-04-01 |  | 2024-02-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6016 |  | 3. | 7669 | MOD-029-2a R2.3. | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | 2016-01-25 |  | 2024-02-01 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6016 |  | 4. | 7670 | MOD-029-2a R2.4. | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | 2016-01-25 |  | 2024-02-01 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6016 |  | 5. | 7671 | MOD-029-2a R2.5. | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 |  | 2024-02-01 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6016 |  | 5. DO NOT USE | RP-2021-07-07-0000016 | MOD-029-2a R2.5. DO NOT USE | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | 2017-04-01 |  | 2024-02-01 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6016 |  | 6. | 7672 | MOD-029-2a R2.6. | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 |  | 2024-02-01 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6016 |  | 6. DO NOT USE | RP-2021-07-07-0000017 | MOD-029-2a R2.6. DO NOT USE | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | 2017-04-01 |  | 2024-02-01 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6016 |  | 7. | 7673 | MOD-029-2a R2.7. | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | 2016-01-25 |  | 2024-02-01 |  |  | 270000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
502 | 6016 |  | 8. | 7674 | MOD-029-2a R2.8. | Create a study report that describes the steps above that were undertaken (R2.1 – R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator that uses the Rated System Path Methodology shall produce the ATCID it uses to show where it has described and used additional modeling criteria in its ACTID that are not otherwise included in MOD-29 (R1.1.4, R.1.1.9, and R1.1.10). | 2016-01-25 |  | 2024-02-01 |  |  | 280000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
503 | 6048 |  | 1. | 6887 | PRC-023-4 R6.1. | Maintain a list of circuits subject to PRC-023-4 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-4, Attachment B applies. |  | DP, GO, PCPA, RC, TO |  | DP |  |  | GO |  |  |  |  | PCPA |  | RC | [5 empty] | TO |  |  |  | Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | 2016-01-25 |  | 2024-03-31 |  | 4.2. Circuits: 4.2.1 Circuits Subject to Requirements R1 – R5: 4.2.1.1 Transmission lines operated at 200 kV and above, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. 4.2.1.2 Transmission lines operated at 100 kV to 200 kV selected by the Planning Coordinator in accordance with Requirement R6. 4.2.1.3 Transmission lines operated below 100 kV that are part of the BES and selected by the Planning Coordinator in accordance with Requirement R6. 4.2.1.4 Transformers with low voltage terminals connected at 200 kV and above. 4.2.1.5 Transformers with low voltage terminals connected at 100 kV to 200 kV selected by the Planning Coordinator in accordance with Requirement R6. 4.2.1.6 Transformers with low voltage terminals connected below 100 kV that are part of the BES and selected by the Planning Coordinator in accordance with Requirement R6. 4.2.2 Circuits Subject to Requirement R6: 4.2.2.1 Transmission lines operated at 100 kV to 200 kV and transformers with low voltage terminals connected at 100 kV to 200 kV, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. 4.2.2.2 Transmission lines operated below 100 kV and transformers with low voltage terminals connected below 100 kV that are part of the BES, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
503 | 6048 |  | 2. | 6888 | PRC-023-4 R6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. |  | DP, GO, PCPA, RC, TO |  | DP |  |  | GO |  |  |  |  | PCPA |  | RC | [5 empty] | TO |  |  |  | Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-4, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | 2016-01-25 |  | 2024-03-31 |  | 4.2. Circuits: 4.2.1 Circuits Subject to Requirements R1 – R5: 4.2.1.1 Transmission lines operated at 200 kV and above, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. 4.2.1.2 Transmission lines operated at 100 kV to 200 kV selected by the Planning Coordinator in accordance with Requirement R6. 4.2.1.3 Transmission lines operated below 100 kV that are part of the BES and selected by the Planning Coordinator in accordance with Requirement R6. 4.2.1.4 Transformers with low voltage terminals connected at 200 kV and above. 4.2.1.5 Transformers with low voltage terminals connected at 100 kV to 200 kV selected by the Planning Coordinator in accordance with Requirement R6. 4.2.1.6 Transformers with low voltage terminals connected below 100 kV that are part of the BES and selected by the Planning Coordinator in accordance with Requirement R6. 4.2.2 Circuits Subject to Requirement R6: 4.2.2.1 Transmission lines operated at 100 kV to 200 kV and transformers with low voltage terminals connected at 100 kV to 200 kV, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. 4.2.2.2 Transmission lines operated below 100 kV and transformers with low voltage terminals connected below 100 kV that are part of the BES, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
505 | 6052 |  | 1. | 7149 | PRC-004-4 R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-05-29 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
505 | 6052 |  | 2. | 7150 | PRC-004-4 R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-05-29 |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
505 | 6052 |  | 3. | 7151 | PRC-004-4 R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-05-29 |  | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
505 | 6053 | 7152 | 1. | 7153 | PRC-004-4 R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO | [6 empty] | 2016-06-30 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
505 | 6053 | 7152 | 2. | 7154 | PRC-004-4 R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO | [6 empty] | 2016-06-30 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
505 | 6053 | 7152 | 3. | 7155 | PRC-004-4 R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO | [6 empty] | 2016-06-30 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
505 | 6053 |  | 1. | 7152 | PRC-004-4 R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-05-29 |  | 2016-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
505 | 6053 |  | 2. | 7156 | PRC-004-4 R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-05-29 |  | 2016-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
506 | 6058 | 6975 | 1. | 7478 | CIP-003-6 R1.1.1. | Personnel and training (CIP-004); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
506 | 6058 | 6975 | 2. | 7479 | CIP-003-6 R1.1.2. | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
506 | 6058 | 6975 | 3. | 7480 | CIP-003-6 R1.1.3. | Physical security of BES Cyber Systems (CIP-006); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
506 | 6058 | 6975 | 4. | 7481 | CIP-003-6 R1.1.4. | System security management (CIP-007); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
506 | 6058 | 6975 | 5. | 7482 | CIP-003-6 R1.1.5. | Incident reporting and response planning (CIP-008); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
506 | 6058 | 6975 | 6. | 7483 | CIP-003-6 R1.1.6. | Recovery plans for BES Cyber Systems (CIP-009); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 116000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
506 | 6058 | 6975 | 7. | 7484 | CIP-003-6 R1.1.7. | Configuration change management and vulnerability assessments (CIP-010); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 117000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
506 | 6058 | 6975 | 8. | 7485 | CIP-003-6 R1.1.8. | Information protection (CIP-011); and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 118000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
506 | 6058 | 6975 | 9. | 7486 | CIP-003-6 R1.1.9. | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 119000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
506 | 6058 | 7042 | 1. | 7043 | CIP-003-6 R1.2.1. | Cyber security awareness; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
506 | 6058 | 7042 | 2. | 7044 | CIP-003-6 R1.2.2. | Physical security controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
506 | 6058 | 7042 | 3. | 7045 | CIP-003-6 R1.2.3. | Electronic access controls for Low Impact External Routable Connectivity (LERC) and Dial-up Connectivity; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
506 | 6058 | 7042 | 4. | 7046 | CIP-003-6 R1.2.4. | Cyber Security Incident response |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
506 | 6058 |  | 1. | 6975 | CIP-003-6 R1.1. | For its high impact and medium impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
506 | 6058 |  | 2. | 7042 | CIP-003-6 R1.2. | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6062 |  | 1. | 7207 | CIP-004-6 R1.1. | Security awareness that, at least once each calendar quarter, reinforces cyber security practices (which may include associated physical security practices) for the Responsible Entity’s personnel who have authorized electronic or authorized unescorted physical access to BES Cyber Systems. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1 An example of evidence may include, but is not limited to, documentation that the quarterly reinforcement has been provided. Examples of evidence of reinforcement may include, but are not limited to, dated copies of information used to reinforce security awareness, as well as evidence of distribution, such as: • direct communications (for example, e-mails, memos, computer-based training); or • indirect communications (for example, posters, intranet, or brochures); or • management support and reinforcement (for example, presentations or meetings). | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6063 | 7208 | 1. | 7209 | CIP-004-6 R2.1.1. | Cyber security policies; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6063 | 7208 | 2. | 7210 | CIP-004-6 R2.1.2. | Physical access controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6063 | 7208 | 3. | 7211 | CIP-004-6 R2.1.3. | Electronic access controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6063 | 7208 | 4. | 7212 | CIP-004-6 R2.1.4. | The visitor control program; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6063 | 7208 | 5. | 7213 | CIP-004-6 R2.1.5. | Handling of BES Cyber System Information and its storage; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 215000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6063 | 7208 | 6. | 7214 | CIP-004-6 R2.1.6. | Identification of a Cyber Security Incident and initial notifications in accordance with the entity’s incident response plan; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 216000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6063 | 7208 | 7. | 7215 | CIP-004-6 R2.1.7. | Recovery plans for BES Cyber Systems; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 217000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6063 | 7208 | 8. | 7216 | CIP-004-6 R2.1.8. | Response to Cyber Security Incidents; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 218000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6063 | 7208 | 9. | 7217 | CIP-004-6 R2.1.9. | Cyber security risks associated with a BES Cyber System’s electronic interconnectivity and interoperability with other Cyber Assets, including Transient Cyber Assets, and with Removable Media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 219000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6063 |  | 1. | 7208 | CIP-004-6 R2.1. | Training content on: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1 Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6063 |  | 2. | 7218 | CIP-004-6 R2.2. | Require completion of the training specified in Part 2.1 prior to granting authorized electronic access and authorized unescorted physical access to applicable Cyber Assets, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. Examples of evidence may include, but are not limited to, training records and documentation of when CIP Exceptional Circumstances were invoked. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6063 |  | 3. | 7245 | CIP-004-6 R2.3. | Require completion of the training specified in Part 2.1 at least once every 15 calendar months. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M.2.3. Examples of evidence may include, but are not limited to, dated individual training records. | 2016-03-31 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6064 | 7247 | 1. | 7516 | CIP-004-6 R3.2.1. | current residence, regardless of duration; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6064 | 7247 | 2. | 7517 | CIP-004-6 R3.2.2. | other locations where, during the seven years immediately prior to the date of the criminal history records check, the subject has resided for six consecutive months or more. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6064 |  | 1. | 7246 | CIP-004-6 R3.1. | Process to confirm identity. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.1. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to confirm identity. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6064 |  | 2. | 7247 | CIP-004-6 R3.2. | Process to perform a seven year criminal history records check as part of each personnel risk assessment that includes: 3.2.1. current residence, regardless of duration; and 3.2.2. other locations where, during the seven years immediately prior to the date of the criminal history records check, the subject has resided for six consecutive months or more. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.2. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6064 |  | 3. | 7518 | CIP-004-6 R3.3. | Criteria or process to evaluate criminal history records checks for authorizing access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.3. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to evaluate criminal history records checks. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6064 |  | 4. | 7519 | CIP-004-6 R3.4. | Criteria or process for verifying that personnel risk assessments performed for contractors or service vendors are conducted according to Parts 3.1 through 3.3. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.4. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s criteria or process for verifying contractors or service vendors personnel risk assessments. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6064 |  | 5. | 7520 | CIP-004-6 R3.5. | Process to ensure that individuals with unescorted physical access have had a personnel risk assessment completed according to Parts 3.1 to 3.4 within the last seven years. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.5. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process for ensuring that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed within the last seven years. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6065 | 7258 | 1. | 7259 | CIP-004-6 R4.1.1. | Electronic access; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6065 | 7258 | 2. | 7260 | CIP-004-6 R4.1.2. | Unescorted physical access into a Physical Security Perimeter; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6065 | 7258 | 3. | 7261 | CIP-004-6 R4.1.3. | Access to designated storage locations, whether physical or electronic, for BES Cyber System Information. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6065 |  | 1. | 7258 | CIP-004-6 R4.1. | Process to authorize based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.1. An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. | 2016-03-31 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6065 |  | 2. | RP-2021-06-30-0000004 | CIP-004-6 R4.2. | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to:  Dated documentation of the verification between the system generated list of individuals who have been authorized for access (i.e., workflow database) and a system generated list of personnel who have access (i.e., user account listing), or  Dated documentation of the verification between a list of individuals who have been authorized for access (i.e., authorization forms) and a list of individuals provisioned for access (i.e., provisioning forms or shared account listing). | 2016-10-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6065 |  | 2. (Delete) | 7262 | CIP-004-6 R4.2. (Delete) | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.2. Examples of evidence may include, but are not limited to: • Dated documentation of the verification between the system generated list of individuals who have been authorized for access (i.e., workflow database) and a system generated list of personnel who have access (i.e., user account listing), or • Dated documentation of the verification between a list of individuals who have been authorized for access (i.e., authorization forms) and a list of individuals provisioned for access (i.e., provisioning forms or shared account listing). | 2016-10-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6065 |  | 3. | 7263 | CIP-004-6 R4.3. | For electronic access, verify at least once every 15 calendar months that all user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and are those that the Responsible Entity determines are necessary. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.3. An example of evidence may include, but is not limited to, documentation of the review that includes all of the following: 1. A dated listing of all accounts/account groups or roles within the system; 2. A summary description of privileges associated with each group or role; 3. Accounts assigned to the group or role; and 4. Dated evidence showing verification of the privileges for the group are authorized and appropriate to the work function performed by people assigned to each account. | 2017-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6065 |  | 4. | 7264 | CIP-004-6 R4.4. | Verify at least once every 15 calendar months that access to the designated storage locations for BES Cyber System Information, whether physical or electronic, are correct and are those that the Responsible Entity determines are necessary for performing assigned work functions. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.4. An example of evidence may include, but is not limited to, the documentation of the review that includes all of the following: 1. A dated listing of authorizations for BES Cyber System information; 2. Any privileges associated with the authorizations; and 3. Dated evidence showing a verification of the authorizations and any privileges were confirmed correct and the minimum necessary for performing assigned work functions. | 2017-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6066 |  | 1. | 7265 | CIP-004-6 R5.1. | A process to initiate removal of an individual’s ability for unescorted physical access and Interactive Remote Access upon a termination action, and complete the removals within 24 hours of the termination action (Removal of the ability for access may be different than deletion, disabling, revocation, or removal of all access rights) |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.1 An example of evidence may include, but is not limited to, documentation of all of the following: 1. Dated workflow or sign-off form verifying access removal associated with the termination action; and 2. Logs or other demonstration showing such persons no longer have access. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6066 |  | 2. | 7266 | CIP-004-6 R5.2. | For reassignments or transfers, revoke the individual’s authorized electronic access to individual accounts and authorized unescorted physical access that the Responsible Entity determines are not necessary by the end of the next calendar day following the date that the Responsible Entity determines that the individual no longer requires retention of that access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.2. An example of evidence may include, but is not limited to, documentation of all of the following: 1. Dated workflow or sign-off form showing a review of logical and physical access; and 2. Logs or other demonstration showing such persons no longer have access that the Responsible Entity determines is not necessary. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6066 |  | 3. | 7267 | CIP-004-6 R5.3. | For termination actions, revoke the individual’s access to the designated storage locations for BES Cyber System Information, whether physical or electronic (unless already revoked according to Requirement R5.1), by the end of the next calendar day following the effective date of the termination action. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.3. An example of evidence may include, but is not limited to, workflow or sign-off form verifying access removal to designated physical areas or cyber systems containing BES Cyber System Information associated with the terminations and dated within the next calendar day of the termination action. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6066 |  | 4. | 7268 | CIP-004-6 R5.4. | For termination actions, revoke the individual’s non-shared user accounts (unless already revoked according to Parts 5.1 or 5.3) within 30 calendar days of the effective date of the termination action. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.4 An example of evidence may include, but is not limited to, workflow or sign-off form showing access removal for any individual BES Cyber Assets and software applications as determined necessary to completing the revocation of access and dated within thirty calendar days of the termination actions. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
507 | 6066 |  | 5. | 7269 | CIP-004-6 R5.5. | For termination actions, change passwords for shared account(s) known to the user within 30 calendar days of the termination action. For reassignments or transfers, change passwords for shared account(s) known to the user within 30 calendar days following the date that the Responsible Entity determines that the individual no longer requires retention of that access. If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances. If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.5 Examples of evidence may include, but are not limited to: • Workflow or sign-off form showing password reset within 30 calendar days of the termination; • Workflow or sign-off form showing password reset within 30 calendar days of the reassignments or transfers; or • Documentation of the extenuating operating circumstance and workflow or sign-off form showing password reset within 10 calendar days following the end of the operating circumstance. | 2016-07-01 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 550000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
508 | 6067 |  | 1. | 7157 | PRC-005-2(i) R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  |  | 2015-05-29 |  | 2016-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
508 | 6067 |  | 2. | 7158 | PRC-005-2(i) R1.2. | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  |  | 2015-05-29 |  | 2016-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
509 | 6072 |  | 1. | 6877 | PRC-005-3(i) R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO | [6 empty] | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
509 | 6072 |  | 2. | 6878 | PRC-005-3(i) R1.2. | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO | [6 empty] | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
510 | 6078 |  | 1. | RP-2021-06-24-0000074 | VAR-002-4 R2.1. | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2017-09-25 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
510 | 6078 |  | 2. | RP-2021-06-24-0000075 | VAR-002-4 R2.2. | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2017-09-25 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
510 | 6078 |  | 3. | 6844 | VAR-002-4 R2.3. | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2017-09-25 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
510 | 6081 | 6845 | 1. | 6846 | VAR-002-4 R5.1.1. | Tap settings. |  | GO |  |  |  |  | GO | [17 empty] | 2015-05-29 |  | 2017-09-25 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
510 | 6081 | 6845 | 2. | 6847 | VAR-002-4 R5.1.2. | Available fixed tap ranges. |  | GO |  |  |  |  | GO | [17 empty] | 2015-05-29 |  | 2017-09-25 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
510 | 6081 | 6845 | 3. | 6848 | VAR-002-4 R5.1.3. | Impedance data. |  | GO |  |  |  |  | GO | [17 empty] | 2015-05-29 |  | 2017-09-25 |  |  | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
510 | 6081 |  | 1. | 6845 | VAR-002-4 R5.1. | For generator step-up and auxiliary transformers5 with primary voltages equal to or greater than the generator terminal voltage: |  | GO |  |  |  |  | GO | [17 empty] | 2015-05-29 |  | 2017-09-25 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
510 | 6082 |  | 1. | 6849 | VAR-002-4 R6.1. | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. |  | GO |  |  |  |  | GO | [17 empty] | 2015-05-29 |  | 2017-09-25 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
511 | 6512 |  | 1. | RP-2021-06-24-0000029 | TOP-001-3 R10.1. | Within its Transmission Operator Area, monitor Facilities and the status of Special Protection Systems, and |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 |  | 2018-06-30 |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
511 | 6512 |  | 2. | 6514 | TOP-001-3 R10.2. | Outside its Transmission Operator Area, obtain and utilize status, voltages, and flow data for Facilities and the status of Special Protection Systems. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2018-06-30 |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
512 | 6090 |  | 1. | 7241 | CIP-011-2 R1.1. | Method(s) to identify information that meets the definition of BES Cyber System Information. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. Examples of acceptable evidence include, but are not limited to: • Documented method to identify BES Cyber System Information from entity’s information protection program; or • Indications on information (e.g., labels or classification) that identify BES Cyber System Information as designated in the entity’s information protection program; or • Training materials that provide personnel with sufficient knowledge to recognize BES Cyber System Information; or • Repository or electronic and physical location designated for housing BES Cyber System Information in the entity’s information protection program. | 2016-03-31 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-011-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
512 | 6090 |  | 2. | 7242 | CIP-011-2 R1.2. | Procedure(s) for protecting and securely handling BES Cyber System Information, including storage, transit, and use. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. Examples of acceptable evidence include, but are not limited to: • Procedures for protecting and securely handling, which include topics such as storage, security during transit, and use of BES Cyber System Information; or • Records indicating that BES Cyber System Information is handled in a manner consistent with the entity’s documented procedure(s). | 2016-03-31 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-011-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
512 | 6091 |  | 1. | 7243 | CIP-011-2 R2.1. | Prior to the release for reuse of applicable Cyber Assets that contain BES Cyber System Information (except for reuse within other systems identified in the “Applicable Systems” column), the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset data storage media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. Examples of acceptable evidence include, but are not limited to: • Records tracking sanitization actions taken to prevent unauthorized retrieval of BES Cyber System Information such as clearing, purging, or destroying; or • Records tracking actions such as encrypting, retaining in the Physical Security Perimeter or other methods used to prevent unauthorized retrieval of BES Cyber System Information. | 2016-03-31 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-011-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
512 | 6091 |  | 2. | 7244 | CIP-011-2 R2.2. | Prior to the disposal of applicable Cyber Assets that contain BES Cyber System Information, the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset or destroy the data storage media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. Examples of acceptable evidence include, but are not limited to: • Records that indicate that data storage media was destroyed prior to the disposal of an applicable Cyber Asset; or • Records of actions taken to prevent unauthorized retrieval of BES Cyber System Information prior to the disposal of an applicable Cyber Asset. | 2016-03-31 |  | 2023-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-011-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6092 |  | 1. | 7286 | CIP-007-6 R1.1. | Where technically feasible, enable only logical network accessible ports that have been determined to be needed by the Responsible Entity, including port ranges or services where needed to handle dynamic ports. If a device has no provision for disabling or restricting logical ports on the device then those ports that are open are deemed needed. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. Examples of evidence may include, but are not limited to: • Documentation of the need for all enabled ports on all applicable Cyber Assets and Electronic Access Points, individually or by group. • Listings of the listening ports on the Cyber Assets, individually or by group, from either the device configuration files, command output (such as netstat), or network scans of open ports; or • Configuration files of host-based firewalls or other device level mechanisms that only allow needed ports and deny all others. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6092 |  | 2. | 7287 | CIP-007-6 R1.2. | Protect against the use of unnecessary physical input/output ports used for network connectivity, console commands, or Removable Media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. An example of evidence may include, but is not limited to, documentation showing types of protection of physical input/output ports, either logically through system configuration or physically using a port lock or signage. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6093 |  | 1. | 7288 | CIP-007-6 R2.1. | A patch management process for tracking, evaluating, and installing cyber security patches for applicable Cyber Assets. The tracking portion shall include the identification of a source or sources that the Responsible Entity tracks for the release of cyber security patches for applicable Cyber Assets that are updateable and for which a patching source exists. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. An example of evidence may include, but is not limited to, documentation of a patch management process and documentation or lists of sources that are monitored, whether on an individual BES Cyber System or Cyber Asset basis. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6093 |  | 2. | 7289 | CIP-007-6 R2.2. | At least once every 35 calendar days, evaluate security patches for applicability that have been released since the last evaluation from the source or sources identified in Part 2.1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. An example of evidence may include, but is not limited to, an evaluation conducted by, referenced by, or on behalf of a Responsible Entity of security-related patches released by the documented sources at least once every 35 calendar days. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6093 |  | 3. | 7290 | CIP-007-6 R2.3. | For applicable patches identified in Part 2.2, within 35 calendar days of the evaluation completion, take one of the following actions: • Apply the applicable patches; or • Create a dated mitigation plan; or • Revise an existing mitigation plan. Mitigation plans shall include the Responsible Entity’s planned actions to mitigate the vulnerabilities addressed by each security patch and a timeframe to complete these mitigations. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.3. Examples of evidence may include, but are not limited to: • Records of the installation of the patch (e.g., exports from automated patch management tools that provide installation date, verification of BES Cyber System Component software revision, or registry exports that show software has been installed); or • A dated plan showing when and how the vulnerability will be addressed, to include documentation of the actions to be taken by the Responsible Entity to mitigate the vulnerabilities addressed by the security patch and a timeframe for the completion of these mitigations. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6093 |  | 4. | 7291 | CIP-007-6 R2.4. | For each mitigation plan created or revised in Part 2.3, implement the plan within the timeframe specified in the plan, unless a revision to the plan or an extension to the timeframe specified in Part 2.3 is approved by the CIP Senior Manager or delegate. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.4. An example of evidence may include, but is not limited to, records of implementation of mitigations. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6094 |  | 1. | 7292 | CIP-007-6 R3.1. | Deploy method(s) to deter, detect, or prevent malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.1. An example of evidence may include, but is not limited to, records of the Responsible Entity’s performance of these processes (e.g., through traditional antivirus, system hardening, policies, etc.). | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6094 |  | 2. | 7293 | CIP-007-6 R3.2. | Mitigate the threat of detected malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.2. Examples of evidence may include, but are not limited to: • Records of response processes for malicious code detection • Records of the performance of these processes when malicious code is detected. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6094 |  | 3. | 7294 | CIP-007-6 R3.3. | For those methods identified in Part 3.1 that use signatures or patterns, have a process for the update of the signatures or patterns. The process must address testing and installing the signatures or patterns. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.3. An example of evidence may include, but is not limited to, documentation showing the process used for the update of signatures or patterns. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6095 | 7295 | 1. | 7302 | CIP-007-6 R4.1.1. | Detected successful login attempts; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.1. Examples of evidence may include, but are not limited to, a paper or system generated listing of event types for which the BES Cyber System is capable of detecting and, for generated events, is configured to log. This listing must include the required types of events. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6095 | 7295 | 2. | 7303 | CIP-007-6 R4.1.2. | Detected failed access attempts and failed login attempts; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.1. Examples of evidence may include, but are not limited to, a paper or system generated listing of event types for which the BES Cyber System is capable of detecting and, for generated events, is configured to log. This listing must include the required types of events. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6095 | 7295 | 3. | 7304 | CIP-007-6 R4.1.3. | Detected malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.1. Examples of evidence may include, but are not limited to, a paper or system generated listing of event types for which the BES Cyber System is capable of detecting and, for generated events, is configured to log. This listing must include the required types of events. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6095 | 7305 | 1. | 7306 | CIP-007-6 R4.2.1. | Detected malicious code from Part 4.1; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.2. Examples of evidence may include, but are not limited to, paper or system-generated listing of security events that the Responsible Entity determined necessitate alerts, including paper or system generated list showing how alerts are configured. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 421000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6095 | 7305 | 2. | 7307 | CIP-007-6 R4.2.2. | Detected failure of Part 4.1 event logging. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.2. Examples of evidence may include, but are not limited to, paper or system-generated listing of security events that the Responsible Entity determined necessitate alerts, including paper or system generated list showing how alerts are configured. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 422000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6095 |  | 1. | 7295 | CIP-007-6 R4.1. | Log events at the BES Cyber System level (per BES Cyber System capability) or at the Cyber Asset level (per Cyber Asset capability) for identification of, and after-the-fact investigations of, Cyber Security Incidents that includes, as a minimum, each of the following types of events: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.1. Examples of evidence may include, but are not limited to, a paper or system generated listing of event types for which the BES Cyber System is capable of detecting and, for generated events, is configured to log. This listing must include the required types of events. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6095 |  | 2. | 7305 | CIP-007-6 R4.2. | Generate alerts for security events that the Responsible Entity determines necessitates an alert, that includes, as a minimum, each of the following types of events (per Cyber Asset or BES Cyber System capability): |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.2. Examples of evidence may include, but are not limited to, paper or system-generated listing of security events that the Responsible Entity determined necessitate alerts, including paper or system generated list showing how alerts are configured. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6095 |  | 3. | 7308 | CIP-007-6 R4.3. | Where technically feasible, retain applicable event logs identified in Part 4.1 for at least the last 90 consecutive calendar days except under CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.3. Examples of evidence may include, but are not limited to, documentation of the event log retention process and paper or system generated reports showing log retention configuration set at 90 days or greater. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6095 |  | 3. DO NOT USE | RP-2021-06-30-0000011 | CIP-007-6 R4.3. DO NOT USE | Where technically feasible, retain applicable event logs identified in Part 4.1 for at least the last 90 consecutive calendar days except under CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the event log retention process and paper or system generated reports showing log retention configuration set at 90 days or greater. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6095 |  | 4. | 7309 | CIP-007-6 R4.4. | Review a summarization or sampling of logged events as determined by the Responsible Entity at intervals no greater than 15 calendar days to identify undetected Cyber Security Incidents. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.4. Examples of evidence may include, but are not limited to, documentation describing the review, any findings from the review (if any), and dated documentation showing the review occurred. | 2016-07-15 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6096 | 7314 | 1. | 7316 | CIP-007-6 R5.5.1. | Password length that is, at least, the lesser of eight characters or the maximum length supported by the Cyber Asset; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to:  System-generated reports or screen-shots of the system-enforced password parameters, including length and complexity; or  Attestations that include a reference to the documented procedures that were followed. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 551000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6096 | 7314 | 2. | 7317 | CIP-007-6 R5.5.2. | Minimum password complexity that is the lesser of three or more different types of characters (e.g., uppercase alphabetic, lowercase alphabetic, numeric, non-alphanumeric) or the maximum complexity supported by the Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to:  System-generated reports or screen-shots of the system-enforced password parameters, including length and complexity; or  Attestations that include a reference to the documented procedures that were followed. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 552000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6096 |  | 1. | 7310 | CIP-007-6 R5.1. | Have a method(s) to enforce authentication of interactive user access, where technically feasible. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.1. An example of evidence may include, but is not limited to, documentation describing how access is authenticated. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6096 |  | 2. | 7311 | CIP-007-6 R5.2. | Identify and inventory all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.2. An example of evidence may include, but is not limited to, a listing of accounts by account types showing the enabled or generic account types in use for the BES Cyber System. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6096 |  | 3. | 7312 | CIP-007-6 R5.3. | Identify individuals who have authorized access to shared accounts. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.3. An example of evidence may include, but is not limited to, listing of shared accounts and the individuals who have authorized access to each shared account. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6096 |  | 4. | 7313 | CIP-007-6 R5.4. | Change known default passwords, per Cyber Asset capability |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.4. Examples of evidence may include, but are not limited to: • Records of a procedure that passwords are changed when new devices are in production; or • Documentation in system manuals or other vendor documents showing default vendor passwords were generated pseudo-randomly and are thereby unique to the device. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6096 |  | 5. | 7314 | CIP-007-6 R5.5. | For password-only authentication for interactive user access, either technically or procedurally enforce the following password parameters: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.5. Examples of evidence may include, but are not limited to: • System-generated reports or screen-shots of the system-enforced password parameters, including length and complexity; or • Attestations that include a reference to the documented procedures that were followed. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 550000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6096 |  | 6. | 7315 | CIP-007-6 R5.6. | Where technically feasible, for password-only authentication for interactive user access, either technically or procedurally enforce password changes or an obligation to change the password at least once every 15 calendar months. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.6. Examples of evidence may include, but are not limited to: • System-generated reports or screen-shots of the system-enforced periodicity of changing passwords; or • Attestations that include a reference to the documented procedures that were followed. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 560000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6096 |  | 6. DO NOT USE | RP-2021-06-30-0000012 | CIP-007-6 R5.6. DO NOT USE | Where technically feasible, for password-only authentication for interactive user access, either technically or procedurally enforce password changes or an obligation to change the password at least once every 15 calendar months. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to:  System-generated reports or screen-shots of the system enforced periodicity of changing passwords; or  Attestations that include a reference to the documented procedures that were followed. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 560000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6096 |  | 7. | 7318 | CIP-007-6 R5.7. | Where technically feasible, either: • Limit the number of unsuccessful authentication attempts; or • Generate alerts after a threshold of unsuccessful authentication attempts. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.7. Examples of evidence may include, but are not limited to: • Documentation of the account-lockout parameters; or • Rules in the alerting configuration showing how the system notified individuals after a determined number of unsuccessful login attempts. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 570000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
513 | 6096 |  | 7. DO NOT USE | RP-2021-06-30-0000013 | CIP-007-6 R5.7. DO NOT USE | Where technically feasible, either:  Limit the number of unsuccessful authentication attempts; or  Generate alerts after a threshold of unsuccessful authentication attempts. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to:  Documentation of the account-lockout parameters; or  Rules in the alerting configuration showing how the system notified individuals after a determined number of unsuccessful login attempts. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 570000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6097 |  | 1. | 6912 | CIP-009-6 R1.1. | Conditions for activation of the recovery plan(s). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. An example of evidence may include, but is not limited to, one or more plans that include language identifying conditions for activation of the recovery plan(s). | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6097 |  | 2. | 6918 | CIP-009-6 R1.2. | Roles and responsibilities of responders. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. An example of evidence may include, but is not limited to, one or more recovery plans that include language identifying the roles and responsibilities of responders. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6097 |  | 3. | 6919 | CIP-009-6 R1.3. | One or more processes for the backup and storage of information required to recover BES Cyber System functionality. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.3. An example of evidence may include, but is not limited to, documentation of specific processes for the backup and storage of information required to recover BES Cyber System functionality. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6097 |  | 4. | 6920 | CIP-009-6 R1.4. | One or more processes to verify the successful completion of the backup processes in Part 1.3 and to address any backup failures. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.4. An example of evidence may include, but is not limited to, logs, workflow or other documentation confirming that the backup process completed successfully and backup failures, if any, were addressed. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6097 |  | 5. | 6921 | CIP-009-6 R1.5. | One or more processes to preserve data, per Cyber Asset capability, for determining the cause of a Cyber Security Incident that triggers activation of the recovery plan(s). Data preservation should not impede or restrict recovery. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.5. An example of evidence may include, but is not limited to, procedures to preserve data, such as preserving a corrupted drive or making a data mirror of the system before proceeding with recovery. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6098 |  | 1. | 6922 | CIP-009-6 R2.1. | Test each of the recovery plans referenced in Requirement R1 at least once every 15 calendar months: • By recovering from an actual incident; • With a paper drill or tabletop exercise; or • With an operational exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. An example of evidence may include, but is not limited to, dated evidence of a test (by recovering from an actual incident, with a paper drill or tabletop exercise, or with an operational exercise) of the recovery plan at least once every 15 calendar months. For the paper drill or full operational exercise, evidence may include meeting notices, minutes, or other records of exercise findings. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6098 |  | 2. | 6923 | CIP-009-6 R2.2. | Test a representative sample of information used to recover BES Cyber System functionality at least once every 15 calendar months to ensure that the information is useable and is compatible with current configurations. An actual recovery that incorporates the information used to recover BES Cyber System functionality substitutes for this test. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. An example of evidence may include, but is not limited to, operational logs or test results with criteria for testing the usability (e.g. sample tape load, browsing tape contents) and compatibility with current system configurations (e.g. manual or automated comparison checkpoints between backup media contents and current configuration). | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6098 |  | 3. | 6924 | CIP-009-6 R2.3. | Test each of the recovery plans referenced in Requirement R1 at least once every 36 calendar months through an operational exercise of the recovery plans in an environment representative of the production environment. An actual recovery response may substitute for an operational exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.3. Examples of evidence may include, but are not limited to, dated documentation of: • An operational exercise at least once every 36 calendar months between exercises, that demonstrates recovery in a representative environment; or • An actual recovery response that occurred within the 36 calendar month timeframe that exercised the recovery plans. | 2018-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6099 | 6925 | 1. | 6927 | CIP-009-6 R3.1.1. | Document any lessons learned associated with a recovery plan test or actual recovery or document the absence of any lessons learned; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following: 1. Dated documentation of identified deficiencies or lessons learned for each recovery plan test or actual incident recovery or dated documentation stating there were no lessons learned; 2. Dated and revised recovery plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6099 | 6925 | 2. | 6928 | CIP-009-6 R3.1.2. | Update the recovery plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following: 1. Dated documentation of identified deficiencies or lessons learned for each recovery plan test or actual incident recovery or dated documentation stating there were no lessons learned; 2. Dated and revised recovery plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6099 | 6925 | 3. | 6929 | CIP-009-6 R3.1.3. | Notify each person or group with a defined role in the recovery plan of the updates to the recovery plan based on any documented lessons learned. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following: 1. Dated documentation of identified deficiencies or lessons learned for each recovery plan test or actual incident recovery or dated documentation stating there were no lessons learned; 2. Dated and revised recovery plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6099 | 6926 | 1. | 6930 | CIP-009-6 R3.2.1. | Update the recovery plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following: 1. Dated and revised recovery plan with changes to the roles or responsibilities, responders, or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6099 | 6926 | 2. | 6931 | CIP-009-6 R3.2.2. | Notify each person or group with a defined role in the recovery plan of the updates. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following: 1. Dated and revised recovery plan with changes to the roles or responsibilities, responders, or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6099 |  | 1. | 6925 | CIP-009-6 R3.1. | No later than 90 calendar days after completion of a recovery plan test or actual recovery: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.1. An example of evidence may include, but is not limited to, all of the following: 1. Dated documentation of identified deficiencies or lessons learned for each recovery plan test or actual incident recovery or dated documentation stating there were no lessons learned; 2. Dated and revised recovery plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6099 |  | 1.2. DO NOT USE | RP-2021-06-30-0000015 | CIP-009-6 R3.1.2. DO NOT USE | Update the recovery plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following: 1. Dated documentation of identified deficiencies or lessons learned for each recovery plan test or actual incident recovery or dated documentation stating there were no lessons learned; 2. Dated and revised recovery plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6099 |  | 2. | 6926 | CIP-009-6 R3.2. | No later than 60 calendar days after a change to the roles or responsibilities, responders, or technology that the Responsible Entity determines would impact the ability to execute the recovery plan: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.2. An example of evidence may include, but is not limited to, all of the following: 1. Dated and revised recovery plan with changes to the roles or responsibilities, responders, or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
514 | 6099 |  | 2.1. DO NOT USE | RP-2021-06-30-0000016 | CIP-009-6 R3.2.1. DO NOT USE | Update the recovery plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following: 1. Dated and revised recovery plan with changes to the roles or responsibilities, responders, or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6101 | 7219 | 1. | 7220 | CIP-010-2 R1.1.1. | Operating system(s) (including version) or firmware where no independent operating system exists; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6101 | 7219 | 2. | 7221 | CIP-010-2 R1.1.2. | Any commercially available or open-source application software (including version) intentionally installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6101 | 7219 | 3. | 7222 | CIP-010-2 R1.1.3. | Any custom software installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6101 | 7219 | 4. | 7223 | CIP-010-2 R1.1.4. | Any logical network accessible ports; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6101 | 7219 | 5. | 7224 | CIP-010-2 R1.1.5. | Any security patches applied. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6101 | 7227 | 1. | 7228 | CIP-010-2 R1.4.1. | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6101 | 7227 | 2. | 7229 | CIP-010-2 R1.4.2. | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6101 | 7227 | 3. | 7230 | CIP-010-2 R1.4.3. | Document the results of the verification. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6101 | RP-2021-06-18-0000011 | 1. | 7232 | CIP-010-2 R1.5.1. | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6101 | RP-2021-06-18-0000011 | 2. | 7233 | CIP-010-2 R1.5.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6101 |  | 1. | 7219 | CIP-010-2 R1.1. | Develop a baseline configuration, individually or by group, which shall include the following items: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. Examples of evidence may include, but are not limited to: • A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or • A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2016-03-31 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6101 |  | 2. | 7225 | CIP-010-2 R1.2. | Authorize and document changes that deviate from the existing baseline configuration. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. Examples of evidence may include, but are not limited to: • A change request record and associated electronic authorization (performed by the individual or group with the authority to authorize the change) in a change management system for each change; or • Documentation that the change was performed in accordance with the requirement. | 2016-03-31 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6101 |  | 3. | 7226 | CIP-010-2 R1.3. | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.3. An example of evidence may include, but is not limited to, updated baseline documentation with a date that is within 30 calendar days of the date of the completion of the change. | 2016-03-31 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6101 |  | 4. | 7227 | CIP-010-2 R1.4. | For a change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.4. An example of evidence may include, but is not limited to, a list of cyber security controls verified or tested along with the dated test results. | 2016-03-31 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6101 |  | 5. | RP-2021-06-18-0000011 | CIP-010-2 R1.5. | Where technically feasible, for each change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6102 |  | 1. | 7234 | CIP-010-2 R2.1. | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. An example of evidence may include, but is not limited to, logs from a system that is monitoring the configuration along with records of investigation for any unauthorized changes that were detected. | 2016-08-05 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6103 | 7236 | 1. | 7237 | CIP-010-2 R3.2.1. | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2018-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6103 | 7236 | 2. | 7238 | CIP-010-2 R3.2.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2018-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6103 |  | 1. | 7235 | CIP-010-2 R3.1. | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.1. Examples of evidence may include, but are not limited to: • A document listing the date of the assessment (performed at least once every 15 calendar months), the controls assessed for each BES Cyber System along with the method of assessment; or • A document listing the date of the assessment and the output of any tools used to perform the assessment. | 2017-07-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6103 |  | 2. | 7236 | CIP-010-2 R3.2. | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.2. An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed at least once every 36 calendar months), the output of the tools used to perform the assessment, and a list of differences between the production and test environments with descriptions of how any differences were accounted for in conducting the assessment. | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6103 |  | 3. | 7239 | CIP-010-2 R3.3. | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.3. An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed prior to the commissioning of the new Cyber Asset) and the output of any tools used to perform the assessment. | 2016-07-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
515 | 6103 |  | 4. | 7240 | CIP-010-2 R3.4. | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.4. An example of evidence may include, but is not limited to, a document listing the results or the review or assessment, a list of action items, documented proposed dates of completion for the action plan, and records of the status of the action items (such as minutes of a status meeting, updates in a work order system, or a spreadsheet tracking the action items). | 2016-07-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1 Balancing Authority 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6104 |  | 1. | 7339 | CIP-006-6 R1.1. | Define operational or procedural controls to restrict physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. An example of evidence may include, but is not limited to, documentation that operational or procedural controls exist. | 2016-07-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6104 |  | 10. | 7348 | CIP-006-6 R1.10. | Restrict physical access to cabling and other nonprogrammable communication components used for connection between applicable Cyber Assets within the same Electronic Security Perimeter in those instances when such cabling and components are located outside of a Physical Security Perimeter. Where physical access restrictions to such cabling and components are not implemented, the Responsible Entity shall document and implement one or more of the following: • encryption of data that transits such cabling and components; or • monitoring the status of the communication link composed of such cabling and components and issuing an alarm or alert in response to detected communication failures to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of detection; or • an equally effective logical protection. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.10 An example of evidence may include, but is not limited to, records of the Responsible Entity’s implementation of the physical access restrictions (e.g., cabling and components secured through conduit or secured cable trays) encryption, monitoring, or equally effective logical protections. | 2016-07-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6104 |  | 2. | 7340 | CIP-006-6 R1.2. | Utilize at least one physical access control to allow unescorted physical access into each applicable Physical Security Perimeter to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. An example of evidence may include, but is not limited to, language in the physical security plan that describes each Physical Security Perimeter and how unescorted physical access is controlled by one or more different methods and proof that unescorted physical access is restricted to only authorized individuals, such as a list of authorized individuals accompanied by access logs. | 2016-07-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6104 |  | 2. DO NOT USE | RP-2021-06-30-0000008 | CIP-006-6 R1.2. DO NOT USE | Utilize at least one physical access control to allow unescorted physical access into each applicable Physical Security Perimeter to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, language in the physical security plan that describes each Physical Security Perimeter and how unescorted physical access is controlled by one or more different methods and proof that unescorted physical access is restricted to only authorized individuals, such as a list of authorized individuals accompanied by access logs. | 2016-07-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6104 |  | 3. | 7341 | CIP-006-6 R1.3. | Where technically feasible, utilize two or more different physical access controls (this does not require two completely independent physical access control systems) to collectively allow unescorted physical access into Physical Security Perimeters to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.3. An example of evidence may include, but is not limited to, language in the physical security plan that describes the Physical Security Perimeters and how unescorted physical access is controlled by two or more different methods and proof that unescorted physical access is restricted to only authorized individuals, such as a list of authorized individuals accompanied by access logs. | 2016-07-01 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6104 |  | 3. DO NOT USE | RP-2021-06-30-0000009 | CIP-006-6 R1.3. DO NOT USE | Where technically feasible, utilize two or more different physical access controls (this does not require two completely independent physical access control systems) to collectively allow unescorted physical access into Physical Security Perimeters to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, language in the physical security plan that describes the Physical Security Perimeters and how unescorted physical access is controlled by two or more different methods and proof that unescorted physical access is restricted to only authorized individuals, such as a list of authorized individuals accompanied by access logs. | 2016-07-01 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6104 |  | 4. | 7342 | CIP-006-6 R1.4. | Monitor for unauthorized access through a physical access point into a Physical Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.4. An example of evidence may include, but is not limited to, documentation of controls that monitor for unauthorized access through a physical access point into a Physical Security Perimeter. | 2016-07-01 |  |  |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6104 |  | 5. | 7343 | CIP-006-6 R1.5. | Issue an alarm or alert in response to detected unauthorized access through a physical access point into a Physical Security Perimeter to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of detection. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.5. An example of evidence may include, but is not limited to, language in the physical security plan that describes the issuance of an alarm or alert in response to unauthorized access through a physical access control into a Physical Security Perimeter and additional evidence that the alarm or alert was issued and communicated as identified in the BES Cyber Security Incident Response Plan, such as manual or electronic alarm or alert logs, cell phone or pager logs, or other evidence that documents that the alarm or alert was generated and communicated. | 2016-07-01 |  |  |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6104 |  | 6. | 7344 | CIP-006-6 R1.6. | Monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control System. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.6. An example of evidence may include, but is not limited to, documentation of controls that monitor for unauthorized physical access to a PACS. | 2016-07-01 |  |  |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6104 |  | 7. | 7345 | CIP-006-6 R1.7. | Issue an alarm or alert in response to detected unauthorized physical access to a Physical Access Control System to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of the detection. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.7. An example of evidence may include, but is not limited to, language in the physical security plan that describes the issuance of an alarm or alert in response to unauthorized physical access to Physical Access Control Systems and additional evidence that the alarm or alerts was issued and communicated as identified in the BES Cyber Security Incident Response Plan, such as alarm or alert logs, cell phone or pager logs, or other evidence that the alarm or alert was generated and communicated. | 2016-07-01 |  |  |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6104 |  | 8. | 7346 | CIP-006-6 R1.8. | Log (through automated means or by personnel who control entry) entry of each individual with authorized unescorted physical access into each Physical Security Perimeter, with information to identify the individual and date and time of entry. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.8. An example of evidence may include, but is not limited to, language in the physical security plan that describes logging and recording of physical entry into each Physical Security Perimeter and additional evidence to demonstrate that this logging has been implemented, such as logs of physical access into Physical Security Perimeters that show the individual and the date and time of entry into Physical Security Perimeter. | 2016-07-01 |  |  |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6104 |  | 9. | 7347 | CIP-006-6 R1.9. | Retain physical access logs of entry of individuals with authorized unescorted physical access into each Physical Security Perimeter for at least ninety calendar days. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.9. An example of evidence may include, but is not limited to, dated documentation such as logs of physical access into Physical Security Perimeters that show the date and time of entry into Physical Security Perimeter. | 2016-07-01 |  |  |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6105 |  | 1. | 7349 | CIP-006-6 R2.1. | Require continuous escorted access of visitors (individuals who are provided access but are not authorized for unescorted physical access) within each Physical Security Perimeter, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. An example of evidence may include, but is not limited to, language in a visitor control program that requires continuous escorted access of visitors within Physical Security Perimeters and additional evidence to demonstrate that the process was implemented, such as visitor logs. | 2016-07-01 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6105 |  | 2. | 7350 | CIP-006-6 R2.2. | Require manual or automated logging of visitor entry into and exit from the Physical Security Perimeter that includes date and time of the initial entry and last exit, the visitor’s name, and the name of an individual point of contact responsible for the visitor, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. An example of evidence may include, but is not limited to, language in a visitor control program that requires continuous escorted access of visitors within Physical Security Perimeters and additional evidence to demonstrate that the process was implemented, such as dated visitor logs that include the required information. | 2016-07-01 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6105 |  | 3. | 7351 | CIP-006-6 R2.3. | Retain visitor logs for at least ninety calendar days. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.3. An example of evidence may include, but is not limited to, documentation showing logs have been retained for at least ninety calendar days. | 2016-07-01 |  |  |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
516 | 6106 |  | 1. | 7352 | CIP-006-6 R3.1. | Maintenance and testing of each Physical Access Control System and locally mounted hardware or devices at the Physical Security Perimeter at least once every 24 calendar months to ensure they function properly. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M.3.1. An example of evidence may include, but is not limited to, a maintenance and testing program that provides for testing each Physical Access Control System and locally mounted hardware or devices associated with each applicable Physical Security Perimeter at least once every 24 calendar months and additional evidence to demonstrate that this testing was done, such as dated maintenance records, or other documentation showing testing and maintenance has been performed on each applicable device or system at least once every 24 calendar months. | 2017-07-01 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
517 | 6109 |  | 1. | 7140 | PRC-024-2 R3.1. | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have evidence that it has documented and communicated any known regulatory or equipment limitations (excluding limitations noted in footnote 3) that resulted in an exception to Requirements R1 or R2 in accordance with Requirement R3 such as a dated email or letter that contains such documentation as study results, experience from an actual event, or manufacturer’s advice. Each Generator Owner shall have evidence that it communicated applicable generator protective relay trip settings in accordance with Requirement R4, such as dated e-mails, correspondence or other evidence and copies of any requests it has received for that information. | 2016-07-01 |  | 2022-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
518 | 6111 | 7137 | 1. | 7138 | PRC-019-2 R1.1.1. | The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Generator Owner and Transmission Owner with applicable Facilities will have evidence (such as examples provided in PRC-019 Section G) that it coordinated the voltage regulating system controls, including in-service2 limiters and protection functions, with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as specified in Requirement R1. This evidence should include dated documentation that demonstrates the coordination was performed. | 2016-07-01 |  |  |  | 4.2. Facilities For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following: 4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.2 Individual synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.3 Generating plant/ Facility consisting of one or more units that are connected to the Bulk Electric System at a common bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3.1 This includes individual generating units of the dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition where voltage regulating control for the facility is performed solely at the individual generating unit of the dispersed power producing resources. 4.2.4 Any generator, regardless of size, that is a blackstart unit material to and designated as part of a Transmission Operator’s restoration plan. | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
518 | 6111 | 7137 | 2. | 7139 | PRC-019-2 R1.1.2. | The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Generator Owner and Transmission Owner with applicable Facilities will have evidence (such as examples provided in PRC-019 Section G) that it coordinated the voltage regulating system controls, including in-service2 limiters and protection functions, with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as specified in Requirement R1. This evidence should include dated documentation that demonstrates the coordination was performed. | 2016-07-01 |  |  |  | 4.2. Facilities For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following: 4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.2 Individual synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.3 Generating plant/ Facility consisting of one or more units that are connected to the Bulk Electric System at a common bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3.1 This includes individual generating units of the dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition where voltage regulating control for the facility is performed solely at the individual generating unit of the dispersed power producing resources. 4.2.4 Any generator, regardless of size, that is a blackstart unit material to and designated as part of a Transmission Operator’s restoration plan. | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
518 | 6111 |  | 1. | 7137 | PRC-019-2 R1.1. | Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Generator Owner and Transmission Owner with applicable Facilities will have evidence (such as examples provided in PRC-019 Section G) that it coordinated the voltage regulating system controls, including in-service2 limiters and protection functions, with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as specified in Requirement R1. This evidence should include dated documentation that demonstrates the coordination was performed. | 2016-07-01 |  |  |  | 4.2. Facilities For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following: 4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.2 Individual synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System. 4.2.3 Generating plant/ Facility consisting of one or more units that are connected to the Bulk Electric System at a common bus with total generation greater than 75 MVA (gross aggregate nameplate rating). 4.2.3.1 This includes individual generating units of the dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition where voltage regulating control for the facility is performed solely at the individual generating unit of the dispersed power producing resources. 4.2.4 Any generator, regardless of size, that is a blackstart unit material to and designated as part of a Transmission Operator’s restoration plan. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
519 | 6114 |  | 1. | 6115 | PRC-001-1.1(ii) R2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2020-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
519 | 6114 |  | 2. | 6116 | PRC-001-1.1(ii) R2.2. | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. |  | TOP | [18 empty] | TOP |  |  |  | 2015-05-29 |  | 2020-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
519 | 6117 |  | 1. | 6118 | PRC-001-1.1(ii) R3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. • Requirement R3.1 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2020-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
519 | 6117 |  | 2. | 6119 | PRC-001-1.1(ii) R3.2. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP |  |  |  | 2015-05-29 |  | 2020-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
519 | 6121 |  | 1. | 6122 | PRC-001-1.1(ii) R5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2020-09-30 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
519 | 6121 |  | 2. | 6123 | PRC-001-1.1(ii) R5.2. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. |  | TOP | [18 empty] | TOP |  |  |  | 2015-05-29 |  | 2020-09-30 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 700 |  | 1. | 701 | FAC-010-1 R1.1. | Be applicable for developing SOLs used in the planning horizon. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 700 |  | 2. | 702 | FAC-010-1 R1.2. | State that SOLs shall not exceed associated Facility Ratings. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 700 |  | 3. | 703 | FAC-010-1 R1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 704 | 706 | 1. | 707 | FAC-010-1 R2.2.1. | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 704 | 706 | 2. | 708 | FAC-010-1 R2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 704 | 706 | 3. | 709 | FAC-010-1 R2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 704 | 710 | 1. | 711 | FAC-010-1 R2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  | 231000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 704 | 710 | 2. | 712 | FAC-010-1 R2.3.2. | System reconfiguration through manual or automatic control or protection actions. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  | 232000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 704 | 710 | 3. | 713 | FAC-010-1 R2.3.3. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  | 233000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 704 | 715 | 1. | 716 | FAC-010-1 R2.5.1. | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  | 251000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 704 |  | 1. | 705 | FAC-010-1 R2.1. | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-05-29 |  | 2009-04-28 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 704 |  | 2. | 706 | FAC-010-1 R2.2. | Following the single Contingencies (see footnote in standard) identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading Outages or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-05-29 |  | 2009-04-28 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 704 |  | 3. | 710 | FAC-010-1 R2.3. | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 704 |  | 4. | 714 | FAC-010-1 R2.4. | Starting with all facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading Outages or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 704 |  | 5. | 715 | FAC-010-1 R2.5. | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 717 |  | 1. | 718 | FAC-010-1 R3.1. | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 717 |  | 2. | 719 | FAC-010-1 R3.2. | Selection of applicable Contingencies. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 717 |  | 3. | 720 | FAC-010-1 R3.3. | Level of detail of system models used to determine SOLs. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 717 |  | 4. | 721 | FAC-010-1 R3.4. | Allowed uses of Special Protection Systems or Remedial Action Plans. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 717 |  | 5. | 722 | FAC-010-1 R3.5. | Anticipated transmission system configuration, generation dispatch and Load level. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 717 |  | 6. | 723 | FAC-010-1 R3.6. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-05-29 |  | 2009-04-28 |  |  | 360000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 724 |  | 1. | 725 | FAC-010-1 R4.1. | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 724 |  | 2. | 726 | FAC-010-1 R4.2. | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
52 | 724 |  | 3. | 727 | FAC-010-1 R4.3. | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
520 | 6128 |  | 1. | 7103 | TOP-002-4 R4.1. | Expected generation resource commitment and dispatch |  | BA | BA | [20 empty] | Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2016-01-26 |  | 2025-09-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
520 | 6128 |  | 2. | 7105 | TOP-002-4 R4.2. | Interchange scheduling |  | BA | BA | [20 empty] | Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2016-01-26 |  | 2025-09-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
520 | 6128 |  | 3. | 7107 | TOP-002-4 R4.3. | Demand patterns |  | BA | BA | [20 empty] | Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2016-01-26 |  | 2025-09-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
520 | 6128 |  | 4. | 7109 | TOP-002-4 R4.4. | Capacity and energy reserve requirements, including deliverability capability |  | BA | BA | [20 empty] | Each Balancing Authority shall have evidence that it has developed a plan to operate within the criteria identified. Such evidence could include but is not limited to dated operator logs or e-mail records. | 2016-01-26 |  | 2025-09-30 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
521 | 6132 | 6817 | 1. | 6818 | IRO-017-1 R1.1.1. | Development and communication of outage schedules. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall make available its dated, current, in force outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. | 2017-04-01 |  |  |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
521 | 6132 | 6817 | 2. | 6819 | IRO-017-1 R1.1.2. | Assignment of coordination responsibilities for outage schedules between Transmission Operator(s) and Balancing Authority(s). |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall make available its dated, current, in force outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. | 2017-04-01 |  |  |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
521 | 6132 |  | 1. | 6817 | IRO-017-1 R1.1. | Identify applicable roles and reporting responsibilities including: |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall make available its dated, current, in force outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. | 2016-01-26 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
521 | 6132 |  | 2. | 6820 | IRO-017-1 R1.2. | Specify outage submission timing requirements. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall make available its dated, current, in force outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. | 2016-01-26 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
521 | 6132 |  | 3. | 6821 | IRO-017-1 R1.3. | Define the process to evaluate the impact of Transmission and generation outages within its Wide Area. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall make available its dated, current, in force outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. | 2016-01-26 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
521 | 6132 |  | 4. | 6822 | IRO-017-1 R1.4. | Define the process to coordinate the resolution of identified outage conflicts with its Transmission Operators and Balancing Authorities, and other Reliability Coordinators. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall make available its dated, current, in force outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. | 2016-01-26 |  |  |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
525 | 6149 |  | 1. | 7047 | IRO-010-2 R1.1. | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. |  | RC | [11 empty] | RC | [10 empty] | 2017-01-01 |  | 2021-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
525 | 6149 |  | 2. | 7048 | IRO-010-2 R1.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | RC | [11 empty] | RC | [10 empty] | 2017-01-01 |  | 2021-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
525 | 6149 |  | 3. | 7049 | IRO-010-2 R1.3. | A periodicity for providing data. |  | RC | [11 empty] | RC | [10 empty] | 2017-01-01 |  | 2021-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
525 | 6149 |  | 4. | 7050 | IRO-010-2 R1.4. | The deadline by which the respondent is to provide the indicated data. |  | RC | [11 empty] | RC | [10 empty] | 2017-01-01 |  | 2021-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
525 | 6151 |  | 1. | 7051 | IRO-010-2 R3.1. | A mutually agreeable format |  | BA, DP, GO, GOP, LSE, RC, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
525 | 6151 |  | 2. | 7052 | IRO-010-2 R3.2. | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, LSE, RC, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
525 | 6151 |  | 3. | 7053 | IRO-010-2 R3.3. | A mutually agreeable security protocol |  | BA, DP, GO, GOP, LSE, RC, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
526 | 6152 |  | 1. | 6809 | IRO-014-3 R1.1. | Criteria and processes for notifications. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Operating Processes, and Operating Plans that require notifications, or the coordination of actions among impacted Reliability Coordinators for conditions or activities that may impact adjacent Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements, and notes from periodic communications. | 2016-01-26 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
526 | 6152 |  | 2. | 6810 | IRO-014-3 R1.2. | Energy and capacity shortages. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Operating Processes, and Operating Plans that require notifications, or the coordination of actions among impacted Reliability Coordinators for conditions or activities that may impact adjacent Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements, and notes from periodic communications. | 2016-01-26 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
526 | 6152 |  | 3. | 6811 | IRO-014-3 R1.3. | Control of voltage, including the coordination of reactive resources. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Operating Processes, and Operating Plans that require notifications, or the coordination of actions among impacted Reliability Coordinators for conditions or activities that may impact adjacent Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements, and notes from periodic communications. | 2016-01-26 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
526 | 6152 |  | 4. | 6812 | IRO-014-3 R1.4. | Exchange of information including planned and unplanned outage information to support its Operational Planning Analyses and Real-time Assessments. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Operating Processes, and Operating Plans that require notifications, or the coordination of actions among impacted Reliability Coordinators for conditions or activities that may impact adjacent Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements, and notes from periodic communications. | 2016-01-26 |  |  |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
526 | 6152 |  | 5. | 6813 | IRO-014-3 R1.5. | Provisions for periodic communications to support reliable operations. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have available the latest approved documented version of its Operating Procedures, Operating Processes, and Operating Plans that require notifications, or the coordination of actions among impacted Reliability Coordinators for conditions or activities that may impact adjacent Reliability Coordinator Areas. This documentation shall include dated, current in force documentation with the specified elements, and notes from periodic communications. | 2016-01-26 |  |  |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
526 | 6153 |  | 1. | 6814 | IRO-014-3 R2.1. | Review and update annually with no more than 15 months between reviews. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have dated evidence that its Operating Procedures, Operating Processes, and Operating Plans that require one or more other Reliability Coordinators to take action were maintained as specified. This evidence may include but is not limited to dated documentation with confirmation of receipt, dated notice of acceptance or agreement to take specified actions, or dated electronic communications with confirmation of receipt and acceptance or agreement to take specified actions. | 2016-01-26 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
526 | 6153 |  | 2. | 6815 | IRO-014-3 R2.2. | Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have dated evidence that its Operating Procedures, Operating Processes, and Operating Plans that require one or more other Reliability Coordinators to take action were maintained as specified. This evidence may include but is not limited to dated documentation with confirmation of receipt, dated notice of acceptance or agreement to take specified actions, or dated electronic communications with confirmation of receipt and acceptance or agreement to take specified actions. | 2016-01-26 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
526 | 6153 |  | 3. | 6816 | IRO-014-3 R2.3. | Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have dated evidence that its Operating Procedures, Operating Processes, and Operating Plans that require one or more other Reliability Coordinators to take action were maintained as specified. This evidence may include but is not limited to dated documentation with confirmation of receipt, dated notice of acceptance or agreement to take specified actions, or dated electronic communications with confirmation of receipt and acceptance or agreement to take specified actions. | 2016-01-26 |  |  |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
527 | 6352 |  | 1. | 6354 | PRC-004-5 R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-11-19 |  | 2017-04-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
527 | 6352 |  | 2. | 6355 | PRC-004-5 R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-11-19 |  | 2017-04-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
527 | 6352 |  | 3. | 6356 | PRC-004-5 R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-11-19 |  | 2017-04-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
527 | 6357 | 6358 | 1. | RP-2021-06-23-0000021 | PRC-004-5 R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2017-04-02 |  | 2017-04-01 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
527 | 6357 | 6358 | 2. | 6361 | PRC-004-5 R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2017-04-02 |  | 2017-04-01 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
527 | 6357 | 6358 | 3. | 6362 | PRC-004-5 R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2017-04-02 |  | 2017-04-01 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
527 | 6357 |  | 1. | 6358 | PRC-004-5 R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-11-19 |  | 2017-04-01 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
527 | 6357 |  | 2. | 6363 | PRC-004-5 R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-11-19 |  | 2017-04-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
528 | 6371 |  | 1. | 6372 | PRC-005-5 R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO | [6 empty] | 2015-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
528 | 6371 |  | 2. | 6373 | PRC-005-5 R1.2. | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO | [6 empty] | 2015-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6379 |  | 1. | RP-2021-06-30-0000043 | CIP-014-2 R1.1. | Subsequent risk assessments shall be performed: • At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or • At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria in Applicability Section 4.1.1 as specified in Requirement R1. Additionally, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment as specified in Requirement R1, Part 1.2. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6379 |  | 2. | 6380 | CIP-014-2 R1.2. | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria in Applicability Section 4.1.1 as specified in Requirement R1. Additionally, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment as specified in Requirement R1, Part 1.2. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6382 |  | 1. | RP-2021-06-30-0000044 | CIP-014-2 R2.1. | Each Transmission Owner shall select an unaffiliated verifying entity that is either: • A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or • An entity that has transmission planning or analysis experience. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6382 |  | 2. | 6383 | CIP-014-2 R2.2. | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6382 |  | 3. | 6385 | CIP-014-2 R2.3. | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation: • Modify its identification under Requirement R1 consistent with the recommendation; or • Document the technical basis for not modifying the identification in accordance with the recommendation. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6382 |  | 4. | 6386 | CIP-014-2 R2.4. | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6387 |  | 1. | 6388 | CIP-014-2 R3.1. | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic notifications or communications that the Transmission Owner notified each Transmission Operator, as applicable, according to Requirement R3. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6389 |  | 1. | RP-2021-06-30-0000045 | CIP-014-2 R4.1. | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6389 |  | 2. | 6391 | CIP-014-2 R4.2. | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6389 |  | 3. | 6392 | CIP-014-2 R4.3. | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6393 |  | 1. | 6394 | CIP-014-2 R5.1. | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6393 |  | 2. | 6395 | CIP-014-2 R5.2. | Law enforcement contact and coordination information. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6393 |  | 3. | 6396 | CIP-014-2 R5.3. | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6393 |  | 4. | 6397 | CIP-014-2 R5.4. | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6399 |  | 1. | 6401 | CIP-014-2 R6.1. | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following: • An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification. • An entity or organization approved by the ERO. • A governmental agency with physical security expertise. • An entity or organization with demonstrated law enforcement, government, or military physical security expertise. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | 2015-10-02 |  | 2022-06-16 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6399 |  | 2. | 6402 | CIP-014-2 R6.2. | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6399 |  | 3. | 6403 | CIP-014-2 R6.3. | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation: • Modify its evaluation or security plan(s) consistent with the recommendation; or • Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
529 | 6399 |  | 4. | 6404 | CIP-014-2 R6.4. | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | 2015-10-02 |  | 2022-06-16 |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. Voltage Value of a Line Weight Value per Line less than 200 kV (not applicable) (not applicable) 200 kV to 299 kV 700 300 kV to 499 kV 1300 500 kV and above 0 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 729 |  | 1. | 730 | FAC-010-2 R1.1. | Be applicable for developing SOLs used in the planning horizon. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 729 |  | 2. | 731 | FAC-010-2 R1.2. | State that SOLs shall not exceed associated Facility Ratings. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 729 |  | 3. | 732 | FAC-010-2 R1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 733 | 735 | 1. | 736 | FAC-010-2 R2.2.1. | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 733 | 735 | 2. | 737 | FAC-010-2 R2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 733 | 735 | 3. | 738 | FAC-010-2 R2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 733 | 739 | 1. | 740 | FAC-010-2 R2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 231000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 733 | 739 | 2. | 741 | FAC-010-2 R2.3.2. | System reconfiguration through manual or automatic control or protection actions. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 232000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 733 | 744 | 1. | 745 | FAC-010-2 R2.6.1. | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 261000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 733 |  | 1. | 734 | FAC-010-2 R2.1. | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 733 |  | 2. | 735 | FAC-010-2 R2.2. | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 733 |  | 3. | 739 | FAC-010-2 R2.3. | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 733 |  | 4. | 742 | FAC-010-2 R2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 733 |  | 5. | 743 | FAC-010-2 R2.5. | Starting with all Facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 733 |  | 6. | 744 | FAC-010-2 R2.6. | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 746 |  | 1. | 747 | FAC-010-2 R3.1. | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 746 |  | 2. | 748 | FAC-010-2 R3.2. | Selection of applicable Contingencies. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 746 |  | 3. | 749 | FAC-010-2 R3.3. | Level of detail of system models used to determine SOLs. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 746 |  | 4. | 750 | FAC-010-2 R3.4. | Allowed uses of Special Protection Systems or Remedial Action Plans. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 746 |  | 5. | 751 | FAC-010-2 R3.5. | Anticipated transmission system configuration, generation dispatch and Load level. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 746 |  | 6. | 752 | FAC-010-2 R3.6. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 360000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 753 |  | 1. | 754 | FAC-010-2 R4.1. | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 753 |  | 2. | 755 | FAC-010-2 R4.2. | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
53 | 753 |  | 3. | 756 | FAC-010-2 R4.3. | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
530 | 6405 |  | 1. | 6406 | PRC-010-2 R1.1. | The implementation of the UVLS Program resolves the identified undervoltage issues that led to its development and design. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Acceptable evidence may include, but is not limited to, date-stamped studies and analyses, reports, or other documentation detailing the effectiveness of the UVLS Program, and date-stamped communications showing that the UVLS Program specifications and implementation schedule were provided to UVLS entities. | 2015-11-19 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
530 | 6405 |  | 2. | RP-2021-07-09-0000036 | PRC-010-2 R1.2. | The UVLS Program is integrated through coordination with generator voltage ride-through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage-based load shedding programs. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Acceptable evidence may include, but is not limited to, date-stamped studies and analyses, reports, or other documentation detailing the effectiveness of the UVLS Program, and date-stamped communications showing that the UVLS Program specifications and implementation schedule were provided to UVLS entities. | 2017-04-02 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
530 | 6409 |  | 1. | RP-2021-07-09-0000037 | PRC-010-2 R3.1. | The UVLS Program resolves the identified undervoltage issues for which the UVLS Program is designed. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Acceptable evidence may include, but is not limited to, date-stamped reports or other documentation detailing the assessment of the UVLS Program. | 2017-04-02 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
530 | 6409 |  | 2. | RP-2021-07-09-0000038 | PRC-010-2 R3.2. | The UVLS Program is integrated through coordination with generator voltage ride-through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage-based load shedding programs. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Acceptable evidence may include, but is not limited to, date-stamped reports or other documentation detailing the assessment of the UVLS Program. | 2017-04-02 |  |  |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
530 | 6410 |  | 1. | RP-2021-07-09-0000039 | PRC-010-2 R4.1. | Whether its UVLS Program resolved the undervoltage issues associated with the event, and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Acceptable evidence may include, but is not limited to, date-stamped event data, event analysis reports, or other documentation detailing the assessment of the UVLS Program and associated equipment. | 2017-04-02 |  |  |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
530 | 6410 |  | 2. | 6412 | PRC-010-2 R4.2. | The performance (i.e., operation and non-operation) of the UVLS Program equipment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Acceptable evidence may include, but is not limited to, date-stamped event data, event analysis reports, or other documentation detailing the assessment of the UVLS Program and associated equipment. | 2015-11-19 |  |  |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
531 | 7440 |  | 1. | 7446 | IRO-009-2 R1.1. | That can be implemented in time to prevent the identified IROL exceedance. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have, and make available upon request, evidence to confirm that it has Operating Processes, Procedures, or Plans to address both preventing and mitigating the magnitude and duration of IROL exceedances in accordance with Requirement R1. This evidence shall include a list of any IROLs (and each associated Tv) identified in advance, along with one or more dated Operating Processes, Procedures, or Plans that will be used. | 2015-12-04 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
531 | 7440 |  | 2. | RP-2021-07-05-0000001 | IRO-009-2 R1.2. | To mitigate the magnitude and duration of an IROL exceedance such that the IROL exceedance is relieved within the IROL’s Tv . |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have, and make available upon request, evidence to confirm that it has Operating Processes, Procedures, or Plans to address both preventing and mitigating the magnitude and duration of IROL exceedances in accordance with Requirement R1. This evidence shall include a list of any IROLs (and each associated Tv) identified in advance, along with one or more dated Operating Processes, Procedures, or Plans that will be used. | 2016-01-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
532 | 7453 |  | 1. | 7454 | BAL-003-1.1 R3.1. | Less than zero at all times, and |  | BA | BA | [20 empty] | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2015-11-13 |  | 2020-11-30 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
532 | 7453 |  | 2. | 7455 | BAL-003-1.1 R3.2. | Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. |  | BA | BA | [20 empty] | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2015-11-13 |  | 2020-11-30 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7457 |  | 1. | 7468 | COM-001-2.1 R1.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7457 |  | 2. | 7469 | COM-001-2.1 R1.2. | Each adjacent Reliability Coordinator within the same Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7458 |  | 1. | 7470 | COM-001-2.1 R2.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7458 |  | 2. | 7471 | COM-001-2.1 R2.2. | Each adjacent Reliability Coordinator within the same Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7459 |  | 1. | 7472 | COM-001-2.1 R3.1. | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7459 |  | 2. | 7473 | COM-001-2.1 R3.2. | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7459 |  | 3. | 7474 | COM-001-2.1 R3.3. | Each Distribution Provider within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7459 |  | 4. | 7475 | COM-001-2.1 R3.4. | Each Generator Operator within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7459 |  | 5. | 7476 | COM-001-2.1 R3.5. | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7459 |  | 6. | 7477 | COM-001-2.1 R3.6. | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  | 360000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7460 |  | 1. | 7487 | COM-001-2.1 R4.1. | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7460 |  | 2. | 7490 | COM-001-2.1 R4.2. | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7460 |  | 3. | 7491 | COM-001-2.1 R4.3. | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7460 |  | 4. | 7492 | COM-001-2.1 R4.4. | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7461 |  | 1. | 7493 | COM-001-2.1 R5.1. | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7461 |  | 2. | 7494 | COM-001-2.1 R5.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7461 |  | 3. | 7495 | COM-001-2.1 R5.3. | Each Distribution Provider within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7461 |  | 4. | 7496 | COM-001-2.1 R5.4. | Each Generator Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7461 |  | 5. | 7497 | COM-001-2.1 R5.5. | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 550000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7462 |  | 1. | 7498 | COM-001-2.1 R6.1. | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7462 |  | 2. | 7499 | COM-001-2.1 R6.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7462 |  | 3. | 7500 | COM-001-2.1 R6.3. | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7463 |  | 1. | 7501 | COM-001-2.1 R7.1. | Its Balancing Authority. |  | DP |  | DP | [20 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7463 |  | 2. | 7502 | COM-001-2.1 R7.2. | Its Transmission Operator. |  | DP |  | DP | [20 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7464 |  | 1. | 7503 | COM-001-2.1 R8.1. | Its Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
533 | 7464 |  | 2. | 7504 | COM-001-2.1 R8.2. | Its Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-11-13 |  | 2017-09-30 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
535 | 7711 |  | 1. | 7712 | VAR-001-4.1 E.A.18.1. | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-11-13 |  | 2017-09-25 |  |  | 1810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
535 | 7711 |  | 2. | 7713 | VAR-001-4.1 E.A.18.2. | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-11-13 |  | 2017-09-25 |  |  | 1820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
535 | 7505 |  | 1. | 7507 | VAR-001-4.1 R1.1. | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
535 | 7509 |  | 1. | 7510 | VAR-001-4.1 R4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
535 | 7511 |  | 1. | RP-2021-06-24-0000063 | VAR-001-4.1 R5.1. | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
535 | 7511 |  | 2. | RP-2021-06-24-0000064 | VAR-001-4.1 R5.2. | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
535 | 7511 |  | 3. | RP-2021-06-24-0000065 | VAR-001-4.1 R5.3. | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
536 | 7521 |  | 1. | 7527 | PRC-004-3(i) R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-12-04 |  | 2016-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
536 | 7521 |  | 2. | 7528 | PRC-004-3(i) R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-12-04 |  | 2016-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
536 | 7521 |  | 3. | 7529 | PRC-004-3(i) R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-12-04 |  | 2016-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
536 | 7522 | 7530 | 1. | 7531 | PRC-004-3(i) R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2016-07-01 |  | 2016-06-30 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
536 | 7522 | 7530 | 2. | 7532 | PRC-004-3(i) R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2016-07-01 |  | 2016-06-30 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
536 | 7522 | 7530 | 3. | 7533 | PRC-004-3(i) R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2016-07-01 |  | 2016-06-30 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
536 | 7522 |  | 1. | 7530 | PRC-004-3(i) R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-12-04 |  | 2016-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
536 | 7522 |  | 2. | 7534 | PRC-004-3(i) R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-12-04 |  | 2016-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
537 | 7535 |  | 1. | 7536 | PRC-004-4(i) R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-12-04 |  | 2017-04-01 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
537 | 7535 |  | 2. | 7537 | PRC-004-4(i) R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-12-04 |  | 2017-04-01 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
537 | 7535 |  | 3. | 7538 | PRC-004-4(i) R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-12-04 |  | 2017-04-01 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
537 | 7539 | 7540 | 1. | 7541 | PRC-004-4(i) R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2016-07-01 |  | 2017-04-01 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
537 | 7539 | 7540 | 2. | 7542 | PRC-004-4(i) R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2016-07-01 |  | 2017-04-01 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
537 | 7539 | 7540 | 3. | 7543 | PRC-004-4(i) R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2016-07-01 |  | 2017-04-01 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
537 | 7539 |  | 1. | 7540 | PRC-004-4(i) R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-12-04 |  | 2017-04-01 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
537 | 7539 |  | 2. | 7544 | PRC-004-4(i) R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-12-04 |  | 2017-04-01 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
538 | 7549 |  | 1. | 7550 | PRC-004-5(i) R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-11-19 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
538 | 7549 |  | 2. | 7551 | PRC-004-5(i) R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-11-19 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
538 | 7549 |  | 3. | 7552 | PRC-004-5(i) R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-11-19 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
538 | 7553 | 7554 | 1. | 7555 | PRC-004-5(i) R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2017-04-02 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
538 | 7553 | 7554 | 2. | 7556 | PRC-004-5(i) R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2017-04-02 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
538 | 7553 | 7554 | 3. | 7558 | PRC-004-5(i) R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2017-04-02 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
538 | 7553 |  | 1. | 7554 | PRC-004-5(i) R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-11-19 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
538 | 7553 |  | 2. | 7557 | PRC-004-5(i) R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2015-11-19 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
539 | 7563 | 7566 | 1. | 7567 | PRC-027-1 R1.3.1. | Provide the proposed Protection System settings to the owner(s) of the electrically joined Facilities. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity established a process to develop settings for its Protection Systems, in accordance with Requirement R1. | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below) 4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
539 | 7563 | 7566 | 2. | 7568 | PRC-027-1 R1.3.2. | Respond to any owner(s) that provided its proposed Protection System settings pursuant to Requirement R1, Part 1.3.1 by identifying any coordination issue(s) or affirming that no coordination issue(s) were identified. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity established a process to develop settings for its Protection Systems, in accordance with Requirement R1. | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below) 4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
539 | 7563 | 7566 | 3. | 7569 | PRC-027-1 R1.3.3. | Verify that identified coordination issue(s) associated with the proposed Protection System settings for the associated BES Elements are addressed prior to implementation. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below) 4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
539 | 7563 | 7566 | 4. | 7570 | PRC-027-1 R1.3.4. | Communicate with the other owner(s) of the electrically joined Facilities regarding revised Protection System settings resulting from unforeseen circumstances that arise during implementation or commissioning, Misoperation investigations, maintenance activities, or emergency replacements required as a result of Protection System component failure. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity established a process to develop settings for its Protection Systems, in accordance with Requirement R1. | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below) 4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
539 | 7563 |  | 1. | 7564 | PRC-027-1 R1.1. | A review and update of short-circuit model data for the BES Elements under study. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity established a process to develop settings for its Protection Systems, in accordance with Requirement R1. | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below) 4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
539 | 7563 |  | 2. | 7565 | PRC-027-1 R1.2. | A review of the developed Protection System settings. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity established a process to develop settings for its Protection Systems, in accordance with Requirement R1. | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below) 4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
539 | 7563 |  | 3. | 7566 | PRC-027-1 R1.3. | For Protection System settings applied on BES Elements that electrically join Facilities owned by separate functional entities (Transmission Owners, Generator Owners, and Distribution Providers), provisions to: |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation to demonstrate that the responsible entity established a process to develop settings for its Protection Systems, in accordance with Requirement R1. | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below) 4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 758 |  | 1. | 759 | FAC-011-1 R1.1. | Be applicable for developing SOLs used in the operations horizon. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 758 |  | 2. | 760 | FAC-011-1 R1.2. | State that SOLs shall not exceed associated Facility Ratings. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 758 |  | 3. | 761 | FAC-011-1 R1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 762 | 764 | 1. | 765 | FAC-011-1 R2.2.1. | Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 762 | 764 | 2. | 766 | FAC-011-1 R2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 762 | 764 | 3. | 767 | FAC-011-1 R2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 762 | 768 | 1. | 769 | FAC-011-1 R2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  | 231000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 762 | 768 | 2. | 770 | FAC-011-1 R2.3.2. | Interruption of other network customers, only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or, if the real-time operating conditions are more adverse than anticipated in the corresponding studies, e.g., load greater than studied. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  | 232000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 762 | 768 | 3. | 771 | FAC-011-1 R2.3.3. | System reconfiguration through manual or automatic control or protection actions. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  | 233000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 762 |  | 1. | 763 | FAC-011-1 R2.1. | In the pre-contingency state, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect current or expected system conditions and shall reflect changes to system topology such as Facility outages. |  | RC | [11 empty] | RC | [10 empty] | 2008-05-29 |  | 2009-04-28 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 762 |  | 2. | 764 | FAC-011-1 R2.2. | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading Outages or uncontrolled separation shall not occur. |  | RC | [11 empty] | RC | [10 empty] | 2008-05-29 |  | 2009-04-28 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 762 |  | 3. | 768 | FAC-011-1 R2.3. | In determining the system’s response to a single Contingency, the following shall be acceptable: |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 762 |  | 4. | 772 | FAC-011-1 R2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 773 | 776 | 1. | 777 | FAC-011-1 R3.3.1. | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  | 331000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 773 |  | 1. | 774 | FAC-011-1 R3.1. | Study model (must include at least the entire Reliability Coordinator Area as well as the critical modeling details from other Reliability Coordinator Areas that would impact the Facility or Facilities under study.) |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 773 |  | 2. | 775 | FAC-011-1 R3.2. | Selection of applicable Contingencies. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 773 |  | 3. | 776 | FAC-011-1 R3.3. | A process for determining which of the stability limits associated with the list of multiple contingencies (provided by the Planning Authority in accordance with FAC-014 Requirement 6) are applicable for use in the operating horizon given the actual or expected system conditions. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 773 |  | 4. | 778 | FAC-011-1 R3.4. | Level of detail of system models used to determine SOLs. |  | RC | [11 empty] | RC | [10 empty] | 2008-05-29 |  | 2009-04-28 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 773 |  | 5. | 779 | FAC-011-1 R3.5. | Allowed uses of Special Protection Systems or Remedial Action Plans. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 773 |  | 6. | 780 | FAC-011-1 R3.6. | Anticipated transmission system configuration, generation dispatch and Load level. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 360000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 773 |  | 7. | 781 | FAC-011-1 R3.7. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 370000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 782 |  | 1. | 783 | FAC-011-1 R4.1. | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 782 |  | 2. | 784 | FAC-011-1 R4.2. | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
54 | 782 |  | 3. | 785 | FAC-011-1 R4.3. | Each Transmission Operator that operates in the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
540 | 7573 |  | 1. | 7579 | PRC-005-6 R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented PSMP in accordance with Requirement R1. For each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type, the documentation shall include the type of maintenance method applied (time-based, performance-based, or a combination of these maintenance methods), and shall include all batteries associated with the station dc supply Component Types in a time-based program as described in Table 1-4 and Table 3. (Part 1.1) | 2015-12-18 |  |  |  | 4.2.1 Protection Systems and Sudden Pressure Relaying that are installed for the purpose of detecting Faults on BES Elements (lines, buses, transformers, etc.) 4.2.2 Protection Systems used for underfrequency load-shedding systems installed per ERO underfrequency load-shedding requirements. 4.2.3 Protection Systems used for undervoltage load-shedding systems installed to prevent system voltage collapse or voltage instability for BES reliability. 4.2.4 Protection Systems installed as a Remedial Action Scheme (RAS) for BES reliability. 4.2.5 Protection Systems and Sudden Pressure Relaying for generator Facilities that are part of the BES, except for generators identified through Inclusion I4 of the BES definition, including: 4.2.5.1 Protection Systems that act to trip the generator either directly or via lockout or auxiliary tripping relays. 4.2.5.2 Protection Systems and Sudden Pressure Relaying for generator step-up transformers for generators that are part of the BES. 4.2.5.3 Protection Systems and Sudden Pressure Relaying for station service or excitation transformers connected to the generator bus of generators which are part of the BES, that act to trip the generator either directly or via lockout or tripping auxiliary relays. 4.2.6 Protection Systems and Sudden Pressure Relaying for the following BES generator Facilities for dispersed power producing resources identified through Inclusion I4 of the BES definition: 4.2.6.1 Protection Systems and Sudden Pressure Relaying for Facilities used in aggregating dispersed BES generation from the point where those resources aggregate to greater than 75 MVA to a common point of connection at 100kV or above. 4.2.7 Automatic Reclosing , including: 4.2.7.1 Automatic Reclosing applied on the terminals of Elements connected to the BES bus located at generating plant substations where the total installed gross generating plant capacity is greater than the gross capacity of the largest BES generating unit within the Balancing Authority Area or, if a member of a Reserve Sharing Group, the largest generating unit within the Reserve Sharing Group. 4.2.7.2 Automatic Reclosing applied on the terminals of all BES Elements at substations one bus away from generating plants specified in Section 4.2.7.1 when the substation is less than 10 circuit-miles from the generating plant substation. 4.2.7.3 Automatic Reclosing applied as an integral part of an RAS specified in Section 4.2.4. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
540 | 7573 |  | 2. | 7580 | PRC-005-6 R1.2. | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. |  | DP, DP-UFLS, GO, TO |  | DP | DP-UFLS |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner and Distribution Provider shall have a documented PSMP in accordance with Requirement R1. For Component Types that use monitoring to extend the maintenance intervals, the responsible entity(s) shall have evidence for each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type (such as manufacturer’s specifications or engineering drawings) of the appropriate monitored Component attributes as specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4- 3, and Table 5. (Part 1.2) | 2015-12-18 |  |  |  | 4.2.1 Protection Systems and Sudden Pressure Relaying that are installed for the purpose of detecting Faults on BES Elements (lines, buses, transformers, etc.) 4.2.2 Protection Systems used for underfrequency load-shedding systems installed per ERO underfrequency load-shedding requirements. 4.2.3 Protection Systems used for undervoltage load-shedding systems installed to prevent system voltage collapse or voltage instability for BES reliability. 4.2.4 Protection Systems installed as a Remedial Action Scheme (RAS) for BES reliability. 4.2.5 Protection Systems and Sudden Pressure Relaying for generator Facilities that are part of the BES, except for generators identified through Inclusion I4 of the BES definition, including: 4.2.5.1 Protection Systems that act to trip the generator either directly or via lockout or auxiliary tripping relays. 4.2.5.2 Protection Systems and Sudden Pressure Relaying for generator step-up transformers for generators that are part of the BES. 4.2.5.3 Protection Systems and Sudden Pressure Relaying for station service or excitation transformers connected to the generator bus of generators which are part of the BES, that act to trip the generator either directly or via lockout or tripping auxiliary relays. 4.2.6 Protection Systems and Sudden Pressure Relaying for the following BES generator Facilities for dispersed power producing resources identified through Inclusion I4 of the BES definition: 4.2.6.1 Protection Systems and Sudden Pressure Relaying for Facilities used in aggregating dispersed BES generation from the point where those resources aggregate to greater than 75 MVA to a common point of connection at 100kV or above. 4.2.7 Automatic Reclosing , including: 4.2.7.1 Automatic Reclosing applied on the terminals of Elements connected to the BES bus located at generating plant substations where the total installed gross generating plant capacity is greater than the gross capacity of the largest BES generating unit within the Balancing Authority Area or, if a member of a Reserve Sharing Group, the largest generating unit within the Reserve Sharing Group. 4.2.7.2 Automatic Reclosing applied on the terminals of all BES Elements at substations one bus away from generating plants specified in Section 4.2.7.1 when the substation is less than 10 circuit-miles from the generating plant substation. 4.2.7.3 Automatic Reclosing applied as an integral part of an RAS specified in Section 4.2.4. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 | 7583 | 1. | 7584 | MOD-031-2 R1.3.1. | Integrated hourly Demands in megawatts for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 | 7583 | 2. | 7585 | MOD-031-2 R1.3.2. | Monthly and annual integrated peak hour Demands in megawatts for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 | 7583 | 3. | 7587 | MOD-031-2 R1.3.3. | Monthly and annual Net Energy for Load in gigawatthours for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 | 7583 | 4. | 7588 | MOD-031-2 R1.3.4. | Monthly and annual peak hour controllable and dispatchable Demand Side Management under the control or supervision of the System Operator in megawatts for the prior calendar year. Three values shall be reported for each hour: 1) the committed megawatts (the amount under control or supervision), 2) the dispatched megawatts (the amount, if any, activated for use by the System Operator), and 3) the realized megawatts (the amount of actual demand reduction). |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 | 7585 | 1. | 7586 | MOD-031-2 R1.3.2.1. | If the annual peak hour actual Demand varies due to weather-related conditions (e.g., temperature, humidity or wind speed), the Applicable Entity shall also provide the weather normalized annual peak hour actual Demand for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 13210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 | 7589 | 1. | 7590 | MOD-031-2 R1.4.1. | Monthly peak hour forecast Total Internal Demands in megawatts for the next two calendar years. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 | 7589 | 2. | 7591 | MOD-031-2 R1.4.2. | Monthly forecast Net Energy for Load in gigawatthours for the next two calendar years. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 | 7589 | 3. | 7592 | MOD-031-2 R1.4.3. | Peak hour forecast Total Internal Demands (summer and winter) in megawatts for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 | 7589 | 4. | 7593 | MOD-031-2 R1.4.4. | Annual forecast Net Energy for Load in gigawatthours for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 144000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 | 7589 | 5. | 7594 | MOD-031-2 R1.4.5. | Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 145000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 | 7595 | 1. | 7596 | MOD-031-2 R1.5.1. | The assumptions and methods used in the development of aggregated Peak Demand and Net Energy for Load forecasts. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 | 7595 | 2. | 7597 | MOD-031-2 R1.5.2. | The Demand and energy effects of controllable and dispatchable Demand Side Management under the control or supervision of the System Operator. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 | 7595 | 3. | 7598 | MOD-031-2 R1.5.3. | How Demand Side Management is addressed in the forecasts of its Peak Demand and annual Net Energy for Load. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 153000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 | 7595 | 4. | 7599 | MOD-031-2 R1.5.4. | How the controllable and dispatchable Demand Side Management forecast compares to actual controllable and dispatchable Demand Side Management for the prior calendar year and, if applicable, how the assumptions and methods for future forecasts were adjusted. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 154000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 | 7595 | 5. | 7600 | MOD-031-2 R1.5.5. | How the peak Demand forecast compares to actual Demand for the prior calendar year with due regard to any relevant weather-related variations (e.g., temperature, humidity, or wind speed) and, if applicable, how the assumptions and methods for future forecasts were adjusted. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 155000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 |  | 1. | 7581 | MOD-031-2 R1.1. | A list of Transmission Planners, Balancing Authorities, Load Serving Entities, and Distribution Providers that are required to provide the data (“Applicable Entities”). |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-02-18 |  | 2021-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 |  | 2. | 7582 | MOD-031-2 R1.2. | A timetable for providing the data. (A minimum of 30 calendar days must be allowed for responding to the request). |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-02-18 |  | 2021-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 |  | 3. | 7583 | MOD-031-2 R1.3. | A request to provide any or all of the following actual data, as necessary: |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-02-18 |  | 2021-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 |  | 4. | 7589 | MOD-031-2 R1.4. | A request to provide any or all of the following forecast data, as necessary: |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-02-18 |  | 2021-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7602 |  | 5. | 7595 | MOD-031-2 R1.5. | A request to provide any or all of the following summary explanations, as necessary,: |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2016-02-18 |  | 2021-03-31 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
542 | 7605 |  | 1. | 7601 | MOD-031-2 R4.1. | If the Applicable Entity does not provide data requested because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. |  | BA, DP, LSE, PCPA, RP, TP | BA | DP | [5 empty] | LSE |  | PCPA |  |  |  | RP | [5 empty] | TP |  |  | 2016-02-18 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
543 | 7606 | 7610 | 1. | 7611 | BAL-002-2 R1.3.1. | 1.3.1 the Responsible Entity: • is a Balancing Authority experiencing a Reliability Coordinator declared Energy Emergency Alert Level or is a Reserve Sharing Group whose member, or members, are experiencing a Reliability Coordinator declared Energy Emergency Alert level, and • is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and • has depleted its Contingency Reserve to a level below its Most Severe Single Contingency or, |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
543 | 7606 | 7610 | 2. | 7612 | BAL-002-2 R1.3.2. | 1.3.2 the Responsible Entity experiences: • multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
543 | 7606 |  | 1. | 7608 | BAL-002-2 R1.1. | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of: • zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or • its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2017-04-03 |  | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
543 | 7606 |  | 2. | 7609 | BAL-002-2 R1.2. | document all Reportable Balancing Contingency Events using CR Form 1. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-04-03 |  | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
543 | 7606 |  | 3. | 7610 | BAL-002-2 R1.3. | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if: |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-04-03 |  | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
544 | 7616 |  | 1. | 7621 | BAL-005-1 R3.1. | that is available a minimum of 99.95% for each calendar year; and, |  | BA | BA | [20 empty] | The Balancing Authority shall have evidence such as dated documents or other evidence in hard copy or electronic format showing the frequency metering equipment used for the calculation of Reporting ACE had a minimum availability of 99.95% for each calendar year and had a minimum accuracy of 0.001 Hz to demonstrate compliance with Requirement R3. | 2017-11-27 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
544 | 7616 |  | 2. | 7622 | BAL-005-1 R3.2. | with a minimum accuracy of 0.001 Hz. |  | BA | BA | [21 empty] | 2017-11-27 |  |  |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
544 | 7620 |  | 1. | 7623 | BAL-005-1 R7.1. | a common source to provide information to both Balancing Authorities for the scan rate values used in the calculation of Reporting ACE; and, |  | BA | BA | [20 empty] | The Balancing Authority shall have dated evidence such as voice recordings or transcripts, operator logs, electronic communications, or other equivalent evidence that will be used to demonstrate a common source for the components used in the calculation of Reporting ACE with its Adjacent Balancing Authority. | 2017-11-27 |  |  |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
544 | 7620 |  | 2. | 7624 | BAL-005-1 R7.2. | a time synchronized common source to determine hourly megawatt-hour values agreed-upon to aid in the identification and mitigation of errors. |  | BA | BA | [20 empty] | The Balancing Authority shall have dated evidence such as voice recordings or transcripts, operator logs, electronic communications, or other equivalent evidence that will be used to demonstrate a common source for the components used in the calculation of Reporting ACE with its Adjacent Balancing Authority. | 2017-11-27 |  |  |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
546 | 7635 |  | 1. | RP-2021-07-01-0000008 | FAC-001-3 R1.1. | generation Facilities; |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | 2017-11-27 |  | 2023-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
546 | 7635 |  | 2. | 7626 | FAC-001-3 R1.2. | transmission Facilities; and |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | 2019-01-01 |  | 2023-12-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
546 | 7635 |  | 3. | 7628 | FAC-001-3 R1.3. | end-user Facilities |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | 2019-01-01 |  | 2023-12-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
546 | 7637 |  | 1. | 7629 | FAC-001-3 R3.1. | Procedures for coordinated studies of new or materially modified existing interconnections and their impacts on affected system(s). |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | 2019-01-01 |  | 2023-12-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
546 | 7637 |  | 2. | 7630 | FAC-001-3 R3.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new or materially modified existing interconnections. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | 2019-01-01 |  | 2023-12-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
546 | 7637 |  | 3. | 7631 | FAC-001-3 R3.3. | Procedures for confirming with those responsible for the reliability of affected systems of new or materially modified transmission Facilities are within a Balancing Authority Area’s metered boundaries. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | 2019-01-01 |  | 2023-12-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
546 | 7638 |  | 1. | 7632 | FAC-001-3 R4.1. | Procedures for coordinated studies of new interconnections and their impacts on affected system(s). |  | GO |  |  |  |  | GO | [16 empty] | Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | 2019-01-01 |  | 2023-12-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
546 | 7638 |  | 2. | 7633 | FAC-001-3 R4.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. |  | GO |  |  |  |  | GO | [16 empty] | Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | 2019-01-01 |  | 2023-12-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
546 | 7638 |  | 3. | 7634 | FAC-001-3 R4.3. | Procedures for confirming with those responsible for the reliability of affected systems of new or materially modified generation Facilities are within a Balancing Authority Area’s metered boundaries. |  | GO |  |  |  |  | GO | [16 empty] | Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | 2019-01-01 |  | 2023-12-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7658 |  | 1. | 7639 | FAC-003-4 R1.1. | An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, (Footnote: If a later confirmation of a Fault by the applicable Transmission Owner or applicable Generator Owner shows that a vegetation encroachment within the MVCD has occurred from vegetation within the ROW, this shall be considered the equivalent of a Real-time observation.) |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R1) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7658 |  | 2. | 7640 | FAC-003-4 R1.2. | An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, (Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24-hour period.) |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R1) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7658 |  | 3. | 7641 | FAC-003-4 R1.3. | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24-hour period. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R1) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7658 |  | 4. | 7642 | FAC-003-4 R1.4. | An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24-hour period. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R1) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7659 |  | 1. | 7643 | FAC-003-4 R2.1. | An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage, Footnote: If a later confirmation of a Fault by the applicable Transmission Owner or applicable Generator Owner shows that a vegetation encroachment within the MVCD has occurred from vegetation within the ROW, this shall be considered the equivalent of a Real-time observation. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R2. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R2) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7659 |  | 2. | 7644 | FAC-003-4 R2.2. | An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24-hour period. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R2. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R2) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7659 |  | 3. | 7645 | FAC-003-4 R2.3. | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24-hour period. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R2. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R2) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7659 |  | 4. | 7646 | FAC-003-4 R2.4. | An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage. Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24-hour period. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R2. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real-time observations of any MVCD encroachments. (R2) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7660 |  | 1. | 7647 | FAC-003-4 R3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The maintenance strategies or procedures or processes or specifications provided demonstrate that the applicable Transmission Owner and applicable Generator Owner can prevent encroachment into the MVCD considering the factors identified in the requirement. (R3) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7660 |  | 2. | 7648 | FAC-003-4 R3.2. | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The maintenance strategies or procedures or processes or specifications provided demonstrate that the applicable Transmission Owner and applicable Generator Owner can prevent encroachment into the MVCD considering the factors identified in the requirement. (R3) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7664 |  | 1. | RP-2021-07-01-0000009 | FAC-003-4 R7.1. | Change in expected growth rate/environmental factors |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2016-10-01 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7664 |  | 2. | 7649 | FAC-003-4 R7.2. | Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner Footnote: Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner include but are not limited to natural disasters such as earthquakes, fires, tornados, hurricanes, landslides, ice storms, floods, or major storms as defined either by the TO or GO or an applicable regulatory body. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7664 |  | 3. | 7650 | FAC-003-4 R7.3. | Rescheduling work between growing seasons |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7664 |  | 4. | 7651 | FAC-003-4 R7.4. | Crew or contractor availability/Mutual assistance agreements |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7664 |  | 5. | 7652 | FAC-003-4 R7.5. | Identified unanticipated high priority work |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 750000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7664 |  | 6. | 7653 | FAC-003-4 R7.6. | Weather conditions/Accessibility |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 760000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7664 |  | 7. | 7655 | FAC-003-4 R7.7. | Permitting delays |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 770000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7664 |  | 8. | 7656 | FAC-003-4 R7.8. | Land ownership changes/Change in land use by the landowner |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 780000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
547 | 7664 |  | 9. | 7657 | FAC-003-4 R7.9. | Emerging technologies |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2016-04-26 |  | 2024-03-31 |  | 4.1. Functional Entities: 4.1.1. Applicable Transmission Owners 4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2. 4.1.2. Applicable Generator Owners 4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.2.1. Each overhead transmission line operated at 200kV or higher. 4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator. 4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. 4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities: 4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are: 4.3.1.1. Operated at 200kV or higher; or 4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or 4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. | 790000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
548 | 7724 |  | 1. | 7725 | TOP-010-1 R1.1. | Criteria for evaluating the quality of Real-time data; |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
548 | 7724 |  | 2. | 7726 | TOP-010-1 R1.2. | Provisions to indicate the quality of Real-time data to the System Operator; and |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
548 | 7724 |  | 3. | 7727 | TOP-010-1 R1.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
548 | 7728 |  | 1. | 7729 | TOP-010-1 R2.1. | Criteria for evaluating the quality of Real-time data; |  | BA | BA | [21 empty] | 2016-09-22 |  | 2018-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
548 | 7728 |  | 2. | 7730 | TOP-010-1 R2.2. | Provisions to indicate the quality of Real-time data to the System Operator; and |  | BA | BA | [21 empty] | 2016-09-22 |  | 2018-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
548 | 7728 |  | 3. | 7731 | TOP-010-1 R2.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. |  | BA | BA | [21 empty] | 2016-09-22 |  | 2018-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
548 | 7732 |  | 1. | 7733 | TOP-010-1 R3.1. | Criteria for evaluating the quality of analysis used in its Real-time Assessments; |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
548 | 7732 |  | 2. | 7734 | TOP-010-1 R3.2. | Provisions to indicate the quality of analysis used in its Real-time Assessments; and |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
548 | 7732 |  | 3. | 7735 | TOP-010-1 R3.3. | Actions to address analysis quality issues affecting its Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
549 | 7737 |  | 1. | 7739 | IRO-018-1 R1.1. | Criteria for evaluating the quality of Real-time data; |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
549 | 7737 |  | 2. | 7740 | IRO-018-1 R1.2. | Provisions to indicate the quality of Real-time data to the System Operator; and |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
549 | 7737 |  | 3. | 7741 | IRO-018-1 R1.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
549 | 7738 |  | 1. | 7742 | IRO-018-1 R2.1. | Criteria for evaluating the quality of analysis used in its Real-time Assessments; |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
549 | 7738 |  | 2. | 7743 | IRO-018-1 R2.2. | Provisions to indicate the quality of analysis used in its Real-time Assessments; and |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
549 | 7738 |  | 3. | 7744 | IRO-018-1 R2.3. | Actions to address analysis quality issues affecting its Real-time Assessments. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R2. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-09-22 |  | 2018-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 787 |  | 1. | 788 | FAC-011-2 R1.1. | Be applicable for developing SOLs used in the operations horizon. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 787 |  | 2. | 789 | FAC-011-2 R1.2. | State that SOLs shall not exceed associated Facility Ratings. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 787 |  | 3. | 790 | FAC-011-2 R1.3. | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 791 | 793 | 1. | 794 | FAC-011-2 R2.2.1. | Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 791 | 793 | 2. | 795 | FAC-011-2 R2.2.2. | Loss of any generator, line, transformer, or shunt device without a Fault. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 791 | 793 | 3. | 796 | FAC-011-2 R2.2.3. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 791 | 797 | 1. | 798 | FAC-011-2 R2.3.1. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 231000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 791 | 797 | 2. | 799 | FAC-011-2 R2.3.2. | Interruption of other network customers, (a) only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or (b) if the real-time operating conditions are more adverse than anticipated in the corresponding studies |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 232000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 791 | 797 | 3. | 800 | FAC-011-2 R2.3.3. | System reconfiguration through manual or automatic control or protection actions. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 233000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 791 |  | 1. | 792 | FAC-011-2 R2.1. | In the pre-contingency state, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect current or expected system conditions and shall reflect changes to system topology such as Facility outages. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 791 |  | 2. | 793 | FAC-011-2 R2.2. | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 791 |  | 3. | 797 | FAC-011-2 R2.3. | In determining the system’s response to a single Contingency, the following shall be acceptable: |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 791 |  | 4. | RP-2021-06-22-0000002 | FAC-011-2 R2.4. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 802 | 805 | 1. | 806 | FAC-011-2 R3.3.1. | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 331000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 802 |  | 1. | 803 | FAC-011-2 R3.1. | Study model (must include at least the entire Reliability Coordinator Area as well as the critical modeling details from other Reliability Coordinator Areas that would impact the Facility or Facilities under study.) |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 802 |  | 2. | 804 | FAC-011-2 R3.2. | Selection of applicable Contingencies |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 802 |  | 3. | 805 | FAC-011-2 R3.3. | A process for determining which of the stability limits associated with the list of multiple contingencies (provided by the Planning Authority in accordance with FAC-014 Requirement 6) are applicable for use in the operating horizon given the actual or expected system conditions. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 802 |  | 4. | 807 | FAC-011-2 R3.4. | Level of detail of system models used to determine SOLs. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 802 |  | 5. | 808 | FAC-011-2 R3.5. | Allowed uses of Special Protection Systems or Remedial Action Plans. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 802 |  | 6. | 809 | FAC-011-2 R3.6. | Anticipated transmission system configuration, generation dispatch and Load level |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 360000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 802 |  | 7. | 810 | FAC-011-2 R3.7. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 370000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 811 |  | 1. | 812 | FAC-011-2 R4.1. | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 811 |  | 2. | 813 | FAC-011-2 R4.2. | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
55 | 811 |  | 3. | 814 | FAC-011-2 R4.3. | Each Transmission Operator that operates in the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7749 | 7750 | 1. | 7751 | PRC-012-2 R4.1.1. | The RAS mitigates the System condition(s) or Contingency(ies) for which it was designed. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7749 | 7750 | 2. | 7752 | PRC-012-2 R4.1.2. | The RAS avoids adverse interactions with other RAS, and protection and control systems. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7749 | 7750 | 3. | 7753 | PRC-012-2 R4.1.3. | For limited impact RAS, the inadvertent operation of the RAS or the failure of the RAS to operate does not cause or contribute to BES Cascading, uncontrolled separation, angular instability, voltage instability, voltage collapse, or unacceptably damped oscillations. |  | PCPA | [9 empty] | PCPA | [11 empty] | Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7749 | 7750 | 4. | 7754 | PRC-012-2 R4.1.4. | Except for limited impact RAS, the possible inadvertent operation of the RAS, resulting from any single RAS component malfunction satisfies all of the following: |  | PCPA | [9 empty] | PCPA | [11 empty] | Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 414000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7749 | 7750 | 5. | 7760 | PRC-012-2 R4.1.5. | Except for limited impact RAS, a single component failure in the RAS, when the RAS is intended to operate does not prevent the BES from meeting the same performance requirements (defined in Reliability Standard TPL-001-4 or its successor) as those required for the events and conditions for which the RAS is designed. |  | PCPA | [9 empty] | PCPA | [11 empty] | Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 415000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7749 | 7754 | 1. | 7755 | PRC-012-2 R4.1.4.1. | The BES shall remain stable. |  | PCPA | [9 empty] | PCPA | [11 empty] | Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 41410000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7749 | 7754 | 2. | 7756 | PRC-012-2 R4.1.4.2. | Cascading shall not occur. |  | PCPA | [9 empty] | PCPA | [11 empty] | Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 41420000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7749 | 7754 | 3. | 7757 | PRC-012-2 R4.1.4.3. | Applicable Facility Ratings shall not be exceeded. |  | PCPA | [9 empty] | PCPA | [11 empty] | Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 41430000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7749 | 7754 | 4. | 7758 | PRC-012-2 R4.1.4.4. | BES voltages shall be within post-Contingency voltage limits and post-Contingency voltage deviation limits as established by the Transmission Planner and the Planning Coordinator. |  | PCPA | [9 empty] | PCPA | [11 empty] | Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 414400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7749 | 7754 | 5. | 7759 | PRC-012-2 R4.1.4.5. | Transient voltage responses shall be within acceptable limits as established by the Transmission Planner and the Planning Coordinator. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 414500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7749 |  | 1. | 7750 | PRC-012-2 R4.1. | Perform an evaluation of each RAS within its planning area to determine whether: |  | PCPA | [9 empty] | PCPA | [11 empty] | Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | 2026-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7749 |  | 2. | 7761 | PRC-012-2 R4.2. | Provide the results of the RAS evaluation including any identified deficiencies to each reviewing Reliability Coordinator and RAS-entity, and each impacted Transmission Planner and Planning Coordinator. |  | PCPA | [9 empty] | PCPA | [11 empty] | Acceptable evidence may include, but is not limited to, dated reports or other documentation of the analyses comprising the evaluation(s) of each RAS and dated communications with the RAS-entity(ies), Transmission Planner(s), Planning Coordinator(s), and the reviewing Reliability Coordinator(s) in accordance with Requirement R4. | 2026-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7762 | 7763 | 1. | 7764 | PRC-012-2 R5.1.1. | The System events and/or conditions appropriately triggered the RAS. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7762 | 7763 | 2. | 7765 | PRC-012-2 R5.1.2. | The RAS responded as designed. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Acceptable evidence may include, but is not limited to, dated documentation detailing the results of the RAS operational performance analysis and dated communications with participating RAS-entities and the reviewing Reliability Coordinator(s) in accordance with Requirement R5. | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7762 | 7763 | 3. | 7766 | PRC-012-2 R5.1.3. | The RAS was effective in mitigating BES performance issues it was designed to address. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Acceptable evidence may include, but is not limited to, dated documentation detailing the results of the RAS operational performance analysis and dated communications with participating RAS-entities and the reviewing Reliability Coordinator(s) in accordance with Requirement R5. | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7762 | 7763 | 4. | 7767 | PRC-012-2 R5.1.4. | The RAS operation resulted in any unintended or adverse BES response. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  |  | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 514000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7762 |  | 1. | 7763 | PRC-012-2 R5.1. | Participate in analyzing the RAS operational performance to determine whether: |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Acceptable evidence may include, but is not limited to, dated documentation detailing the results of the RAS operational performance analysis and dated communications with participating RAS-entities and the reviewing Reliability Coordinator(s) in accordance with Requirement R5. | 2017-11-27 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7762 |  | 2. | 7768 | PRC-012-2 R5.2. | Provide the results of RAS operational performance analysis that identified any deficiencies to its reviewing Reliability Coordinator(s). |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Acceptable evidence may include, but is not limited to, dated documentation detailing the results of the RAS operational performance analysis and dated communications with participating RAS-entities and the reviewing Reliability Coordinator(s) in accordance with Requirement R5. | 2017-11-27 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7770 |  | 1. | 7771 | PRC-012-2 R7.1. | Implement the CAP. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Acceptable evidence may include, but is not limited to, dated documentation such as CAPs, project or work management program records, settings sheets, work orders, maintenance records, and communication with the reviewing Reliability Coordinator(s) that documents the implementation, updating, or completion of a CAP in accordance with Requirement R7. | 2017-11-27 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7770 |  | 2. | RP-2021-07-09-0000042 | PRC-012-2 R7.2. | Update the CAP if actions or timetables change. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Acceptable evidence may include, but is not limited to, dated documentation such as CAPs, project or work management program records, settings sheets, work orders, maintenance records, and communication with the reviewing Reliability Coordinator(s) that documents the implementation, updating, or completion of a CAP in accordance with Requirement R7. | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
550 | 7770 |  | 3. | 7773 | PRC-012-2 R7.3. | Notify each reviewing Reliability Coordinator if CAP actions or timetables change and when the CAP is completed. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Acceptable evidence may include, but is not limited to, dated documentation such as CAPs, project or work management program records, settings sheets, work orders, maintenance records, and communication with the reviewing Reliability Coordinator(s) that documents the implementation, updating, or completion of a CAP in accordance with Requirement R7. | 2017-11-27 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7785 |  | 1. | 7786 | COM-001-3 R1.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have and provide upon request evidence that it has Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R1.) | 2016-10-28 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7785 |  | 2. | 7787 | COM-001-3 R1.2. | Each adjacent Reliability Coordinator within the same Interconnection. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have and provide upon request evidence that it has Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R1.) | 2016-10-28 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7788 |  | 1. | 7789 | COM-001-3 R2.1. | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R2.) | 2016-10-28 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7788 |  | 2. | 7790 | COM-001-3 R2.2. | Each adjacent Reliability Coordinator within the same Interconnection. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with all Transmission Operators and Balancing Authorities within its Reliability Coordinator Area and with each adjacent Reliability Coordinator within the same Interconnection, which could include, but is not limited to: • physical assets, or • dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R2.) | 2016-10-28 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7791 |  | 1. | 7792 | COM-001-3 R3.1. | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | 2016-10-28 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7791 |  | 2. | 7793 | COM-001-3 R3.2. | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | 2016-10-28 |  |  |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7791 |  | 3. | 7794 | COM-001-3 R3.3. | Each Distribution Provider within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | 2016-10-28 |  |  |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7791 |  | 4. | 7795 | COM-001-3 R3.4. | Each Generator Operator within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | 2016-10-28 |  |  |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7791 |  | 5. | 7796 | COM-001-3 R3.5. | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | 2016-10-28 |  |  |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7791 |  | 6. | 7797 | COM-001-3 R3.6. | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority, Distribution Provider, and Generator Operator within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously or synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communication. (R3.) | 2016-10-28 |  |  |  |  | 360000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7798 |  | 1. | 7799 | COM-001-3 R4.1. | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | 2016-10-28 |  |  |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7798 |  | 2. | 7800 | COM-001-3 R4.2. | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | 2016-10-28 |  |  |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7798 |  | 3. | 7801 | COM-001-3 R4.3. | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | 2016-10-28 |  |  |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7798 |  | 4. | 7802 | COM-001-3 R4.4. | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Balancing Authority within its Transmission Operator Area, and each adjacent Transmission Operator asynchronously and synchronously connected, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R4.) | 2016-10-28 |  |  |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7803 |  | 1. | 7804 | COM-001-3 R5.1. | Its Reliability Coordinator. |  | BA | BA | [20 empty] | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | 2016-10-28 |  |  |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7803 |  | 2. | 7805 | COM-001-3 R5.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [20 empty] | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | 2016-10-28 |  |  |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7803 |  | 3. | 7806 | COM-001-3 R5.3. | Each Distribution Provider within its Balancing Authority Area. |  | BA | BA | [20 empty] | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | 2016-10-28 |  |  |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7803 |  | 4. | 7807 | COM-001-3 R5.4. | Each Generator Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [20 empty] | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | 2016-10-28 |  |  |  |  | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7803 |  | 5. | 7808 | COM-001-3 R5.5. | Each Adjacent Balancing Authority. |  | BA | BA | [20 empty] | Each Balancing Authority shall have and provide upon request evidence that it has Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator and Generator Operator that operates Facilities within its Balancing Authority Area, each Distribution Provider within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R5.) | 2016-10-28 |  |  |  |  | 550000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7809 |  | 1. | 7810 | COM-001-3 R6.1. | Its Reliability Coordinator. |  | BA | BA | [20 empty] | Each Balancing Authority shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator that operates Facilities within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R6.) | 2016-10-28 |  |  |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7809 |  | 2. | 7811 | COM-001-3 R6.2. | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [20 empty] | Each Balancing Authority shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator that operates Facilities within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R6.) | 2016-10-28 |  |  |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7809 |  | 3. | 7812 | COM-001-3 R6.3. | Each Adjacent Balancing Authority. |  | BA | BA | [20 empty] | Each Balancing Authority shall have and provide upon request evidence that it designated an Alternative Interpersonal Communication capability with its Reliability Coordinator, each Transmission Operator that operates Facilities within its Balancing Authority Area, and each adjacent Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R6.) | 2016-10-28 |  |  |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7813 |  | 1. | 7814 | COM-001-3 R7.1. | Its Balancing Authority. |  | DP |  | DP | [19 empty] | Each Distribution Provider shall have and provide upon request evidence that it has Interpersonal Communication capability with its Transmission Operator and its Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R7.) | 2016-10-28 |  |  |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7813 |  | 2. | 7815 | COM-001-3 R7.2. | Its Transmission Operator. |  | DP |  | DP | [19 empty] | Each Distribution Provider shall have and provide upon request evidence that it has Interpersonal Communication capability with its Transmission Operator and its Balancing Authority, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R7.) | 2016-10-28 |  |  |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7816 |  | 1. | 7817 | COM-001-3 R8.1. | Its Balancing Authority. |  | GOP | [5 empty] | GOP | [15 empty] | Each Generator Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Balancing Authority and its Transmission Operator, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R8.) | 2016-10-28 |  |  |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
551 | 7816 |  | 2. | 7818 | COM-001-3 R8.2. | Its Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Each Generator Operator shall have and provide upon request evidence that it has Interpersonal Communication capability with its Balancing Authority and its Transmission Operator, which could include, but is not limited to: • Physical assets, or • Dated evidence, such as, equipment specifications and installation documentation, test records, operator logs, voice recordings, transcripts of voice recordings, or electronic communications. (R8.) | 2016-10-28 |  |  |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
554 | 7843 |  | 1. | 7844 | CIP-002-5.1a R1.1. | Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
554 | 7843 |  | 2. | 7845 | CIP-002-5.1a R1.2. | Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
554 | 7843 |  | 3. | 7846 | CIP-002-5.1a R1.3. | Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Acceptable evidence includes, but is not limited to, dated electronic or physical lists required by Requirement R1, and Parts 1.1 and 1.2. | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
554 | 7847 |  | 1. | 7848 | CIP-002-5.1a R2.1. | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
554 | 7847 |  | 2. | 7849 | CIP-002-5.1a R2.2. | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Acceptable evidence includes, but is not limited to, electronic or physical dated records to demonstrate that the Responsible Entity has reviewed and updated, where necessary, the identifications required in Requirement R1 and its parts, and has had its CIP Senior Manager or delegate approve the identifications required in Requirement R1 and its parts at least once every 15 calendar months, even if it has none identified in Requirement R1 and its parts, as required by Requirement R2. | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
555 | 7850 |  | 1. | 7852 | IRO-018-1(i) R1.1. | Criteria for evaluating the quality of Real-time data; |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator or supporting logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-12-14 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
555 | 7850 |  | 2. | 7853 | IRO-018-1(i) R1.2. | Provisions to indicate the quality of Real-time data to the System Operator; and |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator or supporting logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-12-14 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
555 | 7850 |  | 3. | 7854 | IRO-018-1(i) R1.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator or supporting logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-12-14 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
555 | 7855 |  | 1. | 7857 | IRO-018-1(i) R2.1. | Criteria for evaluating the quality of analysis used in its Real-time Assessments; |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R2. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-12-14 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
555 | 7855 |  | 2. | 7858 | IRO-018-1(i) R2.2. | Provisions to indicate the quality of analysis used in its Real-time Assessments; and |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R2. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-12-14 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
555 | 7855 |  | 3. | 7859 | IRO-018-1(i) R2.3. | Actions to address analysis quality issues affecting its Real-time Assessments. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R2. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Reliability Coordinator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-12-14 |  |  |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
556 | 7860 |  | 1. | 7861 | TOP-010-1(i) R1.1. | Criteria for evaluating the quality of Real-time data; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-12-14 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
556 | 7860 |  | 2. | 7862 | TOP-010-1(i) R1.2. | Provisions to indicate the quality of Real-time data to the System Operator; and |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-12-14 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
556 | 7860 |  | 3. | 7863 | TOP-010-1(i) R1.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R1; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-12-14 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
556 | 7864 |  | 1. | 7865 | TOP-010-1(i) R2.1. | Criteria for evaluating the quality of Real-time data; |  | BA | BA | [20 empty] | Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-12-14 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
556 | 7864 |  | 2. | 7866 | TOP-010-1(i) R2.2. | Provisions to indicate the quality of Real-time data to the System Operator; and |  | BA | BA | [20 empty] | Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-12-14 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
556 | 7864 |  | 3. | 7867 | TOP-010-1(i) R2.3. | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. |  | BA | BA | [20 empty] | Each Balancing Authority shall have evidence that it implemented its Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R2; and 2) evidence the Balancing Authority implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-12-14 |  |  |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
556 | 7868 |  | 1. | 7870 | TOP-010-1(i) R3.1. | Criteria for evaluating the quality of analysis used in its Real-time Assessments; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-12-14 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
556 | 7868 |  | 2. | 7871 | TOP-010-1(i) R3.2. | Provisions to indicate the quality of analysis used in its Real-time Assessments; and |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-12-14 |  |  |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
556 | 7868 |  | 3. | 7872 | TOP-010-1(i) R3.3. | Actions to address analysis quality issues affecting its Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have evidence it implemented its Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments as specified in Requirement R3. This evidence could include, but is not limited to: 1) an Operating Process or Operating Procedure in electronic or hard copy format meeting all provisions of Requirement R3; and 2) evidence the Transmission Operator implemented the Operating Process or Operating Procedure as called for in the Operating Process or Operating Procedure, such as dated operator logs, dated checklists, voice recordings, voice transcripts, or other evidence. | 2016-12-14 |  |  |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
557 | 7874 |  | 1. | 7875 | BAL-002-WECC-2a R1.1. | The greater of either: • The amount of Contingency Reserve equal to the loss of the most severe single contingency; • The amount of Contingency Reserve equal to the sum of three percent of hourly integrated Load plus three percent of hourly integrated generation. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.1. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates its Contingency Reserve was maintained in accordance with the amounts identified in Requirement R1, Part 1.1, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Attachment A is a practical illustration showing how the generation amount may be calculated under Requirement R1. • Where Dynamic Schedules are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1 may include, but is not limited to, documentation showing a reciprocal acknowledgement as to which entity is carrying the reserves. This transfer may be all or some portion of the physical generator and is not limited to the entire physical capability of the generator. • Where Pseudo-Ties are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1, may include, but is not limited to, documentation accounting for the transfers included in the Pseudo-Ties. | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 110000000 | WECC-US | [5 empty] | WECC-US
557 | 7874 |  | 2. | 7876 | BAL-002-WECC-2a R1.2. | Comprised of any combination of the reserve types specified below: • Operating Reserve – Spinning • Operating Reserve - Supplemental • Interchange Transactions designated by the Source Balancing Authority as Operating Reserve – Supplemental • Reserve held by other entities by agreement that is deliverable on Firm Transmission Service • A resource, other than generation or load, that can provide energy or reduce energy consumption • Load, including demand response resources, Demand-Side Management resources, Direct Control Load Management, Interruptible Load or Interruptible Demand, or any other Load made available for curtailment by the Balancing Authority or the Reserve Sharing Group via contract or agreement. • All other load, not identified above, once the Reliability Coordinator has declared an energy emergency alert signifying that firm load interruption is imminent or in progress. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.2. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.2. Evidence may include, but is not limited to, documentation that reserves were comprised of the types listed in Requirement R1, Part 1.2 for purposes of meeting the Contingency Reserve obligation of Requirement R1. Additionally, for purposes of the last bullet of Requirement R1, Part 1.2, evidence of compliance may include, but is not limited to, documentation that the reliability coordinator had issued an energy emergency alert, indicating that firm Load interruption was imminent or was in progress. | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 120000000 | WECC-US | [5 empty] | WECC-US
557 | 7874 |  | 3. | 7877 | BAL-002-WECC-2a R1.3. | Based on real-time hourly load and generating energy values averaged over each Clock Hour (excluding Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464). |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.3. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.3. Evidence of compliance with Requirement R1, Part 1.3 may include, but is not limited to, documentation that Contingency Reserve amounts are based upon load and generating data averaged over each Clock Hour and excludes Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464. | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 130000000 | WECC-US | [5 empty] | WECC-US
557 | 7874 |  | 4. | 7878 | BAL-002-WECC-2a R1.4. | An amount of capacity from a resource that is deployable within ten minutes. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.4. Evidence of compliance with Requirement R1, Part 1.4 may include, but is not limited to, documentation that the reserves maintained to comply with Requirement R1, Part 1.4 are fully deployable within ten minutes. | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 140000000 | WECC-US | [5 empty] | WECC-US
557 | 7879 |  | 1. | 7880 | BAL-002-WECC-2a R2.1. | Reserve that is immediately and automatically responsive to frequency deviations through the action of a governor or other control system; |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 210000000 | WECC-US | [5 empty] | WECC-US
557 | 7879 |  | 2. | 7881 | BAL-002-WECC-2a R2.2. | Reserve that is capable of fully responding within ten minutes. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity. 4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 220000000 | WECC-US | [5 empty] | WECC-US
559 | 7886 | 7888 | 1. | 7889 | EOP-008-2 R1.2.1. | Tools and applications to ensure that System Operators have situational awareness of the BES. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | 2019-04-01 |  |  |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7886 | 7888 | 2. | 7890 | EOP-008-2 R1.2.2. | Data exchange capabilities. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | 2019-04-01 |  |  |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7886 | 7888 | 3. | 7891 | EOP-008-2 R1.2.3. | Interpersonal Communications. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | 2019-04-01 |  |  |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7886 | 7888 | 4. | 7892 | EOP-008-2 R1.2.4. | Power source(s). |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | 2019-04-01 |  |  |  |  | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7886 | 7888 | 5. | 7893 | EOP-008-2 R1.2.5. | Physical and cyber security. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | 2019-04-01 |  |  |  |  | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7886 | 7897 | 1. | 7898 | EOP-008-2 R1.6.1. | A list of all entities to notify when there is a change in operating locations. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | 2019-04-01 |  |  |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7886 | 7897 | 2. | 7899 | EOP-008-2 R1.6.2. | Actions to manage the risk to the BES during the transition from primary to backup functionality, as well as during outages of the primary or backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | 2019-04-01 |  |  |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7886 | 7897 | 3. | 7900 | EOP-008-2 R1.6.3. | Identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | 2019-04-01 |  |  |  |  | 163000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7886 |  | 1. | 7887 | EOP-008-2 R1.1. | The location and method of implementation for providing backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | 2018-03-26 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7886 |  | 2. | 7888 | EOP-008-2 R1.2. | A summary description of the elements required to support the backup functionality. These elements shall include: |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | 2018-03-26 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7886 |  | 3. | 7894 | EOP-008-2 R1.3. | An Operating Process for keeping the backup functionality consistent with the primary control center. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | 2018-03-26 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7886 |  | 4. | 7895 | EOP-008-2 R1.4. | Operating Procedures, including decision authority, for use in determining when to implement the Operating Plan for backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | 2018-03-26 |  |  |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7886 |  | 5. | 7896 | EOP-008-2 R1.5. | A transition period between the loss of primary control center functionality and the time to fully implement the backup functionality that is less than or equal to two hours. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | 2018-03-26 |  |  |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7886 |  | 6. | 7897 | EOP-008-2 R1.6. | An Operating Process describing the actions to be taken during the transition period between the loss of primary control center functionality and the time to fully implement backup functionality elements identified in Requirement R1, Part 1.2. The Operating Process shall include: |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a dated, current, and in effect Operating Plan for backup functionality in accordance with Requirement R1, in electronic or hardcopy format. | 2018-03-26 |  |  |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7904 |  | 1. | 7907 | EOP-008-2 R5.1. | An update and approval of the Operating Plan for backup functionality shall take place within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have evidence that its dated, current, and in effect Operating Plan for backup functionality, in electronic or hardcopy format, has been reviewed and approved annually and that it has been updated within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1 in accordance with Requirement R5. | 2018-03-26 |  |  |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7906 |  | 1 . | RP-2021-07-01-0000004 | EOP-008-2 R7.1 . | The transition time between the simulated loss of primary control center functionality and the time to fully implement the backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall provide evidence such as dated records, that it has completed and documented its annual test of its Operating Plan for backup functionality, in accordance with Requirement R7. | 2019-04-01 |  |  |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
559 | 7906 |  | 2. | 7909 | EOP-008-2 R7.2. | The backup functionality for a minimum of two continuous hours. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall provide evidence such as dated records, that it has completed and documented its annual test of its Operating Plan for backup functionality, in accordance with Requirement R7. | 2018-03-26 |  |  |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
56 | 816 | 819 | 1. | 820 | FAC-012-1 R1.3.1. | Transmission system topology |  | PCPA, RC | [9 empty] | PCPA |  | RC | [12 empty] | 2013-03-31 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
56 | 816 | 819 | 2. | 821 | FAC-012-1 R1.3.2. | System demand |  | PCPA, RC | [9 empty] | PCPA |  | RC | [12 empty] | 2013-03-31 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
56 | 816 | 819 | 3. | 822 | FAC-012-1 R1.3.3. | Generation dispatch |  | PCPA, RC | [9 empty] | PCPA |  | RC | [12 empty] | 2013-03-31 |  |  | 133000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
56 | 816 | 819 | 4. | 823 | FAC-012-1 R1.3.4. | Current and projected transmission uses |  | PCPA, RC | [9 empty] | PCPA |  | RC | [12 empty] | 2013-03-31 |  |  | 134000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
56 | 816 |  | 1. | 817 | FAC-012-1 R1.1. | A statement that Transfer Capabilities shall respect all applicable System Operating Limits (SOLs). |  | PCPA, RC | [9 empty] | PCPA |  | RC | [12 empty] | 2013-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
56 | 816 |  | 2. | 818 | FAC-012-1 R1.2. | A definition stating whether the methodology is applicable to the planning horizon or the operating horizon. |  | PCPA, RC | [9 empty] | PCPA |  | RC | [12 empty] | 2013-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
56 | 816 |  | 3. | 819 | FAC-012-1 R1.3. | A description of how each of the following is addressed, including any reliability margins applied to reflect uncertainty with projected BES conditions: |  | PCPA, RC | [9 empty] | PCPA |  | RC | [12 empty] | 2013-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
56 | 824 |  | 1. | 825 | FAC-012-1 R2.1. | Each Adjacent Reliability Coordinator and each Reliability Coordinator that indicated a reliability-related need for the methodology. |  | RC | [11 empty] | RC | [12 empty] | 2013-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
56 | 824 |  | 2. | 826 | FAC-012-1 R2.2. | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  | RC | [11 empty] | RC | [12 empty] | 2013-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
56 | 824 |  | 3. | 827 | FAC-012-1 R2.3. | Each Transmission Operator that operates in the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [12 empty] | 2013-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
56 | 828 |  | 1. | 829 | FAC-012-1 R3.1. | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PCPA | [14 empty] | 2013-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
56 | 828 |  | 2. | 830 | FAC-012-1 R3.2. | Each Adjacent Planning Authority and each Planning Authority that indicated a reliability-related need for the methodology. |  | PCPA | [9 empty] | PCPA | [14 empty] | 2013-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
56 | 828 |  | 3. | 831 | FAC-012-1 R3.3. | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PCPA | [14 empty] | 2013-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
560 | 7911 |  | 1. | 7912 | EOP-006-3 R1.1. | A description of the high-level strategy to be employed during restoration events for restoring the Interconnection, including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have available a dated copy of its restoration plan and will have evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its restoration plan was implemented in accordance with Requirement R1. | 2018-03-26 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
560 | 7911 |  | 2. | 7913 | EOP-006-3 R1.2. | Criteria and conditions for re-establishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have available a dated copy of its restoration plan and will have evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its restoration plan was implemented in accordance with Requirement R1. | 2018-03-26 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
560 | 7911 |  | 3. | 7914 | EOP-006-3 R1.3. | Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have available a dated copy of its restoration plan and will have evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its restoration plan was implemented in accordance with Requirement R1. | 2018-03-26 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
560 | 7911 |  | 4. | 7915 | EOP-006-3 R1.4. | Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have available a dated copy of its restoration plan and will have evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its restoration plan was implemented in accordance with Requirement R1. | 2018-03-26 |  |  |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
560 | 7911 |  | 5. | 7916 | EOP-006-3 R1.5. | Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have available a dated copy of its restoration plan and will have evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its restoration plan was implemented in accordance with Requirement R1. | 2018-03-26 |  |  |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
560 | 7911 |  | 6. | 7917 | EOP-006-3 R1.6. | Criteria for transferring operations and authority back to the Balancing Authority. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have available a dated copy of its restoration plan and will have evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its restoration plan was implemented in accordance with Requirement R1. | 2019-04-01 |  |  |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
560 | 7921 |  | 1. | 7922 | EOP-006-3 R4.1. | If a Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved within 30 calendar days of receipt of written notification. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall provide evidence such as dated review signature sheets or electronic receipt that it has reviewed its neighboring Reliability Coordinator’s restoration plans and resolved any conflicts within the timing requirements of Requirement R4 and Requirement R4, Part 4.1. | 2018-03-26 |  |  |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
560 | 7923 |  | 1. | 7924 | EOP-006-3 R5.1. | The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall provide notification to the Transmission Operator of approval or disapproval, with stated reasons, of the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall provide evidence such as a dated review signature sheet or electronic receipt that it has reviewed, approved or disapproved, and notified its Transmission Operators within 30 calendar days following the receipt of the restoration plan from the Transmission Operator in accordance with Requirement R5. | 2018-03-26 |  |  |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
560 | 7926 |  | 1. | 7927 | EOP-006-3 R7.1. | The coordination role of the Reliability Coordinator; and |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have an electronic copy or hard copy of its training records available showing that it has provided training in accordance with Requirement R7. | 2018-03-26 |  |  |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
560 | 7926 |  | 2. | 7928 | EOP-006-3 R7.2. | Re-establishing the Interconnection. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have an electronic copy or hard copy of its training records available showing that it has provided training in accordance with Requirement R7. | 2018-03-26 |  |  |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
560 | 7929 |  | 1. | 7930 | EOP-006-3 R8.1. | Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least once every two calendar years. |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have evidence, such as dated electronic documents, that it conducted two System restoration drills, exercises, or simulations per calendar year in accordance with Requirement R8. And each Reliability Coordinator shall have evidence that the Reliability Coordinator requested each applicable Transmission Operator and Generator Operator to participate per Requirement R8 and Requirement R8, Part 8.1. | 2018-03-26 |  |  |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7931 |  | 1. | 7932 | EOP-005-3 R1.1. | Strategies for System restoration that are coordinated with its Reliability Coordinator’s high level strategy for restoring the Interconnection. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | 2018-03-26 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7931 |  | 2. | 7933 | EOP-005-3 R1.2. | A description of how all Agreements or mutually-agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | 2018-03-26 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7931 |  | 3. | 7934 | EOP-005-3 R1.3. | Procedures for restoring interconnections with other Transmission Operators under the direction of its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | 2018-03-26 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7931 |  | 4. | 7935 | EOP-005-3 R1.4. | Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | 2018-03-26 |  |  |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7931 |  | 5. | 7936 | EOP-005-3 R1.5. | Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | 2018-03-26 |  |  |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7931 |  | 6. | 7937 | EOP-005-3 R1.6. | Identification of acceptable operating voltage and frequency limits during restoration. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | 2018-03-26 |  |  |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7931 |  | 7. | 7938 | EOP-005-3 R1.7. | Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | 2018-03-26 |  |  |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7931 |  | 8. | 7939 | EOP-005-3 R1.8. | Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | 2018-03-26 |  |  |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7931 |  | 9. | 7940 | EOP-005-3 R1.9. | Operating Processes for transferring operations back to the Balancing Authority in accordance with its Reliability Coordinator’s criteria. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have a dated, documented System restoration plan developed in accordance with Requirement R1 that has been approved by its Reliability Coordinator as shown with the documented approval from its Reliability Coordinator and will have evidence, such as operator logs, voice recordings or other operating documentation, voice recordings or other communication documentation to show that its restoration plan was implemented for times when a Disturbance has occurred, in accordance with Requirement R1. | 2018-03-26 |  |  |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7943 |  | 1. | RP-2021-07-01-0000001 | EOP-005-3 R4.1. | Within 90 calendar days after identifying any unplanned permanent BES modifications. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have documentation such as dated review signature sheets, revision histories, dated electronic receipts, or registered mail receipts, that it has submitted the revised restoration plan to its Reliability Coordinator in accordance with Requirement R4. | 2019-04-01 |  |  |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7943 |  | 2. | 7945 | EOP-005-3 R4.2. | Prior to implementing a planned permanent BES modification subject to its Reliability Coordinator approval requirements per EOP-006. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have documentation such as dated review signature sheets, revision histories, dated electronic receipts, or registered mail receipts, that it has submitted the revised restoration plan to its Reliability Coordinator in accordance with Requirement R4. | 2018-03-26 |  |  |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7947 |  | 1. | 7948 | EOP-005-3 R6.1. | The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have documentation, such as power flow outputs, that it has verified that its latest restoration plan will accomplish its intended function in accordance with Requirement R6. | 2018-03-26 |  |  |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7947 |  | 2. | 7949 | EOP-005-3 R6.2. | The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have documentation, such as power flow outputs, that it has verified that its latest restoration plan will accomplish its intended function in accordance with Requirement R6. | 2018-03-26 |  |  |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7947 |  | 3. | 7950 | EOP-005-3 R6.3. | The capability of generating resources required to control voltages and frequency within acceptable operating limits. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have documentation, such as power flow outputs, that it has verified that its latest restoration plan will accomplish its intended function in accordance with Requirement R6. | 2018-03-26 |  |  |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7951 | 7953 | 1. | 7954 | EOP-005-3 R7.2.1. | The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R7. | 2019-04-01 |  |  |  |  | 721000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7951 | 7953 | 2. | 7955 | EOP-005-3 R7.2.2. | The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R7. | 2019-04-01 |  |  |  |  | 722000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7951 |  | 1. | 7952 | EOP-005-3 R7.1. | The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R7. | 2018-03-26 |  |  |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7951 |  | 2. | 7953 | EOP-005-3 R7.2. | A list of required tests including: |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R7. | 2018-03-26 |  |  |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7951 |  | 3. | 7956 | EOP-005-3 R7.3. | The minimum duration of each of the required tests. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have documented Blackstart Resource testing requirements in accordance with Requirement R7. | 2018-03-26 |  |  |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7957 |  | 1. | 7958 | EOP-005-3 R8.1. | System restoration plan including coordination with its Reliability Coordinator and Generator Operators included in the restoration plan. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R8. | 2018-03-26 |  |  |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7957 |  | 2. | 7959 | EOP-005-3 R8.2. | Restoration priorities. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R8. | 2018-03-26 |  |  |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7957 |  | 3. | 7960 | EOP-005-3 R8.3. | Building of cranking paths. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R8. | 2018-03-26 |  |  |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7957 |  | 4. | 7961 | EOP-005-3 R8.4. | Synchronizing (re-energized sections of the System). |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R8. | 2018-03-26 |  |  |  |  | 840000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7957 |  | 5 . | RP-2021-07-01-0000002 | EOP-005-3 R8.5 . | Transition of Demand and resource balance within its area to the Balancing Authority. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have an electronic or hard copy of the training program material provided for its System Operators for System restoration training in accordance with Requirement R8. | 2019-04-01 |  |  |  |  | 850000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7968 |  | 1. | 7969 | EOP-005-3 R14.1. | Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R7. |  | GOP | [5 empty] | GOP | [15 empty] | Each Generator Operator with a Blackstart Resource shall maintain dated documentation of its Blackstart Resource test results and shall have evidence such as e-mails with receipts or registered mail receipts, that it provided these records to its Reliability Coordinator and Transmission Operator when requested in accordance with Requirement R14. | 2018-03-26 |  |  |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7968 |  | 2. | 8916 | EOP-005-3 R14.2. | Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | Each Generator Operator with a Blackstart Resource shall maintain dated documentation of its Blackstart Resource test results and shall have evidence such as e-mails with receipts or registered mail receipts, that it provided these records to its Reliability Coordinator and Transmission Operator when requested in accordance with Requirement R14. | 2018-03-26 |  |  |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7970 |  | 1. | 7971 | EOP-005-3 R15.1. | System restoration plan including coordination with the Transmission Operator |  | GOP | [5 empty] | GOP | [15 empty] | Each Generator Operator with a Blackstart Resource shall have an electronic or hard copy of the training program material provided to its operating personnel responsible for the startup, energizing a bus and synchronization of its Blackstart Resource generation units and a copy of its dated training records including training dates and durations showing that it has provided training in accordance with Requirement R15. | 2018-03-26 |  |  |  |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
561 | 7970 |  | 2. | 7972 | EOP-005-3 R15.2. | The procedures documented in Requirement R12 |  | GOP | [5 empty] | GOP | [15 empty] | Each Generator Operator with a Blackstart Resource shall have an electronic or hard copy of the training program material provided to its operating personnel responsible for the startup, energizing a bus and synchronization of its Blackstart Resource generation units and a copy of its dated training records including training dates and durations showing that it has provided training in accordance with Requirement R15. | 2018-03-26 |  |  |  |  | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
562 | 7976 |  | 1. | 7977 | VAR-501-WECC-3 R3.1. | PSS shall be set to provide the measured, simulated, or calculated compensated VT/Vref frequency response of the excitation system and synchronous machine such that the phase angle will not exceed ± 30 degrees through the frequency range from 0.2 Hertz to the lesser of 1.0 Hertz or the highest frequency at which the phase of the Vt/Vref frequency response does not exceed 90 degrees. |  | GO |  |  |  |  | GO | [17 empty] | 2017-04-28 |  | 2017-09-25 |  |  | 310000000 | WECC-US | [5 empty] | WECC-US
562 | 7976 |  | 2. | 7978 | VAR-501-WECC-3 R3.2. | PSS output limits shall be set to provide at least ±5% of the synchronous machine’s nominal terminal voltage. |  | GO |  |  |  |  | GO | [17 empty] | 2017-04-28 |  | 2017-09-25 |  |  | 320000000 | WECC-US | [5 empty] | WECC-US
562 | 7976 |  | 3. | 7979 | VAR-501-WECC-3 R3.3. | PSS gain shall be set to between 1/3 and 1/2 of maximum practical gain. |  | GO |  |  |  |  | GO | [17 empty] | 2017-04-28 |  | 2017-09-25 |  |  | 330000000 | WECC-US | [5 empty] | WECC-US
562 | 7976 |  | 4. | 7980 | VAR-501-WECC-3 R3.4. | PSS washout time constant shall be no greater than 30 seconds. |  | GO |  |  |  |  | GO | [17 empty] | 2017-04-28 |  | 2017-09-25 |  |  | 340000000 | WECC-US | [5 empty] | WECC-US
562 | 7976 |  | 5. | RP-2021-06-25-0000013 | VAR-501-WECC-3 R3.5. | Units that have an excitation system or PSS that is incapable of meeting the tuning requirements of Requirement R3 are exempt from Requirement R3 until the voltage regulator is either replaced or retrofitted such that the PSS becomes capable of meeting the tuning requirements. |  | GO |  |  |  |  | GO | [17 empty] | 2017-07-01 |  | 2017-09-25 |  |  | 350000000 | WECC-US | [5 empty] | WECC-US
563 | 7984 | 7986 | 1. | 7988 | CIP-003-7 R1.1.1. | Personnel and training (CIP-004); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 | 7986 | 2. | 7989 | CIP-003-7 R1.1.2. | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 | 7986 | 3. | 7990 | CIP-003-7 R1.1.3. | Physical security of BES Cyber Systems (CIP-006); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 | 7986 | 4. | 7992 | CIP-003-7 R1.1.4. | System security management (CIP-007); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 | 7986 | 5. | 7993 | CIP-003-7 R1.1.5. | Incident reporting and response planning (CIP-008); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 | 7986 | 6. | 7994 | CIP-003-7 R1.1.6. | Recovery plans for BES Cyber Systems (CIP-009); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 116000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 | 7986 | 7. | 7995 | CIP-003-7 R1.1.7. | Configuration change management and vulnerability assessments (CIP-010); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 117000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 | 7986 | 8. | 7996 | CIP-003-7 R1.1.8. | Information protection (CIP-011); and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 118000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 | 7986 | 9. | 7997 | CIP-003-7 R1.1.9. | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 119000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 | 7987 | 1. | 7998 | CIP-003-7 R1.2.1. | Cyber security awareness; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 | 7987 | 2. | 7999 | CIP-003-7 R1.2.2. | Physical security controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 | 7987 | 3. | 8000 | CIP-003-7 R1.2.3. | Electronic access controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 | 7987 | 4. | 8001 | CIP-003-7 R1.2.4. | Cyber Security Incident response; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 | 7987 | 5. | 8002 | CIP-003-7 R1.2.5. | Transient Cyber Assets and Removable Media malicious code risk mitigation; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 | 7987 | 6. | 8003 | CIP-003-7 R1.2.6. | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 |  | 1. | 7986 | CIP-003-7 R1.1. | For its high impact and medium impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2018-06-25 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
563 | 7984 |  | 2. | 7987 | CIP-003-7 R1.2. | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2018-06-25 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
565 | 8021 |  | 1. | 8023 | TOP-001-4 R10.1. | Monitor Facilities within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
565 | 8021 |  | 2. | 8024 | TOP-001-4 R10.2. | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
565 | 8021 |  | 3. | 8025 | TOP-001-4 R10.3. | Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
565 | 8021 |  | 4. | 8026 | TOP-001-4 R10.4. | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
565 | 8021 |  | 5. | 8027 | TOP-001-4 R10.5. | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  | 105000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
565 | 8021 |  | 6. | 8028 | TOP-001-4 R10.6. | Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  | 106000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
566 | 8042 | 8045 | 1. | 8046 | BAL-002-2(i) R1.3.1. | the Responsible Entity: • is a Balancing Authority experiencing a Reliability Coordinator declared Energy Emergency Alert Level or is a Reserve Sharing Group whose member, or members, are experiencing a Reliability Coordinator declared Energy Emergency Alert level, and • is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and • has depleted its Contingency Reserve to a level below its Most Severe Single Contingency or, |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2018-01-01 |  | 2019-03-31 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
566 | 8042 | 8045 | 2. | 8047 | BAL-002-2(i) R1.3.2. | the Responsible Entity experiences: • multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2018-01-01 |  | 2019-03-31 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
566 | 8042 |  | 1. | 8043 | BAL-002-2(i) R1.1. | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of: • zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or, • its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-10-02 |  | 2019-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
566 | 8042 |  | 2. | 8044 | BAL-002-2(i) R1.2. | document all Reportable Balancing Contingency Events using CR Form 1. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2017-10-02 |  | 2019-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
566 | 8042 |  | 3. | 8045 | BAL-002-2(i) R1.3. | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2017-10-02 |  | 2019-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
567 | 8067 |  | 1. | 8068 | VAR-001-4.2 E.A.18.1. | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. |  | GOP | [5 empty] | GOP | [16 empty] | 2017-09-26 |  | 2018-12-31 |  |  | 1810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
567 | 8067 |  | 2. | 8069 | VAR-001-4.2 E.A.18.2. | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [16 empty] | 2017-09-26 |  | 2018-12-31 |  |  | 1820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
567 | 8050 |  | 1. | 8052 | VAR-001-4.2 R1.1. | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
567 | 8055 |  | 1. | 8056 | VAR-001-4.2 R4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
567 | 8057 |  | 1. | RP-2021-06-24-0000066 | VAR-001-4.2 R5.1. | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
567 | 8057 |  | 2. | RP-2021-06-24-0000067 | VAR-001-4.2 R5.2. | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
567 | 8057 |  | 3. | RP-2021-06-24-0000068 | VAR-001-4.2 R5.3. | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
568 | 8071 |  | 1 . | RP-2021-07-12-0000060 | VAR-002-4.1 R2.1 . | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. |  | GOP | [5 empty] | GOP | [15 empty] | For Part 2.1, when a generator’s AVR is out of service or the generator does not have an AVR, a Generator Operator shall have evidence to show an alternative method was used to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. | 2017-09-26 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
568 | 8071 |  | 2 . | RP-2021-07-12-0000061 | VAR-002-4.1 R2.2 . | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [15 empty] | For Part 2.2, the Generator Operator shall have evidence that it complied with the Transmission Operator’s instructions to modify its voltage or provided an explanation to the Transmission Operator of why the Generator Operator was unable to comply with the instruction. Evidence may include, but is not limited to, operator logs, SCADA data, and phone logs. | 2017-09-26 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
568 | 8071 |  | 3. | 8074 | VAR-002-4.1 R2.3. | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. |  | GOP | [5 empty] | GOP | [15 empty] | For Part 2.3, for Generator Operators that do not monitor the voltage at the location specified on the voltage schedule, the Generator Operator shall demonstrate the methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | 2017-09-26 |  |  |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
568 | 8077 | 8078 | 2. | 8081 | VAR-002-4.1 R5.1.2. | Available fixed tap ranges. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | 2017-09-26 |  |  |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
568 | 8077 | 8078 | 3. | 8082 | VAR-002-4.1 R5.1.3. | Impedance data. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | 2017-09-26 |  |  |  |  | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
568 | 8077 |  | 1. | 8078 | VAR-002-4.1 R5.1. | For generator step-up and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: (Footnote: For dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition, this requirement applies only to those transformers that have at least one winding at a voltage of 100 kV or above.) |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | 2017-09-26 |  |  |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
568 | 8077 |  | 1.1. | 8079 | VAR-002-4.1 R5.1.1. | Tap settings. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner shall have evidence it provided its associated Transmission Operator and Transmission Planner with information on its step-up and auxiliary transformers as required in Requirement R5, Part 5.1.1 through Part 5.1.3 within 30 calendar days. | 2017-09-26 |  |  |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
568 | 8083 |  | 1. | 8084 | VAR-002-4.1 R6.1. | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner shall have evidence that its step-up transformer taps were modified per the Transmission Operator’s documentation in accordance with Requirement R6. The Generator Owner shall have evidence that it notified its associated Transmission Operator when it could not comply with the Transmission Operator’s step-up transformer tap specifications in accordance with Requirement R6, Part 6.1. | 2017-09-26 |  |  |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
569 | 8085 | 8087 | 1. | 8088 | CIP-013-1 R1.2.1. | Notification by the vendor of vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers 4.2.2.1. All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-013-1: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
569 | 8085 | 8087 | 2. | 8089 | CIP-013-1 R1.2.2. | Coordination of responses to vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers 4.2.2.1. All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-013-1: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
569 | 8085 | 8087 | 3. | 8090 | CIP-013-1 R1.2.3. | Notification by vendors when remote or onsite access should no longer be granted to vendor representatives; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers 4.2.2.1. All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-013-1: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
569 | 8085 | 8087 | 4. | 8091 | CIP-013-1 R1.2.4. | Disclosure by vendors of known vulnerabilities related to the products or services provided to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers 4.2.2.1. All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-013-1: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
569 | 8085 | 8087 | 5. | 8092 | CIP-013-1 R1.2.5. | Verification of software integrity and authenticity of all software and patches provided by the vendor for use in the BES Cyber System; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers 4.2.2.1. All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-013-1: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
569 | 8085 | 8087 | 6. | 8093 | CIP-013-1 R1.2.6. | Coordination of controls for (i) vendor-initiated Interactive Remote Access, and (ii) system-to-system remote access with a vendor(s). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers 4.2.2.1. All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-013-1: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
569 | 8085 |  | 1. | 8086 | CIP-013-1 R1.1. | One or more process(es) used in planning for the procurement of BES Cyber Systems to identify and assess cyber security risk(s) to the Bulk Electric System from vendor products or services resulting from: (i) procuring and installing vendor equipment and software; and (ii) transitions from one vendor(s) to another vendor(s). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers 4.2.2.1. All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-013-1: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
569 | 8085 |  | 2. | 8087 | CIP-013-1 R1.2. | One or more process(es) used in procuring BES Cyber Systems that address the following, as applicable: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers 4.2.2.1. All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-013-1: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
569 | 8085 |  | 2.5. DO NOT USE | RP-2021-06-30-0000036 | CIP-013-1 R1.2.5. DO NOT USE | Verification of software integrity and authenticity of all software and patches provided by the vendor for use in the BES Cyber System; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Evidence shall include one or more documented supply chain cyber security risk management plan(s) as specified in the Requirement. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers 4.2.2.1. All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-013-1: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
57 | 834 |  | 1. | 835 | FAC-013-1 R2.1. | The Reliability Coordinator shall provide its Transfer Capabilities to its associated Regional Reliability Organization(s), to its adjacent Reliability Coordinators, and to the Transmission Operators, Transmission Service Providers and Planning Authorities that work in its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2013-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
57 | 834 |  | 2. | 836 | FAC-013-1 R2.2. | The Planning Authority shall provide its Transfer Capabilities to its associated Reliability Coordinator(s) and Regional Reliability Organization(s), and to the Transmission Planners and Transmission Service Provider(s) that work in its Planning Authority Area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2007-06-18 |  | 2013-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
570 | 8096 |  | 1. | 8097 | CIP-005-6 R1.1. | All applicable Cyber Assets connected to a network via a routable protocol shall reside within a defined ESP. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of all ESPs with all uniquely identifiable applicable Cyber Assets connected via a routable protocol within each ESP. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
570 | 8096 |  | 2. | 8098 | CIP-005-6 R1.2. | All External Routable Connectivity must be through an identified Electronic Access Point (EAP). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, network diagrams showing all external routable communication paths and the identified EAPs. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
570 | 8096 |  | 3. | 8099 | CIP-005-6 R1.3. | Require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of rules (firewall, access control lists, etc.) that demonstrate that only permitted access is allowed and that each access rule has a documented reason. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
570 | 8096 |  | 4. | 8100 | CIP-005-6 R1.4. | Where technically feasible, perform authentication when establishing Dial-up Connectivity with applicable Cyber Assets. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a documented process that describes how the Responsible Entity is providing authenticated access through each dial-up connection. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
570 | 8096 |  | 5. | 8101 | CIP-005-6 R1.5. | Have one or more methods for detecting known or suspected malicious communications for both inbound and outbound communications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation that malicious communications detection methods (e.g. intrusion detection system, application layer firewall, etc.) are implemented. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
570 | 8102 |  | 1. | 8103 | CIP-005-6 R2.1. | For all Interactive Remote Access, utilize an Intermediate System such that the Cyber Asset initiating Interactive Remote Access does not directly access an applicable Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, network diagrams or architecture documents. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
570 | 8102 |  | 2. | 8104 | CIP-005-6 R2.2. | For all Interactive Remote Access sessions, utilize encryption that terminates at an Intermediate System. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, architecture documents detailing where encryption initiates and terminates. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
570 | 8102 |  | 3. | 8105 | CIP-005-6 R2.3. | Require multi-factor authentication for all Interactive Remote Access sessions. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, architecture documents detailing the authentication factors used. Examples of authenticators may include, but are not limited to, • Something the individual knows such as passwords or PINs. This does not include User ID; • Something the individual has such as tokens, digital certificates, or smart cards; or • Something the individual is such as fingerprints, iris scans, or other biometric characteristics. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
570 | 8102 |  | 4. | 8106 | CIP-005-6 R2.4. | Have one or more methods for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods used to determine active vendor remote access (including Interactive Remote Access and system-to-system remote access), such as: • Methods for accessing logged or monitoring information to determine active vendor remote access sessions; • Methods for monitoring activity (e.g. connection tables or rule hit counters in a firewall, or user activity monitoring) or open ports (e.g. netstat or related commands to display currently active ports) to determine active system to system remote access sessions; or • Methods that control vendor initiation of remote access such as vendors calling and requesting a second factor in order to initiate remote access. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
570 | 8102 |  | 5. | 8107 | CIP-005-6 R2.5. | Have one or more method(s) to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods(s) used to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access), such as: • Methods to disable vendor remote access at the applicable Electronic Access Point for system-to-system remote access; or • Methods to disable vendor Interactive Remote Access at the applicable Intermediate System. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 | 8109 | 1. | 8110 | CIP-010-3 R1.1.1. | Operating system(s) (including version) or firmware where no independent operating system exists; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or • A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 | 8109 | 2. | 8111 | CIP-010-3 R1.1.2. | Any commercially available or open-source application software (including version) intentionally installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or • A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 | 8109 | 3. | 8112 | CIP-010-3 R1.1.3. | Any custom software installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or • A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 | 8109 | 4. | 8113 | CIP-010-3 R1.1.4. | Any logical network accessible ports; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or • A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 | 8109 | 5. | 8114 | CIP-010-3 R1.1.5. | Any security patches applied. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or • A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 | 8117 | 1. | 8118 | CIP-010-3 R1.4.1. | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls verified or tested along with the dated test results. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 | 8117 | 2. | 8119 | CIP-010-3 R1.4.2. | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls verified or tested along with the dated test results. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 | 8117 | 3. | 8120 | CIP-010-3 R1.4.3. | Document the results of the verification. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls verified or tested along with the dated test results. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 | 8121 | 1. | 8122 | CIP-010-3 R1.5.1. | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls tested along with successful test results and a list of differences between the production and test environments with descriptions of how any differences were accounted for, including of the date of the test. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 | 8121 | 2. | 8123 | CIP-010-3 R1.5.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls tested along with successful test results and a list of differences between the production and test environments with descriptions of how any differences were accounted for, including of the date of the test. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 | 8124 | 1. | 8125 | CIP-010-3 R1.6.1. | Verify the identity of the software source; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to a change request record that demonstrates the verification of identity of the software source and integrity of the software was performed prior to the baseline change or a process which documents the mechanisms in place that would automatically ensure the identity of the software source and integrity of the software. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 | 8124 | 2. | 8126 | CIP-010-3 R1.6.2. | Verify the integrity of the software obtained from the software source. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to a change request record that demonstrates the verification of identity of the software source and integrity of the software was performed prior to the baseline change or a process which documents the mechanisms in place that would automatically ensure the identity of the software source and integrity of the software. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 |  | 1. | 8109 | CIP-010-3 R1.1. | Develop a baseline configuration, individually or by group, which shall include the following items: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or • A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 |  | 2. | 8115 | CIP-010-3 R1.2. | Authorize and document changes that deviate from the existing baseline configuration. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A change request record and associated electronic authorization (performed by the individual or group with the authority to authorize the change) in a change management system for each change; or • Documentation that the change was performed in accordance with the requirement. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 |  | 3. | 8116 | CIP-010-3 R1.3. | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, updated baseline documentation with a date that is within 30 calendar days of the date of the completion of the change. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 |  | 4. | 8117 | CIP-010-3 R1.4. | For a change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls verified or tested along with the dated test results. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 |  | 5. | 8121 | CIP-010-3 R1.5. | Where technically feasible, for each change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls tested along with successful test results and a list of differences between the production and test environments with descriptions of how any differences were accounted for, including of the date of the test. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 |  | 6. | 8124 | CIP-010-3 R1.6. | Prior to a change that deviates from the existing baseline configuration associated with baseline items in Parts 1.1.1, 1.1.2, and 1.1.5, and when the method to do so is available to the Responsible Entity from the software source: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to a change request record that demonstrates the verification of identity of the software source and integrity of the software was performed prior to the baseline change or a process which documents the mechanisms in place that would automatically ensure the identity of the software source and integrity of the software. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 |  | 6.1. DO NOT USE | RP-2021-06-30-0000018 | CIP-010-3 R1.6.1. DO NOT USE | Verify the identity of the software source; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to a change request record that demonstrates the verification of identity of the software source and integrity of the software was performed prior to the baseline change or a process which documents the mechanisms in place that would automatically ensure the identity of the software source and integrity of the software. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8108 |  | 6.2. DO NOT USE | RP-2021-06-30-0000019 | CIP-010-3 R1.6.2. DO NOT USE | Verify the integrity of the software obtained from the software source. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to a change request record that demonstrates the verification of identity of the software source and integrity of the software was performed prior to the baseline change or a process which documents the mechanisms in place that would automatically ensure the identity of the software source and integrity of the software. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8127 |  | 1. | 8128 | CIP-010-3 R2.1. | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, logs from a system that is monitoring the configuration along with records of investigation for any unauthorized changes that were detected. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8129 | 8131 | 1. | 8132 | CIP-010-3 R3.2.1. | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed at least once every 36 calendar months), the output of the tools used to perform the assessment, and a list of differences between the production and test environments with descriptions of how any differences were accounted for in conducting the assessment. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8129 | 8131 | 2. | 8133 | CIP-010-3 R3.2.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed at least once every 36 calendar months), the output of the tools used to perform the assessment, and a list of differences between the production and test environments with descriptions of how any differences were accounted for in conducting the assessment. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8129 |  | 1. | 8130 | CIP-010-3 R3.1. | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A document listing the date of the assessment (performed at least once every 15 calendar months), the controls assessed for each BES Cyber System along with the method of assessment; or • A document listing the date of the assessment and the output of any tools used to perform the assessment. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8129 |  | 2. | 8131 | CIP-010-3 R3.2. | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed at least once every 36 calendar months), the output of the tools used to perform the assessment, and a list of differences between the production and test environments with descriptions of how any differences were accounted for in conducting the assessment. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8129 |  | 2. DO NOT USE | RP-2021-06-30-0000020 | CIP-010-3 R3.2. DO NOT USE | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed at least once every 36 calendar months), the output of the tools used to perform the assessment, and a list of differences between the production and test environments with descriptions of how any differences were accounted for in conducting the assessment. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8129 |  | 3. | 8134 | CIP-010-3 R3.3. | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed prior to the commissioning of the new Cyber Asset) and the output of any tools used to perform the assessment. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
571 | 8129 |  | 4. | 8135 | CIP-010-3 R3.4. | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the results or the review or assessment, a list of action items, documented proposed dates of completion for the action plan, and records of the status of the action items (such as minutes of a status meeting, updates in a work order system, or a spreadsheet tracking the action items). | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
572 | 8137 |  | 1. | 8138 | PRC-006-SERC-02 R1.1. | A Planning Coordinator may adjust island boundaries to differ from subregional boundaries where necessary for the sole purpose of producing a contiguous subregional island more suitable for simulation. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as a methodology, procedure, report, or other documentation indicating that its criteria included selection of its SERC subregion(s) as an island per Requirement R1. | 2017-10-16 |  | 2022-03-31 |  |  | 110000000 | SERC-US |  |  |  | SERC-US
572 | 8139 | 8142 | 1. | 8143 | PRC-006-SERC-02 R2.3.1. | This does not apply to UFLS relays with time delay of one second or longer and a higher frequency setpoint applied to prevent the frequency from stalling at less than 60 Hz when recovering from an underfrequency event. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2018-01-01 |  | 2022-03-31 |  |  | 231000000 | SERC-US |  |  |  | SERC-US
572 | 8139 |  | 1. | 8140 | PRC-006-SERC-02 R2.1. | Have the capability of shedding at least 30 percent of the Peak Demand (MW) served from the Planning Coordinator’s transmission system. The Peak Demand may be either summer or winter as determined by the Planning Coordinator. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | 2017-10-16 |  | 2022-03-31 |  |  | 210000000 | SERC-US |  |  |  | SERC-US
572 | 8139 |  | 2. | 8141 | PRC-006-SERC-02 R2.2. | Shed load with a minimum of three frequency set points. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | 2017-10-16 |  | 2022-03-31 |  |  | 220000000 | SERC-US |  |  |  | SERC-US
572 | 8139 |  | 3. | 8142 | PRC-006-SERC-02 R2.3. | The highest frequency set point for relays used to arrest frequency decline shall be no lower than 59.3 Hz and not higher than 59.5 Hz. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | 2017-10-16 |  | 2022-03-31 |  |  | 230000000 | SERC-US |  |  |  | SERC-US
572 | 8139 |  | 4. | 8144 | PRC-006-SERC-02 R2.4. | The lowest frequency set point shall be no lower than 58.4 Hz. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | 2017-10-16 |  | 2022-03-31 |  |  | 240000000 | SERC-US |  |  |  | SERC-US
572 | 8139 |  | 5. | 8145 | PRC-006-SERC-02 R2.5. | The difference between frequency set points shall be at least 0.2 Hz but no greater than 0.5 Hz. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | 2017-10-16 |  | 2022-03-31 |  |  | 250000000 | SERC-US |  |  |  | SERC-US
572 | 8139 |  | 6. | RP-2021-07-09-0000032 | PRC-006-SERC-02 R2.6. | Time delay (from frequency reaching the set point to the trip signal) shall be at leastsix cycles. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | 2018-01-01 |  | 2022-03-31 |  |  | 260000000 | SERC-US |  |  |  | SERC-US
572 | 8148 |  | 1. | 8149 | PRC-006-SERC-02 R4.1. | The percent of load shedding to be implemented shall be based on the actual or estimated substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year’s actual Peak Demand in the season specified by the Planning Coordinator in R2. |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such asreports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | 2017-10-16 |  | 2022-03-31 |  |  | 410000000 | SERC-US |  |  |  | SERC-US
572 | 8148 |  | 2. | 8150 | PRC-006-SERC-02 R4.2. | The amount of load in each load shedding step shall be within -1.0 and +3.0 of the percentage specified by the Planning Coordinator (for example, if the specified percentage step load shed is 12%, the allowable range is 11 to 15%). |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such asreports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | 2017-10-16 |  | 2022-03-31 |  |  | 420000000 | SERC-US |  |  |  | SERC-US
572 | 8148 |  | 3. | 8151 | PRC-006-SERC-02 R4.3. | The amount of total UFLS load of all steps combined shall be within -1.0 and +5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such asreports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | 2017-10-16 |  | 2022-03-31 |  |  | 430000000 | SERC-US |  |  |  | SERC-US
572 | 8152 |  | 1. | 8153 | PRC-006-SERC-02 R5.1. | The percent of load shedding to be implemented shall be based on the actual or estimated substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year actual Peak Demand in the season specified by the Planning Coordinator in R2. |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  | Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R5 (including all the data elements in Parts 5.1and 5.2) unless scheme changes per Requirement R6 are in process. | 2017-10-16 |  | 2022-03-31 |  |  | 510000000 | SERC-US |  |  |  | SERC-US
572 | 8152 |  | 2. | 8154 | PRC-006-SERC-02 R5.2. | The amount of total UFLS load shall be within ± 5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  | Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R5 (including all the data elements in Parts 5.1and 5.2) unless scheme changes per Requirement R6 are in process. | 2017-10-16 |  | 2022-03-31 |  |  | 520000000 | SERC-US |  |  |  | SERC-US
572 | 8156 |  | 1. | 8157 | PRC-006-SERC-02 R7.1. | Underfrequency trip set points (Hz) |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [12 empty] | 2017-10-16 |  | 2022-03-31 |  |  | 710000000 | SERC-US |  |  |  | SERC-US
572 | 8156 |  | 2. | 8158 | PRC-006-SERC-02 R7.2. | Total clearing time associated with each set point (sec). This includes the time from when frequency reaches the set point and ends when the breaker opens. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2018-01-01 |  | 2022-03-31 |  |  | 720000000 | SERC-US |  |  |  | SERC-US
572 | 8156 |  | 3. | 8159 | PRC-006-SERC-02 R7.3. | Amount of previous year actual or estimated load associated with each set point, both in percent and in MW. The percentage and the Load demand (MW) shall be based on the time coincident with the previous year actual Peak Demand. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as reports or other documentation that data specified in Requirement R7 was provided to SERC in accordance with the schedule. | 2017-10-16 |  | 2022-03-31 |  |  | 730000000 | SERC-US |  |  |  | SERC-US
572 | 8160 |  | 1. | 8161 | PRC-006-SERC-02 R8.1. | Generator protection automatic underfrequency and overfrequency trip set points (Hz). |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [16 empty] | Each Generator Owner shall have evidence such as reports or other documentation that data specified in Requirement R8 was provided to SERC as requested. | 2017-10-16 |  | 2022-03-31 |  |  | 810000000 | SERC-US |  |  |  | SERC-US
572 | 8160 |  | 2. | 8162 | PRC-006-SERC-02 R8.2. | Total clearing time associated with each set point (sec). This is defined as the time that begins when frequency reaches the set point and ends when the breaker opens. If inverse time underfrequency relays are used, provide the total clearing time at 59.0, 58.5, 58.0, and 57.0 Hz. |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [17 empty] | 2017-10-16 |  | 2022-03-31 |  |  | 820000000 | SERC-US |  |  |  | SERC-US
572 | 8160 |  | 3. | 8163 | PRC-006-SERC-02 R8.3. | Maximum generator net MW that could be tripped automatically due to an underfrequency or overfrequency condition. |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [16 empty] | Each Generator Owner shall have evidence such as reports or other documentation that data specified in Requirement R8 was provided to SERC as requested. | 2017-10-16 |  | 2022-03-31 |  |  | 830000000 | SERC-US |  |  |  | SERC-US
574 | 8506 |  | 1. | 8507 | PRC-006-3 D.A.3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8506 |  | 2. | 8508 | PRC-006-3 D.A.3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8506 |  | 3. | 8509 | PRC-006-3 D.A.3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each Quebec BES generator bus and associated generator step-up transformer high-side bus |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8510 |  | 1. | 8511 | PRC-006-3 D.A.4.1. | Underfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1A, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8510 |  | 2. | 8512 | PRC-006-3 D.A.4.2. | Overfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 - Attachment 1A, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8510 |  | 3. | 8513 | PRC-006-3 D.A.4.3. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8198 |  | 1. | 8199 | PRC-006-3 D.B.2.1. | Those islands selected by applying the criteria in Requirement D.B.1, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8198 |  | 2. | 8200 | PRC-006-3 D.B.2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8201 | 8204 | 1. | 8205 | PRC-006-3 D.B.3.3.1. | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 331000000 | WECC-US | [5 empty] | WECC-US
574 | 8201 | 8204 | 2. | 8206 | PRC-006-3 D.B.3.3.2. | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 332000000 | WECC-US | [5 empty] | WECC-US
574 | 8201 | 8204 | 3. | 8207 | PRC-006-3 D.B.3.3.3. | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 333000000 | WECC-US | [5 empty] | WECC-US
574 | 8201 |  | 1. | 8202 | PRC-006-3 D.B.3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8201 |  | 2. | 8203 | PRC-006-3 D.B.3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8201 |  | 3. | 8204 | PRC-006-3 D.B.3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8208 |  | 1. | 8209 | PRC-006-3 D.B.4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8208 |  | 2. | 8210 | PRC-006-3 D.B.4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8208 |  | 3. | 8211 | PRC-006-3 D.B.4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8208 |  | 4. | 8212 | PRC-006-3 D.B.4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8208 |  | 5. | 8213 | PRC-006-3 D.B.4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8208 |  | 6. | 8214 | PRC-006-3 D.B.4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 460000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8208 |  | 7. | 8215 | PRC-006-3 D.B.4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 470000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8216 |  | 1. | 8217 | PRC-006-3 D.B.11.1. | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8216 |  | 2. | 8218 | PRC-006-3 D.B.11.2. | The effectiveness of the UFLS program |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 1120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8165 |  | 1. | RP-2021-06-24-0000001 | PRC-006-3 R2.1. | Those islands selected by applying the criteria in Requirement R1, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8165 |  | 2. | 8167 | PRC-006-3 R2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8165 |  | 3. | 8168 | PRC-006-3 R2.3. | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8169 |  | 1. | 8170 | PRC-006-3 R3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8169 |  | 2. | 8171 | PRC-006-3 R3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8169 |  | 3. | RP-2021-06-24-0000002 | PRC-006-3 R3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following:  Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES  Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES  Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8173 |  | 1. | RP-2021-06-24-0000003 | PRC-006-3 R4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8173 |  | 2. | RP-2021-06-24-0000004 | PRC-006-3 R4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8173 |  | 3. | RP-2021-06-24-0000005 | PRC-006-3 R4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8173 |  | 4. | 8177 | PRC-006-3 R4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8173 |  | 5. | 8178 | PRC-006-3 R4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8173 |  | 6. | 8179 | PRC-006-3 R4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 460000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8173 |  | 7. | 8180 | PRC-006-3 R4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 470000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8188 |  | 1. | 8189 | PRC-006-3 R11.1. | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8188 |  | 2. | 8190 | PRC-006-3 R11.2. | The effectiveness of the UFLS program. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8193 |  | 1. | 8700 | PRC-006-3 R14.1. | UFLS program, including a schedule for implementation |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8193 |  | 2. | 8701 | PRC-006-3 R14.2. | UFLS design assessment |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8193 |  | 3. | 8702 | PRC-006-3 R14.3. | Format and schedule of UFLS data submittal |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8194 |  | 1. | 8195 | PRC-006-3 R15.1. | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
574 | 8194 |  | 2. | 8196 | PRC-006-3 R15.2. | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
575 | 8220 | 8221 | 1. | 8222 | BAL-502-RF-03 R1.1.1. | The utilization of Direct Control Load Management or curtailment of Interruptible Demand shall not contribute to the loss of Load probability. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2018-01-01 |  |  |  |  | 111000000 | RF-US |  |  | RF-US
575 | 8220 | 8221 | 2. | 8223 | BAL-502-RF-03 R1.1.2. | The planning reserve margin developed from R1.1 shall be expressed as a percentage of the median forecast peak Net Internal Demand (planning reserve margin). |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 112000000 | RF-US |  |  | RF-US
575 | 8220 | 8224 | 1. | 8225 | BAL-502-RF-03 R1.2.1. | Perform an analysis for Year One. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 121000000 | RF-US |  |  | RF-US
575 | 8220 | 8224 | 2. | 8226 | BAL-502-RF-03 R1.2.2. | Perform an analysis or verification at a minimum for one year in the 2 through 5 year period and at a minimum one year in the 6 though 10 year period. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 122000000 | RF-US |  |  | RF-US
575 | 8220 | 8226 | 1. | 8227 | BAL-502-RF-03 R1.2.2.1. | If the analysis is verified, the verification must be supported by current or past studies for the same planning year. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 12210000 | RF-US |  |  | RF-US
575 | 8220 | 8229 | 1. | 8230 | BAL-502-RF-03 R1.3.1. | Load forecast characteristics: |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 131000000 | RF-US |  |  | RF-US
575 | 8220 | 8229 | 2. | 8237 | BAL-502-RF-03 R1.3.2. | Resource characteristics: |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 132000000 | RF-US |  |  | RF-US
575 | 8220 | 8229 | 3. | 8244 | BAL-502-RF-03 R1.3.3. | Transmission limitations that prevent the delivery of generation reserves |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 133000000 | RF-US |  |  | RF-US
575 | 8220 | 8229 | 4. | 8246 | BAL-502-RF-03 R1.3.4. | Assistance from other interconnected systems including multi-area assessment considering Transmission limitations into the study area. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 134000000 | RF-US |  |  | RF-US
575 | 8220 | 8230 | 1. | 8231 | BAL-502-RF-03 R1.3.1.1. | Median (50:50) forecast peak Load. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 13110000 | RF-US |  |  | RF-US
575 | 8220 | 8230 | 2. | 8232 | BAL-502-RF-03 R1.3.1.2. | Load forecast uncertainty (reflects variability in the Load forecast due to weather and regional economic forecasts). |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 13120000 | RF-US |  |  | RF-US
575 | 8220 | 8230 | 3. | 8233 | BAL-502-RF-03 R1.3.1.3. | Load diversity. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 13130000 | RF-US |  |  | RF-US
575 | 8220 | 8230 | 4. | 8234 | BAL-502-RF-03 R1.3.1.4. | Seasonal Load variations. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 13140000 | RF-US |  |  | RF-US
575 | 8220 | 8230 | 5. | 8235 | BAL-502-RF-03 R1.3.1.5. | Daily demand modeling assumptions (firm, interruptible). |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 13150000 | RF-US |  |  | RF-US
575 | 8220 | 8230 | 6. | 8236 | BAL-502-RF-03 R1.3.1.6. | Contractual arrangements concerning curtailable/Interruptible Demand. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 13160000 | RF-US |  |  | RF-US
575 | 8220 | 8237 | 1. | 8238 | BAL-502-RF-03 R1.3.2.1. | Historic resource performance and any projected changes |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 13210000 | RF-US |  |  | RF-US
575 | 8220 | 8237 | 2. | 8239 | BAL-502-RF-03 R1.3.2.2. | Seasonal resource ratings |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 13220000 | RF-US |  |  | RF-US
575 | 8220 | 8237 | 3. | 8240 | BAL-502-RF-03 R1.3.2.3. | Modeling assumptions of firm capacity purchases from and sales to entities outside the Planning Coordinator area. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 13230000 | RF-US |  |  | RF-US
575 | 8220 | 8237 | 4. | 8241 | BAL-502-RF-03 R1.3.2.4. | Resource planned outage schedules, deratings, and retirements. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 13240000 | RF-US |  |  | RF-US
575 | 8220 | 8237 | 5. | 8242 | BAL-502-RF-03 R1.3.2.5. | Modeling assumptions of intermittent and energy limited resource such as wind and cogeneration. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 13250000 | RF-US |  |  | RF-US
575 | 8220 | 8237 | 6. | 8243 | BAL-502-RF-03 R1.3.2.6. | Criteria for including planned resource additions in the analysis |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 13260000 | RF-US |  |  | RF-US
575 | 8220 | 8244 | 1. | 8245 | BAL-502-RF-03 R1.3.3.1. | Criteria for including planned Transmission Facility additions in the analysis |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 13310000 | RF-US |  |  | RF-US
575 | 8220 | 8247 | 1. | 8248 | BAL-502-RF-03 R1.4.1. | Availability and deliverability of fuel. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 141000000 | RF-US |  |  | RF-US
575 | 8220 | 8247 | 2. | 8249 | BAL-502-RF-03 R1.4.2. | Common mode outages that affect resource availability |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 142000000 | RF-US |  |  | RF-US
575 | 8220 | 8247 | 3. | 8250 | BAL-502-RF-03 R1.4.3. | Environmental or regulatory restrictions of resource availability. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 143000000 | RF-US |  |  | RF-US
575 | 8220 | 8247 | 4. | 8251 | BAL-502-RF-03 R1.4.4. | Any other demand (Load) response programs not included in R1.3.1. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 144000000 | RF-US |  |  | RF-US
575 | 8220 | 8247 | 5. | 8252 | BAL-502-RF-03 R1.4.5. | Sensitivity to resource outage rates. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 145000000 | RF-US |  |  | RF-US
575 | 8220 | 8247 | 6. | 8253 | BAL-502-RF-03 R1.4.6. | Impacts of extreme weather/drought conditions that affect unit availability. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 146000000 | RF-US |  |  | RF-US
575 | 8220 | 8247 | 7. | 8254 | BAL-502-RF-03 R1.4.7. | Modeling assumptions for emergency operation procedures used to make reserves available. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 147000000 | RF-US |  |  | RF-US
575 | 8220 | 8247 | 8. | 8255 | BAL-502-RF-03 R1.4.8. | Market resources not committed to serving Load (uncommitted resources) within the Planning Coordinator area. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2018-01-01 |  |  |  |  | 148000000 | RF-US |  |  | RF-US
575 | 8220 |  | 1. | 8221 | BAL-502-RF-03 R1.1. | Calculate a planning reserve margin that will result in the sum of the probabilities for loss of Load for the integrated peak hour for all days of each planning year analyzed (per R1.2) being equal to 0.1. (This is comparable to a “one day in 10 year” criterion). |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2017-10-16 |  |  |  |  | 110000000 | RF-US |  |  | RF-US
575 | 8220 |  | 2. | 8224 | BAL-502-RF-03 R1.2. | Be performed or verified separately for each of the following planning years: |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2017-10-16 |  |  |  |  | 120000000 | RF-US |  |  | RF-US
575 | 8220 |  | 3. | 8229 | BAL-502-RF-03 R1.3. | Include the following subject matter and documentation of its use: |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2017-10-16 |  |  |  |  | 130000000 | RF-US |  |  | RF-US
575 | 8220 |  | 4. | 8247 | BAL-502-RF-03 R1.4. | Consider the following resource availability characteristics and document how and why they were included in the analysis or why they were not included: |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2017-10-16 |  |  |  |  | 140000000 | RF-US |  |  | RF-US
575 | 8220 |  | 5. | 8256 | BAL-502-RF-03 R1.5. | Consider Transmission maintenance outage schedules and document how and why they were included in the Resource Adequacy analysis or why they were not included |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2017-10-16 |  |  |  |  | 150000000 | RF-US |  |  | RF-US
575 | 8220 |  | 6. | 8257 | BAL-502-RF-03 R1.6. | Document that capacity resources are appropriately accounted for in its Resource Adequacy analysis |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2017-10-16 |  |  |  |  | 160000000 | RF-US |  |  | RF-US
575 | 8220 |  | 7. | 8258 | BAL-502-RF-03 R1.7. | Document that all Load in the Planning Coordinator area is accounted for in its Resource Adequacy analysis |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation that a valid Resource Adequacy analysis was performed or verified in accordance with R1 | 2017-10-16 |  |  |  |  | 170000000 | RF-US |  |  | RF-US
575 | 8259 |  | 1. | 8260 | BAL-502-RF-03 R2.1. | This documentation shall cover each of the years in Year One through ten. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation of its projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis on an annual basis in accordance with R2. | 2017-10-16 |  |  |  |  | 210000000 | RF-US |  |  | RF-US
575 | 8259 |  | 2. | 8261 | BAL-502-RF-03 R2.2. | This documentation shall include the Planning Reserve margin calculated per requirement R1.1 for each of the three years in the analysis. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation of its projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis on an annual basis in accordance with R2. | 2017-10-16 |  |  |  |  | 220000000 | RF-US |  |  | RF-US
575 | 8259 |  | 3. | 8262 | BAL-502-RF-03 R2.3. | The documentation as specified per requirement R2.1 and R2.2 shall be publicly posted no later than 30 calendar days prior to the beginning of Year One. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall possess the documentation of its projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis on an annual basis in accordance with R2. | 2017-10-16 |  |  |  |  | 230000000 | RF-US |  |  | RF-US
576 | 8266 |  | 1. | 8267 | VAR-501-WECC-3.1 R3.1. | PSS shall be set to provide the measured, simulated, or calculated compensated Vt/Vref frequency response of the excitation system and synchronous machine such that the phase angle will not exceed ± 30 degrees through the frequency range from 0.2 Hertz to the lesser of 1.0 Hertz or the highest frequency at which the phase of the Vt/Vref frequency response does not exceed 90 degrees. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3. If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | 2017-09-26 | X | 2024-03-31 |  | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. | 310000000 | WECC-US | [5 empty] | WECC-US
576 | 8266 |  | 2. | 8268 | VAR-501-WECC-3.1 R3.2. | PSS output limits shall be set to provide at least ±5% of the synchronous machine’s nominal terminal voltage. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3. If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | 2017-09-26 | X | 2024-03-31 |  | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. | 320000000 | WECC-US | [5 empty] | WECC-US
576 | 8266 |  | 3. | 8269 | VAR-501-WECC-3.1 R3.3. | PSS gain shall be set to between 1/3 and 1/2 of maximum practical gain. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3. If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | 2017-09-26 | X | 2024-03-31 |  | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. | 330000000 | WECC-US | [5 empty] | WECC-US
576 | 8266 |  | 4. | 8270 | VAR-501-WECC-3.1 R3.4. | PSS washout time constant shall be no greater than 30 seconds. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3. If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | 2017-09-26 | X | 2024-03-31 |  | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. | 340000000 | WECC-US | [5 empty] | WECC-US
576 | 8266 |  | 5 . | RP-2021-07-12-0000062 | VAR-501-WECC-3.1 R3.5 . | Units that have an excitation system or PSS that is incapable of meeting the tuning requirements of Requirement R3 are exempt from Requirement R3 until the voltage regulator is either replaced or retrofitted such that the PSS becomes capable of meeting the tuning requirements. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have documented evidence that its PSS was tuned to meet the specifications of Requirement R3. If the exception under Requirement R3, Part 3.5, is claimed, the Generator Owner will have documented evidence describing: 1) the conditions that render the PSS incapable of meeting the tuning requirements, and 2) the date the voltage regulator was last replaced or retrofitted. | 2017-09-26 | X | 2024-03-31 | Requirement R3 has an effective date of July 1, 2017 for first-time service after regulatory approval; R3 has an effective date of July 1, 2022 for units placed in service prior to final regulatory approval. | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. | 350000000 | WECC-US | [5 empty] | WECC-US
579 | 8329 | 8330 | 1. | 8331 | TPL-007-2 R4.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8329 | 8330 | 2. | 8332 | TPL-007-2 R4.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8329 | 8334 | 1. | 8335 | TPL-007-2 R4.3.1. | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  | 431000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8329 |  | 1. | 8330 | TPL-007-2 R4.1. | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8329 |  | 2. | RP-2021-06-24-0000058 | TPL-007-2 R4.2. | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8329 |  | 3. | 8334 | TPL-007-2 R4.3. | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8336 |  | 1. | 8337 | TPL-007-2 R5.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2019-06-30 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8336 |  | 2. | 8338 | TPL-007-2 R5.2. | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2019-06-30 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8339 |  | 1. | 8340 | TPL-007-2 R6.1. | Be based on the effective GIC flow information provided in Requirement R5; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2019-06-30 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8339 |  | 2. | 8341 | TPL-007-2 R6.2. | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2019-06-30 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8339 |  | 3. | 8342 | TPL-007-2 R6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2019-06-30 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8339 |  | 4. | 8343 | TPL-007-2 R6.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2019-06-30 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8344 | 8347 | 1. | 8348 | TPL-007-2 R7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  | 731000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8344 | 8347 | 2. | 8349 | TPL-007-2 R7.3.2. | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  | 732000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8344 | 8350 | 1. | 8351 | TPL-007-2 R7.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1; |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  | 741000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8344 | 8350 | 2. | 8352 | TPL-007-2 R7.4.2. | Description of the original CAP, and any previous changes to the CAP, with the associated timetable(s) for implementing the selected actions in Part 7.1; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  | 742000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8344 | 8350 | 3. | 8353 | TPL-007-2 R7.4.3. | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures if applicable, and the updated timetable for implementing the selected actions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  | 743000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8344 | 8354 | 1. | 8355 | TPL-007-2 R7.5.1. | If a recipient of the CAP provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  | 751000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8344 |  | 1. | 8345 | TPL-007-2 R7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8344 |  | 2. | 8346 | TPL-007-2 R7.2. | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8344 |  | 3. | 8347 | TPL-007-2 R7.3. | Include a timetable, subject to revision by the responsible entity in Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8344 |  | 4. | 8350 | TPL-007-2 R7.4. | Be revised if situations beyond the control of the responsible entity determined in Requirement R1 prevent implementation of the CAP within the timetable for implementation provided in Part 7.3. The revised CAP shall document the following, and be updated at least once every 12 calendar months until implemented: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8344 |  | 5. | 8354 | TPL-007-2 R7.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  | 750000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8356 | 8357 | 1. | 8358 | TPL-007-2 R8.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  | 811000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8356 | 8357 | 2. | 8359 | TPL-007-2 R8.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  | 812000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8356 | 8362 | 1. | 8363 | TPL-007-2 R8.4.1. | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  | 841000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8356 |  | 1. | 8357 | TPL-007-2 R8.1. | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8356 |  | 2. | RP-2021-09-07-0000006 | TPL-007-2 R8.2. | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8356 |  | 3. | 8361 | TPL-007-2 R8.3. | If the analysis concludes there is Cascading caused by the supplemental GMD event described in Attachment 1, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8356 |  | 4. | 8362 | TPL-007-2 R8.4. | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  | 840000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8364 |  | 1. | 8365 | TPL-007-2 R9.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2019-01-25 |  | 2019-06-30 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8364 |  | 2. | 8366 | TPL-007-2 R9.2. | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2019-06-30 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8367 |  | 1. | 8368 | TPL-007-2 R10.1. | Be based on the effective GIC flow information provided in Requirement R9; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2019-06-30 |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8367 |  | 2. | 8369 | TPL-007-2 R10.2. | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2019-06-30 |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8367 |  | 3. | 8370 | TPL-007-2 R10.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2019-06-30 |  |  | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
579 | 8367 |  | 4. | 8371 | TPL-007-2 R10.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2019-06-30 |  |  | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
58 | 841 | 842 | 1. | 843 | FAC-014-1 R5.1.1. | Identification and status of the associated Facility (or group of Facilities) that is (are) critical to the derivation of the IROL. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-01 |  | 2009-04-28 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
58 | 841 | 842 | 2. | 844 | FAC-014-1 R5.1.2. | The value of the IROL and its associated Tv. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-01 |  | 2009-04-28 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
58 | 841 | 842 | 3. | 845 | FAC-014-1 R5.1.3. | The associated Contingency(ies). |  | RC | [11 empty] | RC | [10 empty] | 2009-01-01 |  | 2009-04-28 |  |  | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
58 | 841 | 842 | 4. | 846 | FAC-014-1 R5.1.4. | The type of limitation represented by the IROL (e.g., voltage collapse, angular stability). |  | RC | [11 empty] | RC | [10 empty] | 2009-01-01 |  | 2009-04-28 |  |  | 514000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
58 | 841 |  | 1. | 842 | FAC-014-1 R5.1. | The Reliability Coordinator shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Reliability Coordinators and Reliability Coordinators who indicate a reliability-related need for those limits, and to the Transmission Operators, Transmission Planners, Transmission Service Providers and Planning Authorities within its Reliability Coordinator Area. For each IROL, the Reliability Coordinator shall provide the following supporting information: |  | RC | [11 empty] | RC | [10 empty] | 2008-05-29 |  | 2009-04-28 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
58 | 841 |  | 2. | 847 | FAC-014-1 R5.2. | The Transmission Operator shall provide any SOLs it developed to its Reliability Coordinator and to the Transmission Service Providers that share its portion of the Reliability Coordinator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2008-02-08 |  | 2009-04-28 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
58 | 841 |  | 3. | 848 | FAC-014-1 R5.3. | The Planning Authority shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Planning Authorities, and to Transmission Planners, Transmission Service Providers, Transmission Operators and Reliability Coordinators that work within its Planning Authority Area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
58 | 841 |  | 4. | 849 | FAC-014-1 R5.4. | The Transmission Planner shall provide its SOLs (including the subset of SOLs that are IROLs) to its Planning Authority, Reliability Coordinators, Transmission Operators, and Transmission Service Providers that work within its Transmission Planning Area and to adjacent Transmission Planners. |  | TP | [19 empty] | TP |  |  | 2008-02-08 |  | 2009-04-28 |  |  | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
58 | 850 |  | 1. | 851 | FAC-014-1 R6.1. | The Planning Authority shall provide this list of multiple contingencies and the associated stability limits to the Reliability Coordinators that monitor the facilities associated with these contingencies and limits. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
58 | 850 |  | 2. | 852 | FAC-014-1 R6.2. | If the Planning Authority does not identify any stability-related multiple contingencies, the Planning Authority shall so notify the Reliability Coordinator. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
581 | 8375 |  | 1. | 8376 | BAL-004-WECC-3 R1.1. | For load-serving Balancing Authorities, 150% of the previous calendar year’s integrated hourly Peak Demand, |  | BA | BA | [20 empty] | Each Balancing Authority will have evidence that it operated its system such that, following the conclusion of each month, the month-end absolute value of its On Peak and Off-Peak, Accumulated Primary Inadvertent Interchange (PIIaccum), as calculated by the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, meets all criteria stated in Requirement R1. | 2018-05-30 |  |  |  |  | 110000000 | WECC-US | [5 empty] | WECC-US
581 | 8375 |  | 2. | 8377 | BAL-004-WECC-3 R1.2. | For generation-only Balancing Authorities, 150% of the previous calendar year’s integrated hourly peak generation. |  | BA | BA | [20 empty] | Each Balancing Authority will have evidence that it operated its system such that, following the conclusion of each month, the month-end absolute value of its On Peak and Off-Peak, Accumulated Primary Inadvertent Interchange (PIIaccum), as calculated by the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, meets all criteria stated in Requirement R1. | 2018-05-30 |  |  |  |  | 120000000 | WECC-US | [5 empty] | WECC-US
581 | 8380 |  | 1. | 8381 | BAL-004-WECC-3 R4.1. | PIIhourly, |  | BA | BA | [20 empty] | Forms of acceptable evidence of compliance with Requirement R4 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from internal Balancing Authority tool that demonstrate compliance; or, • Data from any other databases, spreadsheets, displays that demonstrate compliance. | 2018-05-30 |  |  |  |  | 410000000 | WECC-US | [5 empty] | WECC-US
581 | 8380 |  | 2. | 8382 | BAL-004-WECC-3 R4.2. | PIIaccum, |  | BA | BA | [20 empty] | Forms of acceptable evidence of compliance with Requirement R4 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from internal Balancing Authority tool that demonstrate compliance; or, • Data from any other databases, spreadsheets, displays that demonstrate compliance. | 2018-05-30 |  |  |  |  | 420000000 | WECC-US | [5 empty] | WECC-US
581 | 8380 |  | 3. | 8383 | BAL-004-WECC-3 R4.3. | Automatic Time Error Correction term (IATEC). |  | BA | BA | [20 empty] | Forms of acceptable evidence of compliance with Requirement R4 include but are not limited to any one of the following: • Data, screen shots from the WECC Interchange Tool (WIT) or its successor electronic confirmation tool, that demonstrate compliance; • Data, screen shots from internal Balancing Authority tool that demonstrate compliance; or, • Data from any other databases, spreadsheets, displays that demonstrate compliance. | 2018-05-30 |  |  |  |  | 430000000 | WECC-US | [5 empty] | WECC-US
583 | 8395 | 8396 | 1. | 8397 | PER-003-2 R1.1.1. | Resource and demand balancing |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8395 | 8396 | 2. | 8398 | PER-003-2 R1.1.2. | Transmission operations |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 |  |  |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8395 | 8396 | 3. | 8399 | PER-003-2 R1.1.3. | Emergency preparedness and operations |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8395 | 8396 | 4. | 8400 | PER-003-2 R1.1.4. | System operations |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8395 | 8396 | 5. | 8401 | PER-003-2 R1.1.5. | Protection and control |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8395 | 8396 | 6. | 8402 | PER-003-2 R1.1.6. | Voltage and reactive |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 |  |  |  |  | 116000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8395 | 8396 | 7. | 8403 | PER-003-2 R1.1.7. | Interchange scheduling and coordination |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 117000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8395 | 8396 | 8. | 8404 | PER-003-2 R1.1.8. | Interconnection reliability operations and coordination |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 118000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8395 |  | 1. | 8396 | PER-003-2 R1.1. | Areas of Competency |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2018-11-21 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8405 | 8406 | 1. | 8407 | PER-003-2 R2.1.1. | Transmission operations |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 |  |  |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8405 | 8406 | 2. | 8408 | PER-003-2 R2.1.2. | Emergency preparedness and operations |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8405 | 8406 | 3. | 8409 | PER-003-2 R2.1.3. | System operations |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8405 | 8406 | 4. | 8410 | PER-003-2 R2.1.4. | Protection and control |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8405 | 8406 | 5. | 8411 | PER-003-2 R2.1.5. | Voltage and reactive |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 |  |  |  |  | 215000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8405 |  | 1. | 8406 | PER-003-2 R2.1. | Areas of Competency |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2018-11-21 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8405 |  | 2. | 8412 | PER-003-2 R2.2. | Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2018-11-21 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8413 | 8414 | 1. | 8415 | PER-003-2 R3.1.1. | Resources and demand balancing |  | BA | BA | [20 empty] | Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. | 2019-07-01 |  |  |  |  | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8413 | 8414 | 2. | 8416 | PER-003-2 R3.1.2. | Emergency preparedness and operations |  | BA | BA | [20 empty] | Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. | 2019-07-01 |  |  |  |  | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8413 | 8414 | 3. | 8417 | PER-003-2 R3.1.3. | System operations |  | BA | BA | [20 empty] | Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. | 2019-07-01 |  |  |  |  | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8413 | 8414 | 4. | 8418 | PER-003-2 R3.1.4. | Interchange scheduling and coordination |  | BA | BA | [20 empty] | Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. | 2019-07-01 |  |  |  |  | 314000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8413 |  | 1. | 8414 | PER-003-2 R3.1. | Areas of Competency |  | BA | BA | [20 empty] | Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. | 2018-11-21 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
583 | 8413 |  | 2. | 8419 | PER-003-2 R3.2. | Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator |  | BA | BA | [20 empty] | Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. | 2018-11-21 |  |  |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
585 | 8421 | 8425 | 1. | 8426 | BAL-002-3 R1.3.1. | is (i) a Balancing Authority or (ii) a Reserve Sharing Group with at least one member that: • is experiencing a Reliability Coordinator declared Energy Emergency Alert Level, and • is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and • has depleted its Contingency Reserve to a level below its Most Severe Single Contingency, and • has, during communications with its Reliability Coordinator in accordance with the Energy Emergency Alert procedures, (i) notified the Reliability Coordinator of the conditions described in the preceding two bullet points preventing the Responsible Entity from complying with Requirement R1 part 1.1, and (ii) provided the Reliability Coordinator with an ACE recovery plan, including target recovery time or, |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
585 | 8421 | 8425 | 2. | 8427 | BAL-002-3 R1.3.2. | the Responsible Entity experiences: • multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
585 | 8421 |  | 1. | 8423 | BAL-002-3 R1.1. | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of: • zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or, • its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
585 | 8421 |  | 2. | 8424 | BAL-002-3 R1.2. | document all Reportable Balancing Contingency Events using CR Form 1. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
585 | 8421 |  | 3. | 8425 | BAL-002-3 R1.3. | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if the Responsible Entity |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
586 | 8429 |  | 1. | 8430 | CIP-012-1 R1.1. | Identification of security protection used to mitigate the risks posed by unauthorized disclosure and unauthorized modification of Real-time Assessment and Real-time monitoring data while being transmitted between Control Centers; |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | M1. Evidence may include, but is not limited to, documented plan(s) that meet the security objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). | 2020-04-13 |  |  |  | 4.2. Exemptions: The following are exempt from Reliability Standard CIP-012-1: 4.2.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.2. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3. A Control Center that transmits to another Control Center Real-time Assessment or Real-time monitoring data pertaining only to the generation resource or Transmission station or substation co-located with the transmitting Control Center. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
586 | 8429 |  | 2. | 8431 | CIP-012-1 R1.2. | Identification of where the Responsible Entity applied security protection for transmitting Real-time Assessment and Real-time monitoring data between Control Centers; and |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | M1. Evidence may include, but is not limited to, documented plan(s) that meet the security objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). | 2020-04-13 |  |  |  | 4.2. Exemptions: The following are exempt from Reliability Standard CIP-012-1: 4.2.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.2. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3. A Control Center that transmits to another Control Center Real-time Assessment or Real-time monitoring data pertaining only to the generation resource or Transmission station or substation co-located with the transmitting Control Center. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
586 | 8429 |  | 3. | 8432 | CIP-012-1 R1.3. | If the Control Centers are owned or operated by different Responsible Entities, identification of the responsibilities of each Responsible Entity for applying security protection to the transmission of Real-time Assessment and Real-time monitoring data between those Control Centers. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | M1. Evidence may include, but is not limited to, documented plan(s) that meet the security objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). | 2020-04-13 |  |  |  | 4.2. Exemptions: The following are exempt from Reliability Standard CIP-012-1: 4.2.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.2. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3. A Control Center that transmits to another Control Center Real-time Assessment or Real-time monitoring data pertaining only to the generation resource or Transmission station or substation co-located with the transmitting Control Center. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
587 | 8447 |  | 1. | 8448 | VAR-001-5 E.A.17.1. | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. |  | GOP | [5 empty] | GOP | [16 empty] | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) | 1710000000 | WECC-US | [5 empty] | WECC-US
587 | 8447 |  | 2. | 8449 | VAR-001-5 E.A.17.2. | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [16 empty] | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) | 1720000000 | WECC-US | [5 empty] | WECC-US
587 | 8433 |  | 1. | 8434 | VAR-001-5 R1.1. | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall have evidence that it specified system voltage schedules using either a range or a target value with an associated tolerance band. For part 1.1, the Transmission Operator shall have evidence that the voltage schedules (which is either a range or a target value with an associated tolerance band) were provided to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. Evidence may include, but is not limited to, emails, website postings, and meeting minutes. | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
587 | 8437 |  | 1. | 8604 | VAR-001-5 R4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. |  | TOP | [18 empty] | TOP |  |  | For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
587 | 8438 |  | 1 . | RP-2021-07-12-0000057 | VAR-001-5 R5.1 . | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  | For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
587 | 8438 |  | 2 . | RP-2021-07-12-0000058 | VAR-001-5 R5.2 . | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  | For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
587 | 8438 |  | 3 . | RP-2021-07-12-0000059 | VAR-001-5 R5.3 . | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  | The Transmission Operator shall have evidence of a documented voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8451 | 8452 | 1. | 8453 | TPL-001-5 R1.1.1. | Existing Facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8451 | 8452 | 2. | 8454 | TPL-001-5 R1.1.2. | New planned Facilities and changes to existing Facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8451 | 8452 | 3. | 8455 | TPL-001-5 R1.1.3. | Real and reactive Load forecasts. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8451 | 8452 | 4. | 8456 | TPL-001-5 R1.1.4. | Known commitments for Firm Transmission Service and Interchange. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8451 | 8452 | 5. | 8457 | TPL-001-5 R1.1.5. | Resources (supply or demand side) required for Load. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8451 |  | 1. | 8452 | TPL-001-5 R1.1. | System models shall represent: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8459 | 1. | 8460 | TPL-001-5 R2.1.1. | System peak Load for either Year One or year two, and for year five. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8459 | 2. | 8461 | TPL-001-5 R2.1.2. | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8459 | 3. | 8462 | TPL-001-5 R2.1.3. | For each of the studies described in Requirement R2, Parts 2.1.1 and 2.1.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in System response : • Real and reactive forecasted Load. • Expected transfers. • Expected in service dates of new or modified Transmission Facilities. • Reactive resource capability. • Generation additions, retirements, or other dispatch scenarios. • Controllable Loads and Demand Side Management. • Duration or timing of known Transmission outages. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8459 | 4. | 8463 | TPL-001-5 R2.1.4. | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P0 and P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8459 | 5. | 8464 | TPL-001-5 R2.1.5. | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 215000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8465 | 1. | 8466 | TPL-001-5 R2.2.1. | A current study assessing expected System peak Load conditions for one of the years in the Long-Term Transmission Planning Horizon and the rationale for why that year was selected. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8468 | 1. | 8469 | TPL-001-5 R2.4.1. | System peak Load for one of the five years. System peak Load levels shall include a Load model which represents the expected dynamic behavior of Loads that could impact the study area, considering the behavior of induction motor Loads. An aggregate System Load model which represents the overall dynamic behavior of the Load is acceptable. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 241000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8468 | 2. | 8470 | TPL-001-5 R2.4.2. | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 242000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8468 | 3. | 8471 | TPL-001-5 R2.4.3. | For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in performance: • Load level, Load forecast, or dynamic Load model assumptions. • Expected transfers. • Expected in service dates of new or modified Transmission Facilities. • Reactive resource capability. • Generation additions, retirements, or other dispatch scenarios. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 243000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8468 | 4. | 8472 | TPL-001-5 R2.4.4. | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum, those known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 244000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8468 | 5. | 8473 | TPL-001-5 R2.4.5. | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the selected P1 and P2 category events identified in Table 1 for which the unavailability is expected to produce more severe System impacts on its portion of the BES. The analysis shall simulate the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 245000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8475 | 1. | RP-2021-06-24-0000035 | TPL-001-5 R2.6.1. | For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 261000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8475 | 2. | RP-2021-06-24-0000036 | TPL-001-5 R2.6.2. | For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 262000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8476 | 1. | 8477 | TPL-001-5 R2.7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations. • Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations. • Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan. • Use of rate applications, DSM, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 271000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8476 | 2. | 8478 | TPL-001-5 R2.7.2. | Include actions to resolve performance deficiencies identified in multiple sensitivity studies or provide a rationale for why actions were not necessary. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 272000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8476 | 3. | 8479 | TPL-001-5 R2.7.3. | If situations arise that are beyond the control of the Transmission Planner or Planning Coordinator that prevent the implementation of a Corrective Action Plan in the required timeframe, then the Transmission Planner or Planning Coordinator is permitted to utilize Non-Consequential Load Loss and curtailment of Firm Transmission Service to correct the situation that would normally not be permitted in Table 1, provided that the Transmission Planner or Planning Coordinator documents that they are taking actions to resolve the situation. The Transmission Planner or Planning Coordinator shall document the situation causing the problem, alternatives evaluated, and the use of Non-Consequential Load Loss or curtailment of Firm Transmission Service. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 273000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8476 | 4. | 8480 | TPL-001-5 R2.7.4. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 274000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8481 | 1. | 8482 | TPL-001-5 R2.8.1. | List System deficiencies and the associated actions needed to achieve required System performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 281000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 | 8481 | 2. | 8483 | TPL-001-5 R2.8.2. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 282000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 |  | 1. | 8459 | TPL-001-5 R2.1. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 |  | 2. | 8465 | TPL-001-5 R2.2. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 |  | 3. | RP-2021-06-24-0000032 | TPL-001-5 R2.3. | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 |  | 4. | 8468 | TPL-001-5 R2.4. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 |  | 5. | 8474 | TPL-001-5 R2.5. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6 and shall include documentation to support the technical rationale for determining material changes. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 |  | 6. | 8475 | TPL-001-5 R2.6. | Past studies may be used to support the Planning Assessment if they meet the following requirements: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 |  | 7. | 8476 | TPL-001-5 R2.7. | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments, but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.4 and 2.4.3. The Corrective Action Plan(s) shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 270000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8458 |  | 8. | 8481 | TPL-001-5 R2.8. | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 280000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8484 | 8493 | 1. | 8494 | TPL-001-5 R3.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 331000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8484 | 8493 | 2. | 8495 | TPL-001-5 R3.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide steady state control of electrical system quantities when such devices impact the study area. These devices may include equipment such as phase-shifting transformers, load tap changing transformers, and switched capacitors and inductors. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 332000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8484 | 8494 | 1. | 8496 | TPL-001-5 R3.3.1.1. | Tripping of generators where simulations show generator bus voltages or high side of the generation step up (GSU) voltages are less than known or assumed minimum generator steady state or ride through voltage limitations. Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 33110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8484 | 8494 | 2. | 8497 | TPL-001-5 R3.3.1.2. | Tripping of Transmission elements where relay loadability limits are exceeded. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 33120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8484 | 8498 | 1. | 8500 | TPL-001-5 R3.4.1. | The Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 341000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8484 |  | 1. | 8491 | TPL-001-5 R3.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8484 |  | 2. | 8492 | TPL-001-5 R3.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8484 |  | 3. | 8493 | TPL-001-5 R3.3. | Contingency analyses for Requirement R3, Parts 3.1 and 3.2 shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8484 |  | 4. | 8498 | TPL-001-5 R3.4. | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES shall be identified, and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8484 |  | 5. | RP-2021-06-24-0000040 | TPL-001-5 R3.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8501 |  | 1.1. | RP-2021-06-24-0000041 | TPL-001-5 R4.1.1. | For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Remedial Action Scheme is not considered pulling out of synchronism. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8501 |  | 1.2. | RP-2021-06-24-0000042 | TPL-001-5 R4.1.2. | For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8501 |  | 1.3. | RP-2021-06-24-0000043 | TPL-001-5 R4.1.3. | For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8501 |  | 2. | RP-2021-06-24-0000044 | TPL-001-5 R4.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event (s) shall be conducted. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8501 |  | 3. | RP-2021-06-24-0000045 | TPL-001-5 R4.3. | Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall : |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8501 |  | 3.1. | RP-2021-06-24-0000046 | TPL-001-5 R4.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 431000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8501 |  | 3.1.1. | RP-2021-06-24-0000047 | TPL-001-5 R4.3.1.1. | Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 431100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8501 |  | 3.1.2. | RP-2021-06-24-0000048 | TPL-001-5 R4.3.1.2. | Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 431200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8501 |  | 3.1.3. | RP-2021-06-24-0000049 | TPL-001-5 R4.3.1.3. | Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 431300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8501 |  | 3.2. | RP-2021-06-24-0000050 | TPL-001-5 R4.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 432000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8501 |  | 4. | RP-2021-06-24-0000051 | TPL-001-5 R4.4. | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8501 |  | 4.1. | RP-2021-06-24-0000052 | TPL-001-5 R4.4.1. | Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 441000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8501 |  | 5. | RP-2021-06-24-0000053 | TPL-001-5 R4.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
589 | 8505 |  | 1. | RP-2021-06-24-0000054 | TPL-001-5 R8.1. | If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
59 | 857 | 858 | 2. | 860 | FAC-014-2 R5.1.2.2. | The value of the IROL and its associated Tv. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2024-03-31 |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
59 | 857 | 858 | 4. | 862 | FAC-014-2 R5.1.2.4. | The type of limitation represented by the IROL (e.g., voltage collapse, angular stability). |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2024-03-31 |  |  | 51400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
59 | 857 | RP-2021-07-02-0000005 | 1. | RP-2021-07-02-0000006 | FAC-014-2 R5.1.1. | Identification and status of the associated Facility (or group of Facilities) that is (are) critical to the derivation of the IROL. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2024-03-31 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
59 | 857 | RP-2021-07-02-0000005 | 2. | 858 | FAC-014-2 R5.1.2. | The value of the IROL and its associated Tv. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2024-03-31 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
59 | 857 | RP-2021-07-02-0000005 | 3. | 859 | FAC-014-2 R5.1.3. | The associated Contingency(ies). |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2024-03-31 |  |  | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
59 | 857 | RP-2021-07-02-0000005 | 4. | RP-2021-07-02-0000004 | FAC-014-2 R5.1.4. | The type of limitation represented by the IROL (e.g., voltage collapse, angular stability). |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2024-03-31 |  |  | 514000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
59 | 857 |  | 1. | RP-2021-07-02-0000005 | FAC-014-2 R5.1. | The Reliability Coordinator shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Reliability Coordinators and Reliability Coordinators who indicate a reliability-related need for those limits, and to the Transmission Operators, Transmission Planners, Transmission Service Providers and Planning Authorities within its Reliability Coordinator Area. For each IROL, the Reliability Coordinator shall provide the following supporting information: |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2024-03-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
59 | 857 |  | 2. | 863 | FAC-014-2 R5.2. | The Transmission Operator shall provide any SOLs it developed to its Reliability Coordinator and to the Transmission Service Providers that share its portion of the Reliability Coordinator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2009-04-29 |  | 2024-03-31 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
59 | 857 |  | 3. | RP-2021-07-02-0000003 | FAC-014-2 R5.3. | The Planning Authority shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Planning Authorities, and to Transmission Planners, Transmission Service Providers, Transmission Operators and Reliability Coordinators that work within its Planning Authority Area. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2024-03-31 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
59 | 857 |  | 4. | 864 | FAC-014-2 R5.4. | The Transmission Planner shall provide its SOLs (including the subset of SOLs that are IROLs) to its Planning Authority, Reliability Coordinators, Transmission Operators, and Transmission Service Providers that work within its Transmission Planning Area and to adjacent Transmission Planners. |  | TP | [19 empty] | TP |  |  | 2009-04-29 |  | 2024-03-31 |  |  | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
59 | 866 |  | 1. | 867 | FAC-014-2 R6.1. | The Planning Authority shall provide this list of multiple contingencies and the associated stability limits to the Reliability Coordinators that monitor the facilities associated with these contingencies and limits. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2024-03-31 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
59 | 866 |  | 2. | 868 | FAC-014-2 R6.2. | If the Planning Authority does not identify any stability-related multiple contingencies, the Planning Authority shall so notify the Reliability Coordinator. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2009-04-29 |  | 2024-03-31 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8514 | 8520 | 1. | 8521 | CIP-008-6 R1.2.1. | That include criteria to evaluate and define attempts to compromise; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of Cyber Security Incident response plan(s) that provide guidance or thresholds for determining which Cyber Security Incidents are also Reportable Cyber Security Incidents or a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the “Applicable Systems” column including justification for attempt determination criteria and documented processes for notification. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8514 | 8520 | 2. | 8522 | CIP-008-6 R1.2.2. | To determine if an identified Cyber Security Incident is: • A Reportable Cyber Security Incident; or • An attempt to compromise, as determined by applying the criteria from Part 1.2.1, one or more systems identified in the “Applicable Systems” column for this Part; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of Cyber Security Incident response plan(s) that provide guidance or thresholds for determining which Cyber Security Incidents are also Reportable Cyber Security Incidents or a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the “Applicable Systems” column including justification for attempt determination criteria and documented processes for notification. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8514 | 8520 | 3. | 8523 | CIP-008-6 R1.2.3. | To provide notification per Requirement R4. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of Cyber Security Incident response plan(s) that provide guidance or thresholds for determining which Cyber Security Incidents are also Reportable Cyber Security Incidents or a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the “Applicable Systems” column including justification for attempt determination criteria and documented processes for notification. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8514 |  | 1. | 8519 | CIP-008-6 R1.1. | One or more processes to identify, classify, and respond to Cyber Security Incidents. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated documentation of Cyber Security Incident response plan(s) that include the process(es) to identify, classify, and respond to Cyber Security Incidents. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8514 |  | 2. | 8520 | CIP-008-6 R1.2. | One or more processes: |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of Cyber Security Incident response plan(s) that provide guidance or thresholds for determining which Cyber Security Incidents are also Reportable Cyber Security Incidents or a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the “Applicable Systems” column including justification for attempt determination criteria and documented processes for notification. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8514 |  | 3. | 8524 | CIP-008-6 R1.3. | The roles and responsibilities of Cyber Security Incident response groups or individuals. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated Cyber Security Incident response process(es) or procedure(s) that define roles and responsibilities (e.g., monitoring, reporting, initiating, documenting, etc.) of Cyber Security Incident response groups or individuals. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8514 |  | 4. | 8525 | CIP-008-6 R1.4. | Incident handling procedures for Cyber Security Incidents. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated Cyber Security Incident response process(es) or procedure(s) that address incident handling (e.g., containment, eradication, recovery/incident resolution). | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8526 |  | 1. | 8527 | CIP-008-6 R2.1. | Test each Cyber Security Incident response plan(s) at least once every 15 calendar months: • By responding to an actual Reportable Cyber Security Incident; • With a paper drill or tabletop exercise of a Reportable Cyber Security Incident; or • With an operational exercise of a Reportable Cyber Security Incident. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated evidence of a lessons-learned report that includes a summary of the test or a compilation of notes, logs, and communication resulting from the test. Types of exercises may include discussion or operations based exercises. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8526 |  | 2. | 8528 | CIP-008-6 R2.2. | Use the Cyber Security Incident response plan(s) under Requirement R1 when responding to a Reportable Cyber Security Incident, responding to a Cyber Security Incident that attempted to compromise a system identified in the “Applicable Systems” column for this Part, or performing an exercise of a Reportable Cyber Security Incident. Document deviations from the plan(s) taken during the response to the incident or exercise. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, incident reports, logs, and notes that were kept during the incident response process, and follow-up documentation that describes deviations taken from the plan during the incident response or exercise. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8526 |  | 3. | 8529 | CIP-008-6 R2.3. | Retain records related to Reportable Cyber Security Incidents and Cyber Security Incidents that attempted to compromise a system identified in the “Applicable Systems” column for this Part as per the Cyber Security Incident response plan(s) under Requirement R1. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated documentation, such as security logs, police reports, emails, response forms or checklists, forensic analysis results, restoration records, and post-incident review notes related to Reportable Cyber Security Incidents and a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the “Applicable Systems” column. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8530 | 8532 | 1. | 8533 | CIP-008-6 R3.1.1. | Document any lessons learned or document the absence of any lessons learned; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following: 1. Dated documentation of post incident(s) review meeting notes or follow-up report showing lessons learned associated with the Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response or dated documentation stating there were no lessons learned; 2. Dated and revised Cyber Security Incident response plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8530 | 8532 | 2. | 8534 | CIP-008-6 R3.1.2. | Update the Cyber Security Incident response plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following: 1. Dated documentation of post incident(s) review meeting notes or follow-up report showing lessons learned associated with the Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response or dated documentation stating there were no lessons learned; 2. Dated and revised Cyber Security Incident response plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8530 | 8532 | 3. | 8535 | CIP-008-6 R3.1.3. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates to the Cyber Security Incident response plan based on any documented lessons learned. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following: 1. Dated documentation of post incident(s) review meeting notes or follow-up report showing lessons learned associated with the Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response or dated documentation stating there were no lessons learned; 2. Dated and revised Cyber Security Incident response plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8530 | 8536 | 1. | 8537 | CIP-008-6 R3.2.1. | Update the Cyber Security Incident response plan(s); and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8530 | 8536 | 2. | 8538 | CIP-008-6 R3.2.2. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8530 |  | 1. | 8532 | CIP-008-6 R3.1. | No later than 90 calendar days after completion of a Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following: 1. Dated documentation of post incident(s) review meeting notes or follow-up report showing lessons learned associated with the Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response or dated documentation stating there were no lessons learned; 2. Dated and revised Cyber Security Incident response plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8530 |  | 2. | 8536 | CIP-008-6 R3.2. | No later than 60 calendar days after a change to the roles or responsibilities, Cyber Security Incident response groups or individuals, or technology that the Responsible Entity determines would impact the ability to execute the plan: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8530 |  | 2.1. DO NOT USE | RP-2021-06-30-0000014 | CIP-008-6 R3.2.1. DO NOT USE | Update the Cyber Security Incident response plan(s); and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8531 | 8539 | 1. | 8540 | CIP-008-6 R4.1.1. | The functional impact; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of initial notifications and updates to the E-ISAC and NCCIC. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8531 | 8539 | 2. | 8541 | CIP-008-6 R4.1.2. | The attack vector used; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of initial notifications and updates to the E-ISAC and NCCIC. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8531 | 8539 | 3. | 8542 | CIP-008-6 R4.1.3. | The level of intrusion that was achieved or attempted. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of initial notifications and updates to the E-ISAC and NCCIC. | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8531 |  | 1. | 8539 | CIP-008-6 R4.1. | Initial notifications and updates shall include the following attributes, at a minimum, to the extent known: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of initial notifications and updates to the E-ISAC and NCCIC. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8531 |  | 2. | 8543 | CIP-008-6 R4.2. | After the Responsible Entity’s determination made pursuant to documented process(es) in Requirement R1, Part 1.2, provide initial notification within the following timelines: • One hour after the determination of a Reportable Cyber Security Incident. • By the end of the next calendar day after determination that a Cyber Security Incident was an attempt to compromise a system identified in the “Applicable Systems” column for this Part. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of notices to the E-ISAC and NCCIC. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
590 | 8531 |  | 3. | 8544 | CIP-008-6 R4.3. | Provide updates, if any, within 7 calendar days of determination of new or changed attribute information required in Part 4.1. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of submissions to the E-ISAC and NCCIC. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8551 | 8552 | 1. | 8553 | TPL-007-3 R4.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8551 | 8552 | 2. | 8554 | TPL-007-3 R4.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8551 | 8556 | 1. | 8557 | TPL-007-3 R4.3.1. | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 431000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8551 |  | 1. | 8552 | TPL-007-3 R4.1. | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8551 |  | 2. | 8555 | TPL-007-3 R4.2. | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8551 |  | 3. | 8556 | TPL-007-3 R4.3. | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8558 |  | 1. | 8559 | TPL-007-3 R5.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8558 |  | 2. | 8560 | TPL-007-3 R5.2. | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8561 |  | 1. | 8565 | TPL-007-3 R6.1. | Be based on the effective GIC flow information provided in Requirement R5; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8561 |  | 2. | 8566 | TPL-007-3 R6.2. | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8561 |  | 3. | 8567 | TPL-007-3 R6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8561 |  | 4. | 8568 | TPL-007-3 R6.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8569 | 8573 | 1. | 8577 | TPL-007-3 R7.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1; |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 741000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8569 | 8573 | 2. | 8578 | TPL-007-3 R7.4.2. | Description of the original CAP, and any previous changes to the CAP, with the associated timetable(s) for implementing the selected actions in Part 7.1; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 742000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8569 | 8573 | 3. | 8579 | TPL-007-3 R7.4.3. | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures if applicable, and the updated timetable for implementing the selected actions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 743000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8569 | 8574 | 1. | 8580 | TPL-007-3 R7.5.1. | If a recipient of the CAP provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 751000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8569 | 8648 | 1. | 8649 | TPL-007-3 R7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of the later of the development of the CAP or receipt of regulatory approvals, if required; and | [24 empty] | 2019-07-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 731000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
593 | 8569 | 8648 | 2. | 8650 | TPL-007-3 R7.3.2. | Specify implementation of hardware mitigation, if any, within four years of the later of the development of the CAP or receipt of regulatory approvals, if required. | [24 empty] | 2019-07-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 732000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
593 | 8569 |  | 1. | 8570 | TPL-007-3 R7.1. | 7.1. List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8569 |  | 2. | 8571 | TPL-007-3 R7.2. | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8569 |  | 3. | 8648 | TPL-007-3 R7.3. | Include a timetable, subject to revision by the responsible entity in Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: | This Variance replaces Requirement R7, Part 7.3 | [23 empty] | 2019-07-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 730000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC
593 | 8569 |  | 4. | 8573 | TPL-007-3 R7.4. | Be revised if situations beyond the control of the responsible entity determined in Requirement R1 prevent implementation of the CAP within the timetable for implementation provided in Part 7.3. The revised CAP shall document the following, and be updated at least once every 12 calendar months until implemented: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8569 |  | 5. | 8574 | TPL-007-3 R7.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 750000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8581 | 8582 | 1. | 8586 | TPL-007-3 R8.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 811000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8581 | 8582 | 2. | 8587 | TPL-007-3 R8.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 812000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8581 | 8585 | 1. | 8588 | TPL-007-3 R8.4.1. | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 841000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8581 |  | 1. | 8582 | TPL-007-3 R8.1. | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8581 |  | 2. | 8583 | TPL-007-3 R8.2. | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8581 |  | 3. | 8584 | TPL-007-3 R8.3. | If the analysis concludes there is Cascading caused by the supplemental GMD event described in Attachment 1, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8581 |  | 4. | 8585 | TPL-007-3 R8.4. | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 840000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8589 |  | 1. | 8590 | TPL-007-3 R9.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8589 |  | 2. | 8591 | TPL-007-3 R9.2. | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8592 |  | 1. | 8598 | TPL-007-3 R10.1. | Be based on the effective GIC flow information provided in Requirement R9; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8592 |  | 2. | 8599 | TPL-007-3 R10.2. | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8592 |  | 3. | 8600 | TPL-007-3 R10.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8592 |  | 4. | 8601 | TPL-007-3 R10.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2022-01-01 |  | 2020-09-30 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8978 |  | 1. | 8979 | TPL-007-3 D.A.7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of the later of the development of the CAP or receipt of regulatory approvals, if required; and | [26 empty] | 2020-09-30 |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 731000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
593 | 8978 |  | 2. | 8980 | TPL-007-3 D.A.7.3.2. | Specify implementation of hardware mitigation, if any, within four years of the later of the development of the CAP or receipt of regulatory approvals, if required. | [26 empty] | 2020-09-30 |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 732000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
595 | 8657 |  | 1. | 8658 | IRO-002-6 D.A.7.1. | A method for development, maintenance, and periodic review of a Western Interconnection-wide reference model to serve as the baseline from which Reliability Coordinator’s operational models are derived |  | RC | [11 empty] | RC | [10 empty] | 2019-07-11 |  | 2021-03-31 |  | Applicability As used in this WECC Regional Variance, Reliability Coordinator is specific to those Reliability Coordinators providing Reliability Coordinator service(s) to entities operating within the Western Interconnection, regardless of where the Reliability Coordinator may be located. | 710000000 | WECC-US | [5 empty] | WECC-US
595 | 8657 |  | 2. | 8659 | IRO-002-6 D.A.7.2. | The impacts of Inter-area oscillations; | [24 empty] | 2020-01-01 |  | 2021-03-31 |  | Applicability As used in this WECC Regional Variance, Reliability Coordinator is specific to those Reliability Coordinators providing Reliability Coordinator service(s) to entities operating within the Western Interconnection, regardless of where the Reliability Coordinator may be located. | 720000000 | WECC-US | [5 empty] | WECC-US
595 | 8657 |  | 3. | 8660 | IRO-002-6 D.A.7.3. | A method to determine Contingencies included in analyses and assessments; | [24 empty] | 2020-01-01 |  | 2021-03-31 |  | Applicability As used in this WECC Regional Variance, Reliability Coordinator is specific to those Reliability Coordinators providing Reliability Coordinator service(s) to entities operating within the Western Interconnection, regardless of where the Reliability Coordinator may be located. | 730000000 | WECC-US | [5 empty] | WECC-US
595 | 8657 |  | 4. | 8661 | IRO-002-6 D.A.7.4. | A method to determine Remedial Action Schemes included in analyses and assessments; | [24 empty] | 2020-01-01 |  | 2021-03-31 |  | Applicability As used in this WECC Regional Variance, Reliability Coordinator is specific to those Reliability Coordinators providing Reliability Coordinator service(s) to entities operating within the Western Interconnection, regardless of where the Reliability Coordinator may be located. | 740000000 | WECC-US | [5 empty] | WECC-US
595 | 8657 |  | 5. | 8662 | IRO-002-6 D.A.7.5. | A method to determine forecast data included in analyses and assessments; and | [24 empty] | 2020-01-01 |  | 2021-03-31 |  | Applicability As used in this WECC Regional Variance, Reliability Coordinator is specific to those Reliability Coordinators providing Reliability Coordinator service(s) to entities operating within the Western Interconnection, regardless of where the Reliability Coordinator may be located. | 750000000 | WECC-US | [5 empty] | WECC-US
595 | 8657 |  | 6. | 8663 | IRO-002-6 D.A.7.6. | A method for the validation and periodic review of the Reliability Coordinator’s operational model for steady state and dynamic/oscillatory system response. | [24 empty] | 2020-01-01 |  | 2021-03-31 |  | Applicability As used in this WECC Regional Variance, Reliability Coordinator is specific to those Reliability Coordinators providing Reliability Coordinator service(s) to entities operating within the Western Interconnection, regardless of where the Reliability Coordinator may be located. | 760000000 | WECC-US | [5 empty] | WECC-US
596 | 8671 |  | 1. | 8672 | IRO-002-7 D.A.7.1. | A method for development, maintenance, and periodic review of a Western Interconnection-wide reference model to serve as the baseline from which Reliability Coordinator’s operational models are derived; |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 |  |  |  |  | 710000000 | WECC-US | [5 empty] | WECC-US
596 | 8671 |  | 2. | 8673 | IRO-002-7 D.A.7.2. | The impacts of Inter-area oscillations; |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 |  |  |  |  | 720000000 | WECC-US | [5 empty] | WECC-US
596 | 8671 |  | 3. | 8674 | IRO-002-7 D.A.7.3. | A method to determine Contingencies included in analyses and assessments; |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 |  |  |  |  | 730000000 | WECC-US | [5 empty] | WECC-US
596 | 8671 |  | 4. | 8675 | IRO-002-7 D.A.7.4. | A method to determine Remedial Action Schemes included in analyses and assessments; |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 |  |  |  |  | 740000000 | WECC-US | [5 empty] | WECC-US
596 | 8671 |  | 5. | 8676 | IRO-002-7 D.A.7.5. | A method to determine forecast data included in analyses and assessments; and |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 |  |  |  |  | 750000000 | WECC-US | [5 empty] | WECC-US
596 | 8671 |  | 6. | 8677 | IRO-002-7 D.A.7.6. | A method for the validation and periodic review of the Reliability Coordinator’s operational model for steady state and dynamic/oscillatory system response. |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 |  |  |  |  | 760000000 | WECC-US | [5 empty] | WECC-US
597 | 8679 | 8680 | 1. | 8681 | CIP-003-8 R1.1.1. | Personnel and training (CIP-004); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 | 8680 | 2. | 8682 | CIP-003-8 R1.1.2. | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 | 8680 | 3. | 8683 | CIP-003-8 R1.1.3. | Physical security of BES Cyber Systems (CIP-006); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 | 8680 | 4. | 8684 | CIP-003-8 R1.1.4. | System security management (CIP-007); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 | 8680 | 5. | 8685 | CIP-003-8 R1.1.5. | Incident reporting and response planning (CIP-008); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 | 8680 | 6. | 8686 | CIP-003-8 R1.1.6. | Recovery plans for BES Cyber Systems (CIP-009); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 116000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 | 8680 | 7. | 8687 | CIP-003-8 R1.1.7. | Configuration change management and vulnerability assessments (CIP-010); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 117000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 | 8680 | 8. | 8688 | CIP-003-8 R1.1.8. | Information protection (CIP-011); and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 118000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 | 8680 | 9. | 8689 | CIP-003-8 R1.1.9. | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 119000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 | 8690 | 1. | 8691 | CIP-003-8 R1.2.1. | Cyber security awareness; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 | 8690 | 2. | 8692 | CIP-003-8 R1.2.2. | Physical security controls; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 | 8690 | 3. | 8693 | CIP-003-8 R1.2.3. | Electronic access controls; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 | 8690 | 4. | 8694 | CIP-003-8 R1.2.4. | Cyber Security Incident response; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 | 8690 | 5. | 8695 | CIP-003-8 R1.2.5. | Transient Cyber Assets and Removable Media malicious code risk mitigation; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 | 8690 | 6. | 8696 | CIP-003-8 R1.2.6. | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 |  | 1. | 8680 | CIP-003-8 R1.1. | For its high impact and medium impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
597 | 8679 |  | 2. | 8690 | CIP-003-8 R1.2. | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-04-01 |  | 2026-03-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
598 | 8703 |  | 1. | 8705 | INT-006-5 R1.1. | Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. |  | BA | BA | [20 empty] | Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it responded to each request for its approval to transition an Arranged Interchange to a Confirmed Interchange within the time defined in Attachment 1, Column B. (R1) | 2021-04-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
598 | 8703 |  | 2. | 8706 | INT-006-5 R1.2. | Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. |  | BA | BA | [20 empty] | Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it responded to each request for its approval to transition an Arranged Interchange to a Confirmed Interchange within the time defined in Attachment 1, Column B. (R1) | 2021-04-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
598 | 8704 |  | 1. | 8707 | INT-006-5 R2.1. | Each Transmission Service Provider shall deny the Arranged Interchange or curtail Confirmed Interchange if the transmission path (proper connectivity of adjacent Transmission Service Providers) between it and its adjacent Transmission Service Providers is invalid. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that it responded to each Arranged Interchange or emergency Arranged Interchange within the time defined in Attachment 1, Column B. If the transmission path between the Transmission Service Provider and its adjacent Transmission Service Providers is invalid, each Transmission Service Provider shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that it denied the Arranged Interchange or curtailed confirmed Interchange. (R2) | 2021-04-01 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
599 | 8711 |  | 1. | 8712 | INT-009-3 R1.1. | Identical in magnitude to that of the Adjacent Balancing Authority, and |  | BA | BA | [20 empty] | The Balancing Authority shall have evidence (such as dated logs, voice recordings, electronic records, or other evidence) that its Composite Confirmed Interchange, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange not yet captured in the Composite Confirmed Interchange, was agreed to by each Adjacent Balancing Authority, identical in magnitude to those of each Adjacent Balancing Authority, and opposite in sign to that of each Adjacent Balancing Authority. (R1) | 2021-04-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
599 | 8711 |  | 2. | 8713 | INT-009-3 R1.2. | Opposite in sign or direction to that of the Adjacent Balancing Authority |  | BA | BA | [20 empty] | The Balancing Authority shall have evidence (such as dated logs, voice recordings, electronic records, or other evidence) that its Composite Confirmed Interchange, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange not yet captured in the Composite Confirmed Interchange, was agreed to by each Adjacent Balancing Authority, identical in magnitude to those of each Adjacent Balancing Authority, and opposite in sign to that of each Adjacent Balancing Authority. (R1) | 2021-04-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6 | 37 | 38 | 1. | 39 | BAL-002-WECC-1 R1.1.1. | An amount of reserve equal to the loss of the most severe single contingency; or |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6 | 37 | 38 | 2. | 40 | BAL-002-WECC-1 R1.1.2. | An amount of reserve equal to the sum of three percent of the load (generation minus station service minus Net Actual Interchange) and three percent of net generation (generation minus station service). |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6 | 37 |  | 1. | 38 | BAL-002-WECC-1 R1.1. | The greater of the following: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | · evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. |  |  | 2010-11-26 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6 | 37 |  | 2. | 41 | BAL-002-WECC-1 R1.2. | If the Source Balancing Authority designates an Interchange Transaction(s) as part of its Non-Spinning Contingency Reserve, the Sink Balancing Authority shall carry an amount of additional Non-Spinning Contingency Reserve equal to the Interchange Transaction(s). This type of transaction cannot be designated as Spinning Reserves by the source BA. If the Source Balancing Authority does not designate the Interchange Transaction as part of its Contingency Reserve, the Sink Balancing Authority is not required to carry any additional Contingency Reserves under this Requirement. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6 | 37 |  | 3. | 42 | BAL-002-WECC-1 R1.3. | If the Sink Balancing Authority is designating an Interchange Transaction(s) as part of its Contingency Reserve either Spinning or Non-Spinning, the Source Balancing Authority shall increase its Contingency Reserves equal in amount and type, to the capacity transaction(s) where the Sink Balancing Authority is designating the transaction(s) as a resource to meet its Contingency Reserve requirements. These types of transactions could be designated as either spinning or non-spinning reserves. If designated as Spinning Reserves, all of the requirements of section R2.1 & R2.2 must be met. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6 | 43 |  | 1. | 44 | BAL-002-WECC-1 R2.1. | Immediately and automatically responds proportionally to frequency deviations, e.g. through the action of a governor or other control systems. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6 | 43 |  | 2. | 45 | BAL-002-WECC-1 R2.2. | Capable of fully responding within ten minutes. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6 | 46 |  | 1. | 47 | BAL-002-WECC-1 R3.1. | Spinning Reserve |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Any Reserve Sharing Group or Balancing Authority utilizing Load other than Interruptible Load shall submit documentation demonstrating that the Reliability Coordinator declared a Capacity and/or Energy Emergency prior to utilizing Load for Contingency Reserves. |  |  | 2010-11-26 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6 | 46 |  | 2. | 48 | BAL-002-WECC-1 R3.2. | Interruptible Load; |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6 | 46 |  | 3. | 49 | BAL-002-WECC-1 R3.3. | Interchange Transactions designated by the source Balancing Authority as non-spinning contingency reserve; |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6 | 46 |  | 4. | 50 | BAL-002-WECC-1 R3.4. | Reserve held by other entities by agreement that is deliverable on Firm Transmission Service; |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6 | 46 |  | 5. | 51 | BAL-002-WECC-1 R3.5. | An amount of off-line generation which can be synchronized and generating; or |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6 | 46 |  | 6. | 52 | BAL-002-WECC-1 R3.6. | Load, other than Interruptible Load, once the Reliability Coordinator has declared a capacity or energy emergency. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | 360000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
60 | 869 |  | 1. | RP-2021-06-11-0000001 | FAC-501-WECC-1 R1.1. | Transmission Owners shall annually review their TMIP and update as required. |  | TO | [17 empty] | TO |  |  |  |  | 2011-07-01 |  | 2018-06-30 |  |  | 110000000 | WECC-US | [5 empty] | WECC-US
600 | 8716 |  | 1. | 8723 | FAC-008-4 R1.1. | The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. |  | GO |  |  |  |  | GO | [19 empty] | 2021-02-04 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8716 |  | 2. | 8724 | FAC-008-4 R1.2. | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO |  |  |  |  | GO | [19 empty] | 2021-02-04 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8717 | 8726 | 1. | 8729 | FAC-008-4 R2.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | GO |  |  |  |  | GO | [19 empty] | 2021-02-04 |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8717 | 8726 | 2. | 8730 | FAC-008-4 R2.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | GO |  |  |  |  | GO | [19 empty] | 2021-02-04 |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8717 | 8726 | 3. | 8731 | FAC-008-4 R2.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | GO |  |  |  |  | GO | [19 empty] | 2021-02-04 |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8717 | 8726 | 4. | 8732 | FAC-008-4 R2.2.4. | Operating limitations. |  | GO |  |  |  |  | GO | [19 empty] | 2021-02-04 |  |  | 224000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8717 | 8728 | 1. | 8733 | FAC-008-4 R2.4.1. | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO |  |  |  |  | GO | [19 empty] | 2021-02-04 |  |  | 241000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8717 | 8728 | 2. | 8734 | FAC-008-4 R2.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO |  |  |  |  | GO | [19 empty] | 2021-02-04 |  |  | 242000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8717 |  | 1. | 8725 | FAC-008-4 R2.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | GO |  |  |  |  | GO | [19 empty] | 2021-02-04 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8717 |  | 2. | 8726 | FAC-008-4 R2.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: |  | GO |  |  |  |  | GO | [19 empty] | 2021-02-04 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8717 |  | 3. | 8727 | FAC-008-4 R2.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO |  |  |  |  | GO | [19 empty] | 2021-02-04 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8717 |  | 4. | 8728 | FAC-008-4 R2.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | GO |  |  |  |  | GO | [19 empty] | 2021-02-04 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8718 | 8736 | 1. | 8740 | FAC-008-4 R3.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | TO | [17 empty] | TO | [6 empty] | 2021-02-04 |  |  | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8718 | 8736 | 2. | 8741 | FAC-008-4 R3.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | TO | [17 empty] | TO | [6 empty] | 2021-02-04 |  |  | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8718 | 8736 | 3. | 8742 | FAC-008-4 R3.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | TO | [17 empty] | TO | [6 empty] | 2021-02-04 |  |  | 323000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8718 | 8736 | 4. | 8743 | FAC-008-4 R3.2.4. | Operating limitations. |  | TO | [17 empty] | TO | [6 empty] | 2021-02-04 |  |  | 324000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8718 | 8738 | 1. | 8744 | FAC-008-4 R3.4.1. | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | TO | [17 empty] | TO | [6 empty] | 2021-02-04 |  |  | 341000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8718 | 8738 | 2. | 8745 | FAC-008-4 R3.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | TO | [17 empty] | TO | [6 empty] | 2021-02-04 |  |  | 342000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8718 |  | 1. | 8735 | FAC-008-4 R3.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | TO | [17 empty] | TO | [6 empty] | 2021-02-04 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8718 |  | 2. | 8736 | FAC-008-4 R3.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: |  | TO | [17 empty] | TO | [6 empty] | 2021-02-04 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8718 |  | 3. | 8737 | FAC-008-4 R3.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | TO | [17 empty] | TO | [6 empty] | 2021-02-04 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
600 | 8718 |  | 4. | 8738 | FAC-008-4 R3.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | TO | [17 empty] | TO | [6 empty] | 2021-02-04 |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
601 | 8746 |  | 1. | 8747 | PRC-004-6 R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
601 | 8746 |  | 2. | 8748 | PRC-004-6 R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
601 | 8746 |  | 3. | 8749 | PRC-004-6 R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
601 | 8750 | 8751 | 1. | 8752 | PRC-004-6 R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
601 | 8750 | 8751 | 2. | 8753 | PRC-004-6 R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
601 | 8750 | 8751 | 3. | 8754 | PRC-004-6 R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
601 | 8750 |  | 1. | 8751 | PRC-004-6 R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
601 | 8750 |  | 2. | 8755 | PRC-004-6 R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
603 | 8771 |  | 1. | 8772 | TOP-001-5 R10.1. | Monitor Facilities within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-04-01 |  | 2024-03-31 |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
603 | 8771 |  | 2. | 8773 | TOP-001-5 R10.2. | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-04-01 |  | 2024-03-31 |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
603 | 8771 |  | 3. | 8774 | TOP-001-5 R10.3. | Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-04-01 |  | 2024-03-31 |  |  | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
603 | 8771 |  | 4. | 8775 | TOP-001-5 R10.4. | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-04-01 |  | 2024-03-31 |  |  | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
603 | 8771 |  | 5. | 8776 | TOP-001-5 R10.5. | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-04-01 |  | 2024-03-31 |  |  | 105000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
603 | 8771 |  | 6. | 8777 | TOP-001-5 R10.6. | Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-04-01 |  | 2024-03-31 |  |  | 106000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
604 | 8796 |  | 1. | 8797 | VAR-001-6 E.A.17.1. | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. |  | GOP | [5 empty] | GOP | [18 empty] | 2020-05-14 |  |  | 1710000000 | WECC-US | [5 empty] | WECC-US
604 | 8796 |  | 2. | 8798 | VAR-001-6 E.A.17.2. | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [18 empty] | 2020-05-14 |  |  | 1720000000 | WECC-US | [5 empty] | WECC-US
604 | 8799 |  | 1. | 8800 | VAR-001-6 R1.1. | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
604 | 8803 |  | 1. | 8804 | VAR-001-6 R4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
604 | 8805 |  | 1. | RP-2021-06-24-0000069 | VAR-001-6 R5.1. | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
604 | 8805 |  | 2. | RP-2021-06-24-0000070 | VAR-001-6 R5.2. | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviationsfrom the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
604 | 8805 |  | 3. | RP-2021-06-24-0000071 | VAR-001-6 R5.3. | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
606 | 8835 |  | 1. | 8839 | BAL-002-WECC-3 R1.1. | The greater of either: • The amount of Contingency Reserve equal to the loss of the most severe single contingency; • The amount of Contingency Reserve equal to the sum of three percent of hourly integrated Load plus three percent of hourly integrated generation. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.1 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates its Contingency Reserve was maintained in accordance with the amounts identified in Requirement R1, Part 1.1, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Attachment A is a practical illustration showing how the generation amount may be calculated under Requirement R1. • Where Dynamic Schedules are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1 may include, but is not limited to, documentation showing a reciprocal acknowledgement as to which entity is carrying the reserves. This transfer may be all or some portion of the physical generator and is not limited to the entire physical capability of the generator. • Where Pseudo-Ties are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1, may include, but is not limited to, documentation accounting for the transfers included in the Pseudo-Ties. | 2021-06-28 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 110000000 | WECC-US | [5 empty] | WECC-US
606 | 8835 |  | 2. | 8840 | BAL-002-WECC-3 R1.2. | Composed of any combination of the reserve types specified below: • Operating Reserve—Spinning • Operating Reserve—Supplemental • Interchange Transactions designated by the Source Balancing Authority as Operating Reserve—Supplemental • Reserve held by other entities by agreement that is deliverable on Firm Transmission Service • A resource, other than generation or load, that can provide energy or reduce energy consumption • Load, including demand response resources, Demand-Side Management resources, Direct Control Load Management, Interruptible Load or Interruptible Demand, or any other Load made available for curtailment by the Balancing Authority or the Reserve Sharing Group via contract or agreement. • All other load, not identified above, once the Reliability Coordinator has declared an energy emergency alert signifying that firm load interruption is imminent or in progress. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.2 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.2. Evidence may include, but is not limited to, documentation that reserves were comprised of the types listed in Requirement R1, Part 1.2 for purposes of meeting the Contingency Reserve obligation of Requirement R1. Additionally, for purposes of the last bullet of Requirement R1, Part 1.2, evidence of compliance may include, but is not limited to, documentation that the reliability coordinator had issued an energy emergency alert, indicating that firm Load interruption was imminent or was in progress. | 2021-06-28 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 120000000 | WECC-US | [5 empty] | WECC-US
606 | 8835 |  | 3. | 8841 | BAL-002-WECC-3 R1.3. | Based on real-time hourly load and generating energy values averaged over each Clock Hour (excluding Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464). |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.3 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.3. Evidence of compliance with Requirement R1, Part 1.3 may include, but is not limited to, documentation that Contingency Reserve amounts are based upon load and generating data averaged over each Clock Hour and excludes Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464. | 2021-06-28 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 130000000 | WECC-US | [5 empty] | WECC-US
606 | 8835 |  | 4. | 8842 | BAL-002-WECC-3 R1.4. | An amount of capacity from a resource that is deployable within ten minutes. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.4 Evidence of compliance with Requirement R1, Part 1.4 may include, but is not limited to, documentation that the reserves maintained to comply with Requirement R1, Part 1.4 are fully deployable within ten minutes. | 2021-06-28 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group. 4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. | 140000000 | WECC-US | [5 empty] | WECC-US
607 | 8845 |  | 1. | 8847 | BAL-003-2 R3.1. | Less than zero at all times, and |  | BA | BA | [20 empty] | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2020-07-15 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
607 | 8845 |  | 2. | 8848 | BAL-003-2 R3.2. | Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. |  | BA | BA | [20 empty] | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2020-07-15 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
609 | 8902 |  | 1. | 8907 | PRC-006-NPCC-2 R12.1. | Design measures to prevent the generating unit from tripping directly or indirectly for underfrequency conditions above the appropriate generator tripping threshold curve in Figure 2. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall provide evidence such as reports, data sheets, specifications, memorandum or other documentation that demonstrates that it meets Requirement R12. |  |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators 4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators | 121000000 | NPCC-US |  | NPCC-US
609 | 8902 |  | 2. | 8908 | PRC-006-NPCC-2 R12.2. | Design auxiliary system(s) or devices used for the control and protection of auxiliary system(s), necessary for the generating unit operation such that they will not trip the generating unit during underfrequency conditions above the appropriate generator underfrequency trip protection setting threshold curve in Figure 2. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall provide evidence such as reports, data sheets, specifications, memorandum or other documentation that demonstrates that it meets Requirement R12. |  |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators 4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators | 122000000 | NPCC-US |  | NPCC-US
609 | 8903 |  | 1. | 8909 | PRC-006-NPCC-2 R13.1. | Each Generator Owner shall set the underfrequency protection to operate at the lowest frequency allowed by the plant design and licensing limitations. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner with existing non-nuclear units in service prior to July 1, 2015 which have underfrequency tripping that is not compliant with Requirement R10 shall provide evidence such as reports, spreadsheets, memorandum or dated documentation demonstrating that it meets Requirement R13. | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators 4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators | 131000000 | NPCC-US |  | NPCC-US
609 | 8903 |  | 2. | 8910 | PRC-006-NPCC-2 R13.2. | Each Generator Owner shall transmit the existing underfrequency settings and any changes to the underfrequency settings along with the technical basis for the settings to the Planning Coordinator. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner with existing non-nuclear units in service prior to July 1, 2015 which have underfrequency tripping that is not compliant with Requirement R10 shall provide evidence such as reports, spreadsheets, memorandum or dated documentation demonstrating that it meets Requirement R13. | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators 4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators | 132000000 | NPCC-US |  | NPCC-US
609 | 8903 |  | 3. | 8911 | PRC-006-NPCC-2 R13.3. | Each Planning Coordinator in Ontario, Québec and the Maritime Provinces shall arrange for compensatory load shedding, in accordance with Attachment A and as provided by a Distribution Provider or Transmission Owner, that is adequate to compensate for the loss of generator(s) due to early tripping that is within the UFLS island identified by the Planning Coordinator in Requirement R2. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Generator Owner with existing non-nuclear units in service prior to July 1, 2015 which have underfrequency tripping that is not compliant with Requirement R10 shall provide evidence such as reports, spreadsheets, memorandum or dated documentation demonstrating that it meets Requirement R13. | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators 4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators | 133000000 | NPCC-US |  | NPCC-US
609 | 8903 |  | 4. | 8912 | PRC-006-NPCC-2 R13.4. | Each Generator Owner in the ISO-NE Planning Coordinator area and in NYISO Planning Coordinator area shall arrange for compensatory load shedding, in accordance with Attachment B and as provided by a Distribution Provider or Transmission Owner, that is adequate to compensate for the loss of generator(s) due to early tripping that is within the UFLS island identified by the Planning Coordinator in Requirement R2. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner with existing non-nuclear units in service prior to July 1, 2015 which have underfrequency tripping that is not compliant with Requirement R10 shall provide evidence such as reports, spreadsheets, memorandum or dated documentation demonstrating that it meets Requirement R13. | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators 4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators | 134000000 | NPCC-US |  | NPCC-US
609 | 8906 |  | 1. | 8913 | PRC-006-NPCC-2 R16.1. | Set the underfrequency protection to operate at a frequency setting that is as low as possible in accordance with the plant design and licensing limitations but not greater than 57.8 Hz. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner of nuclear units that have generator trip settings above the generator trip curve in Figure 2 shall provide evidence such as letters, reports and dated documentation that demonstrates that it meets Requirement R16. | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators 4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators | 161000000 | NPCC-US |  | NPCC-US
609 | 8906 |  | 2. | 8914 | PRC-006-NPCC-2 R16.2. | Set the frequency trip setting upper tolerance to no greater than + 0.1 Hz. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner of nuclear units that have generator trip settings above the generator trip curve in Figure 2 shall provide evidence such as letters, reports and dated documentation that demonstrates that it meets Requirement R16. | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators 4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators | 162000000 | NPCC-US |  | NPCC-US
609 | 8906 |  | 3. | RP-2021-07-09-0000030 | PRC-006-NPCC-2 R16.3. | Transmit the initial frequency trip setting and any changes to the setting and the technical basis for the settings to the Planning Coordinator. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner of nuclear units that have generator trip settings above the generator trip curve in Figure 2 shall provide evidence such as letters, reports and dated documentation that demonstrates that it meets Requirement R16. | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators 4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators | 163000000 | NPCC-US |  | NPCC-US
61 | 873 |  | 1. | 874 | INT-001-2 R1.1. | All Dynamic Schedules at the expected average MW profile for each hour. |  | PSE | [10 empty] | PSE | [11 empty] | 2007-06-18 |  | 2008-08-26 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
61 | 875 |  | 1. | 876 | INT-001-2 R2.1. | If a Purchasing-Selling Entity is not involved in the Interchange, such as delivery from a jointly owned generator. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
61 | 875 |  | 2. | 877 | INT-001-2 R2.2. | For each bilateral Inadvertent Interchange payback. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8984 | 8985 | 1. | 8986 | TPL-007-4 R4.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8984 | 8985 | 2. | 8987 | TPL-007-4 R4.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8984 | 8989 | 1. | 8990 | TPL-007-4 R4.3.1. | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 431000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8984 |  | 1. | 8985 | TPL-007-4 R4.1. | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. Part Applicability PCPA | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8984 |  | 2. | 8988 | TPL-007-4 R4.2. | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8984 |  | 3. | 8989 | TPL-007-4 R4.3. | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8991 |  | 1. | 8992 | TPL-007-4 R5.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8991 |  | 2. | 8993 | TPL-007-4 R5.2. | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8994 |  | 1. | 8995 | TPL-007-4 R6.1. | Be based on the effective GIC flow information provided in Requirement R5; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6 | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8994 |  | 2. | 8996 | TPL-007-4 R6.2. | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6 | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8994 |  | 3. | 8997 | TPL-007-4 R6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6 | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8994 |  | 4. | 8998 | TPL-007-4 R6.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6 | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8999 | 9002 | 1. | 9003 | TPL-007-4 R7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 731000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8999 | 9002 | 2. | 9004 | TPL-007-4 R7.3.2. | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 732000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8999 | 9005 | 1. | 9006 | TPL-007-4 R7.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1 and how those circumstances are beyond the control of the responsible entity; |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 741000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8999 | 9005 | 2. | 9007 | TPL-007-4 R7.4.2. | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures, if applicable; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 742000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8999 | 9005 | 3. | 9028 | TPL-007-4 R7.4.3. | Updated timetable for implementing the selected actions in Part 7.1. | [23 empty] | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 743000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8999 | 9008 | 1. | 9009 | TPL-007-4 R7.5.1. | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 751000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8999 |  | 1. | 9000 | TPL-007-4 R7.1. | 7.1. List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8999 |  | 2. | 9001 | TPL-007-4 R7.2. | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8999 |  | 3. | 9002 | TPL-007-4 R7.3. | Include a timetable, subject to approval for any extension sought under Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8999 |  | 4. | 9005 | TPL-007-4 R7.4. | Be submitted to the Compliance Enforcement Authority (CEA) with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. The submitted CAP shall document the following: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 8999 |  | 5. | 9008 | TPL-007-4 R7.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 750000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9010 | 9011 | 1. | 9012 | TPL-007-4 R8.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 811000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9010 | 9011 | 2. | 9013 | TPL-007-4 R8.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 812000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9010 | 9016 | 1. | 9017 | TPL-007-4 R8.3.1. | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 831000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9010 |  | 1. | 9011 | TPL-007-4 R8.1. | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9010 |  | 2. | 9014 | TPL-007-4 R8.2. | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9010 |  | 3. | 9016 | TPL-007-4 R8.3. | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9018 |  | 1. | 9019 | TPL-007-4 R9.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9018 |  | 2. | 9020 | TPL-007-4 R9.2. | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9021 |  | 1. | 9022 | TPL-007-4 R10.1. | Be based on the effective GIC flow information provided in Requirement R9; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9021 |  | 2. | 9023 | TPL-007-4 R10.2. | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9021 |  | 3. | 9024 | TPL-007-4 R10.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9021 |  | 4. | 9025 | TPL-007-4 R10.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9029 | 9032 | 1. | 9033 | TPL-007-4 R11.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 1131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9029 | 9032 | 2. | 9034 | TPL-007-4 R11.3.2. | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 1132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9029 | 9035 | 1. | 9036 | TPL-007-4 R11.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 11.1 and how those circumstances are beyond the control of the responsible entity; |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 1141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9029 | 9035 | 2. | 9037 | TPL-007-4 R11.4.2. | Revisions to the selected actions in Part 11.1, if any, including utilization of Operating Procedures, if applicable; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 1142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9029 | 9035 | 3. | 9038 | TPL-007-4 R11.4.3. | Updated timetable for implementing the selected actions in Part 11.1. | [23 empty] | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 1143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9029 | 9039 | 1. | 9040 | TPL-007-4 R11.5.1. | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 1151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9029 |  | 1. | 9030 | TPL-007-4 R11.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9029 |  | 2. | 9031 | TPL-007-4 R11.2. | Be developed within one year of completion of the supplemental GMD Vulnerability Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9029 |  | 3. | 9032 | TPL-007-4 R11.3. | Include a timetable, subject to approval for any extension sought under Part 11.4, for implementing the selected actions from Part 11.1. The timetable shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9029 |  | 4. | 9035 | TPL-007-4 R11.4. | Be submitted to the CEA with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. The submitted CAP shall document the following: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | 9029 |  | 5. | 9039 | TPL-007-4 R11.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | RQ-2021-07-12-0000001 |  | 1. | RP-2021-07-12-0000050 | TPL-007-4 D.A.7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of the later of the development of the CAP or receipt of regulatory approvals, if required; and |  | GO, PCPA, TO, TP |  |  |  |  | GO |  |  |  |  | PCPA | [7 empty] | TO |  | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.7.4 within 90 calendar days of revision. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 731000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
612 | RQ-2021-07-12-0000001 |  | 2. | RP-2021-07-12-0000051 | TPL-007-4 D.A.7.3.2. | Specify implementation of hardware mitigation, if any, within four years of the later of the development of the CAP or receipt of regulatory approvals, if required. |  | GO, PCPA, TO, TP |  |  |  |  | GO |  |  |  |  | PCPA | [7 empty] | TO |  | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.7.4 within 90 calendar days of revision. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 732000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US