83750000000570 | 837500000008096 |  | 2. | 837500000008098 | CIP-005-6 (Saskatchewan) R1.2. | All External Routable Connectivity must be through an identified Electronic Access Point (EAP). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, network diagrams showing all external routable communication paths and the identified EAPs. | 2020-10-01 |  | 2022-12-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000570 | 837500000008096 |  | 3. | 837500000008099 | CIP-005-6 (Saskatchewan) R1.3. | Require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of rules (firewall, access control lists, etc.) that demonstrate that only permitted access is allowed and that each access rule has a documented reason. | 2020-10-01 |  | 2022-12-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 130000000 | MRO-SK
83750000000570 | 837500000008096 |  | 4. | 837500000008100 | CIP-005-6 (Saskatchewan) R1.4. | Where technically feasible, perform authentication when establishing Dial-up Connectivity with applicable Cyber Assets. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a documented process that describes how the Responsible Entity is providing authenticated access through each dial-up connection. | 2020-10-01 |  | 2022-12-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000570 | 837500000008096 |  | 5. | 837500000008101 | CIP-005-6 (Saskatchewan) R1.5. | Have one or more methods for detecting known or suspected malicious communications for both inbound and outbound communications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation that malicious communications detection methods (e.g. intrusion detection system, application layer firewall, etc.) are implemented. | 2020-10-01 |  | 2022-12-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 150000000 | MRO-SK
83750000000570 | 837500000008102 |  | 1. | 837500000008103 | CIP-005-6 (Saskatchewan) R2.1. | For all Interactive Remote Access, utilize an Intermediate System such that the Cyber Asset initiating Interactive Remote Access does not directly access an applicable Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, network diagrams or architecture documents. | 2020-10-01 |  | 2022-12-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000570 | 837500000008102 |  | 2. | 837500000008104 | CIP-005-6 (Saskatchewan) R2.2. | For all Interactive Remote Access sessions, utilize encryption that terminates at an Intermediate System. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, architecture documents detailing where encryption initiates and terminates. | 2020-10-01 |  | 2022-12-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000570 | 837500000008102 |  | 3. | 837500000008105 | CIP-005-6 (Saskatchewan) R2.3. | Require multi-factor authentication for all Interactive Remote Access sessions. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, architecture documents detailing the authentication factors used. Examples of authenticators may include, but are not limited to, • Something the individual knows such as passwords or PINs. This does not include User ID; • Something the individual has such as tokens, digital certificates, or smart cards; or • Something the individual is such as fingerprints, iris scans, or other biometric characteristics. | 2020-10-01 |  | 2022-12-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000570 | 837500000008102 |  | 4. | 837500000008106 | CIP-005-6 (Saskatchewan) R2.4. | Have one or more methods for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods used to determine active vendor remote access (including Interactive Remote Access and system-to-system remote access), such as: • Methods for accessing logged or monitoring information to determine active vendor remote access sessions; • Methods for monitoring activity (e.g. connection tables or rule hit counters in a firewall, or user activity monitoring) or open ports (e.g. netstat or related commands to display currently active ports) to determine active system to system remote access sessions; or • Methods that control vendor initiation of remote access such as vendors calling and requesting a second factor in order to initiate remote access. | 2020-10-01 |  | 2022-12-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000570 | 837500000008102 |  | 5. | 837500000008107 | CIP-005-6 (Saskatchewan) R2.5. | Have one or more method(s) to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods(s) used to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access), such as: • Methods to disable vendor remote access at the applicable Electronic Access Point for system-to-system remote access; or • Methods to disable vendor Interactive Remote Access at the applicable Intermediate System. | 2020-10-01 |  | 2022-12-31 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000571 | 837500000008108 | 837500000008109 | 1. | 837500000008110 | CIP-010-3 (Saskatchewan) R1.1.1. | Operating system(s) (including version) or firmware where no independent operating system exists; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or • A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 111000000 | MRO-SK
83750000000571 | 837500000008108 | 837500000008109 | 2. | 837500000008111 | CIP-010-3 (Saskatchewan) R1.1.2. | Any commercially available or open-source application software (including version) intentionally installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or • A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 112000000 | MRO-SK
83750000000571 | 837500000008108 | 837500000008109 | 3. | 837500000008112 | CIP-010-3 (Saskatchewan) R1.1.3. | Any custom software installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or • A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 113000000 | MRO-SK
83750000000571 | 837500000008108 | 837500000008109 | 4. | 837500000008113 | CIP-010-3 (Saskatchewan) R1.1.4. | Any logical network accessible ports; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or • A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 114000000 | MRO-SK
83750000000571 | 837500000008108 | 837500000008109 | 5. | 837500000008114 | CIP-010-3 (Saskatchewan) R1.1.5. | Any security patches applied. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or • A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 115000000 | MRO-SK
83750000000571 | 837500000008108 | 837500000008117 | 1. | 837500000008118 | CIP-010-3 (Saskatchewan) R1.4.1. | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls verified or tested along with the dated test results. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 141000000 | MRO-SK
83750000000571 | 837500000008108 | 837500000008117 | 2. | 837500000008119 | CIP-010-3 (Saskatchewan) R1.4.2. | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls verified or tested along with the dated test results. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 142000000 | MRO-SK
83750000000571 | 837500000008108 | 837500000008117 | 3. | 837500000008120 | CIP-010-3 (Saskatchewan) R1.4.3. | Document the results of the verification. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls verified or tested along with the dated test results. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 143000000 | MRO-SK
83750000000571 | 837500000008108 | 837500000008121 | 1. | 837500000008122 | CIP-010-3 (Saskatchewan) R1.5.1. | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls tested along with successful test results and a list of differences between the production and test environments with descriptions of how any differences were accounted for, including of the date of the test. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 151000000 | MRO-SK
83750000000571 | 837500000008108 | 837500000008121 | 2. | 837500000008123 | CIP-010-3 (Saskatchewan) R1.5.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls tested along with successful test results and a list of differences between the production and test environments with descriptions of how any differences were accounted for, including of the date of the test. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 152000000 | MRO-SK
83750000000571 | 837500000008108 | 837500000008124 | 1. | 837500000008125 | CIP-010-3 (Saskatchewan) R1.6.1. | Verify the identity of the software source; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to a change request record that demonstrates the verification of identity of the software source and integrity of the software was performed prior to the baseline change or a process which documents the mechanisms in place that would automatically ensure the identity of the software source and integrity of the software. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 161000000 | MRO-SK
83750000000571 | 837500000008108 | 837500000008124 | 2. | 837500000008126 | CIP-010-3 (Saskatchewan) R1.6.2. | Verify the integrity of the software obtained from the software source. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to a change request record that demonstrates the verification of identity of the software source and integrity of the software was performed prior to the baseline change or a process which documents the mechanisms in place that would automatically ensure the identity of the software source and integrity of the software. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 162000000 | MRO-SK
83750000000571 | 837500000008108 |  | 1. | 837500000008109 | CIP-010-3 (Saskatchewan) R1.1. | Develop a baseline configuration, individually or by group, which shall include the following items: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or • A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000571 | 837500000008108 |  | 2. | 837500000008115 | CIP-010-3 (Saskatchewan) R1.2. | Authorize and document changes that deviate from the existing baseline configuration. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A change request record and associated electronic authorization (performed by the individual or group with the authority to authorize the change) in a change management system for each change; or • Documentation that the change was performed in accordance with the requirement. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000571 | 837500000008108 |  | 3. | 837500000008116 | CIP-010-3 (Saskatchewan) R1.3. | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, updated baseline documentation with a date that is within 30 calendar days of the date of the completion of the change. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000571 | 837500000008108 |  | 4. | 837500000008117 | CIP-010-3 (Saskatchewan) R1.4. | For a change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls verified or tested along with the dated test results. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000571 | 837500000008108 |  | 5. | 837500000008121 | CIP-010-3 (Saskatchewan) R1.5. | Where technically feasible, for each change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls tested along with successful test results and a list of differences between the production and test environments with descriptions of how any differences were accounted for, including of the date of the test. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 150000000 | MRO-SK
83750000000571 | 837500000008108 |  | 6. | 837500000008124 | CIP-010-3 (Saskatchewan) R1.6. | Prior to a change that deviates from the existing baseline configuration associated with baseline items in Parts 1.1.1, 1.1.2, and 1.1.5, and when the method to do so is available to the Responsible Entity from the software source: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to a change request record that demonstrates the verification of identity of the software source and integrity of the software was performed prior to the baseline change or a process which documents the mechanisms in place that would automatically ensure the identity of the software source and integrity of the software. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000571 | 837500000008127 |  | 1. | 837500000008128 | CIP-010-3 (Saskatchewan) R2.1. | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, logs from a system that is monitoring the configuration along with records of investigation for any unauthorized changes that were detected. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000571 | 837500000008129 | 837500000008131 | 1. | 837500000008132 | CIP-010-3 (Saskatchewan) R3.2.1. | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed at least once every 36 calendar months), the output of the tools used to perform the assessment, and a list of differences between the production and test environments with descriptions of how any differences were accounted for in conducting the assessment. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 321000000 | MRO-SK
83750000000571 | 837500000008129 | 837500000008131 | 2. | 837500000008133 | CIP-010-3 (Saskatchewan) R3.2.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed at least once every 36 calendar months), the output of the tools used to perform the assessment, and a list of differences between the production and test environments with descriptions of how any differences were accounted for in conducting the assessment. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 322000000 | MRO-SK
83750000000571 | 837500000008129 |  | 1. | 837500000008130 | CIP-010-3 (Saskatchewan) R3.1. | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A document listing the date of the assessment (performed at least once every 15 calendar months), the controls assessed for each BES Cyber System along with the method of assessment; or • A document listing the date of the assessment and the output of any tools used to perform the assessment. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000571 | 837500000008129 |  | 2. | 837500000008131 | CIP-010-3 (Saskatchewan) R3.2. | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed at least once every 36 calendar months), the output of the tools used to perform the assessment, and a list of differences between the production and test environments with descriptions of how any differences were accounted for in conducting the assessment. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 320000000 | MRO-SK
83750000000571 | 837500000008129 |  | 3. | 837500000008134 | CIP-010-3 (Saskatchewan) R3.3. | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed prior to the commissioning of the new Cyber Asset) and the output of any tools used to perform the assessment. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000571 | 837500000008129 |  | 4. | 837500000008135 | CIP-010-3 (Saskatchewan) R3.4. | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the results or the review or assessment, a list of action items, documented proposed dates of completion for the action plan, and records of the status of the action items (such as minutes of a status meeting, updates in a work order system, or a spreadsheet tracking the action items). | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-3: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000583 | 837500000008395 | 837500000008396 | 1. | 837500000008397 | PER-003-2 (Saskatchewan) R1.1.1. | Resource and demand balancing |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 111000000 | MRO-SK
83750000000583 | 837500000008395 | 837500000008396 | 2. | 837500000008398 | PER-003-2 (Saskatchewan) R1.1.2. | Transmission operations |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 |  |  |  |  | 112000000 | MRO-SK
83750000000583 | 837500000008395 | 837500000008396 | 3. | 837500000008399 | PER-003-2 (Saskatchewan) R1.1.3. | Emergency preparedness and operations |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 113000000 | MRO-SK
83750000000583 | 837500000008395 | 837500000008396 | 4. | 837500000008400 | PER-003-2 (Saskatchewan) R1.1.4. | System operations |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 114000000 | MRO-SK
83750000000583 | 837500000008395 | 837500000008396 | 5. | 837500000008401 | PER-003-2 (Saskatchewan) R1.1.5. | Protection and control |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 115000000 | MRO-SK
83750000000583 | 837500000008395 | 837500000008396 | 6. | 837500000008402 | PER-003-2 (Saskatchewan) R1.1.6. | Voltage and reactive |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 |  |  |  |  | 116000000 | MRO-SK
83750000000583 | 837500000008395 | 837500000008396 | 7. | 837500000008403 | PER-003-2 (Saskatchewan) R1.1.7. | Interchange scheduling and coordination |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 117000000 | MRO-SK
83750000000583 | 837500000008395 | 837500000008396 | 8. | 837500000008404 | PER-003-2 (Saskatchewan) R1.1.8. | Interconnection reliability operations and coordination |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 118000000 | MRO-SK
83750000000583 | 837500000008395 |  | 1. | 837500000008396 | PER-003-2 (Saskatchewan) R1.1. | Areas of Competency |  | RC | [11 empty] | RC | [9 empty] | Each Reliability Coordinator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M1.1 A list of Real-time operating positions. M1.2 A list of System Operators assigned to its Real-time operating positions. M1.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M1.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000583 | 837500000008405 | 837500000008406 | 1. | 837500000008407 | PER-003-2 (Saskatchewan) R2.1.1. | Transmission operations |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 |  |  |  |  | 211000000 | MRO-SK
83750000000583 | 837500000008405 | 837500000008406 | 2. | 837500000008408 | PER-003-2 (Saskatchewan) R2.1.2. | Emergency preparedness and operations |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 212000000 | MRO-SK
83750000000583 | 837500000008405 | 837500000008406 | 3. | 837500000008409 | PER-003-2 (Saskatchewan) R2.1.3. | System operations |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 213000000 | MRO-SK
83750000000583 | 837500000008405 | 837500000008406 | 4. | 837500000008410 | PER-003-2 (Saskatchewan) R2.1.4. | Protection and control |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 214000000 | MRO-SK
83750000000583 | 837500000008405 | 837500000008406 | 5. | 837500000008411 | PER-003-2 (Saskatchewan) R2.1.5. | Voltage and reactive |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 |  |  |  |  | 215000000 | MRO-SK
83750000000583 | 837500000008405 |  | 1. | 837500000008406 | PER-003-2 (Saskatchewan) R2.1. | Areas of Competency |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 210000000 | MRO-SK
83750000000583 | 837500000008405 |  | 2. | 837500000008412 | PER-003-2 (Saskatchewan) R2.2. | Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M2.1 A list of Real-time operating positions. M2.2 A list of System Operators assigned to its Real-time operating positions. M2.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. M2.4 Work schedules, work logs, or other equivalent evidence showing which System Operators were assigned to work in Real-time operating positions. | 2019-07-01 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000583 | 837500000008413 | 837500000008414 | 1. | 837500000008415 | PER-003-2 (Saskatchewan) R3.1.1. | Resources and demand balancing |  | BA | BA | [20 empty] | Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. | 2019-07-01 |  |  |  |  | 311000000 | MRO-SK
83750000000583 | 837500000008413 | 837500000008414 | 2. | 837500000008416 | PER-003-2 (Saskatchewan) R3.1.2. | Emergency preparedness and operations |  | BA | BA | [20 empty] | Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. | 2019-07-01 |  |  |  |  | 312000000 | MRO-SK
83750000000583 | 837500000008413 | 837500000008414 | 3. | 837500000008417 | PER-003-2 (Saskatchewan) R3.1.3. | System operations |  | BA | BA | [20 empty] | Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. | 2019-07-01 |  |  |  |  | 313000000 | MRO-SK
83750000000583 | 837500000008413 | 837500000008414 | 4. | 837500000008418 | PER-003-2 (Saskatchewan) R3.1.4. | Interchange scheduling and coordination |  | BA | BA | [20 empty] | Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. | 2019-07-01 |  |  |  |  | 314000000 | MRO-SK
83750000000583 | 837500000008413 |  | 1. | 837500000008414 | PER-003-2 (Saskatchewan) R3.1. | Areas of Competency |  | BA | BA | [20 empty] | Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. | 2019-07-01 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000583 | 837500000008413 |  | 2. | 837500000008419 | PER-003-2 (Saskatchewan) R3.2. | Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator |  | BA | BA | [20 empty] | Each Balancing Authority shall have the following evidence to show that it staffed its Real-time operating positions performing reliability-related tasks with System Operators who have demonstrated the applicable minimum competency by obtaining and maintaining the appropriate, valid NERC certificate: M3.1 A list of Real-time operating positions. M3.2 A list of System Operators assigned to its Real-time operating positions. M3.3 A copy of each of its System Operator’s NERC certificate or NERC certificate number with expiration date which demonstrates compliance with the applicable Areas of Competency. | 2019-07-01 |  |  |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000585 | 837500000008421 | 837500000008425 | 1. | 837500000008426 | BAL-002-3 (Saskatchewan) R1.3.1. | is (i) a Balancing Authority or (ii) a Reserve Sharing Group with at least one member that: • is experiencing a Reliability Coordinator declared Energy Emergency Alert Level, and • is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and • has depleted its Contingency Reserve to a level below its Most Severe Single Contingency, and • has, during communications with its Reliability Coordinator in accordance with the Energy Emergency Alert procedures, (i) notified the Reliability Coordinator of the conditions described in the preceding two bullet points preventing the Responsible Entity from complying with Requirement R1 part 1.1, and (ii) provided the Reliability Coordinator with an ACE recovery plan, including target recovery time or, |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2019-10-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. | 131000000 | MRO-SK
83750000000585 | 837500000008421 | 837500000008425 | 2. | 837500000008427 | BAL-002-3 (Saskatchewan) R1.3.2. | the Responsible Entity experiences: • multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2019-10-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. | 132000000 | MRO-SK
83750000000585 | 837500000008421 |  | 1. | 837500000008423 | BAL-002-3 (Saskatchewan) R1.1. | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of: • zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or, • its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2019-10-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000585 | 837500000008421 |  | 2. | 837500000008424 | BAL-002-3 (Saskatchewan) R1.2. | document all Reportable Balancing Contingency Events using CR Form 1. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2019-10-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. | 120000000 | MRO-SK
83750000000585 | 837500000008421 |  | 3. | 837500000008425 | BAL-002-3 (Saskatchewan) R1.3. | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if the Responsible Entity |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2019-10-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000586 | 837500000008429 |  | 1. | 837500000008430 | CIP-012-1 (Saskatchewan) R1.1. | Identification of security protection used to mitigate the risks posed by unauthorized disclosure and unauthorized modification of Real-time Assessment and Real-time monitoring data while being transmitted between Control Centers; |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | M1. Evidence may include, but is not limited to, documented plan(s) that meet the security objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). | 2022-07-01 |  |  |  | 4.2. Exemptions: The following are exempt from Reliability Standard CIP-012-1: 4.2.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.2. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3. A Control Center that transmits to another Control Center Real-time Assessment or Real-time monitoring data pertaining only to the generation resource or Transmission station or substation co-located with the transmitting Control Center. | 110000000 | MRO-SK
83750000000586 | 837500000008429 |  | 2. | 837500000008431 | CIP-012-1 (Saskatchewan) R1.2. | Identification of where the Responsible Entity applied security protection for transmitting Real-time Assessment and Real-time monitoring data between Control Centers; and |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | M1. Evidence may include, but is not limited to, documented plan(s) that meet the security objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). | 2022-07-01 |  |  |  | 4.2. Exemptions: The following are exempt from Reliability Standard CIP-012-1: 4.2.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.2. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3. A Control Center that transmits to another Control Center Real-time Assessment or Real-time monitoring data pertaining only to the generation resource or Transmission station or substation co-located with the transmitting Control Center. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000586 | 837500000008429 |  | 3. | 837500000008432 | CIP-012-1 (Saskatchewan) R1.3. | If the Control Centers are owned or operated by different Responsible Entities, identification of the responsibilities of each Responsible Entity for applying security protection to the transmission of Real-time Assessment and Real-time monitoring data between those Control Centers. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | M1. Evidence may include, but is not limited to, documented plan(s) that meet the security objective of Requirement R1 and documentation demonstrating the implementation of the plan(s). | 2022-07-01 |  |  |  | 4.2. Exemptions: The following are exempt from Reliability Standard CIP-012-1: 4.2.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.2. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3. A Control Center that transmits to another Control Center Real-time Assessment or Real-time monitoring data pertaining only to the generation resource or Transmission station or substation co-located with the transmitting Control Center. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000590 | 837500000008514 | 837500000008520 | 1. | 837500000008521 | CIP-008-6 (Saskatchewan) R1.2.1. | That include criteria to evaluate and define attempts to compromise; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of Cyber Security Incident response plan(s) that provide guidance or thresholds for determining which Cyber Security Incidents are also Reportable Cyber Security Incidents or a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the “Applicable Systems” column including justification for attempt determination criteria and documented processes for notification. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 121000000 | MRO-SK
83750000000590 | 837500000008514 | 837500000008520 | 2. | 837500000008522 | CIP-008-6 (Saskatchewan) R1.2.2. | To determine if an identified Cyber Security Incident is: • A Reportable Cyber Security Incident; or • An attempt to compromise, as determined by applying the criteria from Part 1.2.1, one or more systems identified in the “Applicable Systems” column for this Part; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of Cyber Security Incident response plan(s) that provide guidance or thresholds for determining which Cyber Security Incidents are also Reportable Cyber Security Incidents or a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the “Applicable Systems” column including justification for attempt determination criteria and documented processes for notification. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 122000000 | MRO-SK
83750000000590 | 837500000008514 | 837500000008520 | 3. | 837500000008523 | CIP-008-6 (Saskatchewan) R1.2.3. | To provide notification per Requirement R4. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of Cyber Security Incident response plan(s) that provide guidance or thresholds for determining which Cyber Security Incidents are also Reportable Cyber Security Incidents or a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the “Applicable Systems” column including justification for attempt determination criteria and documented processes for notification. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 123000000 | MRO-SK
83750000000590 | 837500000008514 |  | 1. | 837500000008519 | CIP-008-6 (Saskatchewan) R1.1. | One or more processes to identify, classify, and respond to Cyber Security Incidents. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated documentation of Cyber Security Incident response plan(s) that include the process(es) to identify, classify, and respond to Cyber Security Incidents. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000590 | 837500000008514 |  | 2. | 837500000008520 | CIP-008-6 (Saskatchewan) R1.2. | One or more processes: |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of Cyber Security Incident response plan(s) that provide guidance or thresholds for determining which Cyber Security Incidents are also Reportable Cyber Security Incidents or a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the “Applicable Systems” column including justification for attempt determination criteria and documented processes for notification. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000590 | 837500000008514 |  | 3. | 837500000008524 | CIP-008-6 (Saskatchewan) R1.3. | The roles and responsibilities of Cyber Security Incident response groups or individuals. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated Cyber Security Incident response process(es) or procedure(s) that define roles and responsibilities (e.g., monitoring, reporting, initiating, documenting, etc.) of Cyber Security Incident response groups or individuals. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 130000000 | MRO-SK
83750000000590 | 837500000008514 |  | 4. | 837500000008525 | CIP-008-6 (Saskatchewan) R1.4. | Incident handling procedures for Cyber Security Incidents. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated Cyber Security Incident response process(es) or procedure(s) that address incident handling (e.g., containment, eradication, recovery/incident resolution). | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000590 | 837500000008526 |  | 1. | 837500000008527 | CIP-008-6 (Saskatchewan) R2.1. | Test each Cyber Security Incident response plan(s) at least once every 15 calendar months: • By responding to an actual Reportable Cyber Security Incident; • With a paper drill or tabletop exercise of a Reportable Cyber Security Incident; or • With an operational exercise of a Reportable Cyber Security Incident. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated evidence of a lessons-learned report that includes a summary of the test or a compilation of notes, logs, and communication resulting from the test. Types of exercises may include discussion or operations based exercises. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000590 | 837500000008526 |  | 2. | 837500000008528 | CIP-008-6 (Saskatchewan) R2.2. | Use the Cyber Security Incident response plan(s) under Requirement R1 when responding to a Reportable Cyber Security Incident, responding to a Cyber Security Incident that attempted to compromise a system identified in the “Applicable Systems” column for this Part, or performing an exercise of a Reportable Cyber Security Incident. Document deviations from the plan(s) taken during the response to the incident or exercise. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, incident reports, logs, and notes that were kept during the incident response process, and follow-up documentation that describes deviations taken from the plan during the incident response or exercise. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000590 | 837500000008526 |  | 3. | 837500000008529 | CIP-008-6 (Saskatchewan) R2.3. | Retain records related to Reportable Cyber Security Incidents and Cyber Security Incidents that attempted to compromise a system identified in the “Applicable Systems” column for this Part as per the Cyber Security Incident response plan(s) under Requirement R1. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated documentation, such as security logs, police reports, emails, response forms or checklists, forensic analysis results, restoration records, and post-incident review notes related to Reportable Cyber Security Incidents and a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the “Applicable Systems” column. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000590 | 837500000008530 | 837500000008532 | 1. | 837500000008533 | CIP-008-6 (Saskatchewan) R3.1.1. | Document any lessons learned or document the absence of any lessons learned; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following: 1. Dated documentation of post incident(s) review meeting notes or follow-up report showing lessons learned associated with the Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response or dated documentation stating there were no lessons learned; 2. Dated and revised Cyber Security Incident response plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 311000000 | MRO-SK
83750000000590 | 837500000008530 | 837500000008532 | 2. | 837500000008534 | CIP-008-6 (Saskatchewan) R3.1.2. | Update the Cyber Security Incident response plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following: 1. Dated documentation of post incident(s) review meeting notes or follow-up report showing lessons learned associated with the Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response or dated documentation stating there were no lessons learned; 2. Dated and revised Cyber Security Incident response plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 312000000 | MRO-SK
83750000000590 | 837500000008530 | 837500000008532 | 3. | 837500000008535 | CIP-008-6 (Saskatchewan) R3.1.3. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates to the Cyber Security Incident response plan based on any documented lessons learned. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following: 1. Dated documentation of post incident(s) review meeting notes or follow-up report showing lessons learned associated with the Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response or dated documentation stating there were no lessons learned; 2. Dated and revised Cyber Security Incident response plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 313000000 | MRO-SK
83750000000590 | 837500000008530 | 837500000008536 | 1. | 837500000008537 | CIP-008-6 (Saskatchewan) R3.2.1. | Update the Cyber Security Incident response plan(s); and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 321000000 | MRO-SK
83750000000590 | 837500000008530 | 837500000008536 | 2. | 837500000008538 | CIP-008-6 (Saskatchewan) R3.2.2. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 322000000 | MRO-SK
83750000000590 | 837500000008530 |  | 1. | 837500000008532 | CIP-008-6 (Saskatchewan) R3.1. | No later than 90 calendar days after completion of a Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following: 1. Dated documentation of post incident(s) review meeting notes or follow-up report showing lessons learned associated with the Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response or dated documentation stating there were no lessons learned; 2. Dated and revised Cyber Security Incident response plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000590 | 837500000008530 |  | 2. | 837500000008536 | CIP-008-6 (Saskatchewan) R3.2. | No later than 60 calendar days after a change to the roles or responsibilities, Cyber Security Incident response groups or individuals, or technology that the Responsible Entity determines would impact the ability to execute the plan: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: • Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 320000000 | MRO-SK
83750000000590 | 837500000008531 | 837500000008539 | 1. | 837500000008540 | CIP-008-6 (Saskatchewan) R4.1.1. | The functional impact; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of initial notifications and updates to the E-ISAC and NCCIC. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 411000000 | MRO-SK
83750000000590 | 837500000008531 | 837500000008539 | 2. | 837500000008541 | CIP-008-6 (Saskatchewan) R4.1.2. | The attack vector used; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of initial notifications and updates to the E-ISAC and NCCIC. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 412000000 | MRO-SK
83750000000590 | 837500000008531 | 837500000008539 | 3. | 837500000008542 | CIP-008-6 (Saskatchewan) R4.1.3. | The level of intrusion that was achieved or attempted. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of initial notifications and updates to the E-ISAC and NCCIC. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 413000000 | MRO-SK
83750000000590 | 837500000008531 |  | 1. | 837500000008539 | CIP-008-6 (Saskatchewan) R4.1. | Initial notifications and updates shall include the following attributes, at a minimum, to the extent known: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of initial notifications and updates to the E-ISAC and NCCIC. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000590 | 837500000008531 |  | 2. | 837500000008543 | CIP-008-6 (Saskatchewan) R4.2. | After the Responsible Entity’s determination made pursuant to documented process(es) in Requirement R1, Part 1.2, provide initial notification within the following timelines: • One hour after the determination of a Reportable Cyber Security Incident. • By the end of the next calendar day after determination that a Cyber Security Incident was an attempt to compromise a system identified in the “Applicable Systems” column for this Part. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of notices to the E-ISAC and NCCIC. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000590 | 837500000008531 |  | 3. | 837500000008544 | CIP-008-6 (Saskatchewan) R4.3. | Provide updates, if any, within 7 calendar days of determination of new or changed attribute information required in Part 4.1. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of submissions to the E-ISAC and NCCIC. | 2021-04-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that: 4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008551 | 837500000008552 | 1. | 837500000008553 | TPL-007-3 (Saskatchewan) R4.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 411000000 | MRO-SK
83750000000593 | 837500000008551 | 837500000008552 | 2. | 837500000008554 | TPL-007-3 (Saskatchewan) R4.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 412000000 | MRO-SK
83750000000593 | 837500000008551 | 837500000008556 | 1. | 837500000008557 | TPL-007-3 (Saskatchewan) R4.3.1. | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 431000000 | MRO-SK
83750000000593 | 837500000008551 |  | 1. | 837500000008552 | TPL-007-3 (Saskatchewan) R4.1. | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008551 |  | 2. | 837500000008555 | TPL-007-3 (Saskatchewan) R4.2. | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008551 |  | 3. | 837500000008556 | TPL-007-3 (Saskatchewan) R4.3. | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008558 |  | 1. | 837500000008559 | TPL-007-3 (Saskatchewan) R5.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008558 |  | 2. | 837500000008560 | TPL-007-3 (Saskatchewan) R5.2. | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008561 |  | 1. | 837500000008565 | TPL-007-3 (Saskatchewan) R6.1. | Be based on the effective GIC flow information provided in Requirement R5; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008561 |  | 2. | 837500000008566 | TPL-007-3 (Saskatchewan) R6.2. | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008561 |  | 3. | 837500000008567 | TPL-007-3 (Saskatchewan) R6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008561 |  | 4. | 837500000008568 | TPL-007-3 (Saskatchewan) R6.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008569 | 837500000008573 | 1. | 837500000008577 | TPL-007-3 (Saskatchewan) R7.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1; |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 741000000 | MRO-SK
83750000000593 | 837500000008569 | 837500000008573 | 2. | 837500000008578 | TPL-007-3 (Saskatchewan) R7.4.2. | Description of the original CAP, and any previous changes to the CAP, with the associated timetable(s) for implementing the selected actions in Part 7.1; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 742000000 | MRO-SK
83750000000593 | 837500000008569 | 837500000008573 | 3. | 837500000008579 | TPL-007-3 (Saskatchewan) R7.4.3. | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures if applicable, and the updated timetable for implementing the selected actions. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 743000000 | MRO-SK
83750000000593 | 837500000008569 | 837500000008574 | 1. | 837500000008580 | TPL-007-3 (Saskatchewan) R7.5.1. | If a recipient of the CAP provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 751000000 | MRO-SK
83750000000593 | 837500000008569 | 837500000008648 | 1. | 837500000008649 | TPL-007-3 (Saskatchewan) R7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of the later of the development of the CAP or receipt of regulatory approvals, if required; and | [24 empty] | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 731000000 | MRO-SK
83750000000593 | 837500000008569 | 837500000008648 | 2. | 837500000008650 | TPL-007-3 (Saskatchewan) R7.3.2. | Specify implementation of hardware mitigation, if any, within four years of the later of the development of the CAP or receipt of regulatory approvals, if required. | [24 empty] | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 732000000 | MRO-SK
83750000000593 | 837500000008569 |  | 1. | 837500000008570 | TPL-007-3 (Saskatchewan) R7.1. | 7.1. List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008569 |  | 2. | 837500000008571 | TPL-007-3 (Saskatchewan) R7.2. | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008569 |  | 3. | 837500000008648 | TPL-007-3 (Saskatchewan) R7.3. | Include a timetable, subject to revision by the responsible entity in Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: | [24 empty] | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 730000000 | MRO-SK
83750000000593 | 837500000008569 |  | 4. | 837500000008573 | TPL-007-3 (Saskatchewan) R7.4. | Be revised if situations beyond the control of the responsible entity determined in Requirement R1 prevent implementation of the CAP within the timetable for implementation provided in Part 7.3. The revised CAP shall document the following, and be updated at least once every 12 calendar months until implemented: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 740000000 | MRO-SK
83750000000593 | 837500000008569 |  | 5. | 837500000008574 | TPL-007-3 (Saskatchewan) R7.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 750000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008581 | 837500000008582 | 1. | 837500000008586 | TPL-007-3 (Saskatchewan) R8.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 811000000 | MRO-SK
83750000000593 | 837500000008581 | 837500000008582 | 2. | 837500000008587 | TPL-007-3 (Saskatchewan) R8.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 812000000 | MRO-SK
83750000000593 | 837500000008581 | 837500000008585 | 1. | 837500000008588 | TPL-007-3 (Saskatchewan) R8.4.1. | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 841000000 | MRO-SK
83750000000593 | 837500000008581 |  | 1. | 837500000008582 | TPL-007-3 (Saskatchewan) R8.1. | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008581 |  | 2. | 837500000008583 | TPL-007-3 (Saskatchewan) R8.2. | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008581 |  | 3. | 837500000008584 | TPL-007-3 (Saskatchewan) R8.3. | If the analysis concludes there is Cascading caused by the supplemental GMD event described in Attachment 1, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008581 |  | 4. | 837500000008585 | TPL-007-3 (Saskatchewan) R8.4. | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 840000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008589 |  | 1. | 837500000008590 | TPL-007-3 (Saskatchewan) R9.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008589 |  | 2. | 837500000008591 | TPL-007-3 (Saskatchewan) R9.2. | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 920000000 | MRO-SK
83750000000593 | 837500000008592 |  | 1. | 837500000008598 | TPL-007-3 (Saskatchewan) R10.1. | Be based on the effective GIC flow information provided in Requirement R9; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008592 |  | 2. | 837500000008599 | TPL-007-3 (Saskatchewan) R10.2. | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008592 |  | 3. | 837500000008600 | TPL-007-3 (Saskatchewan) R10.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008592 |  | 4. | 837500000008601 | TPL-007-3 (Saskatchewan) R10.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2020-01-01 |  | 2021-03-31 |  | 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000593 | 837500000008978 |  | 1. | 837500000008979 | TPL-007-3 (Saskatchewan) D.A.7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of the later of the development of the CAP or receipt of regulatory approvals, if required; and | [24 empty] | 2020-01-01 |  | 2021-03-31 |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 731000000 | MRO-SK
83750000000593 | 837500000008978 |  | 2. | 837500000008980 | TPL-007-3 (Saskatchewan) D.A.7.3.2. | Specify implementation of hardware mitigation, if any, within four years of the later of the development of the CAP or receipt of regulatory approvals, if required. | [24 empty] | 2020-01-01 |  | 2021-03-31 |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 732000000 | MRO-SK
83750000000597 | 837500000008679 | 837500000008680 | 1. | 837500000008681 | CIP-003-8 (Saskatchewan) R1.1.1. | Personnel and training (CIP-004); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 111000000 | MRO-SK
83750000000597 | 837500000008679 | 837500000008680 | 2. | 837500000008682 | CIP-003-8 (Saskatchewan) R1.1.2. | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 112000000 | MRO-SK
83750000000597 | 837500000008679 | 837500000008680 | 3. | 837500000008683 | CIP-003-8 (Saskatchewan) R1.1.3. | Physical security of BES Cyber Systems (CIP-006); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 113000000 | MRO-SK
83750000000597 | 837500000008679 | 837500000008680 | 4. | 837500000008684 | CIP-003-8 (Saskatchewan) R1.1.4. | System security management (CIP-007); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 114000000 | MRO-SK
83750000000597 | 837500000008679 | 837500000008680 | 5. | 837500000008685 | CIP-003-8 (Saskatchewan) R1.1.5. | Incident reporting and response planning (CIP-008); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 115000000 | MRO-SK
83750000000597 | 837500000008679 | 837500000008680 | 6. | 837500000008686 | CIP-003-8 (Saskatchewan) R1.1.6. | Recovery plans for BES Cyber Systems (CIP-009); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 116000000 | MRO-SK
83750000000597 | 837500000008679 | 837500000008680 | 7. | 837500000008687 | CIP-003-8 (Saskatchewan) R1.1.7. | Configuration change management and vulnerability assessments (CIP-010); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 117000000 | MRO-SK
83750000000597 | 837500000008679 | 837500000008680 | 8. | 837500000008688 | CIP-003-8 (Saskatchewan) R1.1.8. | Information protection (CIP-011); and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 118000000 | MRO-SK
83750000000597 | 837500000008679 | 837500000008680 | 9. | 837500000008689 | CIP-003-8 (Saskatchewan) R1.1.9. | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 119000000 | MRO-SK
83750000000597 | 837500000008679 | 837500000008690 | 1. | 837500000008691 | CIP-003-8 (Saskatchewan) R1.2.1. | Cyber security awareness; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 121000000 | MRO-SK
83750000000597 | 837500000008679 | 837500000008690 | 2. | 837500000008692 | CIP-003-8 (Saskatchewan) R1.2.2. | Physical security controls; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 122000000 | MRO-SK
83750000000597 | 837500000008679 | 837500000008690 | 3. | 837500000008693 | CIP-003-8 (Saskatchewan) R1.2.3. | Electronic access controls; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 123000000 | MRO-SK
83750000000597 | 837500000008679 | 837500000008690 | 4. | 837500000008694 | CIP-003-8 (Saskatchewan) R1.2.4. | Cyber Security Incident response; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 124000000 | MRO-SK
83750000000597 | 837500000008679 | 837500000008690 | 5. | 837500000008695 | CIP-003-8 (Saskatchewan) R1.2.5. | Transient Cyber Assets and Removable Media malicious code risk mitigation; and | [23 empty] | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 125000000 | MRO-SK
83750000000597 | 837500000008679 | 837500000008690 | 6. | 837500000008696 | CIP-003-8 (Saskatchewan) R1.2.6. | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 126000000 | MRO-SK
83750000000597 | 837500000008679 |  | 1. | 837500000008680 | CIP-003-8 (Saskatchewan) R1.1. | For its high impact and medium impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000597 | 837500000008679 |  | 2. | 837500000008690 | CIP-003-8 (Saskatchewan) R1.2. | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2020-10-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000598 | 837500000008703 |  | 1. | 837500000008705 | INT-006-5 (Saskatchewan) R1.1. | Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. |  | BA | BA | [20 empty] | Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it responded to each request for its approval to transition an Arranged Interchange to a Confirmed Interchange within the time defined in Attachment 1, Column B. (R1) | 2021-04-01 |  |  |  |  | 110000000 | MRO-SK
83750000000598 | 837500000008703 |  | 2. | 837500000008706 | INT-006-5 (Saskatchewan) R1.2. | Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. |  | BA | BA | [20 empty] | Each Balancing Authority shall have evidence (such as dated and time stamped electronic logs, or other evidence) that it responded to each request for its approval to transition an Arranged Interchange to a Confirmed Interchange within the time defined in Attachment 1, Column B. (R1) | 2021-04-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000598 | 837500000008704 |  | 1. | 837500000008707 | INT-006-5 (Saskatchewan) R2.1. | Each Transmission Service Provider shall deny the Arranged Interchange or curtail Confirmed Interchange if the transmission path (proper connectivity of adjacent Transmission Service Providers) between it and its adjacent Transmission Service Providers is invalid. |  | TSP | [20 empty] | TSP | Each Transmission Service Provider shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that it responded to each Arranged Interchange or emergency Arranged Interchange within the time defined in Attachment 1, Column B. If the transmission path between the Transmission Service Provider and its adjacent Transmission Service Providers is invalid, each Transmission Service Provider shall have evidence (such as dated and time stamped electronic logs, studies, or other evidence) that it denied the Arranged Interchange or curtailed confirmed Interchange. (R2) | 2021-04-01 |  |  |  |  | 210000000 | MRO-SK
83750000000599 | 837500000008711 |  | 1. | 837500000008712 | INT-009-3 (Saskatchewan) R1.1. | Identical in magnitude to that of the Adjacent Balancing Authority, and |  | BA | BA | [20 empty] | The Balancing Authority shall have evidence (such as dated logs, voice recordings, electronic records, or other evidence) that its Composite Confirmed Interchange, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange not yet captured in the Composite Confirmed Interchange, was agreed to by each Adjacent Balancing Authority, identical in magnitude to those of each Adjacent Balancing Authority, and opposite in sign to that of each Adjacent Balancing Authority. (R1) | 2021-04-01 |  |  |  |  | 110000000 | MRO-SK
83750000000599 | 837500000008711 |  | 2. | 837500000008713 | INT-009-3 (Saskatchewan) R1.2. | Opposite in sign or direction to that of the Adjacent Balancing Authority |  | BA | BA | [20 empty] | The Balancing Authority shall have evidence (such as dated logs, voice recordings, electronic records, or other evidence) that its Composite Confirmed Interchange, excluding Dynamic Schedules and Pseudo-Ties and including any Interchange not yet captured in the Composite Confirmed Interchange, was agreed to by each Adjacent Balancing Authority, identical in magnitude to those of each Adjacent Balancing Authority, and opposite in sign to that of each Adjacent Balancing Authority. (R1) | 2021-04-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000601 | 837500000008746 |  | 1. | 837500000008747 | PRC-004-6 (Saskatchewan) R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000601 | 837500000008746 |  | 2. | 837500000008748 | PRC-004-6 (Saskatchewan) R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 120000000 | MRO-SK
83750000000601 | 837500000008746 |  | 3. | 837500000008749 | PRC-004-6 (Saskatchewan) R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates it identified the Misoperation of its Protection System component(s), if any, that meet the circumstances in Requirement R1, Parts 1.1, 1.2, and 1.3 within the allotted time period. Acceptable evidence for Requirement R1, including Parts 1.1, 1.2, and 1.3 may include, but is not limited to the following dated documentation (electronic or hardcopy format): reports, databases, spreadsheets, emails, facsimiles, lists, logs, records, declarations, analyses of sequence of events, relay targets, Disturbance Monitoring Equipment (DME) records, test results, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000601 | 837500000008750 | 837500000008751 | 1. | 837500000008752 | PRC-004-6 (Saskatchewan) R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 211000000 | MRO-SK
83750000000601 | 837500000008750 | 837500000008751 | 2. | 837500000008753 | PRC-004-6 (Saskatchewan) R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 212000000 | MRO-SK
83750000000601 | 837500000008750 | 837500000008751 | 3. | 837500000008754 | PRC-004-6 (Saskatchewan) R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 213000000 | MRO-SK
83750000000601 | 837500000008750 |  | 1. | 837500000008751 | PRC-004-6 (Saskatchewan) R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 210000000 | MRO-SK
83750000000601 | 837500000008750 |  | 2. | 837500000008755 | PRC-004-6 (Saskatchewan) R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner, Generator Owner, and Distribution Provider shall have dated evidence that demonstrates notification to the other owner(s), within the allotted time period for either Requirement R2, Part 2.1, including subparts 2.1.1, 2.1.2, and 2.1.3 and Requirement R2, Part 2.2. Acceptable evidence for Requirement R2, including Parts 2.1 and 2.2 may include, but is not limited to the following dated documentation (electronic or hardcopy format): emails, facsimiles, or transmittals. | 2021-04-01 |  |  |  | 4.2. Facilities: 4.2.1 Protection Systems for BES Elements, with the following exclusions: 4.2.1.1 Non-protective functions that are embedded within a Protection System. 4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS). 4.2.1.4 Remedial Action Schemes (RAS). 4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities. 4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements. 4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000603 | 837500000008771 |  | 1. | 837500000008772 | TOP-001-5 (Saskatchewan) R10.1. | Monitor Facilities within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-04-01 |  | 2024-03-31 |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000603 | 837500000008771 |  | 2. | 837500000008773 | TOP-001-5 (Saskatchewan) R10.2. | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-04-01 |  | 2024-03-31 |  |  | 102000000 | MRO-SK
83750000000603 | 837500000008771 |  | 3. | 837500000008774 | TOP-001-5 (Saskatchewan) R10.3. | Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-04-01 |  | 2024-03-31 |  |  | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000603 | 837500000008771 |  | 4. | 837500000008775 | TOP-001-5 (Saskatchewan) R10.4. | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-04-01 |  | 2024-03-31 |  |  | 104000000 | MRO-SK
83750000000603 | 837500000008771 |  | 5. | 837500000008776 | TOP-001-5 (Saskatchewan) R10.5. | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-04-01 |  | 2024-03-31 |  |  | 105000000 | MRO-SK
83750000000603 | 837500000008771 |  | 6. | 837500000008777 | TOP-001-5 (Saskatchewan) R10.6. | Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2021-04-01 |  | 2024-03-31 |  |  | 106000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000607 | 837500000008845 |  | 1. | 837500000008847 | BAL-003-2 (Saskatchewan) R3.1. | Less than zero at all times, and |  | BA | BA | [20 empty] | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2020-12-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000607 | 837500000008845 |  | 2. | 837500000008848 | BAL-003-2 (Saskatchewan) R3.2. | Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. |  | BA | BA | [20 empty] | The Balancing Authority that is a member of a multiple Balancing Authority Interconnection, is not receiving Overlap Regulation Service and is utilizing variable Frequency Bias shall have evidence such as a dated report in hard copy or electronic format showing the average clock-minute average Frequency Bias Setting was less than zero and during periods when the clock-minute average frequency was outside of the range 59.964 Hz to 60.036 Hz was equal to or more negative than its Frequency Response Obligation to demonstrate compliance with Requirement R3. | 2020-12-01 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000008984 | 837500000008985 | 1. | 837500000008986 | TPL-007-4 (Saskatchewan) R4.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 411000000 | MRO-SK
83750000000612 | 837500000008984 | 837500000008985 | 2. | 837500000008987 | TPL-007-4 (Saskatchewan) R4.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 412000000 | MRO-SK
83750000000612 | 837500000008984 | 837500000008989 | 1. | 837500000008990 | TPL-007-4 (Saskatchewan) R4.3.1. | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 431000000 | MRO-SK
83750000000612 | 837500000008984 |  | 1. | 837500000008985 | TPL-007-4 (Saskatchewan) R4.1. | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. Part Applicability PCPA | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000008984 |  | 2. | 837500000008988 | TPL-007-4 (Saskatchewan) R4.2. | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000008984 |  | 3. | 837500000008989 | TPL-007-4 (Saskatchewan) R4.3. | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000008991 |  | 1. | 837500000008992 | TPL-007-4 (Saskatchewan) R5.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000008991 |  | 2. | 837500000008993 | TPL-007-4 (Saskatchewan) R5.2. | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R5, Part 5.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000008994 |  | 1. | 837500000008995 | TPL-007-4 (Saskatchewan) R6.1. | Be based on the effective GIC flow information provided in Requirement R5; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6 | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000008994 |  | 2. | 837500000008996 | TPL-007-4 (Saskatchewan) R6.2. | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6 | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000008994 |  | 3. | 837500000008997 | TPL-007-4 (Saskatchewan) R6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6 | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000008994 |  | 4. | 837500000008998 | TPL-007-4 (Saskatchewan) R6.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its benchmark thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its thermal impact assessment to the responsible entities as specified in Requirement R6 | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000008999 | 837500000009002 | 1. | 837500000009003 | TPL-007-4 (Saskatchewan) R7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 731000000 | MRO-SK
83750000000612 | 837500000008999 | 837500000009002 | 2. | 837500000009004 | TPL-007-4 (Saskatchewan) R7.3.2. | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 732000000 | MRO-SK
83750000000612 | 837500000008999 | 837500000009005 | 1. | 837500000009006 | TPL-007-4 (Saskatchewan) R7.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1 and how those circumstances are beyond the control of the responsible entity; |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 741000000 | MRO-SK
83750000000612 | 837500000008999 | 837500000009005 | 2. | 837500000009007 | TPL-007-4 (Saskatchewan) R7.4.2. | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures, if applicable; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 742000000 | MRO-SK
83750000000612 | 837500000008999 | 837500000009005 | 3. | 837500000009028 | TPL-007-4 (Saskatchewan) R7.4.3. | Updated timetable for implementing the selected actions in Part 7.1. | [23 empty] | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 743000000 | MRO-SK
83750000000612 | 837500000008999 | 837500000009008 | 1. | 837500000009009 | TPL-007-4 (Saskatchewan) R7.5.1. | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 751000000 | MRO-SK
83750000000612 | 837500000008999 |  | 1. | 837500000009000 | TPL-007-4 (Saskatchewan) R7.1. | 7.1. List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000008999 |  | 2. | 837500000009001 | TPL-007-4 (Saskatchewan) R7.2. | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 720000000 | MRO-SK
83750000000612 | 837500000008999 |  | 3. | 837500000009002 | TPL-007-4 (Saskatchewan) R7.3. | Include a timetable, subject to approval for any extension sought under Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000008999 |  | 4. | 837500000009005 | TPL-007-4 (Saskatchewan) R7.4. | Be submitted to the Compliance Enforcement Authority (CEA) with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. The submitted CAP shall document the following: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000008999 |  | 5. | 837500000009008 | TPL-007-4 (Saskatchewan) R7.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 750000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009010 | 837500000009011 | 1. | 837500000009012 | TPL-007-4 (Saskatchewan) R8.1.1. | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 811000000 | MRO-SK
83750000000612 | 837500000009010 | 837500000009011 | 2. | 837500000009013 | TPL-007-4 (Saskatchewan) R8.1.2. | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 812000000 | MRO-SK
83750000000612 | 837500000009010 | 837500000009016 | 1. | 837500000009017 | TPL-007-4 (Saskatchewan) R8.3.1. | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 831000000 | MRO-SK
83750000000612 | 837500000009010 |  | 1. | 837500000009011 | TPL-007-4 (Saskatchewan) R8.1. | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009010 |  | 2. | 837500000009014 | TPL-007-4 (Saskatchewan) R8.2. | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its supplemental GMD Vulnerability Assessment meeting all of the requirements in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its supplemental GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later, as specified in Requirement R8. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its supplemental GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R8. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009010 |  | 3. | 837500000009016 | TPL-007-4 (Saskatchewan) R8.3. | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009018 |  | 1. | 837500000009019 | TPL-007-4 (Saskatchewan) R9.1. | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009018 |  | 2. | 837500000009020 | TPL-007-4 (Saskatchewan) R9.2. | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided the maximum effective GIC values to the Transmission Owner and Generator Owner that owns each applicable BES power transformer in the planning area as specified in Requirement R9, Part 9.1. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided GIC(t) in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009021 |  | 1. | 837500000009022 | TPL-007-4 (Saskatchewan) R10.1. | Be based on the effective GIC flow information provided in Requirement R9; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009021 |  | 2. | 837500000009023 | TPL-007-4 (Saskatchewan) R10.2. | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 102000000 | MRO-SK
83750000000612 | 837500000009021 |  | 3. | 837500000009024 | TPL-007-4 (Saskatchewan) R10.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009021 |  | 4. | 837500000009025 | TPL-007-4 (Saskatchewan) R10.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner shall have evidence such as electronic or hard copies of its supplemental thermal impact assessment for all of its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater, and shall have evidence such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has provided its supplemental thermal impact assessment to the responsible entities as specified in Requirement R10. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009029 | 837500000009032 | 1. | 837500000009033 | TPL-007-4 (Saskatchewan) R11.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 1131000000 | MRO-SK
83750000000612 | 837500000009029 | 837500000009032 | 2. | 837500000009034 | TPL-007-4 (Saskatchewan) R11.3.2. | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 1132000000 | MRO-SK
83750000000612 | 837500000009029 | 837500000009035 | 1. | 837500000009036 | TPL-007-4 (Saskatchewan) R11.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 11.1 and how those circumstances are beyond the control of the responsible entity; |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 1141000000 | MRO-SK
83750000000612 | 837500000009029 | 837500000009035 | 2. | 837500000009037 | TPL-007-4 (Saskatchewan) R11.4.2. | Revisions to the selected actions in Part 11.1, if any, including utilization of Operating Procedures, if applicable; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, shall have dated evidence such as electronic or hard copies of its benchmark GMD Vulnerability Assessment meeting all of the requirements in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its benchmark GMD Vulnerability Assessment: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later, as specified in Requirement R4. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its benchmark GMD Vulnerability Assessment within 90 calendar days of receipt of those comments in accordance with Requirement R4. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 1142000000 | MRO-SK
83750000000612 | 837500000009029 | 837500000009035 | 3. | 837500000009038 | TPL-007-4 (Saskatchewan) R11.4.3. | Updated timetable for implementing the selected actions in Part 11.1. | [23 empty] | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 1143000000 | MRO-SK
83750000000612 | 837500000009029 | 837500000009039 | 1. | 837500000009040 | TPL-007-4 (Saskatchewan) R11.5.1. | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 1151000000 | MRO-SK
83750000000612 | 837500000009029 |  | 1. | 837500000009030 | TPL-007-4 (Saskatchewan) R11.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 111000000 | MRO-SK
83750000000612 | 837500000009029 |  | 2. | 837500000009031 | TPL-007-4 (Saskatchewan) R11.2. | Be developed within one year of completion of the supplemental GMD Vulnerability Assessment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009029 |  | 3. | 837500000009032 | TPL-007-4 (Saskatchewan) R11.3. | Include a timetable, subject to approval for any extension sought under Part 11.4, for implementing the selected actions from Part 11.1. The timetable shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009029 |  | 4. | 837500000009035 | TPL-007-4 (Saskatchewan) R11.4. | Be submitted to the CEA with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. The submitted CAP shall document the following: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009029 |  | 5. | 837500000009039 | TPL-007-4 (Saskatchewan) R11.5. | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it submitted a request for extension to the CEA if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | RQ-2021-07-12-0000001-SK |  | 1. | RP-2021-07-12-0000050-SK | TPL-007-4 (Saskatchewan) D.A.7.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of the later of the development of the CAP or receipt of regulatory approvals, if required; and |  | GO, PCPA, TO, TP |  |  |  |  | GO |  |  |  |  | PCPA | [7 empty] | TO |  | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.7.4 within 90 calendar days of revision. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 731000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | RQ-2021-07-12-0000001-SK |  | 2. | RP-2021-07-12-0000051-SK | TPL-007-4 (Saskatchewan) D.A.7.3.2. | Specify implementation of hardware mitigation, if any, within four years of the later of the development of the CAP or receipt of regulatory approvals, if required. |  | GO, PCPA, TO, TP |  |  |  |  | GO |  |  |  |  | PCPA | [7 empty] | TO |  | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.7.4 within 90 calendar days of revision. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 732000000 | MRO-SK
83750000000612 | 837500000009042 |  | 1. | 837500000009043 | TPL-007-4 (Saskatchewan) D.A.7.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1 and how those circumstances are beyond the control of the responsible entity; | [23 empty] | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.7.4 within 90 calendar days of revision. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 741000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009042 |  | 2. | 837500000009044 | TPL-007-4 (Saskatchewan) D.A.7.4.2. | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures if applicable; and | [23 empty] | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.7.4 within 90 calendar days of revision. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 742000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009042 |  | 3. | RP-2021-07-12-0000047-SK | TPL-007-4 (Saskatchewan) D.A.7.4.3. | Updated timetable for implementing the selected actions in Part 7.1 |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.7.4 within 90 calendar days of revision. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 743000000
83750000000612 | 837500000009046 |  | 1. | 837500000009047 | TPL-007-4 (Saskatchewan) D.A.7.5.1. | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | [23 empty] | Each responsible entity, as determined in Requirement R1, that concludes, through the benchmark GMD Vulnerability Assessment conducted in Requirement R4, that the responsible entity’s System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R7. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R7, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.7.4 within 90 calendar days of revision. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R7. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 751000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009048 |  | 1. | 837500000009049 | TPL-007-4 (Saskatchewan) D.A.11.3.1. | Specify implementation of non-hardware mitigation, if any, within two years of the later of the development of the CAP or receipt of regulatory approvals, if required; and | [23 empty] | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.11.4 within 90 calendar days of revision. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 113100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009048 |  | 2. | 837500000009050 | TPL-007-4 (Saskatchewan) D.A.11.3.2. | Specify implementation of hardware mitigation, if any, within four years of the later of the development of the CAP or receipt of regulatory approvals, if required. | [23 empty] | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.11.4 within 90 calendar days of revision. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 113200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009051 |  | 1. | 837500000009052 | TPL-007-4 (Saskatchewan) D.A.11.4.1. | Circumstances causing the delay for fully or partially implementing the selected actions in Part 11.1 and how those circumstances are beyond the control of the responsible entity; | [23 empty] | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.11.4 within 90 calendar days of revision. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 114100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009051 |  | 2. | 837500000009053 | TPL-007-4 (Saskatchewan) D.A.11.4.2. | Revisions to the selected actions in Part 11.1, if any, including utilization of Operating Procedures if applicable; and | [23 empty] | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.11.4 within 90 calendar days of revision. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 114200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000612 | 837500000009051 |  | 3. | RP-2021-07-12-0000048-SK | TPL-007-4 (Saskatchewan) D.A.11.4.3. | Updated timetable for implementing the selected actions in Part 11.1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.11.4 within 90 calendar days of revision. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 114300000
83750000000612 | 837500000009055 |  | 1. | 837500000009056 | TPL-007-4 (Saskatchewan) D.A.11.5.1. | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | [23 empty] | Each responsible entity, as determined in Requirement R1, that concludes, through the supplemental GMD Vulnerability Assessment conducted in Requirement R8, that the responsible entity’s System does not meet the performance requirements for the steady state planning supplemental GMD event contained in Table 1 shall have evidence such as dated electronic or hard copies of its CAP including timetable for implementing selected actions, as specified in Requirement R11. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records or postal receipts showing recipient and date, that it has revised its CAP if situations beyond the responsible entity's control prevent implementation of the CAP within the timetable specified. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email records, web postings with an electronic notice of posting, or postal receipts showing recipient and date, that it has distributed its CAP or relevant information, if any, (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later as specified in Requirement R11, and (iii) to the Compliance Enforcement Authority or Applicable Governmental Authority when revised under D.A.11.4 within 90 calendar days of revision. Each responsible entity, as determined in Requirement R1, shall also provide evidence, such as email notices or postal receipts showing recipient and date, that it has provided a documented response to comments received on its CAP within 90 calendar days of receipt of those comments, in accordance with Requirement R11. | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. | 115100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000614 | 837500000009057 |  | 1. | 837500000009058 | FAC-002-3 (Saskatchewan) R1.1. | The reliability impact of the new interconnection, or materially modified existing interconnection, on affected system(s); |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | 2021-04-01 |  |  |  | Applicable Generator Owner: Generator Owner with a fully executed Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000614 | 837500000009057 |  | 2. | 837500000009059 | FAC-002-3 (Saskatchewan) R1.2. | Adherence to applicable NERC Reliability Standards; regional and Transmission Owner planning criteria; and Facility interconnection requirements; |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | 2021-04-01 |  |  |  | Applicable Generator Owner: Generator Owner with a fully executed Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000614 | 837500000009057 |  | 3. | 837500000009060 | FAC-002-3 (Saskatchewan) R1.3. | Steady-state, short-circuit, and dynamics studies, as necessary, to evaluate system performance under both normal and contingency conditions; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | 2021-04-01 |  |  |  | Applicable Generator Owner: Generator Owner with a fully executed Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000614 | 837500000009057 |  | 4. | 837500000009061 | FAC-002-3 (Saskatchewan) R1.4. | Study assumptions, system performance, alternatives considered, and coordinated recommendations. While these studies may be performed independently, the results shall be evaluated and coordinated by the entities involved. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | 2021-04-01 |  |  |  | Applicable Generator Owner: Generator Owner with a fully executed Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | 140000000 | MRO-SK
83750000000615 | 837500000009066 |  | 1. | 837500000009067 | IRO-010-3 (Saskatchewan) R1.1. | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2024-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000615 | 837500000009066 |  | 2. | 837500000009068 | IRO-010-3 (Saskatchewan) R1.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2024-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000615 | 837500000009066 |  | 3. | 837500000009069 | IRO-010-3 (Saskatchewan) R1.3. | A periodicity for providing data. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2024-03-31 |  |  | 130000000 | MRO-SK
83750000000615 | 837500000009066 |  | 4. | 837500000009070 | IRO-010-3 (Saskatchewan) R1.4. | The deadline by which the respondent is to provide the indicated data. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2024-03-31 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000615 | 837500000009072 |  | 1. | 837500000009073 | IRO-010-3 (Saskatchewan) R3.1. | A mutually agreeable format |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | The Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Reliability Coordinator, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall make available evidence that it satisfied the obligations of the documented specification using the specified criteria. Such evidence could include but is not limited to electronic or hard copies of data transmittals or attestations of receiving entities. | 2021-04-01 |  | 2024-03-31 |  |  | 310000000 | MRO-SK
83750000000615 | 837500000009072 |  | 2. | 837500000009074 | IRO-010-3 (Saskatchewan) R3.2. | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | The Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Reliability Coordinator, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall make available evidence that it satisfied the obligations of the documented specification using the specified criteria. Such evidence could include but is not limited to electronic or hard copies of data transmittals or attestations of receiving entities. | 2021-04-01 |  | 2024-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000615 | 837500000009072 |  | 3. | 837500000009075 | IRO-010-3 (Saskatchewan) R3.3. | A mutually agreeable security protocol |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | The Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Reliability Coordinator, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall make available evidence that it satisfied the obligations of the documented specification using the specified criteria. Such evidence could include but is not limited to electronic or hard copies of data transmittals or attestations of receiving entities. | 2021-04-01 |  | 2024-03-31 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000616 | 837500000009076 | 837500000009079 | 1. | 837500000009080 | MOD-031-3 (Saskatchewan) R1.3.1. | Integrated hourly Demands in megawatts for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 131000000 | MRO-SK
83750000000616 | 837500000009076 | 837500000009079 | 2. | 837500000009081 | MOD-031-3 (Saskatchewan) R1.3.2. | Monthly and annual integrated peak hour Demands in megawatts for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 132000000 | MRO-SK
83750000000616 | 837500000009076 | 837500000009079 | 3. | 837500000009083 | MOD-031-3 (Saskatchewan) R1.3.3. | Monthly and annual Net Energy for Load in gigawatthours for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 133000000 | MRO-SK
83750000000616 | 837500000009076 | 837500000009079 | 4. | 837500000009084 | MOD-031-3 (Saskatchewan) R1.3.4. | Monthly and annual peak hour controllable and dispatchable Demand Side Management under the control or supervision of the System Operator in megawatts for the prior calendar year. Three values shall be reported for each hour: 1) the committed megawatts (the amount under control or supervision), 2) the dispatched megawatts (the amount, if any, activated for use by the System Operator), and 3) the realized megawatts (the amount of actual demand reduction). |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 134000000 | MRO-SK
83750000000616 | 837500000009076 | 837500000009081 | 1. | 837500000009082 | MOD-031-3 (Saskatchewan) R1.3.2.1. | If the annual peak hour actual Demand varies due to weather-related conditions (e.g., temperature, humidity or wind speed), the Applicable Entity shall also provide the weather normalized annual peak hour actual Demand for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 13210000 | MRO-SK
83750000000616 | 837500000009076 | 837500000009085 | 1. | 837500000009086 | MOD-031-3 (Saskatchewan) R1.4.1. | Monthly peak hour forecast Total Internal Demands in megawatts for the next two calendar years. |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 141000000 | MRO-SK
83750000000616 | 837500000009076 | 837500000009085 | 2. | 837500000009087 | MOD-031-3 (Saskatchewan) R1.4.2. | Monthly forecast Net Energy for Load in gigawatthours for the next two calendar years. |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 142000000 | MRO-SK
83750000000616 | 837500000009076 | 837500000009085 | 3. | 837500000009088 | MOD-031-3 (Saskatchewan) R1.4.3. | Peak hour forecast Total Internal Demands (summer and winter) in megawatts for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 143000000 | MRO-SK
83750000000616 | 837500000009076 | 837500000009085 | 4. | 837500000009089 | MOD-031-3 (Saskatchewan) R1.4.4. | Annual forecast Net Energy for Load in gigawatthours for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 144000000 | MRO-SK
83750000000616 | 837500000009076 | 837500000009085 | 5. | 837500000009090 | MOD-031-3 (Saskatchewan) R1.4.5. | Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  |  | 145000000 | MRO-SK
83750000000616 | 837500000009076 | 837500000009091 | 1. | 837500000009092 | MOD-031-3 (Saskatchewan) R1.5.1. | The assumptions and methods used in the development of aggregated Peak Demand and Net Energy for Load forecasts. |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 151000000 | MRO-SK
83750000000616 | 837500000009076 | 837500000009091 | 2. | 837500000009093 | MOD-031-3 (Saskatchewan) R1.5.2. | The Demand and energy effects of controllable and dispatchable Demand Side Management under the control or supervision of the System Operator. |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 152000000 | MRO-SK
83750000000616 | 837500000009076 | 837500000009091 | 3. | 837500000009094 | MOD-031-3 (Saskatchewan) R1.5.3. | How Demand Side Management is addressed in the forecasts of its Peak Demand and annual Net Energy for Load. |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 153000000 | MRO-SK
83750000000616 | 837500000009076 | 837500000009091 | 4. | 837500000009095 | MOD-031-3 (Saskatchewan) R1.5.4. | How the controllable and dispatchable Demand Side Management forecast compares to actual controllable and dispatchable Demand Side Management for the prior calendar year and, if applicable, how the assumptions and methods for future forecasts were adjusted. |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 154000000 | MRO-SK
83750000000616 | 837500000009076 | 837500000009091 | 5. | 837500000009096 | MOD-031-3 (Saskatchewan) R1.5.5. | How the peak Demand forecast compares to actual Demand for the prior calendar year with due regard to any relevant weather-related variations (e.g., temperature, humidity, or wind speed) and, if applicable, how the assumptions and methods for future forecasts were adjusted. |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 155000000 | MRO-SK
83750000000616 | 837500000009076 |  | 1. | 837500000009077 | MOD-031-3 (Saskatchewan) R1.1. | A list of Transmission Planners, Balancing Authorities, and Distribution Providers that are required to provide the data (“Applicable Entities”). |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000616 | 837500000009076 |  | 2. | 837500000009078 | MOD-031-3 (Saskatchewan) R1.2. | A timetable for providing the data. (A minimum of 30 calendar days must be allowed for responding to the request). |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 120000000 | MRO-SK
83750000000616 | 837500000009076 |  | 3. | 837500000009079 | MOD-031-3 (Saskatchewan) R1.3. | A request to provide any or all of the following actual data, as necessary: |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000616 | 837500000009076 |  | 4. | 837500000009085 | MOD-031-3 (Saskatchewan) R1.4. | A request to provide any or all of the following forecast data, as necessary: |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000616 | 837500000009076 |  | 5. | 837500000009091 | MOD-031-3 (Saskatchewan) R1.5. | A request to provide any or all of the following summary explanations, as necessary,: |  | BA, PCPA | BA | [8 empty] | PCPA | [11 empty] | The Planning Coordinator or Balancing Authority shall have a dated data request, either in hardcopy or electronic format, in accordance with Requirement R1. | 2021-04-01 |  |  |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000616 | 837500000009099 |  | 1. | 837500000009100 | MOD-031-3 (Saskatchewan) R4.1. | If the Applicable Entity does not provide data requested because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. |  | BA, DP, PCPA, RP, TP | BA | DP | [7 empty] | PCPA |  |  |  | RP | [5 empty] | TP |  | Each Applicable Entity identified in Requirement R4 shall have evidence such as dated e-mails or dated transmittal letters that it provided the data requested or provided a written response specifying the data that is not being provided and the basis for not providing the data in accordance with Requirement R4. | 2021-04-01 |  |  |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009170 |  | 1. | 837500000009171 | PRC-006-4 (Saskatchewan) R2.1. | Those islands selected by applying the criteria in Requirement R1, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009170 |  | 2. | 837500000009172 | PRC-006-4 (Saskatchewan) R2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009170 |  | 3. | 837500000009173 | PRC-006-4 (Saskatchewan) R2.3. | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009174 |  | 1. | 837500000009175 | PRC-006-4 (Saskatchewan) R3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009174 |  | 2. | 837500000009176 | PRC-006-4 (Saskatchewan) R3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009174 |  | 3. | RP-2021-06-24-0000009-SK | PRC-006-4 (Saskatchewan) R3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following:  Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES  Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES  Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 330000000 | MRO-SK
83750000000619 | 837500000009178 |  | 1. | RP-2021-06-24-0000010-SK | PRC-006-4 (Saskatchewan) R4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 410000000 | MRO-SK
83750000000619 | 837500000009178 |  | 2. | RP-2021-06-24-0000011-SK | PRC-006-4 (Saskatchewan) R4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009178 |  | 3. | RP-2021-06-24-0000012-SK | PRC-006-4 (Saskatchewan) R4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009178 |  | 4. | 837500000009182 | PRC-006-4 (Saskatchewan) R4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009178 |  | 5. | 837500000009183 | PRC-006-4 (Saskatchewan) R4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009178 |  | 6. | 837500000009184 | PRC-006-4 (Saskatchewan) R4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 460000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009178 |  | 7. | 837500000009185 | PRC-006-4 (Saskatchewan) R4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 470000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009192 |  | 1. | 837500000009193 | PRC-006-4 (Saskatchewan) R11.1. | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009192 |  | 2. | 837500000009194 | PRC-006-4 (Saskatchewan) R11.2. | The effectiveness of the UFLS program. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009197 |  | 1. | 837500000009198 | PRC-006-4 (Saskatchewan) R14.1. | UFLS program, including a schedule for implementation |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009197 |  | 2. | 837500000009199 | PRC-006-4 (Saskatchewan) R14.2. | UFLS design assessment |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009197 |  | 3. | 837500000009200 | PRC-006-4 (Saskatchewan) R14.3. | Format and schedule of UFLS data submittal |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009201 |  | 1. | 837500000009202 | PRC-006-4 (Saskatchewan) R15.1. | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009201 |  | 2. | 837500000009203 | PRC-006-4 (Saskatchewan) R15.2. | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009147 |  | 1. | 837500000009148 | PRC-006-4 (Saskatchewan) D.B.2.1. | Those islands selected by applying the criteria in Requirement D.B.1, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009147 |  | 2. | 837500000009149 | PRC-006-4 (Saskatchewan) D.B.2.2. | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009138 |  | 1. | 837500000009139 | PRC-006-4 (Saskatchewan) D.A.3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009138 |  | 2. | 837500000009140 | PRC-006-4 (Saskatchewan) D.A.3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009138 |  | 3. | 837500000009141 | PRC-006-4 (Saskatchewan) D.A.3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each Quebec BES generator bus and associated generator step-up transformer high-side bus |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009150 | 837500000009153 | 1. | 837500000009154 | PRC-006-4 (Saskatchewan) D.B.3.3.1. | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES | [24 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 331000000 | MRO-SK
83750000000619 | 837500000009150 | 837500000009153 | 2. | 837500000009155 | PRC-006-4 (Saskatchewan) D.B.3.3.2. | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES | [24 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 332000000 | MRO-SK
83750000000619 | 837500000009150 | 837500000009153 | 3. | 837500000009156 | PRC-006-4 (Saskatchewan) D.B.3.3.3. | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | [24 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 333000000 | MRO-SK
83750000000619 | 837500000009150 |  | 1. | 837500000009151 | PRC-006-4 (Saskatchewan) D.B.3.1. | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009150 |  | 2. | 837500000009152 | PRC-006-4 (Saskatchewan) D.B.3.2. | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009150 |  | 3. | 837500000009153 | PRC-006-4 (Saskatchewan) D.B.3.3. | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009142 |  | 1. | 837500000009143 | PRC-006-4 (Saskatchewan) D.A.4.1. | Underfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1A, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009142 |  | 2. | 837500000009144 | PRC-006-4 (Saskatchewan) D.A.4.2. | Overfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 - Attachment 1A, and |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009142 |  | 3. | 837500000009145 | PRC-006-4 (Saskatchewan) D.A.4.3. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009157 |  | 1. | 837500000009158 | PRC-006-4 (Saskatchewan) D.B.4.1. | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009157 |  | 2. | 837500000009159 | PRC-006-4 (Saskatchewan) D.B.4.2. | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 420000000 | MRO-SK
83750000000619 | 837500000009157 |  | 3. | 837500000009160 | PRC-006-4 (Saskatchewan) D.B.4.3. | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009157 |  | 4. | 837500000009161 | PRC-006-4 (Saskatchewan) D.B.4.4. | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009157 |  | 5. | 837500000009162 | PRC-006-4 (Saskatchewan) D.B.4.5. | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009157 |  | 6. | 837500000009163 | PRC-006-4 (Saskatchewan) D.B.4.6. | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 460000000 | MRO-SK
83750000000619 | 837500000009157 |  | 7. | 837500000009164 | PRC-006-4 (Saskatchewan) D.B.4.7. | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 470000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009165 |  | 1. | 837500000009166 | PRC-006-4 (Saskatchewan) D.B.11.1. | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 1110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000619 | 837500000009165 |  | 2. | 837500000009167 | PRC-006-4 (Saskatchewan) D.B.11.2. | The effectiveness of the UFLS program |  | PCPA | [9 empty] | PCPA | [12 empty] | 2021-04-01 |  |  |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: | 1120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000620 | 837500000009204 |  | 1. | 837500000009205 | TOP-003-4 (Saskatchewan) R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2023-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000620 | 837500000009204 |  | 2. | 837500000009206 | TOP-003-4 (Saskatchewan) R1.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2023-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000620 | 837500000009204 |  | 3. | 837500000009207 | TOP-003-4 (Saskatchewan) R1.3. | A periodicity for providing data. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2023-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000620 | 837500000009204 |  | 4. | 837500000009208 | TOP-003-4 (Saskatchewan) R1.4. | The deadline by which the respondent is to provide the indicated data. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2023-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000620 | 837500000009209 |  | 1. | 837500000009210 | TOP-003-4 (Saskatchewan) R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2023-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000620 | 837500000009209 |  | 2. | 837500000009211 | TOP-003-4 (Saskatchewan) R2.2. | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2023-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000620 | 837500000009209 |  | 3. | 837500000009212 | TOP-003-4 (Saskatchewan) R2.3. | A periodicity for providing data. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2023-06-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000620 | 837500000009209 |  | 4. | 837500000009213 | TOP-003-4 (Saskatchewan) R2.4. | The deadline by which the respondent is to provide the indicated data. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2021-04-01 |  | 2023-06-30 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000620 | 837500000009216 |  | 1. | 837500000009217 | TOP-003-4 (Saskatchewan) R5.1. | A mutually agreeable format |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2021-04-01 |  | 2023-06-30 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000620 | 837500000009216 |  | 2. | 837500000009218 | TOP-003-4 (Saskatchewan) R5.2. | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2021-04-01 |  | 2023-06-30 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000620 | 837500000009216 |  | 3. | 837500000009219 | TOP-003-4 (Saskatchewan) R5.3. | A mutually agreeable security protocol |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2021-04-01 |  | 2023-06-30 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000621 | 837500000009222 |  | 1. | 837500000009223 | PRC-024-3 (Saskatchewan) R3.1. | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. |  | GO |  |  |  |  | GO | [17 empty] | 2022-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Generator Owners that apply protection listed in Section 4.2.1. 4.1.2 Transmission Owners (in the Quebec Interconnection only) that own a BES generator step-up (GSU) transformer or main power transformer (MPT)1 and apply protection listed in Section 4.2.1. 4.1.3 Planning Coordinators (in the Quebec Interconnection only) 4.2. Facilities2: 4.2.1 Frequency, voltage, and volts per hertz protection (whether provided by relaying or functions within associated control systems) that respond to electrical signals and: (i) directly trip the generating resource(s); or (ii) provide signals to the generating resource(s) to either trip or cease injecting current; and are applied to the following: 4.2.1.1 BES generating resource(s). 4.2.1.2 BES GSU transformer(s). 4.2.1.3 High side of the generator-connected unit auxiliary transformer3 (UAT) installed on BES generating resource(s). 4.2.1.4 Individual dispersed power producing resource(s) identified in the BES Definition, Inclusion I4. 4.2.1.5 Elements that are designed primarily for the delivery of capacity from the individual dispersed power producing resources identified in the BES Definition, Inclusion I4, to the point where those resources aggregate to greater than 75 MVA. 4.2.1.6 MPT4 of resource(s) identified in the BES Definition, Inclusion I4. 4.2.2 Exemptions: Protection on all auxiliary equipment within the generating Facility. 1 For the purpose of this standard, the MPT is the power transformer that steps up voltage from the collection system voltage to the nominal transmission/interconnecting system voltage for dispersed power producing resources. 2 It is not required to install or activate the protections described in Facilities Section 4.2. 3 These transformers are variably referred to as station power UAT, or station service transformer(s) used to provide overall auxiliary power to the generating resource(s). This UAT is the transformer connected on the generator bus between the low side of the GSU and the generator terminal. 4 For the purpose of this standard, the MPT is the power transformer that steps up voltage from the collection system voltage to the nominal transmission/interconnecting system voltage for dispersed power producing resources | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009295 |  | 1. | 837500000009296 | TPL-001-5.1 (Saskatchewan) R1.1. | System models shall represent: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009295 |  | 1.1. | RP-2021-07-12-0000001-SK | TPL-001-5.1 (Saskatchewan) R1.1.1. | Existing Facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M1. Each Transmission Planner and Planning Coordinator shall provide evidence, in electronic or hard copy format, that it is maintaining System models within its respective area, using data consistent with MOD-032, including items represented in the Corrective Action Plan, representing projected System conditions, and that the models represent the required information in accordance with Requirement R1. | 2023-07-01 |  |  |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009295 |  | 1.2. | RP-2021-07-12-0000002-SK | TPL-001-5.1 (Saskatchewan) R1.1.2. | New planned Facilities and changes to existing Facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 112000000 | MRO-SK
83750000000627 | 837500000009295 |  | 1.3. | RP-2021-07-12-0000003-SK | TPL-001-5.1 (Saskatchewan) R1.1.3. | Real and reactive Load forecasts. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009295 |  | 1.4. | RP-2021-07-12-0000004-SK | TPL-001-5.1 (Saskatchewan) R1.1.4. | Known commitments for Firm Transmission Service and Interchange. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009295 |  | 1.5. | RP-2021-07-12-0000006-SK | TPL-001-5.1 (Saskatchewan) R1.1.5. | Resources (supply or demand side) required for Load. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 1. | 837500000009303 | TPL-001-5.1 (Saskatchewan) R2.1. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 1.1. | RP-2021-07-12-0000005-SK | TPL-001-5.1 (Saskatchewan) R2.1.1. | System peak Load for either Year One or year two, and for year five. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 1.2. | RP-2021-07-12-0000007-SK | TPL-001-5.1 (Saskatchewan) R2.1.2. | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 1.3. | RP-2021-07-12-0000008-SK | TPL-001-5.1 (Saskatchewan) R2.1.3. | For each of the studies described in Requirement R2, Parts 2.1.1 and 2.1.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in System response :  Real and reactive forecasted Load.  Expected transfers.  Expected in service dates of new or modified Transmission Facilities.  Reactive resource capability.  Generation additions, retirements, or other dispatch scenarios.  Controllable Loads and Demand Side Management.  Duration or timing of known Transmission outages. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 1.4. | RP-2021-07-12-0000009-SK | TPL-001-5.1 (Saskatchewan) R2.1.4. | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P0 and P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 1.5. | RP-2021-07-12-0000010-SK | TPL-001-5.1 (Saskatchewan) R2.1.5. | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 215000000 | MRO-SK
83750000000627 | 837500000009302 |  | 2. | 837500000009309 | TPL-001-5.1 (Saskatchewan) R2.2. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 2.1. | RP-2021-07-12-0000011-SK | TPL-001-5.1 (Saskatchewan) R2.2.1. | A current study assessing expected System peak Load conditions for one of the years in the Long-Term Transmission Planning Horizon and the rationale for why that year was selected. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 221000000 | MRO-SK
83750000000627 | 837500000009302 |  | 3. | 837500000009311 | TPL-001-5.1 (Saskatchewan) R2.3. | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 4. | 837500000009312 | TPL-001-5.1 (Saskatchewan) R2.4. | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 4.1. | RP-2021-07-12-0000012-SK | TPL-001-5.1 (Saskatchewan) R2.4.1. | System peak Load for one of the five years. System peak Load levels shall include a Load model which represents the expected dynamic behavior of Loads that could impact the study area, considering the behavior of induction motor Loads. An aggregate System Load model which represents the overall dynamic behavior of the Load is acceptable. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 241000000 | MRO-SK
83750000000627 | 837500000009302 |  | 4.2. | RP-2021-07-12-0000013-SK | TPL-001-5.1 (Saskatchewan) R2.4.2. | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 242000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 4.3. | RP-2021-07-12-0000014-SK | TPL-001-5.1 (Saskatchewan) R2.4.3. | For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in performance:  Load level, Load forecast, or dynamic Load model assumptions.  Expected transfers.  Expected in service dates of new or modified Transmission Facilities.  Reactive resource capability.  Generation additions, retirements, or other dispatch scenarios. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 243000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 4.4. | RP-2021-07-12-0000015-SK | TPL-001-5.1 (Saskatchewan) R2.4.4. | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum, those known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 244000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 4.5. | RP-2021-07-12-0000016-SK | TPL-001-5.1 (Saskatchewan) R2.4.5. | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the selected P1 and P2 category events identified in Table 1 for which the unavailability is expected to produce more severe System impacts on its portion of the BES. The analysis shall simulate the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 245000000 | MRO-SK
83750000000627 | 837500000009302 |  | 5. | 837500000009318 | TPL-001-5.1 (Saskatchewan) R2.5. | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6 and shall include documentation to support the technical rationale for determining material changes. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 6. | 837500000009319 | TPL-001-5.1 (Saskatchewan) R2.6. | Past studies may be used to support the Planning Assessment if they meet the following requirements: 2.6.1. For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. 2.6.2. For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 6.1. | RP-2021-07-12-0000017-SK | TPL-001-5.1 (Saskatchewan) R2.6.1. | For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 261000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 6.2. | RP-2021-07-12-0000018-SK | TPL-001-5.1 (Saskatchewan) R2.6.2. | For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 262000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 7. | 837500000009320 | TPL-001-5.1 (Saskatchewan) R2.7. | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments, but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.3 and 2.4.3. The Corrective Action Plan(s) shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 270000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 7.1. | RP-2021-07-12-0000019-SK | TPL-001-5.1 (Saskatchewan) R2.7.1. | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: - Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. - Installation, modification, or removal of Protection Systems or Remedial Action Schemes. - Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations. - Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations. - Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan. - Use of rate applications, DSM, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 271000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 7.2. | RP-2021-07-12-0000020-SK | TPL-001-5.1 (Saskatchewan) R2.7.2. | Include actions to resolve performance deficiencies identified in multiple sensitivity studies or provide a rationale for why actions were not necessary. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 272000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 7.3. | RP-2021-07-12-0000021-SK | TPL-001-5.1 (Saskatchewan) R2.7.3. | If situations arise that are beyond the control of the Transmission Planner or Planning Coordinator that prevent the implementation of a Corrective Action Plan in the required timeframe, then the Transmission Planner or Planning Coordinator is permitted to utilize Non-Consequential Load Loss and curtailment of Firm Transmission Service to correct the situation that would normally not be permitted in Table 1, provided that the Transmission Planner or Planning Coordinator documents that they are taking actions to resolve the situation. The Transmission Planner or Planning Coordinator shall document the situation causing the problem, alternatives evaluated, and the use of Non-Consequential Load Loss or curtailment of Firm Transmission Service. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 273000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 7.4. | RP-2021-07-12-0000022-SK | TPL-001-5.1 (Saskatchewan) R2.7.4. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 274000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 8. | 837500000009325 | TPL-001-5.1 (Saskatchewan) R2.8. | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 280000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 8.1. | RP-2021-07-12-0000023-SK | TPL-001-5.1 (Saskatchewan) R2.8.1. | List System deficiencies and the associated actions needed to achieve required System performance. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 281000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009302 |  | 8.2. | RP-2021-07-12-0000024-SK | TPL-001-5.1 (Saskatchewan) R2.8.2. | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M2. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of its annual Planning Assessment, that it has prepared an annual Planning Assessment of its portion of the BES in accordance with Requirement R2. | 2023-07-01 |  |  |  |  | 282000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009328 |  | 1. | 837500000009329 | TPL-001-5.1 (Saskatchewan) R3.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009328 |  | 2. | 837500000009330 | TPL-001-5.1 (Saskatchewan) R3.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 320000000 | MRO-SK
83750000000627 | 837500000009328 |  | 3. | 837500000009331 | TPL-001-5.1 (Saskatchewan) R3.3. | Contingency analyses for Requirement R3, Parts 3.1 and 3.2 shall: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2023-07-01 |  |  |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009328 |  | 3.1. | RP-2021-07-12-0000025-SK | TPL-001-5.1 (Saskatchewan) R3.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 331000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009328 |  | 3.1.1. | RP-2021-07-12-0000026-SK | TPL-001-5.1 (Saskatchewan) R3.3.1.1. | Tripping of generators where simulations show generator bus voltages or high side of the generation step up (GSU) voltages are less than known or assumed minimum generator steady state or ride through voltage limitations. Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2023-07-01 |  |  |  |  | 331100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009328 |  | 3.1.2. | RP-2021-07-12-0000027-SK | TPL-001-5.1 (Saskatchewan) R3.3.1.2. | Tripping of Transmission elements where relay loadability limits are exceeded. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 331200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009328 |  | 3.2. | RP-2021-07-12-0000028-SK | TPL-001-5.1 (Saskatchewan) R3.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide steady state control of electrical system quantities when such devices impact the study area. These devices may include equipment such as phase-shifting transformers, load tap changing transformers, and switched capacitors and inductors. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 332000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009328 |  | 4. | 837500000009336 | TPL-001-5.1 (Saskatchewan) R3.4. | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES shall be identified, and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009328 |  | 4.1. | RP-2021-07-12-0000030-SK | TPL-001-5.1 (Saskatchewan) R3.4.1. | The Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2023-07-01 |  |  |  |  | 341000000 | MRO-SK
83750000000627 | 837500000009328 |  | 5. | 837500000009338 | TPL-001-5.1 (Saskatchewan) R3.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2023-07-01 |  |  |  |  | 350000000 | MRO-SK
83750000000627 | 837500000009339 |  | 1. | RP-2021-07-12-0000032-SK | TPL-001-5.1 (Saskatchewan) R4.1. | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009339 |  | 1.1. | RP-2021-07-12-0000033-SK | TPL-001-5.1 (Saskatchewan) R4.1.1. | For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Remedial Action Scheme is not considered pulling out of synchronism. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2023-07-01 |  |  |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009339 |  | 1.2. | RP-2021-07-12-0000034-SK | TPL-001-5.1 (Saskatchewan) R4.1.2. | For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 412000000 | MRO-SK
83750000000627 | 837500000009339 |  | 1.3. | RP-2021-07-12-0000035-SK | TPL-001-5.1 (Saskatchewan) R4.1.3. | For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2023-07-01 |  |  |  |  | 413000000 | MRO-SK
83750000000627 | 837500000009339 |  | 2. | RP-2021-07-12-0000036-SK | TPL-001-5.1 (Saskatchewan) R4.2. | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event (s) shall be conducted. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009339 |  | 3. | RP-2021-07-12-0000037-SK | TPL-001-5.1 (Saskatchewan) R4.3. | Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall : |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2023-07-01 |  |  |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009339 |  | 3.1. | RP-2021-07-12-0000038-SK | TPL-001-5.1 (Saskatchewan) R4.3.1. | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 431000000 | MRO-SK
83750000000627 | 837500000009339 |  | 3.1.1. | RP-2021-07-12-0000039-SK | TPL-001-5.1 (Saskatchewan) R4.3.1.1. | Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 431100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009339 |  | 3.1.2. | RP-2021-07-12-0000040-SK | TPL-001-5.1 (Saskatchewan) R4.3.1.2. | Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M3. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment, in accordance with Requirement R3. | 2023-07-01 |  |  |  |  | 431200000 | MRO-SK
83750000000627 | 837500000009339 |  | 3.1.3. | RP-2021-07-12-0000041-SK | TPL-001-5.1 (Saskatchewan) R4.3.1.3. | Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2023-07-01 |  |  |  |  | 431300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009339 |  | 3.2. | RP-2021-07-12-0000042-SK | TPL-001-5.1 (Saskatchewan) R4.3.2. | Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 432000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009339 |  | 4. | RP-2021-07-12-0000043-SK | TPL-001-5.1 (Saskatchewan) R4.4. | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2023-07-01 |  |  |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009339 |  | 4.1. | RP-2021-07-12-0000044-SK | TPL-001-5.1 (Saskatchewan) R4.4.1. | Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M4. Each Transmission Planner and Planning Coordinator shall provide dated evidence, such as electronic or hard copies of the studies utilized in preparing the Planning Assessment in accordance with Requirement R4. | 2023-07-01 |  |  |  |  | 441000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009339 |  | 5. | RP-2021-07-12-0000045-SK | TPL-001-5.1 (Saskatchewan) R4.5. | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000627 | 837500000009343 |  | 1. | RP-2021-07-12-0000046-SK | TPL-001-5.1 (Saskatchewan) R8.1. | If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  |  | 2023-07-01 |  |  |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000632 | 837500000009431 | 837500000009433 | 1. | RP-2021-06-30-0000037-SK | CIP-013-2 (Saskatchewan) R1.2.1. | Notification by the vendor of vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 121000000 | MRO-SK
83750000000632 | 837500000009431 | 837500000009433 | 2. | RP-2021-06-30-0000038-SK | CIP-013-2 (Saskatchewan) R1.2.2. | Coordination of responses to vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 122000000 | MRO-SK
83750000000632 | 837500000009431 | 837500000009433 | 3. | RP-2021-06-30-0000039-SK | CIP-013-2 (Saskatchewan) R1.2.3. | Notification by vendors when remote or onsite access should no longer be granted to vendor representatives; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 123000000 | MRO-SK
83750000000632 | 837500000009431 | 837500000009433 | 4. | RP-2021-06-30-0000040-SK | CIP-013-2 (Saskatchewan) R1.2.4. | Disclosure by vendors of known vulnerabilities related to the products or services provided to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 124000000 | MRO-SK
83750000000632 | 837500000009431 | 837500000009433 | 5. | RP-2021-06-30-0000041-SK | CIP-013-2 (Saskatchewan) R1.2.5. | Verification of software integrity and authenticity of all software and patches provided by the vendor for use in the BES Cyber System and their associated EACMS and PACS; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 125000000 | MRO-SK
83750000000632 | 837500000009431 | 837500000009433 | 6. | RP-2021-06-30-0000042-SK | CIP-013-2 (Saskatchewan) R1.2.6. | Coordination of controls for vendor-initiated remote access. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 126000000 | MRO-SK
83750000000632 | 837500000009431 |  | 1. | 837500000009432 | CIP-013-2 (Saskatchewan) R1.1. | One or more process(es) used in planning for the procurement of BES Cyber Systems and their associated EACMS and PACS to identify and assess cyber security risk(s) to the Bulk Electric System from vendor products or services resulting from: (i) procuring and installing vendor equipment and software; and (ii) transitions from one vendor(s) to another vendor(s). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 110000000 | MRO-SK
83750000000632 | 837500000009431 |  | 2. | 837500000009433 | CIP-013-2 (Saskatchewan) R1.2. | One or more process(es) used in procuring BES Cyber Systems, and their associated EACMS and PACS, that address the following, as applicable: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009444 | 837500000009463 | 1. | 837500000009464 | CIP-010-4 (Saskatchewan) R1.1.1. | Operating system(s) (including version) or firmware where no independent operating system exists; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 111000000 | MRO-SK
83750000000634 | 837500000009444 |  | 1. | 837500000009463 | CIP-010-4 (Saskatchewan) R1.1. | Develop a baseline configuration, individually or by group, which shall include the following items: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009444 |  | 1.2. | RP-2021-06-30-0000021-SK | CIP-010-4 (Saskatchewan) R1.1.2. | Any commercially available or open-source application software (including version) intentionally installed; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 112000000 | MRO-SK
83750000000634 | 837500000009444 |  | 1.3. | RP-2021-06-30-0000022-SK | CIP-010-4 (Saskatchewan) R1.1.3. | Any custom software installed; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009444 |  | 1.4. | RP-2021-06-30-0000023-SK | CIP-010-4 (Saskatchewan) R1.1.4. | Any logical network accessible ports; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009444 |  | 1.5. | RP-2021-06-30-0000024-SK | CIP-010-4 (Saskatchewan) R1.1.5. | Any security patches applied. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009444 |  | 2. | 837500000009470 | CIP-010-4 (Saskatchewan) R1.2. | Authorize and document changes that deviate from the existing baseline configuration. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009444 |  | 3. | 837500000009471 | CIP-010-4 (Saskatchewan) R1.3. | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 130000000 | MRO-SK
83750000000634 | 837500000009444 |  | 4. | 837500000009472 | CIP-010-4 (Saskatchewan) R1.4. | For a change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009444 |  | 4.1. | RP-2021-06-30-0000025-SK | CIP-010-4 (Saskatchewan) R1.4.1. | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009444 |  | 4.2. | RP-2021-06-30-0000026-SK | CIP-010-4 (Saskatchewan) R1.4.2. | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009444 |  | 4.3. | RP-2021-06-30-0000027-SK | CIP-010-4 (Saskatchewan) R1.4.3. | Document the results of the verification. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009444 |  | 5. | 837500000009476 | CIP-010-4 (Saskatchewan) R1.5. | Where technically feasible, for each change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009444 |  | 5.1. | RP-2021-06-30-0000029-SK | CIP-010-4 (Saskatchewan) R1.5.1. | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009444 |  | 5.2. | RP-2021-06-30-0000030-SK | CIP-010-4 (Saskatchewan) R1.5.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 152000000 | MRO-SK
83750000000634 | 837500000009444 |  | 6. | 837500000009479 | CIP-010-4 (Saskatchewan) R1.6. | Prior to a change that deviates from the existing baseline configuration associated with baseline items in Parts 1.1.1, 1.1.2, and 1.1.5, and when the method to do so is available to the Responsible Entity from the software source: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009444 |  | 6.1. | RP-2021-06-30-0000031-SK | CIP-010-4 (Saskatchewan) R1.6.1. | Verify the identity of the software source; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009444 |  | 6.2. | RP-2021-06-30-0000032-SK | CIP-010-4 (Saskatchewan) R1.6.2. | Verify the integrity of the software obtained from the software source. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009445 |  | 1. | 837500000009482 | CIP-010-4 (Saskatchewan) R2.1. | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009446 |  | 1. | 837500000009483 | CIP-010-4 (Saskatchewan) R3.1. | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009446 |  | 2. | 837500000009484 | CIP-010-4 (Saskatchewan) R3.2. | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009446 |  | 2.1. | RP-2021-06-30-0000034-SK | CIP-010-4 (Saskatchewan) R3.2.1. | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009446 |  | 2.2. | RP-2021-06-30-0000035-SK | CIP-010-4 (Saskatchewan) R3.2.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009446 |  | 3. | 837500000009487 | CIP-010-4 (Saskatchewan) R3.3. | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000634 | 837500000009446 |  | 4. | 837500000009488 | CIP-010-4 (Saskatchewan) R3.4. | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000635 | 837500000009448 |  | 1. | 837500000009451 | CIP-005-7 (Saskatchewan) R1.1. | All applicable Cyber Assets connected to a network via a routable protocol shall reside within a defined ESP. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include,but is not limited to, a list of all ESPs with all uniquely identifiable applicable Cyber Assets connected via a routable protocol within each ESP. | 2023-01-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000635 | 837500000009448 |  | 2. | 837500000009452 | CIP-005-7 (Saskatchewan) R1.2. | All External Routable Connectivity must be through an identified Electronic Access Point (EAP). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, network diagrams showing all external routable communication paths and the identified EAPs. | 2023-01-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000635 | 837500000009448 |  | 3. | 837500000009453 | CIP-005-7 (Saskatchewan) R1.3. | Require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of rules (firewall, access control lists, etc.) that demonstrate that only permitted access is allowed and that each access rule has a documented reason. | 2023-01-01 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000635 | 837500000009448 |  | 4. | 837500000009454 | CIP-005-7 (Saskatchewan) R1.4. | Where technically feasible, perform authentication when establishing Dial-up Connectivity with applicable Cyber Assets. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-01-01 |  |  |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000635 | 837500000009448 |  | 5. | 837500000009455 | CIP-005-7 (Saskatchewan) R1.5. | Have one or more methods for detecting known or suspected malicious communications for both inbound and outbound communications. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation that malicious communications detection methods (e.g. intrusion detection system, application layer firewall, etc.) are implemented. | 2023-01-01 |  |  |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000635 | 837500000009449 |  | 1. | 837500000009456 | CIP-005-7 (Saskatchewan) R2.1. | For all Interactive Remote Access, utilize an Intermediate System such that the Cyber Asset initiating Interactive Remote Access does not directly access an applicable Cyber Asset. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include,but are not limited to, network diagrams or architecture documents. | 2023-01-01 |  |  |  |  | 210000000 | MRO-SK
83750000000635 | 837500000009449 |  | 2. | 837500000009457 | CIP-005-7 (Saskatchewan) R2.2. | For all Interactive Remote Access sessions, utilize encryption that terminates at an Intermediate System. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, architecture documents detailing where encryption initiates and terminates. | 2023-01-01 |  |  |  |  | 220000000 | MRO-SK
83750000000635 | 837500000009449 |  | 3. | 837500000009458 | CIP-005-7 (Saskatchewan) R2.3. | Require multi-factor authentication for all Interactive Remote Access sessions. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, architecture documents detailing the authentication factors used. Examples of authenticators may include, but are not limited to, • Something the individual knows such as passwords or PINs. This does not include User ID; • Something the individual has such as tokens, digital certificates, or smart cards; or • Something the individual is such as fingerprints, iris scans, or other biometric characteristics. | 2023-01-01 |  |  |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000635 | 837500000009449 |  | 4. | 837500000009459 | CIP-005-7 (Saskatchewan) R2.4. | Have one or more methods for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods used to determine active vendor remote access (including Interactive Remote Access and system-to-system remote access), such as: • Methods for accessing logged or monitoring information to determine active vendor remote access sessions; • Methods for monitoring activity (e.g. connection tables or rule hit counters in a firewall, or user activity monitoring) or open ports (e.g. netstat or related commands to display currently active ports) to determine active system to system remote access sessions; or • Methods that control vendor initiation of remote access such as vendors calling and requesting a second factor in order to initiate remote access. | 2023-01-01 |  |  |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000635 | 837500000009449 |  | 5. | 837500000009460 | CIP-005-7 (Saskatchewan) R2.5. | Have one or more method(s) to disable active vendor remote access including Interactive Remote Access and system-to-system remote access). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods(s) used to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access), such as: • Methods to disable vendor remote access at the applicable Electronic Access Point for system-to-system remote access; or • Methods to disable vendor Interactive Remote Access at the applicable Intermediate System | 2023-01-01 |  |  |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000635 | 837500000009450 |  | 1. | 837500000009461 | CIP-005-7 (Saskatchewan) R3.1. | Have one or more method(s) to determine authenticated vendor-initiated remote connections. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods used to determine authenticated vendor-initiated remote connections, such as: • Methods for accessing logged or monitoring information to determine authenticated vendor-initiated remote connections. | 2023-01-01 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
83750000000635 | 837500000009450 |  | 2. | 837500000009462 | CIP-005-7 (Saskatchewan) R3.2. | Have one or more method(s) to terminate authenticated vendor-initiated remote connections and control the ability to reconnect. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods(s) used to terminate authenticated vendor-initiated remote connections to applicable systems. Examples include terminating an active vendor-initiated shell/process/session or dropping an active vendor-initiated connection in a firewall. Methods to control the ability to reconnect, if necessary, could be: disabling an Active Directory account; disabling a security token; restricting IP addresses from vendor sources in a firewall; or physically disconnecting a network cable to prevent a reconnection. | 2023-01-01 |  |  |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
837500000008 | 8375000000066 |  | 1. | 8375000000067 | BAL-003-0.1b (Saskatchewan) R1.1. | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  | BA | BA | [21 empty] | 2010-03-30 |  | 2015-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
837500000008 | 8375000000066 |  | 2. | 8375000000068 | BAL-003-0.1b (Saskatchewan) R1.2. | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  | BA | BA | [21 empty] | 2010-03-30 |  | 2015-03-31 |  |  | 120000000 | MRO-SK
837500000008 | 8375000000069 |  | 1. | 8375000000070 | BAL-003-0.1b (Saskatchewan) R2.1. | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  | BA | BA | [21 empty] | 2010-03-30 |  | 2015-03-31 |  |  | 210000000 | MRO-SK
837500000008 | 8375000000069 |  | 2. | 8375000000071 | BAL-003-0.1b (Saskatchewan) R2.2. | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  | BA | BA | [21 empty] | 2010-03-30 |  | 2015-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
837500000008 | 8375000000073 |  | 1. | 8375000000074 | BAL-003-0.1b (Saskatchewan) R4.1. | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  | BA | BA | [21 empty] | 2010-03-30 |  | 2015-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
837500000008 | 8375000000073 |  | 2. | 8375000000075 | BAL-003-0.1b (Saskatchewan) R4.2. | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  | BA | BA | [21 empty] | 2010-03-30 |  | 2015-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
837500000008 | 8375000000076 |  | 1. | 8375000000077 | BAL-003-0.1b (Saskatchewan) R5.1. | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  | BA | BA | [21 empty] | 2010-03-30 |  | 2015-03-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
86 | 995 |  | 1. | 996 | IRO-005-1 R1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
86 | 995 |  | 10. | 997 | IRO-005-1 R1.10. | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
86 | 995 |  | 2. | 998 | IRO-005-1 R1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
86 | 995 |  | 3. | 999 | IRO-005-1 R1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
86 | 995 |  | 4. | 1000 | IRO-005-1 R1.4. | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
86 | 995 |  | 5. | 1001 | IRO-005-1 R1.5. | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
86 | 995 |  | 6. | 1002 | IRO-005-1 R1.6. | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
86 | 995 |  | 7. | 1003 | IRO-005-1 R1.7. | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
86 | 995 |  | 8. | 1004 | IRO-005-1 R1.8. | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
86 | 995 |  | 9. | 1005 | IRO-005-1 R1.9. | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
87 | 1022 |  | 1. | 1023 | IRO-005-2 R1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
87 | 1022 |  | 10. | 1024 | IRO-005-2 R1.10. | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
87 | 1022 |  | 2. | 1025 | IRO-005-2 R1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
87 | 1022 |  | 3. | 1026 | IRO-005-2 R1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
87 | 1022 |  | 4. | 1027 | IRO-005-2 R1.4. | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
87 | 1022 |  | 5. | 1028 | IRO-005-2 R1.5. | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
87 | 1022 |  | 6. | 1029 | IRO-005-2 R1.6. | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
87 | 1022 |  | 7. | 1030 | IRO-005-2 R1.7. | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
87 | 1022 |  | 8. | 1031 | IRO-005-2 R1.8. | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
87 | 1022 |  | 9. | 1032 | IRO-005-2 R1.9. | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
88 | 1049 |  | 1. | 1050 | IRO-005-3a R1.1. | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
88 | 1049 |  | 10. | 1051 | IRO-005-3a R1.10. | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
88 | 1049 |  | 2. | 1052 | IRO-005-3a R1.2. | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
88 | 1049 |  | 3. | 1053 | IRO-005-3a R1.3. | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
88 | 1049 |  | 4. | 1054 | IRO-005-3a R1.4. | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
88 | 1049 |  | 5. | 1055 | IRO-005-3a R1.5. | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
88 | 1049 |  | 6. | 1056 | IRO-005-3a R1.6. | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
88 | 1049 |  | 7. | 1057 | IRO-005-3a R1.7. | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
88 | 1049 |  | 8. | 1058 | IRO-005-3a R1.8. | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
88 | 1049 |  | 9. | 1059 | IRO-005-3a R1.9. | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
89 | 1072 |  | 1. | 1073 | IRO-006-3 R2.1. | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection is provided in Attachment 1-IRO-006-0. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-04-22 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
89 | 1072 |  | 2. | 1074 | IRO-006-3 R2.2. | The equivalent Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is the “WSCC Unscheduled Flow Mitigation Plan,” provided at: http://www.wecc.biz/documents/library/UFAS/UFAS_ mitigation_plan _rev_2001-clean_8-8-03.pdf. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-04-22 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
89 | 1072 |  | 3. | 1075 | IRO-006-3 R2.3. | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: http://www.ercot.com/tac/retailisoadhoccommittee/protocols/keydocs/draftercotprotocols.htm. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-04-22 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9 | 79 |  | 1. | 80 | BAL-003-0a R1.1. | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9 | 79 |  | 2. | 81 | BAL-003-0a R1.2. | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9 | 82 |  | 1. | 83 | BAL-003-0a R2.1. | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9 | 82 |  | 2. | 84 | BAL-003-0a R2.2. | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9 | 86 |  | 1. | 87 | BAL-003-0a R4.1. | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9 | 86 |  | 2. | 88 | BAL-003-0a R4.2. | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9 | 89 |  | 1. | 90 | BAL-003-0a R5.1. | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
90 | 1080 |  | 1. | 1081 | IRO-006-4 R1.1. | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection provided in Attachment 1-IRO-006-4. The TLR procedure alone is an inappropriate and ineffective tool to mitigate an IROL violation due to the time required to implement the procedure. Other acceptable and more effective procedures to mitigate actual IROL violations include: reconfiguration, redispatch, or load shedding. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-23 |  | 2009-12-09 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
90 | 1080 |  | 2. | 1082 | IRO-006-4 R1.2. | The Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is WECC-IRO-STD-006-0 provided at: ftp://www.nerc.com/pub/sys/all_updl/standards/rrs/IRO-STD-006- 0_17Jan07.pdf. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-23 |  | 2009-12-09 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
90 | 1080 |  | 3. | 1083 | IRO-006-4 R1.3. | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: http://www.ercot.com/mktrules/protocols/current.html |  | RC | [11 empty] | RC | [10 empty] | 2009-04-23 |  | 2009-12-09 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
94 | 1098 |  | 1. | 1099 | IRO-010-1 R1.1. | List of required data and information needed by the Reliability Coordinator to support Real-Time Monitoring, Operational Planning Analyses, and Real-Time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2009-08-05 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
94 | 1098 |  | 2. | 1100 | IRO-010-1 R1.2. | Mutually agreeable format. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2009-08-05 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
94 | 1098 |  | 3. | RP-2021-06-22-0000003 | IRO-010-1 R1.3. | Timeframe and periodicity for providing data and information (based on its hardware and software requirements, and the time needed to do its Operational Planning Analyses). |  | RC | [11 empty] | RC | [12 empty] | 2009-08-05 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
94 | 1098 |  | 4. | 1102 | IRO-010-1 R1.4. | Process for data provision when automated Real-Time system operating data is unavailable. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2009-08-05 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
95 | 1105 | RP-2021-06-22-0000005 | 1. | 1107 | IRO-014-1 R1.1.1. | Communications and notifications, including the conditions under which one Reliability Coordinator notifies other Reliability Coordinators; the process to follow in making those notifications; and the data and information to be exchanged with other Reliability Coordinators. |  | RC | [11 empty] | RC | [9 empty] | M1.1.1 Communications and notifications, including the conditions under which one Reliability Coordinator notifies other Reliability Coordinators; the process to follow in making those notifications; and the data and information to be exchanged with other Reliability Coordinators. | 2007-06-18 |  | 2017-03-31 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
95 | 1105 | RP-2021-06-22-0000005 | 2. | 1108 | IRO-014-1 R1.1.2. | Energy and capacity shortages. |  | RC | [11 empty] | RC | [9 empty] | M1.1.2 Energy and capacity shortages. | 2007-06-18 |  | 2017-03-31 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
95 | 1105 | RP-2021-06-22-0000005 | 3. | 1109 | IRO-014-1 R1.1.3. | Planned or unplanned outage information. |  | RC | [11 empty] | RC | [9 empty] | M1.1.3 Planned or unplanned outage information. | 2007-06-18 |  | 2017-03-31 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
95 | 1105 | RP-2021-06-22-0000005 | 4. | 1110 | IRO-014-1 R1.1.4. | Voltage control, including the coordination of reactive resources for voltage control. |  | RC | [11 empty] | RC | [9 empty] | M1.1.4 Voltage control, including the coordination of reactive resources for voltage control. | 2007-06-18 |  | 2017-03-31 |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
95 | 1105 | RP-2021-06-22-0000005 | 5. | 1111 | IRO-014-1 R1.1.5. | Coordination of information exchange to support reliability assessments. |  | RC | [11 empty] | RC | [9 empty] | M1.1.5 Coordination of information exchange to support reliability assessments. | 2007-06-18 |  | 2017-03-31 |  |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
95 | 1105 | RP-2021-06-22-0000005 | 6. | 1112 | IRO-014-1 R1.1.6. | Authority to act to prevent and mitigate instances of causing Adverse Reliability Impacts to other Reliability Coordinator Areas. |  | RC | [11 empty] | RC | [9 empty] | M1.1.6 Authority to act to prevent and mitigate instances of causing Adverse Reliability Impacts to other Reliability Coordinator Areas. | 2007-06-18 |  | 2017-03-31 |  |  | 116000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
95 | 1105 |  | 1. | RP-2021-06-22-0000005 | IRO-014-1 R1.1. | These Operating Procedures, Processes, or Plans shall collectively address, as a minimum, the following: |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
95 | 1113 |  | 1. | 1114 | IRO-014-1 R2.1. | Agreed to by all the Reliability Coordinators required to take the indicated action(s). |  | RC | [11 empty] | RC | [9 empty] | M2.1 Agreed to by all the Reliability Coordinators required to take the indicated action(s). | 2007-06-18 |  | 2017-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
95 | 1113 |  | 2. | 1115 | IRO-014-1 R2.2. | Distributed to all Reliability Coordinators that are required to take the indicated action(s). |  | RC | [11 empty] | RC | [9 empty] | M2.2 Distributed to all Reliability Coordinators that are required to take the indicated action(s) | 2007-06-18 |  | 2017-03-31 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
95 | 1116 |  | 1. | 1117 | IRO-014-1 R3.1. | A reference to the associated Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan. |  | RC | [11 empty] | RC | [9 empty] | M3.1 Be available to the Reliability Coordinator’s System Operators for Real-time use, | 2007-06-18 |  | 2017-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
95 | 1116 |  | 2. | 1118 | IRO-014-1 R3.2. | The agreed-upon actions from the associated Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan. |  | RC | [11 empty] | RC | [9 empty] | M3.2 Include a reference to the associated source document, and Support the agreed-upon actions from the source document. | 2007-06-18 |  | 2017-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
95 | 1119 |  | 1. | 1120 | IRO-014-1 R4.1. | Include version control number or date. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
95 | 1119 |  | 2. | 1121 | IRO-014-1 R4.2. | Include a distribution list. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
95 | 1119 |  | 3. | 1122 | IRO-014-1 R4.3. | Be reviewed, at least once every three years, and updated if needed. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
96 | 1123 |  | 1. | 1124 | IRO-015-1 R1.1. | The Reliability Coordinator shall make notifications to other Reliability Coordinators of conditions in its Reliability Coordinator Area that may impact other Reliability Coordinator Areas. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
96 | 1125 |  | 1. | 1126 | IRO-015-1 R2.1. | The frequency of these conference calls shall be agreed upon by all involved Reliability Coordinators and shall be at least weekly. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
97 | 1128 | 1130 | 1. | 1131 | IRO-016-1 R1.2.1. | If time permits, this re-evaluation shall be done before taking corrective actions. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
97 | 1128 | 1130 | 2. | 1132 | IRO-016-1 R1.2.2. | If time does not permit, then each Reliability Coordinator shall operate as though the problem(s) exist(s) until the conflicting system status is resolved. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
97 | 1128 |  | 1. | 1129 | IRO-016-1 R1.1. | If the involved Reliability Coordinators agree on the problem and the actions to take to prevent or mitigate the system condition, each involved Reliability Coordinator shall implement the agreed-upon solution, and notify the involved Reliability Coordinators of the action(s) taken. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
97 | 1128 |  | 2. | 1130 | IRO-016-1 R1.2. | If the involved Reliability Coordinators cannot agree on the problem(s) each Reliability Coordinator shall re-evaluate the causes of the disagreement (bad data, status, study results, tools, etc.). |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
97 | 1128 |  | 3. | 1133 | IRO-016-1 R1.3. | If the involved Reliability Coordinators cannot agree on the solution, the more conservative solution shall be implemented. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
99 | 1136 | 1141 | 1. | 1142 | MOD-001-0 R1.5.1. | Daily values for current week at least once per day. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
99 | 1136 | 1141 | 2. | 1143 | MOD-001-0 R1.5.2. | Daily values for day 8 through the first month at least once per week. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
99 | 1136 | 1141 | 3. | 1144 | MOD-001-0 R1.5.3. | Monthly values for months 2 through 13 at least once per month. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 153000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
99 | 1136 |  | 1. | 1137 | MOD-001-0 R1.1. | A narrative explaining how TTC and ATC values are determined. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
99 | 1136 |  | 2. | 1138 | MOD-001-0 R1.2. | An accounting for how the reservations and schedules for firm (non-recallable) and non-firm (recallable) transfers, both within and outside the Transmission Service Provider’s system, are included. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
99 | 1136 |  | 3. | 1139 | MOD-001-0 R1.3. | An accounting for the ultimate points of power injection (sources) and power extraction (sinks) in TTC and ATC calculations. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
99 | 1136 |  | 4. | 1140 | MOD-001-0 R1.4. | A description of how incomplete or so-called partial path transmission reservations are addressed. (Incomplete or partial path transmission reservations are those for which all transmission reservations necessary to complete the transmission path from ultimate source to ultimate sink are not identifiable due to differing reservation priorities, durations, or because the reservations have not all been made.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
99 | 1136 |  | 5. | 1141 | MOD-001-0 R1.5. | A requirement that TTC and ATC values shall be determined and posted as follows: |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
99 | 1136 |  | 6. | 1145 | MOD-001-0 R1.6. | Indication of the treatment and level of customer demands, including interruptible demands. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
99 | 1136 |  | 7. | 1146 | MOD-001-0 R1.7. | A specification of how system conditions, limiting facilities, contingencies, transmission reservations, energy schedules, and other data needed by Transmission Service Providers for the calculation of TTC and ATC values are shared and used within the Regional Reliability Organization and with neighboring interconnected electric systems, including adjacent systems, subregions, and Regional Reliability Organizations. In addition, specify how this information is to be used to determine TTC and ATC values. If some data is not used, provide an explanation. |  | RRO, TSP | [14 empty] | RRO | [5 empty] | TSP |  |  |  | 2009-11-24 |  |  | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
99 | 1136 |  | 8. | 1147 | MOD-001-0 R1.8. | A description of how the assumptions for and the calculations of TTC and ATC values change over different time (such as hourly, daily, and monthly) horizons. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
99 | 1136 |  | 9. | 1148 | MOD-001-0 R1.9. | A description of the Regional Reliability Organization’s practice on the netting of transmission reservations for purposes of TTC and ATC determination. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000001 |  | 1 | RP-2021-04-12-0000001 | FAC-008-5 R1.1 | The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have documentation that shows how its Facility Ratings were determined as identified in Requirement 1. | 2021-10-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000001 |  | 2 | RP-2021-04-12-0000002 | FAC-008-5 R1.2 | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have documentation that shows how its Facility Ratings were determined as identified in Requirement 1. | 2021-10-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000002 |  | 1 | RP-2021-04-12-0000003 | FAC-008-5 R2.1 | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2021-10-01 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000002 |  | 2 | RP-2021-04-12-0000004 | FAC-008-5 R2.2 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2021-10-01 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000002 |  | 2.1. | RP-2021-04-12-0000009 | FAC-008-5 R2.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2021-10-01 |  |  |  |  | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000002 |  | 2.2. | RP-2021-04-12-0000010 | FAC-008-5 R2.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2021-10-01 |  |  |  |  | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000002 |  | 2.3. | RP-2021-04-12-0000005 | FAC-008-5 R2.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2021-10-01 |  |  |  |  | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000002 |  | 2.4. | RP-2021-04-12-0000006 | FAC-008-5 R2.2.4. | Operating limitations. Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2021-10-01 |  |  |  |  | 224000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000002 |  | 3. | RP-2021-04-12-0000007 | FAC-008-5 R2.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2021-10-01 |  |  |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000002 |  | 4. | RP-2021-04-12-0000008 | FAC-008-5 R2.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2021-10-01 |  |  |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000002 |  | 4.1 | RP-2021-04-12-0000011 | FAC-008-5 R2.4.1 | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2021-10-01 |  |  |  |  | 241000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000002 |  | 4.2 | RP-2021-04-12-0000012 | FAC-008-5 R2.4.2 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2021-10-01 |  |  |  |  | 242000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000003 |  | 1 | RP-2021-04-12-0000013 | FAC-008-5 R3.1 | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2021-10-01 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000003 |  | 2 | RP-2021-04-12-0000014 | FAC-008-5 R3.2 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2021-10-01 |  |  |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000003 |  | 2.1. | RP-2021-04-12-0000019 | FAC-008-5 R3.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2021-10-01 |  |  |  |  | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000003 |  | 2.2. | RP-2021-04-12-0000020 | FAC-008-5 R3.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2021-10-01 |  |  |  |  | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000003 |  | 2.3. | RP-2021-04-12-0000015 | FAC-008-5 R3.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2021-10-01 |  |  |  |  | 323000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000003 |  | 2.4. | RP-2021-04-12-0000016 | FAC-008-5 R3.2.4. | Operating limitations. Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2021-10-01 |  |  |  |  | 324000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000003 |  | 3. | RP-2021-04-12-0000017 | FAC-008-5 R3.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2021-10-01 |  |  |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000003 |  | 4. | RP-2021-04-12-0000018 | FAC-008-5 R3.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2021-10-01 |  |  |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000003 |  | 4.1 | RP-2021-04-12-0000021 | FAC-008-5 R3.4.1 | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2021-10-01 |  |  |  |  | 341000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000003 |  | 4.2 | RP-2021-04-12-0000022 | FAC-008-5 R3.4.2 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2021-10-01 |  |  |  |  | 342000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000008 |  | 1 | RP-2021-04-12-0000023 | FAC-008-5 R8.1 | As scheduled by the requesting entities: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2021-10-01 |  |  |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000008 |  | 1.1. | RP-2021-04-12-0000026 | FAC-008-5 R8.1.1. | Facility Ratings |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2021-10-01 |  |  |  |  | 811000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000008 |  | 1.2. | RP-2021-04-12-0000024 | FAC-008-5 R8.1.2. | Identity of the most limiting equipment of the Facilities |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2021-10-01 |  |  |  |  | 812000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000008 |  | 2. | RP-2021-04-12-0000025 | FAC-008-5 R8.2. | Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2021-10-01 |  |  |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000008 |  | 2.1 | RP-2021-04-12-0000027 | FAC-008-5 R8.2.1 | Identity of the existing next most limiting equipment of the Facility |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2021-10-01 |  |  |  |  | 821000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001 | RQ-2021-04-12-0000008 |  | 2.2 | RP-2021-04-12-0000028 | FAC-008-5 R8.2.2 | The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2021-10-01 |  |  |  |  | 822000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000001-MB |  | 1 | RP-2021-04-12-0000001-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R1.1 | The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have documentation that shows how its Facility Ratings were determined as identified in Requirement 1. | 2022-07-01 |  |  |  |  | 110000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000001-MB |  | 2 | RP-2021-04-12-0000002-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R1.2 | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have documentation that shows how its Facility Ratings were determined as identified in Requirement 1. | 2022-07-01 |  |  |  |  | 120000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000002-MB |  | 1 | RP-2021-04-12-0000003-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R2.1 | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-07-01 |  |  |  |  | 210000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000002-MB |  | 2 | RP-2021-04-12-0000004-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R2.2 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-07-01 |  |  |  |  | 220000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000002-MB |  | 2.1. | RP-2021-04-12-0000009-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R2.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-07-01 |  |  |  |  | 221000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000002-MB |  | 2.2. | RP-2021-04-12-0000010-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R2.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-07-01 |  |  |  |  | 222000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000002-MB |  | 2.3. | RP-2021-04-12-0000005-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R2.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-07-01 |  |  |  |  | 223000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000002-MB |  | 2.4. | RP-2021-04-12-0000006-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R2.2.4. | Operating limitations. Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-07-01 |  |  |  |  | 224000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000002-MB |  | 3. | RP-2021-04-12-0000007-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R2.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-07-01 |  |  |  |  | 230000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000002-MB |  | 4. | RP-2021-04-12-0000008-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R2.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-07-01 |  |  |  |  | 240000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000002-MB |  | 4.1 | RP-2021-04-12-0000011-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R2.4.1 | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-07-01 |  |  |  |  | 241000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000002-MB |  | 4.2 | RP-2021-04-12-0000012-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R2.4.2 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-07-01 |  |  |  |  | 242000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000003-MB |  | 1 | RP-2021-04-12-0000013-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R3.1 | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-07-01 |  |  |  |  | 310000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000003-MB |  | 2 | RP-2021-04-12-0000014-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R3.2 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-07-01 |  |  |  |  | 320000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000003-MB |  | 2.1. | RP-2021-04-12-0000019-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R3.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-07-01 |  |  |  |  | 321000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000003-MB |  | 2.2. | RP-2021-04-12-0000020-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R3.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-07-01 |  |  |  |  | 322000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000003-MB |  | 2.3. | RP-2021-04-12-0000015-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R3.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-07-01 |  |  |  |  | 323000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000003-MB |  | 2.4. | RP-2021-04-12-0000016-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R3.2.4. | Operating limitations. Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-07-01 |  |  |  |  | 324000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000003-MB |  | 3. | RP-2021-04-12-0000017-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R3.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-07-01 |  |  |  |  | 330000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000003-MB |  | 4. | RP-2021-04-12-0000018-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R3.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-07-01 |  |  |  |  | 340000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000003-MB |  | 4.1 | RP-2021-04-12-0000021-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R3.4.1 | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-07-01 |  |  |  |  | 341000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000003-MB |  | 4.2 | RP-2021-04-12-0000022-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R3.4.2 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-07-01 |  |  |  |  | 342000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000008-MB |  | 1 | RP-2021-04-12-0000023-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R8.1 | As scheduled by the requesting entities: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2022-07-01 |  |  |  |  | 810000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000008-MB |  | 1.1. | RP-2021-04-12-0000026-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R8.1.1. | Facility Ratings |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2022-07-01 |  |  |  |  | 811000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000008-MB |  | 1.2. | RP-2021-04-12-0000024-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R8.1.2. | Identity of the most limiting equipment of the Facilities |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2022-07-01 |  |  |  |  | 812000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000008-MB |  | 2. | RP-2021-04-12-0000025-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R8.2. | Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2022-07-01 |  |  |  |  | 820000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000008-MB |  | 2.1 | RP-2021-04-12-0000027-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R8.2.1 | Identity of the existing next most limiting equipment of the Facility |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2022-07-01 |  |  |  |  | 821000000 | MRO-MB
ST-2021-04-12-0000001-MB | RQ-2021-04-12-0000008-MB |  | 2.2 | RP-2021-04-12-0000028-MB | FAC-008-5 (Excl. R4, R5) (Manitoba) R8.2.2 | The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2022-07-01 |  |  |  |  | 822000000 | MRO-MB
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000001-NS |  | 1 | RP-2021-04-12-0000001-NS | FAC-008-5 (Nova Scotia) R1.1 | The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have documentation that shows how its Facility Ratings were determined as identified in Requirement 1. | 2022-01-01 |  |  |  |  | 110000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000001-NS |  | 2 | RP-2021-04-12-0000002-NS | FAC-008-5 (Nova Scotia) R1.2 | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have documentation that shows how its Facility Ratings were determined as identified in Requirement 1. | 2022-01-01 |  |  |  |  | 120000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000002-NS |  | 1 | RP-2021-04-12-0000003-NS | FAC-008-5 (Nova Scotia) R2.1 | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-01-01 |  |  |  |  | 210000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000002-NS |  | 2 | RP-2021-04-12-0000004-NS | FAC-008-5 (Nova Scotia) R2.2 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-01-01 |  |  |  |  | 220000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000002-NS |  | 2.1. | RP-2021-04-12-0000009-NS | FAC-008-5 (Nova Scotia) R2.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-01-01 |  |  |  |  | 221000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000002-NS |  | 2.2. | RP-2021-04-12-0000010-NS | FAC-008-5 (Nova Scotia) R2.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-01-01 |  |  |  |  | 222000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000002-NS |  | 2.3. | RP-2021-04-12-0000005-NS | FAC-008-5 (Nova Scotia) R2.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-01-01 |  |  |  |  | 223000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000002-NS |  | 2.4. | RP-2021-04-12-0000006-NS | FAC-008-5 (Nova Scotia) R2.2.4. | Operating limitations. Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-01-01 |  |  |  |  | 224000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000002-NS |  | 3. | RP-2021-04-12-0000007-NS | FAC-008-5 (Nova Scotia) R2.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-01-01 |  |  |  |  | 230000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000002-NS |  | 4. | RP-2021-04-12-0000008-NS | FAC-008-5 (Nova Scotia) R2.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-01-01 |  |  |  |  | 240000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000002-NS |  | 4.1 | RP-2021-04-12-0000011-NS | FAC-008-5 (Nova Scotia) R2.4.1 | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-01-01 |  |  |  |  | 241000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000002-NS |  | 4.2 | RP-2021-04-12-0000012-NS | FAC-008-5 (Nova Scotia) R2.4.2 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 2, Parts 2.1 through 2.4. | 2022-01-01 |  |  |  |  | 242000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000003-NS |  | 1 | RP-2021-04-12-0000013-NS | FAC-008-5 (Nova Scotia) R3.1 | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-01-01 |  |  |  |  | 310000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000003-NS |  | 2 | RP-2021-04-12-0000014-NS | FAC-008-5 (Nova Scotia) R3.2 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-01-01 |  |  |  |  | 320000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000003-NS |  | 2.1. | RP-2021-04-12-0000019-NS | FAC-008-5 (Nova Scotia) R3.2.1. | Equipment Rating standard(s) used in development of this methodology. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-01-01 |  |  |  |  | 321000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000003-NS |  | 2.2. | RP-2021-04-12-0000020-NS | FAC-008-5 (Nova Scotia) R3.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-01-01 |  |  |  |  | 322000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000003-NS |  | 2.3. | RP-2021-04-12-0000015-NS | FAC-008-5 (Nova Scotia) R3.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-01-01 |  |  |  |  | 323000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000003-NS |  | 2.4. | RP-2021-04-12-0000016-NS | FAC-008-5 (Nova Scotia) R3.2.4. | Operating limitations. Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-01-01 |  |  |  |  | 324000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000003-NS |  | 3. | RP-2021-04-12-0000017-NS | FAC-008-5 (Nova Scotia) R3.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-01-01 |  |  |  |  | 330000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000003-NS |  | 4. | RP-2021-04-12-0000018-NS | FAC-008-5 (Nova Scotia) R3.4. | The process by which the Rating of equipment that comprises a Facility is determined. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-01-01 |  |  |  |  | 340000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000003-NS |  | 4.1 | RP-2021-04-12-0000021-NS | FAC-008-5 (Nova Scotia) R3.4.1 | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-01-01 |  |  |  |  | 341000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000003-NS |  | 4.2 | RP-2021-04-12-0000022-NS | FAC-008-5 (Nova Scotia) R3.4.2 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have a documented Facility Ratings methodology that includes all of the items identified in Requirement 3, Parts 3.1 through 3.4. | 2022-01-01 |  |  |  |  | 342000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000008-NS |  | 1 | RP-2021-04-12-0000023-NS | FAC-008-5 (Nova Scotia) R8.1 | As scheduled by the requesting entities: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2022-01-01 |  |  |  |  | 810000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000008-NS |  | 1.1. | RP-2021-04-12-0000026-NS | FAC-008-5 (Nova Scotia) R8.1.1. | Facility Ratings |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2022-01-01 |  |  |  |  | 811000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000008-NS |  | 1.2. | RP-2021-04-12-0000024-NS | FAC-008-5 (Nova Scotia) R8.1.2. | Identity of the most limiting equipment of the Facilities |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2022-01-01 |  |  |  |  | 812000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000008-NS |  | 2. | RP-2021-04-12-0000025-NS | FAC-008-5 (Nova Scotia) R8.2. | Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2022-01-01 |  |  |  |  | 820000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000008-NS |  | 2.1 | RP-2021-04-12-0000027-NS | FAC-008-5 (Nova Scotia) R8.2.1 | Identity of the existing next most limiting equipment of the Facility |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2022-01-01 |  |  |  |  | 821000000 | NPCC-NS
ST-2021-04-12-0000001-NS | RQ-2021-04-12-0000008-NS |  | 2.2 | RP-2021-04-12-0000028-NS | FAC-008-5 (Nova Scotia) R8.2.2 | The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner (and Generator Owner subject to Requirement R2) shall have evidence, such as a copy of a dated electronic note, or other comparable evidence to show that it provided its Facility Ratings and identity of limiting equipment to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) in accordance with Requirement R8. | 2022-01-01 |  |  |  |  | 822000000 | NPCC-NS
ST-2021-06-24-0000001 | RQ-2021-06-24-0000001 |  | 1. | RP-2021-06-24-0000078 | EOP-011-2 R1.1. | Roles and responsibilities for activating the Operating Plan(s); |  | TOP | [18 empty] | TOP |  |  |  | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000001 |  | 2. | RP-2021-06-24-0000079 | EOP-011-2 R1.2. | Processes to prepare for and mitigate Emergencies including: |  | TOP | [18 empty] | TOP |  |  |  | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000001 |  | 2.1. | RP-2021-06-24-0000080 | EOP-011-2 R1.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; |  | TOP | [18 empty] | TOP |  |  |  | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000001 |  | 2.2. | RP-2021-06-24-0000081 | EOP-011-2 R1.2.2. | Cancellation or recall of Transmission and generation outages; |  | TOP | [18 empty] | TOP |  |  |  | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000001 |  | 2.3. | RP-2021-06-24-0000082 | EOP-011-2 R1.2.3. | Transmission system reconfiguration; |  | TOP | [18 empty] | TOP |  |  |  | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000001 |  | 2.4. | RP-2021-06-24-0000083 | EOP-011-2 R1.2.4. | Redispatch of generation request; |  | TOP | [18 empty] | TOP |  |  |  | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000001 |  | 2.5. | RP-2021-06-24-0000084 | EOP-011-2 R1.2.5. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and |  | TOP | [18 empty] | TOP |  |  |  | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000001 |  | 2.6. | RP-2021-06-24-0000085 | EOP-011-2 R1.2.6. | Provisions to determine reliability impacts of: |  | TOP | [18 empty] | TOP |  |  |  | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000001 |  | 2.6.1. | RP-2021-06-24-0000086 | EOP-011-2 R1.2.6.1. | cold weather conditions; and |  | TOP | [18 empty] | TOP |  |  |  | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 126100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000001 |  | 2.6.2. | RP-2021-06-24-0000087 | EOP-011-2 R1.2.6.2. | extreme weather conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 126200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 1. | RP-2021-06-24-0000088 | EOP-011-2 R2.1. | Roles and responsibilities for activating the Operating Plan(s); |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2. | RP-2021-06-24-0000089 | EOP-011-2 R2.2. | Processes to prepare for and mitigate Emergencies including: |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2.1. | RP-2021-06-24-0000090 | EOP-011-2 R2.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2.2. | RP-2021-06-24-0000091 | EOP-011-2 R2.2.2. | Requesting an Energy Emergency Alert, per Attachment 1; |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2.3. | RP-2021-06-24-0000092 | EOP-011-2 R2.2.3. | Managing generating resources in its Balancing Authority Area to address: |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2.3.1. | RP-2021-06-24-0000093 | EOP-011-2 R2.2.3.1. | capability and availability; |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 223100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2.3.2. | RP-2021-06-24-0000094 | EOP-011-2 R2.2.3.2. | fuel supply and inventory concerns; |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 223200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2.3.3. | RP-2021-06-24-0000095 | EOP-011-2 R2.2.3.3. | fuel switching capabilities; and |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 223300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2.3.4. | RP-2021-06-24-0000096 | EOP-011-2 R2.2.3.4. | environmental constraints. |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 223400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2.4. | RP-2021-06-24-0000097 | EOP-011-2 R2.2.4. | Public appeals for voluntary Load reductions; |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 224000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2.5. | RP-2021-06-24-0000098 | EOP-011-2 R2.2.5. | Requests to government agencies to implement their programs to achieve necessary energy reductions; |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 225000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2.6. | RP-2021-06-24-0000099 | EOP-011-2 R2.2.6. | Reduction of internal utility energy use; |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 226000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2.7. | RP-2021-06-24-0000100 | EOP-011-2 R2.2.7. | Use of Interruptible Load, curtailable Load and demand response; |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 227000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2.8. | RP-2021-06-24-0000101 | EOP-011-2 R2.2.8. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 228000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2.9. | RP-2021-06-24-0000102 | EOP-011-2 R2.2.9. | Provisions to determine reliability impacts of: |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 229000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2.9.1. | RP-2021-06-24-0000103 | EOP-011-2 R2.2.9.1. | cold weather conditions; and |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 229100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000002 |  | 2.9.2. | RP-2021-06-24-0000104 | EOP-011-2 R2.2.9.2. | extreme weather conditions. |  | BA | BA | [21 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 229200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000003 |  | 1. | RP-2021-06-24-0000105 | EOP-011-2 R3.1. | Within 30 calendar days of receipt, the Reliability Coordinator shall: |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000003 |  | 1.1. | RP-2021-06-24-0000106 | EOP-011-2 R3.1.1. | Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000003 |  | 1.2. | RP-2021-06-24-0000107 | EOP-011-2 R3.1.2. | Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000003 |  | 1.3. | RP-2021-06-24-0000108 | EOP-011-2 R3.1.3. | Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000007 | RP-2021-06-24-0000111 | 1. | RP-2021-06-24-0000112 | EOP-011-2 R7.3.1. | Generating unit(s) operating limitations in cold weather to include: |  | GO |  |  |  |  | GO | [17 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 731000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000007 | RP-2021-06-24-0000111 | 2. | RP-2021-06-24-0000117 | EOP-011-2 R7.3.2. | Generating unit(s) minimum: |  | GO |  |  |  |  | GO | [17 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 732000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000007 | RP-2021-06-24-0000112 | 1. | RP-2021-06-24-0000113 | EOP-011-2 R7.3.1.1. | capability and availability; |  | GO |  |  |  |  | GO | [17 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 101100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000007 | RP-2021-06-24-0000112 | 2. | RP-2021-06-24-0000114 | EOP-011-2 R7.3.1.2. | fuel supply and inventory concerns; |  | GO |  |  |  |  | GO | [17 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 101200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000007 | RP-2021-06-24-0000112 | 4. | RP-2021-06-24-0000116 | EOP-011-2 R7.3.1.4. | environmental constraints. |  | GO |  |  |  |  | GO | [17 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 101400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000007 | RP-2021-06-24-0000117 | 1. | RP-2021-06-24-0000118 | EOP-011-2 R7.3.2.1. | design temperature; or |  | GO |  |  |  |  | GO | [17 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 102100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000007 | RP-2021-06-24-0000117 | 2. | RP-2021-06-24-0000119 | EOP-011-2 R7.3.2.2. | historical operating temperature; or |  | GO |  |  |  |  | GO | [17 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 102200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000007 | RP-2021-06-24-0000117 | 3. | RP-2021-06-24-0000120 | EOP-011-2 R7.3.2.3. | current cold weather performance temperature determined by an engineering analysis. |  | GO |  |  |  |  | GO | [17 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 101300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000007 |  | 1. | RP-2021-06-24-0000109 | EOP-011-2 R7.1. | Generating unit(s) freeze protection measures based on geographical location and plant configuration; |  | GO |  |  |  |  | GO | [17 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000007 |  | 2. | RP-2021-06-24-0000110 | EOP-011-2 R7.2. | Annual inspection and maintenance of generating unit(s) freeze protection measures; |  | GO |  |  |  |  | GO | [17 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001 | RQ-2021-06-24-0000007 |  | 3. | RP-2021-06-24-0000111 | EOP-011-2 R7.3. | Generating unit(s) cold weather data, to include: |  | GO |  |  |  |  | GO | [17 empty] | 2023-04-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000001-NS |  | 1. | RP-2021-06-24-0000078-NS | EOP-011-2 (Nova Scotia) R1.1. | Roles and responsibilities for activating the Operating Plan(s); |  | TOP | [18 empty] | TOP |  |  |  | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 110000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000001-NS |  | 2. | RP-2021-06-24-0000079-NS | EOP-011-2 (Nova Scotia) R1.2. | Processes to prepare for and mitigate Emergencies including: |  | TOP | [18 empty] | TOP |  |  |  | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 120000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000001-NS |  | 2.1. | RP-2021-06-24-0000080-NS | EOP-011-2 (Nova Scotia) R1.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; |  | TOP | [18 empty] | TOP |  |  |  | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 121000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000001-NS |  | 2.2. | RP-2021-06-24-0000081-NS | EOP-011-2 (Nova Scotia) R1.2.2. | Cancellation or recall of Transmission and generation outages; |  | TOP | [18 empty] | TOP |  |  |  | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 122000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000001-NS |  | 2.3. | RP-2021-06-24-0000082-NS | EOP-011-2 (Nova Scotia) R1.2.3. | Transmission system reconfiguration; |  | TOP | [18 empty] | TOP |  |  |  | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 123000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000001-NS |  | 2.4. | RP-2021-06-24-0000083-NS | EOP-011-2 (Nova Scotia) R1.2.4. | Redispatch of generation request; |  | TOP | [18 empty] | TOP |  |  |  | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 124000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000001-NS |  | 2.5. | RP-2021-06-24-0000084-NS | EOP-011-2 (Nova Scotia) R1.2.5. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and |  | TOP | [18 empty] | TOP |  |  |  | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 125000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000001-NS |  | 2.6. | RP-2021-06-24-0000085-NS | EOP-011-2 (Nova Scotia) R1.2.6. | Provisions to determine reliability impacts of: |  | TOP | [18 empty] | TOP |  |  |  | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 126000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000001-NS |  | 2.6.1. | RP-2021-06-24-0000086-NS | EOP-011-2 (Nova Scotia) R1.2.6.1. | cold weather conditions; and |  | TOP | [18 empty] | TOP |  |  |  | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 126100000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000001-NS |  | 2.6.2. | RP-2021-06-24-0000087-NS | EOP-011-2 (Nova Scotia) R1.2.6.2. | extreme weather conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 126200000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 1. | RP-2021-06-24-0000088-NS | EOP-011-2 (Nova Scotia) R2.1. | Roles and responsibilities for activating the Operating Plan(s); |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 210000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2. | RP-2021-06-24-0000089-NS | EOP-011-2 (Nova Scotia) R2.2. | Processes to prepare for and mitigate Emergencies including: |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 220000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2.1. | RP-2021-06-24-0000090-NS | EOP-011-2 (Nova Scotia) R2.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 221000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2.2. | RP-2021-06-24-0000091-NS | EOP-011-2 (Nova Scotia) R2.2.2. | Requesting an Energy Emergency Alert, per Attachment 1; |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 222000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2.3. | RP-2021-06-24-0000092-NS | EOP-011-2 (Nova Scotia) R2.2.3. | Managing generating resources in its Balancing Authority Area to address: |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 223000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2.3.1. | RP-2021-06-24-0000093-NS | EOP-011-2 (Nova Scotia) R2.2.3.1. | capability and availability; |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 223100000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2.3.2. | RP-2021-06-24-0000094-NS | EOP-011-2 (Nova Scotia) R2.2.3.2. | fuel supply and inventory concerns; |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 223200000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2.3.3. | RP-2021-06-24-0000095-NS | EOP-011-2 (Nova Scotia) R2.2.3.3. | fuel switching capabilities; and |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 223300000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2.3.4. | RP-2021-06-24-0000096-NS | EOP-011-2 (Nova Scotia) R2.2.3.4. | environmental constraints. |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 223400000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2.4. | RP-2021-06-24-0000097-NS | EOP-011-2 (Nova Scotia) R2.2.4. | Public appeals for voluntary Load reductions; |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 224000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2.5. | RP-2021-06-24-0000098-NS | EOP-011-2 (Nova Scotia) R2.2.5. | Requests to government agencies to implement their programs to achieve necessary energy reductions; |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 225000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2.6. | RP-2021-06-24-0000099-NS | EOP-011-2 (Nova Scotia) R2.2.6. | Reduction of internal utility energy use; |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 226000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2.7. | RP-2021-06-24-0000100-NS | EOP-011-2 (Nova Scotia) R2.2.7. | Use of Interruptible Load, curtailable Load and demand response; |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 227000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2.8. | RP-2021-06-24-0000101-NS | EOP-011-2 (Nova Scotia) R2.2.8. | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 228000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2.9. | RP-2021-06-24-0000102-NS | EOP-011-2 (Nova Scotia) R2.2.9. | Provisions to determine reliability impacts of: |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 229000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2.9.1. | RP-2021-06-24-0000103-NS | EOP-011-2 (Nova Scotia) R2.2.9.1. | cold weather conditions; and |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 229100000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000002-NS |  | 2.9.2. | RP-2021-06-24-0000104-NS | EOP-011-2 (Nova Scotia) R2.2.9.2. | extreme weather conditions. |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 229200000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000003-NS |  | 1. | RP-2021-06-24-0000105-NS | EOP-011-2 (Nova Scotia) R3.1. | Within 30 calendar days of receipt, the Reliability Coordinator shall: |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 310000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000003-NS |  | 1.1. | RP-2021-06-24-0000106-NS | EOP-011-2 (Nova Scotia) R3.1.1. | Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 311000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000003-NS |  | 1.2. | RP-2021-06-24-0000107-NS | EOP-011-2 (Nova Scotia) R3.1.2. | Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 312000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000003-NS |  | 1.3. | RP-2021-06-24-0000108-NS | EOP-011-2 (Nova Scotia) R3.1.3. | Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 313000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000007-NS | RP-2021-06-24-0000111-NS | 1. | RP-2021-06-24-0000112-NS | EOP-011-2 (Nova Scotia) R7.3.1. | Generating unit(s) operating limitations in cold weather to include: |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 731000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000007-NS | RP-2021-06-24-0000111-NS | 2. | RP-2021-06-24-0000117-NS | EOP-011-2 (Nova Scotia) R7.3.2. | Generating unit(s) minimum: |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 732000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000007-NS | RP-2021-06-24-0000112-NS | 1. | RP-2021-06-24-0000113-NS | EOP-011-2 (Nova Scotia) R7.3.1.1. | capability and availability; |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 101100000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000007-NS | RP-2021-06-24-0000112-NS | 2. | RP-2021-06-24-0000114-NS | EOP-011-2 (Nova Scotia) R7.3.1.2. | fuel supply and inventory concerns; |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 101200000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000007-NS | RP-2021-06-24-0000112-NS | 3. | RP-2021-06-24-0000120-NS | EOP-011-2 (Nova Scotia) R7.3.1.3. | current cold weather performance temperature determined by an engineering analysis. |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 101300000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000007-NS | RP-2021-06-24-0000112-NS | 4. | RP-2021-06-24-0000116-NS | EOP-011-2 (Nova Scotia) R7.3.1.4. | environmental constraints. |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 101400000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000007-NS | RP-2021-06-24-0000117-NS | 1. | RP-2021-06-24-0000118-NS | EOP-011-2 (Nova Scotia) R7.3.2.1. | design temperature; or |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 102100000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000007-NS | RP-2021-06-24-0000117-NS | 2. | RP-2021-06-24-0000119-NS | EOP-011-2 (Nova Scotia) R7.3.2.2. | historical operating temperature; or |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 102200000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000007-NS |  | 1. | RP-2021-06-24-0000109-NS | EOP-011-2 (Nova Scotia) R7.1. | Generating unit(s) freeze protection measures based on geographical location and plant configuration; |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 710000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000007-NS |  | 2. | RP-2021-06-24-0000110-NS | EOP-011-2 (Nova Scotia) R7.2. | Annual inspection and maintenance of generating unit(s) freeze protection measures; |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 720000000 | NPCC-NS
ST-2021-06-24-0000001-NS | RQ-2021-06-24-0000007-NS |  | 3. | RP-2021-06-24-0000111-NS | EOP-011-2 (Nova Scotia) R7.3. | Generating unit(s) cold weather data, to include: |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. | 730000000 | NPCC-NS
ST-2021-06-24-0000002 | RQ-2021-06-24-0000009 |  | 1. | RP-2021-06-24-0000121 | IRO-010-4 R1.1. | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  | 2025-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000009 |  | 2. | RP-2021-06-24-0000122 | IRO-010-4 R1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  | 2025-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000009 |  | 3. | RP-2021-06-24-0000123 | IRO-010-4 R1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  | 2025-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000009 |  | 3.1. | RP-2021-06-24-0000133 | IRO-010-4 R1.3.1. | Operating limitations based on: |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  | 2025-06-30 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000009 |  | 3.1.1. | RP-2021-06-24-0000134 | IRO-010-4 R1.3.1.1. | capability and availability; |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  | 2025-06-30 |  |  | 131100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000009 |  | 3.1.2. | RP-2021-06-24-0000124 | IRO-010-4 R1.3.1.2. | fuel supply and inventory concerns; |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  | 2025-06-30 |  |  | 131200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000009 |  | 3.1.3. | RP-2021-06-24-0000129 | IRO-010-4 R1.3.1.3. | fuel switching capabilities; and |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  | 2025-06-30 |  |  | 131300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000009 |  | 3.1.4. | RP-2021-06-24-0000125 | IRO-010-4 R1.3.1.4. | environmental constraints |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  | 2025-06-30 |  |  | 131400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000009 |  | 3.2. | RP-2021-06-24-0000126 | IRO-010-4 R1.3.2. | Generating unit(s) minimum: |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  | 2025-06-30 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000009 |  | 3.2.1. | RP-2021-06-24-0000127 | IRO-010-4 R1.3.2.1. | design temperature; or |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  | 2025-06-30 |  |  | 132100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000009 |  | 3.2.2. | RP-2021-06-24-0000128 | IRO-010-4 R1.3.2.2. | historical operating temperature; or |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  | 2025-06-30 |  |  | 132200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000009 |  | 3.2.3. | RP-2021-06-24-0000130 | IRO-010-4 R1.3.2.3. | current cold weather performance temperature determined by an engineering analysis. |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  | 2025-06-30 |  |  | 132300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000009 |  | 4. | RP-2021-06-24-0000131 | IRO-010-4 R1.4. | A periodicity for providing data. |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  | 2025-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000009 |  | 5. | RP-2021-06-24-0000132 | IRO-010-4 R1.5. | The deadline by which the respondent is to provide the indicated data. |  | RC | [11 empty] | RC | [10 empty] | 2023-04-01 |  | 2025-06-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000011 |  | 1. | RP-2021-06-24-0000135 | IRO-010-4 R3.1. | A mutually agreeable format |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-04-01 |  | 2025-06-30 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000011 |  | 2. | RP-2021-06-24-0000136 | IRO-010-4 R3.2. | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-04-01 |  | 2025-06-30 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002 | RQ-2021-06-24-0000011 |  | 3. | RP-2021-06-24-0000137 | IRO-010-4 R3.3. | A mutually agreeable security protocol |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-04-01 |  | 2025-06-30 |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000009-NS |  | 1. | RP-2021-06-24-0000121-NS | IRO-010-4 (Nova Scotia) R1.1. | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  |  | 110000000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000009-NS |  | 2. | RP-2021-06-24-0000122-NS | IRO-010-4 (Nova Scotia) R1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  |  | 120000000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000009-NS |  | 3. | RP-2021-06-24-0000123-NS | IRO-010-4 (Nova Scotia) R1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 130000000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000009-NS |  | 3.1. | RP-2021-06-24-0000133-NS | IRO-010-4 (Nova Scotia) R1.3.1. | Operating limitations based on: |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  |  | 131000000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000009-NS |  | 3.1.1. | RP-2021-06-24-0000134-NS | IRO-010-4 (Nova Scotia) R1.3.1.1. | capability and availability; |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  |  | 131100000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000009-NS |  | 3.1.2. | RP-2021-06-24-0000124-NS | IRO-010-4 (Nova Scotia) R1.3.1.2. | fuel supply and inventory concerns; |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  |  | 131200000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000009-NS |  | 3.1.3. | RP-2021-06-24-0000129-NS | IRO-010-4 (Nova Scotia) R1.3.1.3. | fuel switching capabilities; and |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  |  | 131300000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000009-NS |  | 3.1.4. | RP-2021-06-24-0000125-NS | IRO-010-4 (Nova Scotia) R1.3.1.4. | environmental constraints |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  |  | 131400000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000009-NS |  | 3.2. | RP-2021-06-24-0000126-NS | IRO-010-4 (Nova Scotia) R1.3.2. | Generating unit(s) minimum: |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  |  | 132000000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000009-NS |  | 3.2.1. | RP-2021-06-24-0000127-NS | IRO-010-4 (Nova Scotia) R1.3.2.1. | design temperature; or |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  |  | 132100000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000009-NS |  | 3.2.2. | RP-2021-06-24-0000128-NS | IRO-010-4 (Nova Scotia) R1.3.2.2. | historical operating temperature; or |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  |  | 132200000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000009-NS |  | 3.2.3. | RP-2021-06-24-0000130-NS | IRO-010-4 (Nova Scotia) R1.3.2.3. | current cold weather performance temperature determined by an engineering analysis. |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  |  | 132300000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000009-NS |  | 4. | RP-2021-06-24-0000131-NS | IRO-010-4 (Nova Scotia) R1.4. | A periodicity for providing data. |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  |  | 140000000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000009-NS |  | 5. | RP-2021-06-24-0000132-NS | IRO-010-4 (Nova Scotia) R1.5. | The deadline by which the respondent is to provide the indicated data. |  | RC | [11 empty] | RC | [10 empty] | 2023-07-01 |  |  |  |  | 150000000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000011-NS |  | 1. | RP-2021-06-24-0000135-NS | IRO-010-4 (Nova Scotia) R3.1. | A mutually agreeable format |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 310000000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000011-NS |  | 2. | RP-2021-06-24-0000136-NS | IRO-010-4 (Nova Scotia) R3.2. | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 320000000 | NPCC-NS
ST-2021-06-24-0000002-NS | RQ-2021-06-24-0000011-NS |  | 3. | RP-2021-06-24-0000137-NS | IRO-010-4 (Nova Scotia) R3.3. | A mutually agreeable security protocol |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 330000000 | NPCC-NS
ST-2021-06-24-0000003 | RQ-2021-06-24-0000012 |  | 1. | RP-2021-06-24-0000138 | TOP-003-5 R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000012 |  | 2. | RP-2021-06-24-0000139 | TOP-003-5 R1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000012 |  | 3. | RP-2021-06-24-0000140 | TOP-003-5 R1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000012 |  | 3.1. | RP-2021-06-24-0000141 | TOP-003-5 R1.3.1. | Operating limitations based on: |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000012 |  | 3.1.1. | RP-2021-06-24-0000142 | TOP-003-5 R1.3.1.1. | capability and availability; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 131100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000012 |  | 3.1.2. | RP-2021-06-24-0000143 | TOP-003-5 R1.3.1.2. | fuel supply and inventory concerns; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 131200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000012 |  | 3.1.3. | RP-2021-06-24-0000144 | TOP-003-5 R1.3.1.3. | fuel switching capabilities; and |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 131300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000012 |  | 3.1.4. | RP-2021-06-24-0000145 | TOP-003-5 R1.3.1.4. | environmental constraints |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 131400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000012 |  | 3.2. | RP-2021-06-24-0000146 | TOP-003-5 R1.3.2. | Generating unit(s) minimum: |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000012 |  | 3.2.1. | RP-2021-06-24-0000147 | TOP-003-5 R1.3.2.1. | design temperature; or |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 132100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000012 |  | 3.2.2. | RP-2021-06-24-0000148 | TOP-003-5 R1.3.2.2. | historical operating temperature; or |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 132200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000012 |  | 3.2.3. | RP-2021-06-24-0000149 | TOP-003-5 R1.3.2.3. | current cold weather performance temperature determined by an engineering analysis. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 132300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000012 |  | 4. | RP-2021-06-24-0000150 | TOP-003-5 R1.4. | A periodicity for providing data. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000012 |  | 5. | RP-2021-06-24-0000151 | TOP-003-5 R1.5. | The deadline by which the respondent is to provide the indicated data. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000013 | RP-2021-06-24-0000154 | 1. | RP-2021-06-24-0000155 | TOP-003-5 R2.3.1. | Operating limitations based on: |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 231000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000013 | RP-2021-06-24-0000154 | 2. | RP-2021-06-24-0000160 | TOP-003-5 R2.3.2. | Generating unit(s) minimum: |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 232000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000013 | RP-2021-06-24-0000155 | 1. | RP-2021-06-24-0000156 | TOP-003-5 R2.3.1.1. | capability and availability; |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000013 | RP-2021-06-24-0000155 | 2. | RP-2021-06-24-0000157 | TOP-003-5 R2.3.1.2. | fuel supply and inventory concerns; |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000013 | RP-2021-06-24-0000155 | 3. | RP-2021-06-24-0000158 | TOP-003-5 R2.3.1.3. | fuel switching capabilities; and |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000013 | RP-2021-06-24-0000155 | 4. | RP-2021-06-24-0000159 | TOP-003-5 R2.3.1.4. | environmental constraints. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 51400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000013 | RP-2021-06-24-0000160 | 1. | RP-2021-06-24-0000161 | TOP-003-5 R2.3.2.1. | design temperature; or |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 52100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000013 | RP-2021-06-24-0000160 | 2. | RP-2021-06-24-0000162 | TOP-003-5 R2.3.2.2. | historical operating temperature; or |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 52200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000013 | RP-2021-06-24-0000160 | 3. | RP-2021-06-24-0000163 | TOP-003-5 R2.3.2.3. | current cold weather performance temperature determined by an engineering analysis. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000013 |  | 1. | RP-2021-06-24-0000152 | TOP-003-5 R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000013 |  | 2. | RP-2021-06-24-0000153 | TOP-003-5 R2.2. | Provisions for notification of current Protection System and Remedial Action Scheme status or degradation that impacts System reliability. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000013 |  | 3. | RP-2021-06-24-0000154 | TOP-003-5 R2.3. | Provisions for notification of BES generating unit(s) status during local forecasted cold weather to include: |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000013 |  | 4. | RP-2021-06-24-0000164 | TOP-003-5 R2.4. | A periodicity for providing data. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000013 |  | 5. | RP-2021-06-24-0000166 | TOP-003-5 R2.5. | The deadline by which the respondent is to provide the indicated data. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-04-01 |  | 2025-06-30 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000016 |  | 1. | RP-2021-06-24-0000167 | TOP-003-5 R5.1. | A mutually agreeable format |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2023-04-01 |  | 2025-06-30 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000016 |  | 2. | RP-2021-06-24-0000168 | TOP-003-5 R5.2. | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2023-04-01 |  | 2025-06-30 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003 | RQ-2021-06-24-0000016 |  | 3. | RP-2021-06-24-0000169 | TOP-003-5 R5.3. | A mutually agreeable security protocol |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2023-04-01 |  | 2025-06-30 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000012-NS |  | 1. | RP-2021-06-24-0000138-NS | TOP-003-5 (Nova Scotia) R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 110000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000012-NS |  | 2. | RP-2021-06-24-0000139-NS | TOP-003-5 (Nova Scotia) R1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 120000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000012-NS |  | 3. | RP-2021-06-24-0000140-NS | TOP-003-5 (Nova Scotia) R1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 130000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000012-NS |  | 3.1. | RP-2021-06-24-0000141-NS | TOP-003-5 (Nova Scotia) R1.3.1. | Operating limitations based on: |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 131000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000012-NS |  | 3.1.1. | RP-2021-06-24-0000142-NS | TOP-003-5 (Nova Scotia) R1.3.1.1. | capability and availability; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 131100000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000012-NS |  | 3.1.2. | RP-2021-06-24-0000143-NS | TOP-003-5 (Nova Scotia) R1.3.1.2. | fuel supply and inventory concerns; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 131200000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000012-NS |  | 3.1.3. | RP-2021-06-24-0000144-NS | TOP-003-5 (Nova Scotia) R1.3.1.3. | fuel switching capabilities; and |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 131300000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000012-NS |  | 3.1.4. | RP-2021-06-24-0000145-NS | TOP-003-5 (Nova Scotia) R1.3.1.4. | environmental constraints |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 131400000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000012-NS |  | 3.2. | RP-2021-06-24-0000146-NS | TOP-003-5 (Nova Scotia) R1.3.2. | Generating unit(s) minimum: |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 132000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000012-NS |  | 3.2.1. | RP-2021-06-24-0000147-NS | TOP-003-5 (Nova Scotia) R1.3.2.1. | design temperature; or |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 132100000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000012-NS |  | 3.2.2. | RP-2021-06-24-0000148-NS | TOP-003-5 (Nova Scotia) R1.3.2.2. | historical operating temperature; or |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 132200000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000012-NS |  | 3.2.3. | RP-2021-06-24-0000149-NS | TOP-003-5 (Nova Scotia) R1.3.2.3. | current cold weather performance temperature determined by an engineering analysis. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 132300000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000012-NS |  | 4. | RP-2021-06-24-0000150-NS | TOP-003-5 (Nova Scotia) R1.4. | A periodicity for providing data. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 140000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000012-NS |  | 5. | RP-2021-06-24-0000151-NS | TOP-003-5 (Nova Scotia) R1.5. | The deadline by which the respondent is to provide the indicated data. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 150000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000013-NS | RP-2021-06-24-0000154-NS | 1. | RP-2021-06-24-0000155-NS | TOP-003-5 (Nova Scotia) R2.3.1. | Operating limitations based on: |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 231000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000013-NS | RP-2021-06-24-0000154-NS | 2. | RP-2021-06-24-0000160-NS | TOP-003-5 (Nova Scotia) R2.3.2. | Generating unit(s) minimum: |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 232000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000013-NS | RP-2021-06-24-0000155-NS | 1. | RP-2021-06-24-0000156-NS | TOP-003-5 (Nova Scotia) R2.3.1.1. | capability and availability; |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 51100000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000013-NS | RP-2021-06-24-0000155-NS | 2. | RP-2021-06-24-0000157-NS | TOP-003-5 (Nova Scotia) R2.3.1.2. | fuel supply and inventory concerns; |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 51200000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000013-NS | RP-2021-06-24-0000155-NS | 3. | RP-2021-06-24-0000158-NS | TOP-003-5 (Nova Scotia) R2.3.1.3. | fuel switching capabilities; and |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 51300000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000013-NS | RP-2021-06-24-0000155-NS | 4. | RP-2021-06-24-0000159-NS | TOP-003-5 (Nova Scotia) R2.3.1.4. | environmental constraints. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 51400000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000013-NS | RP-2021-06-24-0000160-NS | 1. | RP-2021-06-24-0000161-NS | TOP-003-5 (Nova Scotia) R2.3.2.1. | design temperature; or |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 52100000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000013-NS | RP-2021-06-24-0000160-NS | 2. | RP-2021-06-24-0000162-NS | TOP-003-5 (Nova Scotia) R2.3.2.2. | historical operating temperature; or |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 52200000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000013-NS | RP-2021-06-24-0000160-NS | 3. | RP-2021-06-24-0000163-NS | TOP-003-5 (Nova Scotia) R2.3.2.3. | current cold weather performance temperature determined by an engineering analysis. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 52300000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000013-NS |  | 1. | RP-2021-06-24-0000152-NS | TOP-003-5 (Nova Scotia) R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 210000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000013-NS |  | 2. | RP-2021-06-24-0000153-NS | TOP-003-5 (Nova Scotia) R2.2. | Provisions for notification of current Protection System and Remedial Action Scheme status or degradation that impacts System reliability. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 220000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000013-NS |  | 3. | RP-2021-06-24-0000154-NS | TOP-003-5 (Nova Scotia) R2.3. | Provisions for notification of BES generating unit(s) status during local forecasted cold weather to include: |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 230000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000013-NS |  | 4. | RP-2021-06-24-0000164-NS | TOP-003-5 (Nova Scotia) R2.4. | A periodicity for providing data. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 240000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000013-NS |  | 5. | RP-2021-06-24-0000166-NS | TOP-003-5 (Nova Scotia) R2.5. | The deadline by which the respondent is to provide the indicated data. |  | BA | BA | [20 empty] | Each Balancing Authority shall make available its dated, current, in force documented specification for data. | 2023-07-01 |  |  |  |  | 250000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000016-NS |  | 1. | RP-2021-06-24-0000167-NS | TOP-003-5 (Nova Scotia) R5.1. | A mutually agreeable format |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2023-07-01 |  |  |  |  | 510000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000016-NS |  | 2. | RP-2021-06-24-0000168-NS | TOP-003-5 (Nova Scotia) R5.2. | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2023-07-01 |  |  |  |  | 520000000 | NPCC-NS
ST-2021-06-24-0000003-NS | RQ-2021-06-24-0000016-NS |  | 3. | RP-2021-06-24-0000169-NS | TOP-003-5 (Nova Scotia) R5.3. | A mutually agreeable security protocol |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall make available evidence that it has satisfied the obligations of the documented specifications. Such evidence could include, but is not limited to, electronic or hard copies of data transmittals or attestations of receiving entities. | 2023-07-01 |  |  |  |  | 530000000 | NPCC-NS
ST-2021-07-12-0000001 | RQ-2021-07-13-0000002 |  | 1. | RP-2021-07-13-0000001 | TOP-001-6 R10.1. | Monitor Facilities within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2024-04-01 |  |  |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-12-0000001 | RQ-2021-07-13-0000002 |  | 2. | RP-2021-07-13-0000002 | TOP-001-6 R10.2. | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2024-04-01 |  |  |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-12-0000001 | RQ-2021-07-13-0000002 |  | 3. | RP-2021-07-13-0000003 | TOP-001-6 R10.3. | Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2024-04-01 |  |  |  |  | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-12-0000001 | RQ-2021-07-13-0000002 |  | 4. | RP-2021-07-13-0000004 | TOP-001-6 R10.4. | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2024-04-01 |  |  |  |  | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-12-0000001 | RQ-2021-07-13-0000002 |  | 5. | RP-2021-07-13-0000005 | TOP-001-6 R10.5. | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2024-04-01 |  |  |  |  | 105000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-12-0000001 | RQ-2021-07-13-0000002 |  | 6. | RP-2021-07-13-0000006 | TOP-001-6 R10.6. | Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2024-04-01 |  |  |  |  | 106000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-12-0000001-NS | RQ-2021-07-13-0000002-NS |  | 1. | RP-2021-07-13-0000001-NS | TOP-001-6 (Nova Scotia) R10.1. | Monitor Facilities within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2024-10-01 |  |  |  |  | 101000000 | NPCC-NS
ST-2021-07-12-0000001-NS | RQ-2021-07-13-0000002-NS |  | 2. | RP-2021-07-13-0000002-NS | TOP-001-6 (Nova Scotia) R10.2. | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2024-10-01 |  |  |  |  | 102000000 | NPCC-NS
ST-2021-07-12-0000001-NS | RQ-2021-07-13-0000002-NS |  | 3. | RP-2021-07-13-0000003-NS | TOP-001-6 (Nova Scotia) R10.3. | Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2024-10-01 |  |  |  |  | 103000000 | NPCC-NS
ST-2021-07-12-0000001-NS | RQ-2021-07-13-0000002-NS |  | 4. | RP-2021-07-13-0000004-NS | TOP-001-6 (Nova Scotia) R10.4. | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2024-10-01 |  |  |  |  | 104000000 | NPCC-NS
ST-2021-07-12-0000001-NS | RQ-2021-07-13-0000002-NS |  | 5. | RP-2021-07-13-0000005-NS | TOP-001-6 (Nova Scotia) R10.5. | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2024-10-01 |  |  |  |  | 105000000 | NPCC-NS
ST-2021-07-12-0000001-NS | RQ-2021-07-13-0000002-NS |  | 6. | RP-2021-07-13-0000006-NS | TOP-001-6 (Nova Scotia) R10.6. | Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator shall have, and provide upon request, evidence that could include but is not limited to Energy Management System description documents, computer printouts, Supervisory Control and Data Acquisition (SCADA) data collection, or other equivalent evidence that will be used to confirm that it monitored or obtained and utilized data as required to determine any System Operating Limit (SOL) exceedances within its Transmission Operator Area. | 2024-10-01 |  |  |  |  | 106000000 | NPCC-NS
ST-2021-07-13-0000001 | RQ-2021-07-13-0000020 |  | 1. | RP-2021-07-13-0000007 | FAC-011-4 R3.1. | Require that each BES bus/station have an associated System Voltage Limits, unless its SOL methodology specifically allows the exclusion of BES buses/stations from the requirement to have an associated System Voltage Limit; |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R3. | 2024-04-01 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000020 |  | 2. | RP-2021-07-13-0000008 | FAC-011-4 R3.2. | Require that System Voltage Limits respect voltage-based Facility Ratings; |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R3. | 2024-04-01 |  |  |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000020 |  | 3. | RP-2021-07-13-0000009 | FAC-011-4 R3.3. | Require that System Voltage Limits are greater than or equal to in-service BES relay settings for undervoltage load shedding systems and Undervoltage Load Shedding Programs; |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R3. | 2024-04-01 |  |  |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000020 |  | 4. | RP-2021-07-13-0000010 | FAC-011-4 R3.4. | Identify the minimum allowable System Voltage Limit; |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R3. | 2024-04-01 |  |  |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000020 |  | 5. | RP-2021-07-13-0000011 | FAC-011-4 R3.5. | Define the method for determining common System Voltage Limits between the Reliability Coordinator and its Transmission Operators, between adjacent Transmission Operators, and between adjacent Reliability Coordinators within an Interconnection. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R3. | 2024-04-01 |  |  |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000021 |  | 1. | RP-2021-07-13-0000012 | FAC-011-4 R4.1. | Specify stability performance criteria, including any margins applied. The criteria shall, at a minimum, include the following: |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | 2024-04-01 |  |  |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000021 |  | 1.1. | RP-2021-07-13-0000013 | FAC-011-4 R4.1.1. | steady-state voltage stability; |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | 2024-04-01 |  |  |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000021 |  | 1.2. | RP-2021-07-13-0000014 | FAC-011-4 R4.1.2. | transient voltage response; |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | 2024-04-01 |  |  |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000021 |  | 1.3. | RP-2021-07-13-0000015 | FAC-011-4 R4.1.3. | angular stability; and |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | 2024-04-01 |  |  |  |  | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000021 |  | 1.4. | RP-2021-07-13-0000016 | FAC-011-4 R4.1.4. | System damping. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | 2024-04-01 |  |  |  |  | 414000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000021 |  | 2. | RP-2021-07-13-0000017 | FAC-011-4 R4.2. | Require that stability limits are established to meet the criteria specified in Part 4.1 for the Contingencies identified in Requirement R5 applicable to the establishment of stability limits that are expected to produce more severe System impacts on its portion of the BES. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | 2024-04-01 |  |  |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000021 |  | 3. | RP-2021-07-13-0000018 | FAC-011-4 R4.3. | Describe how the Reliability Coordinator establishes stability limits when there is an impact to more than one Transmission Operator in its Reliability Coordinator Area or other Reliability Coordinator Areas. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | 2024-04-01 |  |  |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000021 |  | 4. | RP-2021-07-13-0000019 | FAC-011-4 R4.4. | Describe how stability limits are determined, considering levels of transfers, Load and generation dispatch, and System conditions including any changes to System topology such as Facility outages. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | 2024-04-01 |  |  |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000021 |  | 5. | RP-2021-07-13-0000020 | FAC-011-4 R4.5. | Describe the level of detail that is required for the study model(s), including the portion modeled of the Reliability Coordinator Area, and the critical modeling details from other Reliability Coordinator Areas, necessary to determine different types of stability limits. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | 2024-04-01 |  |  |  |  | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000021 |  | 6. | RP-2021-07-13-0000021 | FAC-011-4 R4.6. | Describe the allowed uses of Remedial Action Schemes and other automatic post-Contingency mitigation actions in establishing stability limits used in operations. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | 2024-04-01 |  |  |  |  | 460000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000021 |  | 7. | RP-2021-07-13-0000022 | FAC-011-4 R4.7. | State that the use of underfrequency load shedding (UFLS) programs and Undervoltage Load Shedding (UVLS) Programs are not allowed in the establishment of stability limits. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R4. | 2024-04-01 |  |  |  |  | 470000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000022 |  | 1. | RP-2021-07-13-0000023 | FAC-011-4 R5.1. | Specify the following single Contingency events |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R5. | 2024-04-01 |  |  |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000022 |  | 1.1. | RP-2021-07-13-0000024 | FAC-011-4 R5.1.1. | Loss of any of the following either by single phase to ground or three phase Fault (whichever is more severe) with Normal Clearing, or without a Fault: · generator; · transmission circuit; · transformer; · shunt device; or · single pole block in a monopolar or bipolar high voltage direct current system. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R5. | 2024-04-01 |  |  |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000022 |  | 2. | RP-2021-07-13-0000025 | FAC-011-4 R5.2. | Specify additional single or multiple Contingency events or types of Contingency events, if any. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R5. | 2024-04-01 |  |  |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000022 |  | 3. | RP-2021-07-13-0000026 | FAC-011-4 R5.3. | Describe the method(s) for identifying which, if any, of the Contingency events provided by the Planning Coordinator or Transmission Planner in accordance with FAC-014-3, Requirement R7, to use in determining stability limits. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R5. | 2024-04-01 |  |  |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000023 |  | 1. | RP-2021-07-13-0000027 | FAC-011-4 R6.1. | System performance for no Contingencies demonstrates the following: |  | RC | [11 empty] | RC | [9 empty] | 6. Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | 2024-04-01 |  |  |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000023 |  | 1.1. | RP-2021-07-13-0000028 | FAC-011-4 R6.1.1. | Steady state flow through Facilities are within Normal Ratings; however, Emergency Ratings may be used when System adjustments to return the flow within its Normal Rating could be executed and completed within the specified time duration of those Emergency Ratings. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | 2024-04-01 |  |  |  |  | 611000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000023 |  | 1.2. | RP-2021-07-13-0000029 | FAC-011-4 R6.1.2. | Steady state voltages are within normal System Voltage Limits; however, emergency System Voltage Limits may be used when System adjustments to return the voltage within its normal System Voltage Limits could be executed and completed within the specified time duration of those emergency System Voltage Limits. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | 2024-04-01 |  |  |  |  | 612000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000023 |  | 1.3. | RP-2021-07-13-0000030 | FAC-011-4 R6.1.3. | Predetermined stability limits are not exceeded. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | 2024-04-01 |  |  |  |  | 613000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000023 |  | 1.4. | RP-2021-07-13-0000031 | FAC-011-4 R6.1.4. | Instability, Cascading or uncontrolled separation that adversely impact the reliability of the Bulk Electric System does not occur. Footnote: Stability evaluations and assessments of instability, Cascading, and uncontrolled separation can be performed using real-time stability assessments, predetermined stability limits or other offline analysis techniques. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | 2024-04-01 |  |  |  |  | 614000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000023 |  | 2. | RP-2021-07-13-0000032 | FAC-011-4 R6.2. | System performance for the single Contingencies listed in Part 5.1 demonstrates the following: |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | 2024-04-01 |  |  |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000023 |  | 2.1. | RP-2021-07-13-0000033 | FAC-011-4 R6.2.1. | Steady state post-Contingency flow through Facilities within applicable Emergency Ratings. Steady state post-Contingency flow through a Facility must not be above the Facility’s highest Emergency Rating. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | 2024-04-01 |  |  |  |  | 621000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000023 |  | 2.2. | RP-2021-07-13-0000034 | FAC-011-4 R6.2.2. | Steady state post-Contingency voltages are within emergency System Voltage Limits. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | 2024-04-01 |  |  |  |  | 622000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000023 |  | 2.3. | RP-2021-07-13-0000035 | FAC-011-4 R6.2.3. | The stability performance criteria defined in the Reliability Coordinator’s SOL methodology are met. Footnote: Stability evaluations and assessments of instability, Cascading, and uncontrolled separation can be performed using real-time stability assessments, predetermined stability limits or other offline analysis techniques. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | 2024-04-01 |  |  |  |  | 623000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000023 |  | 2.4. | RP-2021-07-13-0000036 | FAC-011-4 R6.2.4. | Instability, Cascading or uncontrolled separation that adversely impact the reliability of the Bulk Electric System does not occur. Footnote: Stability evaluations and assessments of instability, Cascading, and uncontrolled separation can be performed using real-time stability assessments, predetermined stability limits or other offline analysis techniques. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | 2024-04-01 |  |  |  |  | 624000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000023 |  | 3. | RP-2021-07-13-0000037 | FAC-011-4 R6.3. | System performance for applicable Contingencies identified in Part 5.2 demonstrates that: instability, Cascading, or uncontrolled separation that adversely impact the reliability of the Bulk Electric System does not occur. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | 2024-04-01 |  |  |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000023 |  | 4. | RP-2021-07-13-0000038 | FAC-011-4 R6.4. | In determining the System’s response to any Contingency identified in Requirement R5, planned manual load shedding is acceptable only after all other available System adjustments have been made. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R6. | 2024-04-01 |  |  |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000024 |  | 1. | RP-2021-07-13-0000039 | FAC-011-4 R7.1. | A requirement that the following SOL exceedances will always be communicated, within a timeframe identified by the Reliability Coordinator. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | 2024-04-01 |  |  |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000024 |  | 1.1. | RP-2021-07-13-0000040 | FAC-011-4 R7.1.1. | IROL exceedances; |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | 2024-04-01 |  |  |  |  | 711000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000024 |  | 1.2. | RP-2021-07-13-0000041 | FAC-011-4 R7.1.2. | SOL exceedances of stability limits; |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | 2024-04-01 |  |  |  |  | 712000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000024 |  | 1.3. | RP-2021-07-13-0000042 | FAC-011-4 R7.1.3. | Post Contingency SOL exceedances that are identified to have a validated risk of instability, Cascading, and uncontrolled separation; |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | 2024-04-01 |  |  |  |  | 713000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000024 |  | 1.4. | RP-2021-07-13-0000043 | FAC-011-4 R7.1.4. | Pre-Contingency SOL exceedances of Facility Ratings; and |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | 2024-04-01 |  |  |  |  | 714000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000024 |  | 1.5. | RP-2021-07-13-0000044 | FAC-011-4 R7.1.5. | Pre-Contingency SOL exceedances of normal minimum System Voltage Limits. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | 2024-04-01 |  |  |  |  | 715000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000024 |  | 2. | RP-2021-07-13-0000045 | FAC-011-4 R7.2. | A requirement that the following SOL exceedances must be communicated, if not resolved within 30 minutes, within a timeframe identified by the Reliability Coordinator. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | 2024-04-01 |  |  |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000024 |  | 2.1. | RP-2021-07-13-0000046 | FAC-011-4 R7.2.1. | Post-Contingency SOL exceedances of Facility Ratings and emergency System Voltage Limits, and |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | 2024-04-01 |  |  |  |  | 721000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000024 |  | 2.2. | RP-2021-07-13-0000047 | FAC-011-4 R7.2.2. | Pre-Contingency SOL exceedances of normal maximum System Voltage Limits. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R7. | 2024-04-01 |  |  |  |  | 722000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000025 |  | 1. | RP-2021-07-13-0000048 | FAC-011-4 R8.1. | A description of how to identify the subset of SOLs that qualify as Interconnection Reliability Operating Limits (IROLs). |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R8. | 2024-04-01 |  |  |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000025 |  | 2. | RP-2021-07-13-0000049 | FAC-011-4 R8.2. | Criteria for determining when exceeding a SOL qualifies as exceeding an IROL and criteria for developing any associated IROL Tv. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation of its SOL methodology that addresses the items listed in Requirement R8. | 2024-04-01 |  |  |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000026 |  | 1. | RP-2021-07-13-0000050 | FAC-011-4 R9.1. | Each Reliability Coordinator that requests and indicates it has a reliability-related need within 30 days of a request. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation such as emails with receipts, registered mail receipts, or postings to a secure web site with accompanying notification(s). | 2024-04-01 |  |  |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000026 |  | 2. | RP-2021-07-13-0000051 | FAC-011-4 R9.2. | Each of the following entities prior to the effective date of the SOL methodology: |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation such as emails with receipts, registered mail receipts, or postings to a secure web site with accompanying notification(s). | 2024-04-01 |  |  |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000026 |  | 2.1. | RP-2021-07-13-0000052 | FAC-011-4 R9.2.1. | Each adjacent Reliability Coordinator within the same; Interconnection; |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation such as emails with receipts, registered mail receipts, or postings to a secure web site with accompanying notification(s). | 2024-04-01 |  |  |  |  | 921000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000026 |  | 2.2. | RP-2021-07-13-0000053 | FAC-011-4 R9.2.2. | Each Planning Coordinator and Transmission Planner that is responsible for planning any portion of the Reliability Coordinator Area; |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation such as emails with receipts, registered mail receipts, or postings to a secure web site with accompanying notification(s). | 2024-04-01 |  |  |  |  | 922000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000026 |  | 2.3. | RP-2021-07-13-0000054 | FAC-011-4 R9.2.3. | Each Transmission Operator within its Reliability Coordinator Area; and |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation such as emails with receipts, registered mail receipts, or postings to a secure web site with accompanying notification(s). | 2024-04-01 |  |  |  |  | 923000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000001 | RQ-2021-07-13-0000026 |  | 2.4. | RP-2021-07-13-0000055 | FAC-011-4 R9.2.4. | Each Reliability Coordinator that has requested to receive updates and indicated it had a reliability-related need. |  | RC | [11 empty] | RC | [9 empty] | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation such as emails with receipts, registered mail receipts, or postings to a secure web site with accompanying notification(s). | 2024-04-01 |  |  |  |  | 924000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000031 |  | 1. | RP-2021-07-13-0000056 | FAC-014-3 R5.1. | Each Planning Coordinator and each Transmission Planner within its Reliability Coordinator Area, the SOLs for its Reliability Coordinator Area (including the subset of SOLs that are IROLs) at least once every twelve calendar months. |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-04-01 |  |  |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000031 |  | 2. | RP-2021-07-13-0000057 | FAC-014-3 R5.2. | Each impacted Planning Coordinator and each impacted Transmission Planner within its Reliability Coordinator Area, the following information for each established stability limit and each established IROL at least once every twelve calendar months: |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-04-01 |  |  |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000031 |  | 2.1. | RP-2021-07-13-0000058 | FAC-014-3 R5.2.1. | The value of the stability limit or IROL; |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-04-01 |  |  |  |  | 521000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000031 |  | 2.2. | RP-2021-07-13-0000059 | FAC-014-3 R5.2.2. | Identification of the Facilities that are critical to the derivation of the stability limit or the IROL; |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-04-01 |  |  |  |  | 522000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000031 |  | 2.3. | RP-2021-07-13-0000060 | FAC-014-3 R5.2.3. | The associated IROL Tv for any IROL; |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-04-01 |  |  |  |  | 523000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000031 |  | 2.4. | RP-2021-07-13-0000061 | FAC-014-3 R5.2.4. | The associated critical Contingency(ies); |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-04-01 |  |  |  |  | 524000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000031 |  | 2.5. | RP-2021-07-13-0000062 | FAC-014-3 R5.2.5. | A description of system conditions associated with the stability limit or IROL; and |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-04-01 |  |  |  |  | 525000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000031 |  | 2.6. | RP-2021-07-13-0000063 | FAC-014-3 R5.2.6. | The type of limitation represented by the stability limit or IROL (e.g., voltage collapse, angular stability). |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-04-01 |  |  |  |  | 526000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000031 |  | 3. | RP-2021-07-13-0000064 | FAC-014-3 R5.3. | Each impacted Transmission Operator within its Reliability Coordinator Area, the value of the stability limits established pursuant to Requirement R4 and each IROL established pursuant to Requirement R1, in an agreed upon time frame necessary for inclusion in the Transmission Operator’s Operational Planning Analyses, Real- time monitoring, and Real-time Assessments. |  | RC, TOP | [11 empty] | RC | [6 empty] | TOP |  |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-04-01 |  |  |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000031 |  | 4. | RP-2021-07-13-0000065 | FAC-014-3 R5.4. | Each impacted Transmission Operator within its Reliability Coordinator Area, the information identified in Requirement R5 Parts 5.2.2 – 5.2.6 for each established stability limit and each established IROL, and any updates to that information within an agreed upon time frame necessary for inclusion in the Transmission Operator’s Operational Planning Analyses. |  | RC, TOP | [11 empty] | RC | [6 empty] | TOP |  |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-04-01 |  |  |  |  | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000031 |  | 5. | RP-2021-07-13-0000066 | FAC-014-3 R5.5. | Each requesting Transmission Operator within its Reliability Coordinator Area, requested SOL information for its Reliability Coordinator Area, on a mutually agreed upon schedule. |  | RC, TOP | [11 empty] | RC | [6 empty] | TOP |  |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-04-01 |  |  |  |  | 550000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000031 |  | 6. | RP-2021-07-13-0000067 | FAC-014-3 R5.6. | Each impacted Generator Owner or Transmission Owner, within its Reliability Coordinator Area, with a list of their Facilities that have been identified as critical to the derivation of an IROL and its associated critical contingencies at least once every twelve calendar months. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-04-01 |  |  |  |  | 560000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000033 |  | 1. | RP-2021-07-13-0000068 | FAC-014-3 R7.1. | The Corrective Action Plan developed to mitigate the identified instability, including any automatic control or operator-assisted actions (such as Remedial Action Schemes, under voltage load shedding, or any Operating Procedures); |  | PCPA, RC, TOP, TP | [9 empty] | PCPA |  | RC | [6 empty] | TOP | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hardcopy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | 2024-04-01 |  |  |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000033 |  | 2. | RP-2021-07-13-0000069 | FAC-014-3 R7.2. | The type of instability addressed by the Corrective Action Plan (e.g. steady-state and/or transient voltage instability, angular instability including generating unit loss of synchronism and/or unacceptable damping); |  | PCPA, RC, TOP, TP | [9 empty] | PCPA |  | RC | [6 empty] | TOP | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hardcopy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | 2024-04-01 |  |  |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000033 |  | 3. | RP-2021-07-13-0000070 | FAC-014-3 R7.3. | The associated stability criteria violation requiring the Corrective Action Plan (e.g. violation of transient voltage response criteria or damping rate criteria); |  | PCPA, RC, TOP, TP | [9 empty] | PCPA |  | RC | [6 empty] | TOP | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hardcopy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | 2024-04-01 |  |  |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000033 |  | 4. | RP-2021-07-13-0000071 | FAC-014-3 R7.4. | The planning event Contingency(ies) associated with the identified instability requiring the Corrective Action Plan; |  | PCPA, RC, TOP, TP | [9 empty] | PCPA |  | RC | [6 empty] | TOP | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hardcopy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | 2024-04-01 |  |  |  |  | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002 | RQ-2021-07-13-0000033 |  | 5. | RP-2021-07-13-0000072 | FAC-014-3 R7.5. | The System conditions and Facilities associated with the identified instability requiring the Corrective Action Plan. |  | PCPA, RC, TOP, TP | [9 empty] | PCPA |  | RC | [6 empty] | TOP | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hardcopy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | 2024-04-01 |  |  |  |  | 750000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000031-NS |  | 1. | RP-2021-07-13-0000056-NS | FAC-014-3 (Nova Scotia) R5.1. | Each Planning Coordinator and each Transmission Planner within its Reliability Coordinator Area, the SOLs for its Reliability Coordinator Area (including the subset of SOLs that are IROLs) at least once every twelve calendar months. |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-10-01 |  |  |  |  | 510000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000031-NS |  | 2. | RP-2021-07-13-0000057-NS | FAC-014-3 (Nova Scotia) R5.2. | Each impacted Planning Coordinator and each impacted Transmission Planner within its Reliability Coordinator Area, the following information for each established stability limit and each established IROL at least once every twelve calendar months: |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-10-01 |  |  |  |  | 520000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000031-NS |  | 2.1. | RP-2021-07-13-0000058-NS | FAC-014-3 (Nova Scotia) R5.2.1. | The value of the stability limit or IROL; |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-10-01 |  |  |  |  | 521000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000031-NS |  | 2.2. | RP-2021-07-13-0000059-NS | FAC-014-3 (Nova Scotia) R5.2.2. | Identification of the Facilities that are critical to the derivation of the stability limit or the IROL; |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-10-01 |  |  |  |  | 522000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000031-NS |  | 2.3. | RP-2021-07-13-0000060-NS | FAC-014-3 (Nova Scotia) R5.2.3. | The associated IROL Tv for any IROL; |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-10-01 |  |  |  |  | 523000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000031-NS |  | 2.4. | RP-2021-07-13-0000061-NS | FAC-014-3 (Nova Scotia) R5.2.4. | The associated critical Contingency(ies); |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-10-01 |  |  |  |  | 524000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000031-NS |  | 2.5. | RP-2021-07-13-0000062-NS | FAC-014-3 (Nova Scotia) R5.2.5. | A description of system conditions associated with the stability limit or IROL; and |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-10-01 |  |  |  |  | 525000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000031-NS |  | 2.6. | RP-2021-07-13-0000063-NS | FAC-014-3 (Nova Scotia) R5.2.6. | The type of limitation represented by the stability limit or IROL (e.g., voltage collapse, angular stability). |  | PCPA, RC, TP | [9 empty] | PCPA |  | RC | [7 empty] | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-10-01 |  |  |  |  | 526000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000031-NS |  | 3. | RP-2021-07-13-0000064-NS | FAC-014-3 (Nova Scotia) R5.3. | Each impacted Transmission Operator within its Reliability Coordinator Area, the value of the stability limits established pursuant to Requirement R4 and each IROL established pursuant to Requirement R1, in an agreed upon time frame necessary for inclusion in the Transmission Operator’s Operational Planning Analyses, Real- time monitoring, and Real-time Assessments. |  | RC, TOP | [11 empty] | RC | [6 empty] | TOP |  |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-10-01 |  |  |  |  | 530000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000031-NS |  | 4. | RP-2021-07-13-0000065-NS | FAC-014-3 (Nova Scotia) R5.4. | Each impacted Transmission Operator within its Reliability Coordinator Area, the information identified in Requirement R5 Parts 5.2.2 – 5.2.6 for each established stability limit and each established IROL, and any updates to that information within an agreed upon time frame necessary for inclusion in the Transmission Operator’s Operational Planning Analyses. |  | RC, TOP | [11 empty] | RC | [6 empty] | TOP |  |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-10-01 |  |  |  |  | 540000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000031-NS |  | 5. | RP-2021-07-13-0000066-NS | FAC-014-3 (Nova Scotia) R5.5. | Each requesting Transmission Operator within its Reliability Coordinator Area, requested SOL information for its Reliability Coordinator Area, on a mutually agreed upon schedule. |  | RC, TOP | [11 empty] | RC | [6 empty] | TOP |  |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-10-01 |  |  |  |  | 550000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000031-NS |  | 6. | RP-2021-07-13-0000067-NS | FAC-014-3 (Nova Scotia) R5.6. | Each impacted Generator Owner or Transmission Owner, within its Reliability Coordinator Area, with a list of their Facilities that have been identified as critical to the derivation of an IROL and its associated critical contingencies at least once every twelve calendar months. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | Acceptable evidence may include, but is not limited to, dated electronic or hard copy documentation, posting to a secure website, or other electronic means, that demonstrates the Reliability Coordinator provided the information in accordance with Requirement R5. | 2024-10-01 |  |  |  |  | 560000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000033-NS |  | 1. | RP-2021-07-13-0000068-NS | FAC-014-3 (Nova Scotia) R7.1. | The Corrective Action Plan developed to mitigate the identified instability, including any automatic control or operator-assisted actions (such as Remedial Action Schemes, under voltage load shedding, or any Operating Procedures); |  | PCPA, RC, TOP, TP | [9 empty] | PCPA |  | RC | [6 empty] | TOP | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hardcopy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | 2024-10-01 |  |  |  |  | 710000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000033-NS |  | 2. | RP-2021-07-13-0000069-NS | FAC-014-3 (Nova Scotia) R7.2. | The type of instability addressed by the Corrective Action Plan (e.g. steady-state and/or transient voltage instability, angular instability including generating unit loss of synchronism and/or unacceptable damping); |  | PCPA, RC, TOP, TP | [9 empty] | PCPA |  | RC | [6 empty] | TOP | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hardcopy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | 2024-10-01 |  |  |  |  | 720000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000033-NS |  | 3. | RP-2021-07-13-0000070-NS | FAC-014-3 (Nova Scotia) R7.3. | The associated stability criteria violation requiring the Corrective Action Plan (e.g. violation of transient voltage response criteria or damping rate criteria); |  | PCPA, RC, TOP, TP | [9 empty] | PCPA |  | RC | [6 empty] | TOP | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hardcopy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | 2024-10-01 |  |  |  |  | 730000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000033-NS |  | 4. | RP-2021-07-13-0000071-NS | FAC-014-3 (Nova Scotia) R7.4. | The planning event Contingency(ies) associated with the identified instability requiring the Corrective Action Plan; |  | PCPA, RC, TOP, TP | [9 empty] | PCPA |  | RC | [6 empty] | TOP | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hardcopy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | 2024-10-01 |  |  |  |  | 740000000 | NPCC-NS
ST-2021-07-13-0000002-NS | RQ-2021-07-13-0000033-NS |  | 5. | RP-2021-07-13-0000072-NS | FAC-014-3 (Nova Scotia) R7.5. | The System conditions and Facilities associated with the identified instability requiring the Corrective Action Plan. |  | PCPA, RC, TOP, TP | [9 empty] | PCPA |  | RC | [6 empty] | TOP | TP |  | Acceptable evidence may include, but is not limited to, dated electronic or hardcopy documentation demonstrating the Planning Coordinator and Transmission Planner communicated the information in accordance with Requirement R7. | 2024-10-01 |  |  |  |  | 750000000 | NPCC-NS
ST-2021-07-13-0000003 | RQ-2021-07-13-0000035 |  | 1. | RP-2021-07-13-0000073 | FAC-003-5 R1.1. | An encroachment into the MVCD as shown in FAC‐003‐Table 2, observed in Real‐ time, absent a Sustained Outage, Footnote: If a later confirmation of a Fault by the applicable Transmission Owner or applicable Generator Owner shows that a vegetation encroachment within the MVCD has occurred from vegetation within the ROW, this shall be considered the equivalent of a Real‐time observation. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real‐time observations of any MVCD encroachments. (R1) | 2024-04-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000003 | RQ-2021-07-13-0000035 |  | 2. | RP-2021-07-13-0000074 | FAC-003-5 R1.2. | An encroachment due to a fall‐in from inside the ROW that caused a vegetation‐ related Sustained Outage, Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24‐hour period. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real‐time observations of any MVCD encroachments. (R1) | 2024-04-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000003 | RQ-2021-07-13-0000035 |  | 3. | RP-2021-07-13-0000075 | FAC-003-5 R1.3. | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation‐related Sustained Outage, Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24‐hour period. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real‐time observations of any MVCD encroachments. (R1) | 2024-04-01 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000003 | RQ-2021-07-13-0000035 |  | 4. | RP-2021-07-13-0000076 | FAC-003-5 R1.4. | An encroachment due to vegetation growth into the MVCD that caused a vegetation‐related Sustained Outage. Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24‐hour period. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real‐time observations of any MVCD encroachments. (R1) | 2024-04-01 |  |  |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000003 | RQ-2021-07-13-0000037 |  | 1. | RP-2021-07-13-0000077 | FAC-003-5 R3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The maintenance strategies or procedures or processes or specifications provided demonstrate that the applicable Transmission Owner and applicable Generator Owner can prevent encroachment into the MVCD considering the factors identified in the requirement. (R3) | 2024-04-01 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000003 | RQ-2021-07-13-0000037 |  | 2. | RP-2021-07-13-0000078 | FAC-003-5 R3.2. | Inter‐relationships between vegetation growth rates, vegetation control methods, and inspection frequency. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The maintenance strategies or procedures or processes or specifications provided demonstrate that the applicable Transmission Owner and applicable Generator Owner can prevent encroachment into the MVCD considering the factors identified in the requirement. (R3) | 2024-04-01 |  |  |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000003 | RQ-2021-07-13-0000041 |  | 1. | RP-2021-07-13-0000079 | FAC-003-5 R7.1. | Change in expected growth rate/environmental factors |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-04-01 |  |  |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000003 | RQ-2021-07-13-0000041 |  | 2. | RP-2021-07-13-0000080 | FAC-003-5 R7.2. | Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner Footnote: Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner include but are not limited to natural disasters such as earthquakes, fires, tornados, hurricanes, landslides, ice storms, floods, or major storms as defined either by the TO or GO or an applicable regulatory body. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-04-01 |  |  |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000003 | RQ-2021-07-13-0000041 |  | 3. | RP-2021-07-13-0000081 | FAC-003-5 R7.3. | Rescheduling work between growing seasons |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-04-01 |  |  |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000003 | RQ-2021-07-13-0000041 |  | 4. | RP-2021-07-13-0000082 | FAC-003-5 R7.4. | Crew or contractor availability/Mutual assistance agreements |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-04-01 |  |  |  |  | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000003 | RQ-2021-07-13-0000041 |  | 5. | RP-2021-07-13-0000083 | FAC-003-5 R7.5. | Identified unanticipated high priority work |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-04-01 |  |  |  |  | 750000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000003 | RQ-2021-07-13-0000041 |  | 6. | RP-2021-07-13-0000084 | FAC-003-5 R7.6. | Weather conditions/Accessibility |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-04-01 |  |  |  |  | 760000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000003 | RQ-2021-07-13-0000041 |  | 7. | RP-2021-07-14-0000001 | FAC-003-5 R7.7. | Permitting delays |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-04-01 |  |  |  |  | 770000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000003 | RQ-2021-07-13-0000041 |  | 8. | RP-2021-07-14-0000002 | FAC-003-5 R7.8. | Land ownership changes/Change in land use by the landowner |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-04-01 |  |  |  |  | 780000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000003 | RQ-2021-07-13-0000041 |  | 9. | RP-2021-07-14-0000003 | FAC-003-5 R7.9. | Emerging technologies |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 790000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-13-0000003-NS | RQ-2021-07-13-0000035-NS |  | 1. | RP-2021-07-13-0000073-NS | FAC-003-5 (Nova Scotia) R1.1. | An encroachment into the MVCD as shown in FAC‐003‐Table 2, observed in Real‐ time, absent a Sustained Outage, Footnote: If a later confirmation of a Fault by the applicable Transmission Owner or applicable Generator Owner shows that a vegetation encroachment within the MVCD has occurred from vegetation within the ROW, this shall be considered the equivalent of a Real‐time observation. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real‐time observations of any MVCD encroachments. (R1) | 2024-10-01 |  |  |  |  | 110000000 | NPCC-NS
ST-2021-07-13-0000003-NS | RQ-2021-07-13-0000035-NS |  | 2. | RP-2021-07-13-0000074-NS | FAC-003-5 (Nova Scotia) R1.2. | An encroachment due to a fall‐in from inside the ROW that caused a vegetation‐ related Sustained Outage, Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24‐hour period. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real‐time observations of any MVCD encroachments. (R1) | 2024-10-01 |  |  |  |  | 120000000 | NPCC-NS
ST-2021-07-13-0000003-NS | RQ-2021-07-13-0000035-NS |  | 3. | RP-2021-07-13-0000075-NS | FAC-003-5 (Nova Scotia) R1.3. | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation‐related Sustained Outage, Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24‐hour period. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real‐time observations of any MVCD encroachments. (R1) | 2024-10-01 |  |  |  |  | 130000000 | NPCC-NS
ST-2021-07-13-0000003-NS | RQ-2021-07-13-0000035-NS |  | 4. | RP-2021-07-13-0000076-NS | FAC-003-5 (Nova Scotia) R1.4. | An encroachment due to vegetation growth into the MVCD that caused a vegetation‐related Sustained Outage. Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24‐hour period. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it managed vegetation to prevent encroachment into the MVCD as described in R1. Examples of acceptable forms of evidence may include dated attestations, dated reports containing no Sustained Outages associated with encroachment types 2 through 4 above, or records confirming no Real‐time observations of any MVCD encroachments. (R1) | 2024-10-01 |  |  |  |  | 140000000 | NPCC-NS
ST-2021-07-13-0000003-NS | RQ-2021-07-13-0000037-NS |  | 1. | RP-2021-07-13-0000077-NS | FAC-003-5 (Nova Scotia) R3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The maintenance strategies or procedures or processes or specifications provided demonstrate that the applicable Transmission Owner and applicable Generator Owner can prevent encroachment into the MVCD considering the factors identified in the requirement. (R3) | 2024-10-01 |  |  |  |  | 310000000 | NPCC-NS
ST-2021-07-13-0000003-NS | RQ-2021-07-13-0000037-NS |  | 2. | RP-2021-07-13-0000078-NS | FAC-003-5 (Nova Scotia) R3.2. | Inter‐relationships between vegetation growth rates, vegetation control methods, and inspection frequency. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The maintenance strategies or procedures or processes or specifications provided demonstrate that the applicable Transmission Owner and applicable Generator Owner can prevent encroachment into the MVCD considering the factors identified in the requirement. (R3) | 2024-10-01 |  |  |  |  | 320000000 | NPCC-NS
ST-2021-07-13-0000003-NS | RQ-2021-07-13-0000041-NS |  | 1. | RP-2021-07-13-0000079-NS | FAC-003-5 (Nova Scotia) R7.1. | Change in expected growth rate/environmental factors |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-10-01 |  |  |  |  | 710000000 | NPCC-NS
ST-2021-07-13-0000003-NS | RQ-2021-07-13-0000041-NS |  | 2. | RP-2021-07-13-0000080-NS | FAC-003-5 (Nova Scotia) R7.2. | Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner Footnote: Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner include but are not limited to natural disasters such as earthquakes, fires, tornados, hurricanes, landslides, ice storms, floods, or major storms as defined either by the TO or GO or an applicable regulatory body. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-10-01 |  |  |  |  | 720000000 | NPCC-NS
ST-2021-07-13-0000003-NS | RQ-2021-07-13-0000041-NS |  | 3. | RP-2021-07-13-0000081-NS | FAC-003-5 (Nova Scotia) R7.3. | Rescheduling work between growing seasons |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-10-01 |  |  |  |  | 730000000 | NPCC-NS
ST-2021-07-13-0000003-NS | RQ-2021-07-13-0000041-NS |  | 4. | RP-2021-07-13-0000082-NS | FAC-003-5 (Nova Scotia) R7.4. | Crew or contractor availability/Mutual assistance agreements |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-10-01 |  |  |  |  | 740000000 | NPCC-NS
ST-2021-07-13-0000003-NS | RQ-2021-07-13-0000041-NS |  | 5. | RP-2021-07-13-0000083-NS | FAC-003-5 (Nova Scotia) R7.5. | Identified unanticipated high priority work |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-10-01 |  |  |  |  | 750000000 | NPCC-NS
ST-2021-07-13-0000003-NS | RQ-2021-07-13-0000041-NS |  | 6. | RP-2021-07-13-0000084-NS | FAC-003-5 (Nova Scotia) R7.6. | Weather conditions/Accessibility |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-10-01 |  |  |  |  | 760000000 | NPCC-NS
ST-2021-07-13-0000003-NS | RQ-2021-07-13-0000041-NS |  | 7. | RP-2021-07-14-0000001-NS | FAC-003-5 (Nova Scotia) R7.7. | Permitting delays |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-10-01 |  |  |  |  | 770000000 | NPCC-NS
ST-2021-07-13-0000003-NS | RQ-2021-07-13-0000041-NS |  | 8. | RP-2021-07-14-0000002-NS | FAC-003-5 (Nova Scotia) R7.8. | Land ownership changes/Change in land use by the landowner |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. (R7) | 2024-10-01 |  |  |  |  | 780000000 | NPCC-NS
ST-2021-07-13-0000003-NS | RQ-2021-07-13-0000041-NS |  | 9. | RP-2021-07-14-0000003-NS | FAC-003-5 (Nova Scotia) R7.9. | Emerging technologies |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-10-01 |  |  |  |  | 790000000 | NPCC-NS
ST-2021-07-14-0000002 | RQ-2021-07-14-0000008 |  | 1. | RP-2021-07-15-0000001 | PRC-002-3 R1.1. | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-3, Attachment 1. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-3, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. |  |  | 2024-03-31 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000008 |  | 2. | RP-2021-07-15-0000002 | PRC-002-3 R1.2. | Notify other owners of BES Elements connected to those BES buses, if any, within 90-calendar days of completion of Part 1.1, that those BES Elements require SER data and/or FR data. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-3, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. |  |  | 2024-03-31 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000008 |  | 3. | RP-2021-07-15-0000003 | PRC-002-3 R1.3. | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners, if any, in accordance with Part 1.2, and implement the re-evaluated list of BES buses as per the Implementation Plan. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-3, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. |  |  | 2024-03-31 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000010 |  | 1. | RP-2021-07-15-0000004 | PRC-002-3 R3.1. | Phase-to-neutral voltage for each phase of each specified BES bus. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. |  |  | 2024-03-31 |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000010 |  | 2. | RP-2021-07-15-0000005 | PRC-002-3 R3.2. | Each phase current and the residual or neutral current for the following BES Elements: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. |  |  | 2024-03-31 |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000010 |  | 2.1. | RP-2021-07-15-0000006 | PRC-002-3 R3.2.1. | Transformers that have a low-side operating voltage of 100kV or above. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. |  |  | 2024-03-31 |  |  | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000010 |  | 2.2. | RP-2021-07-15-0000007 | PRC-002-3 R3.2.2. | Transmission Lines. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. |  |  | 2024-03-31 |  |  | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000011 |  | 1. | RP-2021-07-15-0000008 | PRC-002-3 R4.1. | A single record or multiple records that include: • A pre-trigger record length of at least two cycles and a total record length of at least 30-cycles for the same trigger point, or • At least two cycles of the pre-trigger data, the first three cycles of the post- trigger data, and the final cycle of the fault as seen by the fault recorder. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. |  |  | 2024-03-31 |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000011 |  | 2. | RP-2021-07-15-0000009 | PRC-002-3 R4.2. | A minimum recording rate of 16 samples per cycle. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. |  |  | 2024-03-31 |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000011 |  | 3. | RP-2021-07-15-0000010 | PRC-002-3 R4.3. | Trigger settings for at least the following: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. |  |  | 2024-03-31 |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000011 |  | 3.1. | RP-2021-07-15-0000011 | PRC-002-3 R4.3.1. | Neutral (residual) overcurrent. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. |  |  | 2024-03-31 |  |  | 431000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000011 |  | 3.2. | RP-2021-07-15-0000012 | PRC-002-3 R4.3.2. | Phase undervoltage or overcurrent. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. |  |  | 2024-03-31 |  |  | 432000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000012 |  | 1. | RP-2021-07-15-0000013 | PRC-002-3 R5.1. | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. |  |  | 2024-03-31 |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000012 |  | 1.1. | RP-2021-07-15-0000014 | PRC-002-3 R5.1.1. | Generating resource(s) with: |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. |  |  | 2024-03-31 |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000012 |  | 1.1.1. | RP-2021-07-15-0000015 | PRC-002-3 R5.1.1.1. | Gross individual nameplate rating greater than or equal to 500 MVA. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. |  |  | 2024-03-31 |  |  | 511100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000012 |  | 1.1.2. | RP-2021-07-15-0000016 | PRC-002-3 R5.1.1.2. | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. |  |  | 2024-03-31 |  |  | 511200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000012 |  | 1.2. | RP-2021-07-15-0000017 | PRC-002-3 R5.1.2. | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. |  |  | 2024-03-31 |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000012 |  | 1.3. | RP-2021-07-15-0000018 | PRC-002-3 R5.1.3. | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. |  |  | 2024-03-31 |  |  | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000012 |  | 1.4. | RP-2021-07-15-0000019 | PRC-002-3 R5.1.4. | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. |  |  | 2024-03-31 |  |  | 514000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000012 |  | 1.5. | RP-2021-07-15-0000020 | PRC-002-3 R5.1.5. | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. |  |  | 2024-03-31 |  |  | 515000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000012 |  | 2. | RP-2021-07-15-0000021 | PRC-002-3 R5.2. | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. |  |  | 2024-03-31 |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000012 |  | 2.1. | RP-2021-07-15-0000022 | PRC-002-3 R5.2.1. | One BES Element; and |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. |  |  | 2024-03-31 |  |  | 521000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000012 |  | 2.2. | RP-2021-07-15-0000023 | PRC-002-3 R5.2.2. | One BES Element per 3,000 MW of the Reliability Coordinator’s historical simultaneous peak System Demand. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. |  |  | 2024-03-31 |  |  | 522000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000012 |  | 3. | RP-2021-07-15-0000024 | PRC-002-3 R5.3. | Notify all owners of identified BES Elements, within 90-calendar days of completion of Part 5.1, that their respective BES Elements require DDR data when requested. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. |  |  | 2024-03-31 |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000012 |  | 4. | RP-2021-07-15-0000025 | PRC-002-3 R5.4. | Re-evaluate all BES Elements at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3 to implement the re-evaluated list of BES Elements as per the Implementation Plan. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. |  |  | 2024-03-31 |  |  | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000013 |  | 1. | RP-2021-07-15-0000026 | PRC-002-3 R6.1. | One phase-to-neutral or positive sequence voltage. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. |  |  | 2024-03-31 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000013 |  | 2. | RP-2021-07-15-0000027 | PRC-002-3 R6.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. |  |  | 2024-03-31 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000013 |  | 3. | RP-2021-07-15-0000028 | PRC-002-3 R6.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. |  |  | 2024-03-31 |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000013 |  | 4. | RP-2021-07-15-0000029 | PRC-002-3 R6.4. | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. |  |  | 2024-03-31 |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000014 |  | 1. | RP-2021-07-15-0000030 | PRC-002-3 R7.1. | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. |  |  | 2024-03-31 |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000014 |  | 2. | RP-2021-07-15-0000031 | PRC-002-3 R7.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. |  |  | 2024-03-31 |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000014 |  | 3. | RP-2021-07-15-0000032 | PRC-002-3 R7.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. |  |  | 2024-03-31 |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000014 |  | 4. | RP-2021-07-15-0000033 | PRC-002-3 R7.4. | Frequency of at least one of the voltages in Requirement R7, Part 7.1. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. |  |  | 2024-03-31 |  |  | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000015 |  | 1. | RP-2021-07-15-0000034 | PRC-002-3 R8.1. | Triggered record lengths of at least three minutes. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. |  |  | 2024-03-31 |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-14-0000015 |  | 2. | RP-2021-07-15-0000035 | PRC-002-3 R8.2. | At least one of the following three triggers: · Off nominal frequency trigger set at: Low High o Eastern Interconnection <59.75 Hz >61.0 Hz o Western Interconnection <59.55 Hz >61.0 Hz o ERCOT Interconnection <59.35 Hz >61.0 Hz o Hydro-Quebec Interconnection <58.55 Hz >61.5 Hz · Rate of change of frequency trigger set at: o Eastern Interconnection < -0.03125 Hz/sec > 0.125 Hz/sec o Western Interconnection < -0.05625 Hz/sec > 0.125 Hz/sec o ERCOT Interconnection < -0.08125 Hz/sec > 0.125 Hz/sec o Hydro-Quebec Interconnection < -0.18125 Hz/sec > 0.1875 Hz/sec · Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. |  |  | 2024-03-31 |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-15-0000001 |  | 1. | RP-2021-07-15-0000036 | PRC-002-3 R9.1. | Input sampling rate of at least 960 samples per second. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). |  |  | 2024-03-31 |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-15-0000001 |  | 2. | RP-2021-07-15-0000037 | PRC-002-3 R9.2. | Output recording rate of electrical quantities of at least 30 times per second. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). |  |  | 2024-03-31 |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-15-0000002 |  | 1. | RP-2021-07-15-0000038 | PRC-002-3 R10.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. |  |  | 2024-03-31 |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-15-0000002 |  | 2. | RP-2021-07-15-0000039 | PRC-002-3 R10.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. |  |  | 2024-03-31 |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-15-0000003 |  | 1. | RP-2021-07-15-0000040 | PRC-002-3 R11.1. | Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. |  |  | 2024-03-31 |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-15-0000003 |  | 2. | RP-2021-07-15-0000041 | PRC-002-3 R11.2. | Data subject to Part 11.1 will be provided within 30-calendar days of a request unless an extension is granted by the requestor. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. |  |  | 2024-03-31 |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-15-0000003 |  | 3. | RP-2021-07-15-0000042 | PRC-002-3 R11.3. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. |  |  | 2024-03-31 |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-15-0000003 |  | 4. | RP-2021-07-15-0000043 | PRC-002-3 R11.4. | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. |  |  | 2024-03-31 |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002 | RQ-2021-07-15-0000003 |  | 5. | RP-2021-07-15-0000044 | PRC-002-3 R11.5. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. |  |  | 2024-03-31 |  |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000008-NS |  | 1. | RP-2021-07-15-0000001-NS | PRC-002-3 (Nova Scotia) R1.1. | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-3, Attachment 1. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-3, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. | 2024-10-01 |  |  |  |  | 110000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000008-NS |  | 2. | RP-2021-07-15-0000002-NS | PRC-002-3 (Nova Scotia) R1.2. | Notify other owners of BES Elements connected to those BES buses, if any, within 90-calendar days of completion of Part 1.1, that those BES Elements require SER data and/or FR data. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-3, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. | 2024-10-01 |  |  |  |  | 120000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000008-NS |  | 3. | RP-2021-07-15-0000003-NS | PRC-002-3 (Nova Scotia) R1.3. | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners, if any, in accordance with Part 1.2, and implement the re-evaluated list of BES buses as per the Implementation Plan. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-3, Attachment 1, and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1. The Transmission Owner will also have dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1. | 2024-10-01 |  |  |  |  | 130000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000010-NS |  | 1. | RP-2021-07-15-0000004-NS | PRC-002-3 (Nova Scotia) R3.1. | Phase-to-neutral voltage for each phase of each specified BES bus. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-10-01 |  |  |  |  | 310000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000010-NS |  | 2. | RP-2021-07-15-0000005-NS | PRC-002-3 (Nova Scotia) R3.2. | Each phase current and the residual or neutral current for the following BES Elements: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-10-01 |  |  |  |  | 320000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000010-NS |  | 2.1. | RP-2021-07-15-0000006-NS | PRC-002-3 (Nova Scotia) R3.2.1. | Transformers that have a low-side operating voltage of 100kV or above. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-10-01 |  |  |  |  | 321000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000010-NS |  | 2.2. | RP-2021-07-15-0000007-NS | PRC-002-3 (Nova Scotia) R3.2.2. | Transmission Lines. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-10-01 |  |  |  |  | 322000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000011-NS |  | 1. | RP-2021-07-15-0000008-NS | PRC-002-3 (Nova Scotia) R4.1. | A single record or multiple records that include: • A pre-trigger record length of at least two cycles and a total record length of at least 30-cycles for the same trigger point, or • At least two cycles of the pre-trigger data, the first three cycles of the post- trigger data, and the final cycle of the fault as seen by the fault recorder. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | 2024-10-01 |  |  |  |  | 410000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000011-NS |  | 2. | RP-2021-07-15-0000009-NS | PRC-002-3 (Nova Scotia) R4.2. | A minimum recording rate of 16 samples per cycle. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | 2024-10-01 |  |  |  |  | 420000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000011-NS |  | 3. | RP-2021-07-15-0000010-NS | PRC-002-3 (Nova Scotia) R4.3. | Trigger settings for at least the following: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | 2024-10-01 |  |  |  |  | 430000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000011-NS |  | 3.1. | RP-2021-07-15-0000011-NS | PRC-002-3 (Nova Scotia) R4.3.1. | Neutral (residual) overcurrent. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | 2024-10-01 |  |  |  |  | 431000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000011-NS |  | 3.2. | RP-2021-07-15-0000012-NS | PRC-002-3 (Nova Scotia) R4.3.2. | Phase undervoltage or overcurrent. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | 2024-10-01 |  |  |  |  | 432000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000012-NS |  | 1. | RP-2021-07-15-0000013-NS | PRC-002-3 (Nova Scotia) R5.1. | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-10-01 |  |  |  |  | 510000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000012-NS |  | 1.1. | RP-2021-07-15-0000014-NS | PRC-002-3 (Nova Scotia) R5.1.1. | Generating resource(s) with: |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-10-01 |  |  |  |  | 511000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000012-NS |  | 1.1.1. | RP-2021-07-15-0000015-NS | PRC-002-3 (Nova Scotia) R5.1.1.1. | Gross individual nameplate rating greater than or equal to 500 MVA. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-10-01 |  |  |  |  | 511100000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000012-NS |  | 1.1.2. | RP-2021-07-15-0000016-NS | PRC-002-3 (Nova Scotia) R5.1.1.2. | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-10-01 |  |  |  |  | 511200000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000012-NS |  | 1.2. | RP-2021-07-15-0000017-NS | PRC-002-3 (Nova Scotia) R5.1.2. | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-10-01 |  |  |  |  | 512000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000012-NS |  | 1.3. | RP-2021-07-15-0000018-NS | PRC-002-3 (Nova Scotia) R5.1.3. | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-10-01 |  |  |  |  | 513000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000012-NS |  | 1.4. | RP-2021-07-15-0000019-NS | PRC-002-3 (Nova Scotia) R5.1.4. | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-10-01 |  |  |  |  | 514000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000012-NS |  | 1.5. | RP-2021-07-15-0000020-NS | PRC-002-3 (Nova Scotia) R5.1.5. | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-10-01 |  |  |  |  | 515000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000012-NS |  | 2. | RP-2021-07-15-0000021-NS | PRC-002-3 (Nova Scotia) R5.2. | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-10-01 |  |  |  |  | 520000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000012-NS |  | 2.1. | RP-2021-07-15-0000022-NS | PRC-002-3 (Nova Scotia) R5.2.1. | One BES Element; and |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-10-01 |  |  |  |  | 521000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000012-NS |  | 2.2. | RP-2021-07-15-0000023-NS | PRC-002-3 (Nova Scotia) R5.2.2. | One BES Element per 3,000 MW of the Reliability Coordinator’s historical simultaneous peak System Demand. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-10-01 |  |  |  |  | 522000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000012-NS |  | 3. | RP-2021-07-15-0000024-NS | PRC-002-3 (Nova Scotia) R5.3. | Notify all owners of identified BES Elements, within 90-calendar days of completion of Part 5.1, that their respective BES Elements require DDR data when requested. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-10-01 |  |  |  |  | 530000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000012-NS |  | 4. | RP-2021-07-15-0000025-NS | PRC-002-3 (Nova Scotia) R5.4. | Re-evaluate all BES Elements at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3 to implement the re-evaluated list of BES Elements as per the Implementation Plan. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-10-01 |  |  |  |  | 540000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000013-NS |  | 1. | RP-2021-07-15-0000026-NS | PRC-002-3 (Nova Scotia) R6.1. | One phase-to-neutral or positive sequence voltage. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-10-01 |  |  |  |  | 610000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000013-NS |  | 2. | RP-2021-07-15-0000027-NS | PRC-002-3 (Nova Scotia) R6.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-10-01 |  |  |  |  | 620000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000013-NS |  | 3. | RP-2021-07-15-0000028-NS | PRC-002-3 (Nova Scotia) R6.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-10-01 |  |  |  |  | 630000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000013-NS |  | 4. | RP-2021-07-15-0000029-NS | PRC-002-3 (Nova Scotia) R6.4. | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-10-01 |  |  |  |  | 640000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000014-NS |  | 1. | RP-2021-07-15-0000030-NS | PRC-002-3 (Nova Scotia) R7.1. | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-10-01 |  |  |  |  | 710000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000014-NS |  | 2. | RP-2021-07-15-0000031-NS | PRC-002-3 (Nova Scotia) R7.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-10-01 |  |  |  |  | 720000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000014-NS |  | 3. | RP-2021-07-15-0000032-NS | PRC-002-3 (Nova Scotia) R7.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-10-01 |  |  |  |  | 730000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000014-NS |  | 4. | RP-2021-07-15-0000033-NS | PRC-002-3 (Nova Scotia) R7.4. | Frequency of at least one of the voltages in Requirement R7, Part 7.1. |  | GO |  |  |  |  | GO | [16 empty] | The Generator Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R7. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-10-01 |  |  |  |  | 740000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000015-NS |  | 1. | RP-2021-07-15-0000034-NS | PRC-002-3 (Nova Scotia) R8.1. | Triggered record lengths of at least three minutes. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | 2024-10-01 |  |  |  |  | 810000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-14-0000015-NS |  | 2. | RP-2021-07-15-0000035-NS | PRC-002-3 (Nova Scotia) R8.2. | At least one of the following three triggers: · Off nominal frequency trigger set at: Low High o Eastern Interconnection <59.75 Hz >61.0 Hz o Western Interconnection <59.55 Hz >61.0 Hz o ERCOT Interconnection <59.35 Hz >61.0 Hz o Hydro-Quebec Interconnection <58.55 Hz >61.5 Hz · Rate of change of frequency trigger set at: o Eastern Interconnection < -0.03125 Hz/sec > 0.125 Hz/sec o Western Interconnection < -0.05625 Hz/sec > 0.125 Hz/sec o ERCOT Interconnection < -0.08125 Hz/sec > 0.125 Hz/sec o Hydro-Quebec Interconnection < -0.18125 Hz/sec > 0.1875 Hz/sec · Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | 2024-10-01 |  |  |  |  | 820000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-15-0000001-NS |  | 1. | RP-2021-07-15-0000036-NS | PRC-002-3 (Nova Scotia) R9.1. | Input sampling rate of at least 960 samples per second. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | 2024-10-01 |  |  |  |  | 910000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-15-0000001-NS |  | 2. | RP-2021-07-15-0000037-NS | PRC-002-3 (Nova Scotia) R9.2. | Output recording rate of electrical quantities of at least 30 times per second. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | 2024-10-01 |  |  |  |  | 920000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-15-0000002-NS |  | 1. | RP-2021-07-15-0000038-NS | PRC-002-3 (Nova Scotia) R10.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | 2024-10-01 |  |  |  |  | 101000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-15-0000002-NS |  | 2. | RP-2021-07-15-0000039-NS | PRC-002-3 (Nova Scotia) R10.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | 2024-10-01 |  |  |  |  | 102000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-15-0000003-NS |  | 1. | RP-2021-07-15-0000040-NS | PRC-002-3 (Nova Scotia) R11.1. | Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | 2024-10-01 |  |  |  |  | 111000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-15-0000003-NS |  | 2. | RP-2021-07-15-0000041-NS | PRC-002-3 (Nova Scotia) R11.2. | Data subject to Part 11.1 will be provided within 30-calendar days of a request unless an extension is granted by the requestor. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | 2024-10-01 |  |  |  |  | 112000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-15-0000003-NS |  | 3. | RP-2021-07-15-0000042-NS | PRC-002-3 (Nova Scotia) R11.3. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | 2024-10-01 |  |  |  |  | 113000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-15-0000003-NS |  | 4. | RP-2021-07-15-0000043-NS | PRC-002-3 (Nova Scotia) R11.4. | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | 2024-10-01 |  |  |  |  | 114000000 | NPCC-NS
ST-2021-07-14-0000002-NS | RQ-2021-07-15-0000003-NS |  | 5. | RP-2021-07-15-0000044-NS | PRC-002-3 (Nova Scotia) R11.5. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | 2024-10-01 |  |  |  |  | 115000000 | NPCC-NS
ST-2021-07-15-0000001 | RQ-2021-07-15-0000010 |  | 1. | RP-2021-07-15-0000045 | PRC-023-5 R6.1. | Maintain a list of circuits subject to PRC-023-5 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-5, Attachment B applies. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-5, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | 2024-04-01 | X | 2024-03-31 |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-15-0000001 | RQ-2021-07-15-0000010 |  | 2. | RP-2021-07-15-0000046 | PRC-023-5 R6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-5, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | 2024-04-01 | X | 2024-03-31 |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-15-0000001-NS | RQ-2021-07-15-0000010-NS |  | 1. | RP-2021-07-15-0000045-NS | PRC-023-5 (Nova Scotia) R6.1. | Maintain a list of circuits subject to PRC-023-5 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-5, Attachment B applies. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-5, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | 2024-10-01 |  |  |  |  | 610000000 | NPCC-NS
ST-2021-07-15-0000001-NS | RQ-2021-07-15-0000010-NS |  | 2. | RP-2021-07-15-0000046-NS | PRC-023-5 (Nova Scotia) R6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. |  | DP, GO, TO |  | DP |  |  | GO | [12 empty] | TO |  |  |  | Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-5, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | 2024-10-01 |  |  |  |  | 620000000 | NPCC-NS
ST-2021-07-15-0000002 | RQ-2021-07-15-0000012 |  | 1. | RP-2021-07-15-0000047 | PRC-026-2 R2.1. | Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-2 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-2 – Attachment B criteria has not been performed in the last five calendar years. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Generator Owner and Transmission Owner shall have dated evidence that demonstrates the evaluation was performed according to Requirement R2. Evidence may include, but is not limited to, the following documentation: apparent impedance characteristic plots, email, design drawings, facsimiles, R-X plots, software output, records, reports, transmittals, lists, settings sheets, or spreadsheets. | 2024-04-01 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-15-0000002 | RQ-2021-07-15-0000012 |  | 2. | RP-2021-07-15-0000048 | PRC-026-2 R2.2. | Within 12 full calendar months of becoming aware2 of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable3 power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-2 – Attachment B. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Generator Owner and Transmission Owner shall have dated evidence that demonstrates the evaluation was performed according to Requirement R2. Evidence may include, but is not limited to, the following documentation: apparent impedance characteristic plots, email, design drawings, facsimiles, R-X plots, software output, records, reports, transmittals, lists, settings sheets, or spreadsheets. | 2024-04-01 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-07-15-0000002-NS | RQ-2021-07-15-0000012-NS |  | 1. | RP-2021-07-15-0000047-NS | PRC-026-2 (Nova Scotia) R2.1. | Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-2 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-2 – Attachment B criteria has not been performed in the last five calendar years. |  | GO, PCPA, TO |  |  |  |  | GO |  |  |  |  | PCPA | [7 empty] | TO |  |  |  | Each Generator Owner and Transmission Owner shall have dated evidence that demonstrates the evaluation was performed according to Requirement R2. Evidence may include, but is not limited to, the following documentation: apparent impedance characteristic plots, email, design drawings, facsimiles, R-X plots, software output, records, reports, transmittals, lists, settings sheets, or spreadsheets. | 2024-10-01 |  |  |  |  | 210000000 | NPCC-NS
ST-2021-07-15-0000002-NS | RQ-2021-07-15-0000012-NS |  | 2. | RP-2021-07-15-0000048-NS | PRC-026-2 (Nova Scotia) R2.2. | Within 12 full calendar months of becoming aware2 of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable3 power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-2 – Attachment B. |  | GO, PCPA, TO |  |  |  |  | GO |  |  |  |  | PCPA | [7 empty] | TO |  |  |  | Each Generator Owner and Transmission Owner shall have dated evidence that demonstrates the evaluation was performed according to Requirement R2. Evidence may include, but is not limited to, the following documentation: apparent impedance characteristic plots, email, design drawings, facsimiles, R-X plots, software output, records, reports, transmittals, lists, settings sheets, or spreadsheets. | 2024-10-01 |  |  |  |  | 220000000 | NPCC-NS
ST-2021-08-17-0000001 | RQ-2021-08-17-0000001 |  | 1. | RP-2021-08-17-0000001 | CIP-004-7 R1.1. | Security awareness that, at least once each calendar quarter, reinforces cyber security practices (which may include associated physical security practices) for the Responsible Entity’s personnel who have authorized electronic or authorized unescorted physical access to BES Cyber Systems. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation that the quarterly reinforcement has been provided. Examples of evidence of reinforcement may include, but are not limited to, dated copies of information used to reinforce security awareness, as well as evidence of distribution, such as: • direct communications (for example, e-mails, memos, computer-based training); or • indirect communications (for example, posters, intranet, or brochures); or • management support and reinforcement (for example, presentations or meetings). | 2024-01-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000002 | RP-2021-08-17-0000002 | 1. | RP-2021-08-17-0000003 | CIP-004-7 R2.1.1. | Cyber security policies; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-01-01 |  |  |  |  | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000002 |  | 1. | RP-2021-08-17-0000002 | CIP-004-7 R2.1. | Training content on: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-01-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000002 |  | 1.2. | RP-2021-08-17-0000004 | CIP-004-7 R2.1.2. | Physical access controls; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-01-01 |  |  |  |  | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000002 |  | 1.3. | RP-2021-08-17-0000005 | CIP-004-7 R2.1.3. | Electronic access controls; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-01-01 |  |  |  |  | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000002 |  | 1.4. | RP-2021-08-17-0000006 | CIP-004-7 R2.1.4. | The visitor control program; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-01-01 |  |  |  |  | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000002 |  | 1.5. | RP-2021-08-17-0000007 | CIP-004-7 R2.1.5. | Handling of BES Cyber System Information and its storage; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-01-01 |  |  |  |  | 215000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000002 |  | 1.6. | RP-2021-08-17-0000008 | CIP-004-7 R2.1.6. | Identification of a Cyber Security Incident and initial notifications in accordance with the entity’s incident response plan; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-01-01 |  |  |  |  | 216000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000002 |  | 1.7. | RP-2021-08-17-0000009 | CIP-004-7 R2.1.7. | Recovery plans for BES Cyber Systems; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-01-01 |  |  |  |  | 217000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000002 |  | 1.8. | RP-2021-08-17-0000010 | CIP-004-7 R2.1.8. | Response to Cyber Security Incidents; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-01-01 |  |  |  |  | 218000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000002 |  | 1.9. | RP-2021-08-17-0000011 | CIP-004-7 R2.1.9. | Cyber security risks associated with a BES Cyber System’s electronic interconnectivity and interoperability with other Cyber Assets, including Transient Cyber Assets, and with Removable Media. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-01-01 |  |  |  |  | 219000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000002 |  | 2. | RP-2021-08-17-0000012 | CIP-004-7 R2.2. | Require completion of the training specified in Part 2.1 prior to granting authorized electronic access and authorized unescorted physical access to applicable Cyber Assets, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training records and documentation of when CIP Exceptional Circumstances were invoked. | 2024-01-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000002 |  | 3. | RP-2021-08-17-0000013 | CIP-004-7 R2.3. | Require completion of the training specified in Part 2.1 at least once every 15 calendar months. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated individual training records. | 2024-01-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000003 |  | 1. | RP-2021-08-17-0000014 | CIP-004-7 R3.1. | Process to confirm identity. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to confirm identity. | 2024-01-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000003 |  | 2. | RP-2021-08-17-0000015 | CIP-004-7 R3.2. | Process to perform a seven year criminal history records check as part of each personnel risk assessment that includes: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. | 2024-01-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000003 |  | 2.1. | RP-2021-08-17-0000016 | CIP-004-7 R3.2.1. | current residence, regardless of duration; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. | 2024-01-01 |  |  |  |  | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000003 |  | 2.2. | RP-2021-08-17-0000017 | CIP-004-7 R3.2.2. | other locations where, during the seven years immediately prior to the date of the criminal history records check, the subject has resided for six consecutive months or more. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. | 2024-01-01 |  |  |  |  | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000003 |  | 3. | RP-2021-08-17-0000018 | CIP-004-7 R3.3. | Criteria or process to evaluate criminal history records checks for authorizing access. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to evaluate criminal history records checks. | 2024-01-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000003 |  | 4. | RP-2021-08-17-0000019 | CIP-004-7 R3.4. | Criteria or process for verifying that personnel risk assessments performed for contractors or service vendors are conducted according to Parts 3.1 through 3.3. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s criteria or process for verifying contractors or service vendors personnel risk assessments. | 2024-01-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000003 |  | 5. | RP-2021-08-17-0000020 | CIP-004-7 R3.5. | Process to ensure that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed according to Parts 3.1 to 3.4 within the last seven years. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process for ensuring that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed within the last seven years. | 2024-01-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000004 | RP-2021-08-17-0000021 | 1. | RP-2023-07-27-0000001 | CIP-004-7 R4.1.1. | Electronic access; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include,but is not limited to, dated documentation of the process to authorize electronic access, and unescorted physical access in a Physical Security Perimeter | 2024-01-01 |  |  |  |  | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000004 | RP-2021-08-17-0000021 | 2. | RP-2023-07-27-0000002 | CIP-004-7 R4.1.2. | Unescorted physical access into a Physical Security Perimeter |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include,but is not limited to, dated documentation of the process to authorize electronic access, and unescorted physical access in a Physical Security Perimeter. | 2024-01-01 |  |  |  |  | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000004 |  | 1. | RP-2021-08-17-0000021 | CIP-004-7 R4.1. | Process to authorize based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, and unescorted physical access in a Physical Security Perimeter. | 2024-01-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000004 |  | 2. | RP-2021-08-17-0000024 | CIP-004-7 R4.2. | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • Dated documentation of the verification between the system generated list of individuals who have been authorized for access (i.e., workflow database) and a system generated list of personnel who have access (i.e., user account listing), or Dated documentation of the verification between a list of individuals who have been authorized for access (i.e., authorization forms) and a list of individuals provisioned for access (i.e., provisioning forms or shared account listing). | 2024-01-01 |  |  |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000004 |  | 3. | RP-2021-08-17-0000025 | CIP-004-7 R4.3. | For electronic access, verify at least once every 15 calendar months that all user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and are those that the Responsible Entity determines are necessary. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the review that includes all of the following: 1. A dated listing of all accounts/account groups or roles within the system; 2. A summary description of privileges associated with each group or role; 3. Accounts assigned to the group or role; and Dated evidence showing verification of the privileges for the group are authorized and appropriate to the work function performed by people assigned to each account. | 2024-01-01 |  |  |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000005 |  | 1. | RP-2021-08-17-0000026 | CIP-004-7 R5.1. | A process to initiate removal of an individual’s ability for unescorted physical access and Interactive Remote Access upon a termination action, and complete the removals within 24 hours of the termination action (Removal of the ability for access may be different than deletion, disabling, revocation, or removal of all access rights). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of all of the following: 1. Dated workflow or sign-off form verifying access removal associated with the termination action; and Logs or other demonstration showing such persons no longer have access. | 2024-01-01 |  |  |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000005 |  | 2. | RP-2021-08-17-0000027 | CIP-004-7 R5.2. | For reassignments or transfers, revoke the individual’s authorized electronic access to individual accounts and authorized unescorted physical access that the Responsible Entity determines are not necessary by the end of the next calendar day following the date that the Responsible Entity determines that the individual no longer requires retention of that access. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of all of the following: 1. Dated workflow or sign-off form showing a review of logical and physical access; and Logs or other demonstration showing such persons no longer have access that the Responsible Entity determines is not necessary. | 2024-01-01 |  |  |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000005 |  | 3. | RP-2021-08-17-0000028 | CIP-004-7 R5.3. | For termination actions, revoke the individual’s non-shared user accounts (unless already revoked according to Part 5.1) within 30 calendar days of the effective date of the termination action. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, workflow or sign-off form showing access removal for any individual BES Cyber Assets and software applications as determined necessary to completing the revocation of access and dated within thirty calendar days of the termination actions. | 2024-01-01 |  |  |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000005 |  | 4. | RP-2021-08-17-0000029 | CIP-004-7 R5.4. | For termination actions, change passwords for shared account(s) known to the user within 30 calendar days of the termination action. For reassignments or transfers, change passwords for shared account(s) known to the user within 30 calendar days following the date that the Responsible Entity determines that the individual no longer requires retention of that access. If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • Workflow or sign-off form showing password reset within 30 calendar days of the termination; • Workflow or sign-off form showing password reset within 30 calendar days of the reassignments or transfers; or Documentation of the extenuating operating circumstance and workflow or sign-off form showing password reset within 10 calendar days following the end of the operating circumstance. | 2024-01-01 |  |  |  |  | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000006 |  | 1. | RP-2021-08-17-0000030 | CIP-004-7 R6.1. | Prior to provisioning, authorize (unless already authorized according to Part 4.1.) based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, individual records or lists that include who is authorized, the date of the authorization, and the justification of business need for the provisioned access. | 2024-01-01 |  |  |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000006 |  | 1.1. | RP-2021-08-17-0000031 | CIP-004-7 R6.1.1. | Provisioned electronic access to electronic BCSI; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, individual records or lists that include who is authorized, the date of the authorization, and the justification of business need for the provisioned access. | 2024-01-01 |  |  |  |  | 611000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000006 |  | 1.2. | RP-2021-08-17-0000032 | CIP-004-7 R6.1.2. | Provisioned physical access to physical BCSI. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, individual records or lists that include who is authorized, the date of the authorization, and the justification of business need for the provisioned access. | 2024-01-01 |  |  |  |  | 612000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000006 |  | 2. | RP-2021-08-17-0000033 | CIP-004-7 R6.2. | Verify at least once every 15 calendar months that all individuals with provisioned access to BCSI: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, the documentation of the review that includes all of the following: • List of authorized individuals; • List of individuals who have been provisioned access; • Verification that provisioned access is appropriate based on need; and • Documented reconciliation actions, if any. | 2024-01-01 |  |  |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000006 |  | 2.1. | RP-2021-08-17-0000034 | CIP-004-7 R6.2.1. | have an authorization record; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, the documentation of the review that includes all of the following: • List of authorized individuals; • List of individuals who have been provisioned access; • Verification that provisioned access is appropriate based on need; and • Documented reconciliation actions, if any. | 2024-01-01 |  |  |  |  | 621000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000006 |  | 2.2. | RP-2021-08-17-0000035 | CIP-004-7 R6.2.2. | still need the provisioned access to perform their current work functions, as determined by the Responsible Entity. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, the documentation of the review that includes all of the following: • List of authorized individuals; • List of individuals who have been provisioned access; • Verification that provisioned access is appropriate based on need; and • Documented reconciliation actions, if any. | 2024-01-01 |  |  |  |  | 622000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001 | RQ-2021-08-17-0000006 |  | 3. | RP-2021-08-17-0000036 | CIP-004-7 R6.3. | For termination actions, remove the individual’s ability to use provisioned access to BCSI (unless already revoked according to Part 5.1) by the end of the next calendar day following the effective date of the termination action. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of dated evidence may include, but are not limited to, access revocation records associated with the terminations and dated within the next calendar day of the termination action. | 2024-01-01 |  |  |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000001-NS |  | 1. | RP-2021-08-17-0000001-NS | CIP-004-7 (Nova Scotia) R1.1. | Security awareness that, at least once each calendar quarter, reinforces cyber security practices (which may include associated physical security practices) for the Responsible Entity’s personnel who have authorized electronic or authorized unescorted physical access to BES Cyber Systems. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation that the quarterly reinforcement has been provided. Examples of evidence of reinforcement may include, but are not limited to, dated copies of information used to reinforce security awareness, as well as evidence of distribution, such as: • direct communications (for example, e-mails, memos, computer-based training); or • indirect communications (for example, posters, intranet, or brochures); or • management support and reinforcement (for example, presentations or meetings). | 2024-04-01 |  |  |  |  | 110000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000002-NS | RP-2021-08-17-0000002-NS | 1. | RP-2021-08-17-0000003-NS | CIP-004-7 (Nova Scotia) R2.1.1. | Cyber security policies; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-04-01 |  |  |  |  | 211000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000002-NS |  | 1. | RP-2021-08-17-0000002-NS | CIP-004-7 (Nova Scotia) R2.1. | Training content on: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-04-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 210000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000002-NS |  | 1.2. | RP-2021-08-17-0000004-NS | CIP-004-7 (Nova Scotia) R2.1.2. | Physical access controls; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-04-01 |  |  |  |  | 212000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000002-NS |  | 1.3. | RP-2021-08-17-0000005-NS | CIP-004-7 (Nova Scotia) R2.1.3. | Electronic access controls; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-04-01 |  |  |  |  | 213000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000002-NS |  | 1.4. | RP-2021-08-17-0000006-NS | CIP-004-7 (Nova Scotia) R2.1.4. | The visitor control program; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-04-01 |  |  |  |  | 214000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000002-NS |  | 1.5. | RP-2021-08-17-0000007-NS | CIP-004-7 (Nova Scotia) R2.1.5. | Handling of BES Cyber System Information and its storage; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-04-01 |  |  |  |  | 215000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000002-NS |  | 1.6. | RP-2021-08-17-0000008-NS | CIP-004-7 (Nova Scotia) R2.1.6. | Identification of a Cyber Security Incident and initial notifications in accordance with the entity’s incident response plan; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-04-01 |  |  |  |  | 216000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000002-NS |  | 1.7. | RP-2021-08-17-0000009-NS | CIP-004-7 (Nova Scotia) R2.1.7. | Recovery plans for BES Cyber Systems; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-04-01 |  |  |  |  | 217000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000002-NS |  | 1.8. | RP-2021-08-17-0000010-NS | CIP-004-7 (Nova Scotia) R2.1.8. | Response to Cyber Security Incidents; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-04-01 |  |  |  |  | 218000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000002-NS |  | 1.9. | RP-2021-08-17-0000011-NS | CIP-004-7 (Nova Scotia) R2.1.9. | Cyber security risks associated with a BES Cyber System’s electronic interconnectivity and interoperability with other Cyber Assets, including Transient Cyber Assets, and with Removable Media. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2024-04-01 |  |  |  |  | 219000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000002-NS |  | 2. | RP-2021-08-17-0000012-NS | CIP-004-7 (Nova Scotia) R2.2. | Require completion of the training specified in Part 2.1 prior to granting authorized electronic access and authorized unescorted physical access to applicable Cyber Assets, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training records and documentation of when CIP Exceptional Circumstances were invoked. | 2024-04-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 220000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000002-NS |  | 3. | RP-2021-08-17-0000013-NS | CIP-004-7 (Nova Scotia) R2.3. | Require completion of the training specified in Part 2.1 at least once every 15 calendar months. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated individual training records. | 2024-04-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 230000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000003-NS |  | 1. | RP-2021-08-17-0000014-NS | CIP-004-7 (Nova Scotia) R3.1. | Process to confirm identity. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to confirm identity. | 2024-04-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 310000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000003-NS |  | 2. | RP-2021-08-17-0000015-NS | CIP-004-7 (Nova Scotia) R3.2. | Process to perform a seven year criminal history records check as part of each personnel risk assessment that includes: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. | 2024-04-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 320000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000003-NS |  | 2.1. | RP-2021-08-17-0000016-NS | CIP-004-7 (Nova Scotia) R3.2.1. | current residence, regardless of duration; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. | 2024-04-01 |  |  |  |  | 321000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000003-NS |  | 2.2. | RP-2021-08-17-0000017-NS | CIP-004-7 (Nova Scotia) R3.2.2. | other locations where, during the seven years immediately prior to the date of the criminal history records check, the subject has resided for six consecutive months or more. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. | 2024-04-01 |  |  |  |  | 322000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000003-NS |  | 3. | RP-2021-08-17-0000018-NS | CIP-004-7 (Nova Scotia) R3.3. | Criteria or process to evaluate criminal history records checks for authorizing access. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to evaluate criminal history records checks. | 2024-04-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 330000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000003-NS |  | 4. | RP-2021-08-17-0000019-NS | CIP-004-7 (Nova Scotia) R3.4. | Criteria or process for verifying that personnel risk assessments performed for contractors or service vendors are conducted according to Parts 3.1 through 3.3. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s criteria or process for verifying contractors or service vendors personnel risk assessments. | 2024-04-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 340000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000003-NS |  | 5. | RP-2021-08-17-0000020-NS | CIP-004-7 (Nova Scotia) R3.5. | Process to ensure that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed according to Parts 3.1 to 3.4 within the last seven years. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process for ensuring that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed within the last seven years. | 2024-04-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 350000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000004-NS |  | 1. | RP-2021-08-17-0000021-NS | CIP-004-7 (Nova Scotia) R4.1. | Process to authorize based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, and unescorted physical access in a Physical Security Perimeter. | 2024-04-01 |  |  |  | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: 1. EACMS; and 2. PACS | 410000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000004-NS |  | 1.1. | RP-2021-08-17-0000022-NS | CIP-004-7 (Nova Scotia) R4.1.1. | Electronic access; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, and unescorted physical access in a Physical Security Perimeter. | 2024-04-01 |  |  |  |  | 411000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000004-NS |  | 1.2. | RP-2021-08-17-0000023-NS | CIP-004-7 (Nova Scotia) R4.1.2. | Unescorted physical access into a Physical Security Perimeter |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, and unescorted physical access in a Physical Security Perimeter. | 2024-04-01 |  |  |  |  | 412000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000004-NS |  | 2. | RP-2021-08-17-0000024-NS | CIP-004-7 (Nova Scotia) R4.2. | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • Dated documentation of the verification between the system generated list of individuals who have been authorized for access (i.e., workflow database) and a system generated list of personnel who have access (i.e., user account listing), or Dated documentation of the verification between a list of individuals who have been authorized for access (i.e., authorization forms) and a list of individuals provisioned for access (i.e., provisioning forms or shared account listing). | 2024-04-01 |  |  |  |  | 420000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000004-NS |  | 3. | RP-2021-08-17-0000025-NS | CIP-004-7 (Nova Scotia) R4.3. | For electronic access, verify at least once every 15 calendar months that all user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and are those that the Responsible Entity determines are necessary. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the review that includes all of the following: 1. A dated listing of all accounts/account groups or roles within the system; 2. A summary description of privileges associated with each group or role; 3. Accounts assigned to the group or role; and Dated evidence showing verification of the privileges for the group are authorized and appropriate to the work function performed by people assigned to each account. | 2024-04-01 |  |  |  |  | 430000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000005-NS |  | 1. | RP-2021-08-17-0000026-NS | CIP-004-7 (Nova Scotia) R5.1. | A process to initiate removal of an individual’s ability for unescorted physical access and Interactive Remote Access upon a termination action, and complete the removals within 24 hours of the termination action (Removal of the ability for access may be different than deletion, disabling, revocation, or removal of all access rights). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of all of the following: 1. Dated workflow or sign-off form verifying access removal associated with the termination action; and Logs or other demonstration showing such persons no longer have access. | 2024-04-01 |  |  |  |  | 510000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000005-NS |  | 2. | RP-2021-08-17-0000027-NS | CIP-004-7 (Nova Scotia) R5.2. | For reassignments or transfers, revoke the individual’s authorized electronic access to individual accounts and authorized unescorted physical access that the Responsible Entity determines are not necessary by the end of the next calendar day following the date that the Responsible Entity determines that the individual no longer requires retention of that access. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of all of the following: 1. Dated workflow or sign-off form showing a review of logical and physical access; and Logs or other demonstration showing such persons no longer have access that the Responsible Entity determines is not necessary. | 2024-04-01 |  |  |  |  | 520000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000005-NS |  | 3. | RP-2021-08-17-0000028-NS | CIP-004-7 (Nova Scotia) R5.3. | For termination actions, revoke the individual’s non-shared user accounts (unless already revoked according to Part 5.1) within 30 calendar days of the effective date of the termination action. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, workflow or sign-off form showing access removal for any individual BES Cyber Assets and software applications as determined necessary to completing the revocation of access and dated within thirty calendar days of the termination actions. | 2024-04-01 |  |  |  |  | 530000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000005-NS |  | 4. | RP-2021-08-17-0000029-NS | CIP-004-7 (Nova Scotia) R5.4. | For termination actions, change passwords for shared account(s) known to the user within 30 calendar days of the termination action. For reassignments or transfers, change passwords for shared account(s) known to the user within 30 calendar days following the date that the Responsible Entity determines that the individual no longer requires retention of that access. If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • Workflow or sign-off form showing password reset within 30 calendar days of the termination; • Workflow or sign-off form showing password reset within 30 calendar days of the reassignments or transfers; or Documentation of the extenuating operating circumstance and workflow or sign-off form showing password reset within 10 calendar days following the end of the operating circumstance. | 2024-04-01 |  |  |  |  | 540000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000006-NS |  | 1. | RP-2021-08-17-0000030-NS | CIP-004-7 (Nova Scotia) R6.1. | Prior to provisioning, authorize (unless already authorized according to Part 4.1.) based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, individual records or lists that include who is authorized, the date of the authorization, and the justification of business need for the provisioned access. | 2024-04-01 |  |  |  |  | 610000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000006-NS |  | 1.1. | RP-2021-08-17-0000031-NS | CIP-004-7 (Nova Scotia) R6.1.1. | Provisioned electronic access to electronic BCSI; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, individual records or lists that include who is authorized, the date of the authorization, and the justification of business need for the provisioned access. | 2024-04-01 |  |  |  |  | 611000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000006-NS |  | 1.2. | RP-2021-08-17-0000032-NS | CIP-004-7 (Nova Scotia) R6.1.2. | Provisioned physical access to physical BCSI. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, individual records or lists that include who is authorized, the date of the authorization, and the justification of business need for the provisioned access. | 2024-04-01 |  |  |  |  | 612000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000006-NS |  | 2. | RP-2021-08-17-0000033-NS | CIP-004-7 (Nova Scotia) R6.2. | Verify at least once every 15 calendar months that all individuals with provisioned access to BCSI: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, the documentation of the review that includes all of the following: • List of authorized individuals; • List of individuals who have been provisioned access; • Verification that provisioned access is appropriate based on need; and • Documented reconciliation actions, if any. | 2024-04-01 |  |  |  |  | 620000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000006-NS |  | 2.1. | RP-2021-08-17-0000034-NS | CIP-004-7 (Nova Scotia) R6.2.1. | have an authorization record; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, the documentation of the review that includes all of the following: • List of authorized individuals; • List of individuals who have been provisioned access; • Verification that provisioned access is appropriate based on need; and • Documented reconciliation actions, if any. | 2024-04-01 |  |  |  |  | 621000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000006-NS |  | 2.2. | RP-2021-08-17-0000035-NS | CIP-004-7 (Nova Scotia) R6.2.2. | still need the provisioned access to perform their current work functions, as determined by the Responsible Entity. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, the documentation of the review that includes all of the following: • List of authorized individuals; • List of individuals who have been provisioned access; • Verification that provisioned access is appropriate based on need; and • Documented reconciliation actions, if any. | 2024-04-01 |  |  |  |  | 622000000 | NPCC-NS
ST-2021-08-17-0000001-NS | RQ-2021-08-17-0000006-NS |  | 3. | RP-2021-08-17-0000036-NS | CIP-004-7 (Nova Scotia) R6.3. | For termination actions, remove the individual’s ability to use provisioned access to BCSI (unless already revoked according to Part 5.1) by the end of the next calendar day following the effective date of the termination action. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of dated evidence may include, but are not limited to, access revocation records associated with the terminations and dated within the next calendar day of the termination action. | 2024-04-01 |  |  |  |  | 630000000 | NPCC-NS
ST-2021-08-17-0000002 | RQ-2021-08-17-0000007 |  | 1. | RP-2021-08-17-0000037 | CIP-011-3 R1.1. | Method(s) to identify BCSI. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of acceptable evidence may include, but are not limited to, the following: • Documented method(s) to identify BCSI from the entity’s information protection program; or • Indications on information (e.g., labels or classification) that identify BCSI as designated in the entity’s information protection program; or • Training materials that provide personnel with sufficient knowledge to identify BCSI; or • Storage locations identified for housing BCSI in the entity’s information protection program. | 2024-01-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000002 | RQ-2021-08-17-0000007 |  | 2. | RP-2021-08-17-0000038 | CIP-011-3 R1.2. | Method(s) to protect and securely handle BCSI to mitigate risks of compromising confidentiality. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence for on-premise BCSI may include, but are not limited to, the following: • Procedures for protecting and securely handling, which include topics such as storage, security during transit, and use of BCSI; or • Records indicating that BCSI is handled in a manner consistent with the entity’s documented procedure(s). Examples of evidence for off-premise BCSI may include, but are not limited to, the following: • Implementation of electronic technical method(s) to protect electronic BCSI (e.g., data masking, encryption, hashing, tokenization, cipher, electronic key management); or • Implementation of physical technical method(s) to protect physical BCSI (e.g., physical lock and key management, physical badge management, biometrics, alarm system); or • Implementation of administrative method(s) to protect BCSI (e.g., vendor service risk assessments, business agreements). | 2024-01-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000002 | RQ-2021-08-17-0000008 |  | 1. | RP-2021-08-17-0000039 | CIP-011-3 R2.1. | Prior to the release for reuse of applicable Cyber Assets that contain BCSI (except for reuse within other systems identified in the "Applicable Systems" column), the Responsible Entity shall take action to prevent the unauthorized retrieval of BCSI from the Cyber Asset data storage media. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of acceptable evidence may include, but are not limited to, the following: • Records tracking sanitization actions taken to prevent unauthorized retrieval of BCSI such as clearing, purging, or destroying; or • Records tracking actions such as encrypting, retaining in the Physical Security Perimeter or other methods used to prevent unauthorized retrieval of BCSI. | 2024-01-01 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000002 | RQ-2021-08-17-0000008 |  | 2. | RP-2021-08-17-0000040 | CIP-011-3 R2.2. | Prior to the disposal of applicable Cyber Assets that contain BCSI, the Responsible Entity shall take action to prevent the unauthorized retrieval of BCSI from the Cyber Asset or destroy the data storage media. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of acceptable evidence may include, but are not limited to, the following: • Records that indicate that data storage media was destroyed prior to the disposal of an applicable Cyber Asset; or • Records of actions taken to prevent unauthorized retrieval of BCSI prior to the disposal of an applicable Cyber Asset. | 2024-01-01 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-17-0000002-NS | RQ-2021-08-17-0000007-NS |  | 1. | RP-2021-08-17-0000037-NS | CIP-011-3 (Nova Scotia) R1.1. | Method(s) to identify BCSI. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of acceptable evidence may include, but are not limited to, the following: • Documented method(s) to identify BCSI from the entity’s information protection program; or • Indications on information (e.g., labels or classification) that identify BCSI as designated in the entity’s information protection program; or • Training materials that provide personnel with sufficient knowledge to identify BCSI; or • Storage locations identified for housing BCSI in the entity’s information protection program. | 2024-04-01 |  |  |  |  | 110000000 | NPCC-NS
ST-2021-08-17-0000002-NS | RQ-2021-08-17-0000007-NS |  | 2. | RP-2021-08-17-0000038-NS | CIP-011-3 (Nova Scotia) R1.2. | Method(s) to protect and securely handle BCSI to mitigate risks of compromising confidentiality. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence for on-premise BCSI may include, but are not limited to, the following: • Procedures for protecting and securely handling, which include topics such as storage, security during transit, and use of BCSI; or • Records indicating that BCSI is handled in a manner consistent with the entity’s documented procedure(s). Examples of evidence for off-premise BCSI may include, but are not limited to, the following: • Implementation of electronic technical method(s) to protect electronic BCSI (e.g., data masking, encryption, hashing, tokenization, cipher, electronic key management); or • Implementation of physical technical method(s) to protect physical BCSI (e.g., physical lock and key management, physical badge management, biometrics, alarm system); or • Implementation of administrative method(s) to protect BCSI (e.g., vendor service risk assessments, business agreements). | 2024-04-01 |  |  |  |  | 120000000 | NPCC-NS
ST-2021-08-17-0000002-NS | RQ-2021-08-17-0000008-NS |  | 1. | RP-2021-08-17-0000039-NS | CIP-011-3 (Nova Scotia) R2.1. | Prior to the release for reuse of applicable Cyber Assets that contain BCSI (except for reuse within other systems identified in the "Applicable Systems" column), the Responsible Entity shall take action to prevent the unauthorized retrieval of BCSI from the Cyber Asset data storage media. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of acceptable evidence may include, but are not limited to, the following: • Records tracking sanitization actions taken to prevent unauthorized retrieval of BCSI such as clearing, purging, or destroying; or • Records tracking actions such as encrypting, retaining in the Physical Security Perimeter or other methods used to prevent unauthorized retrieval of BCSI. | 2024-04-01 |  |  |  |  | 210000000 | NPCC-NS
ST-2021-08-17-0000002-NS | RQ-2021-08-17-0000008-NS |  | 2. | RP-2021-08-17-0000040-NS | CIP-011-3 (Nova Scotia) R2.2. | Prior to the disposal of applicable Cyber Assets that contain BCSI, the Responsible Entity shall take action to prevent the unauthorized retrieval of BCSI from the Cyber Asset or destroy the data storage media. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of acceptable evidence may include, but are not limited to, the following: • Records that indicate that data storage media was destroyed prior to the disposal of an applicable Cyber Asset; or • Records of actions taken to prevent unauthorized retrieval of BCSI prior to the disposal of an applicable Cyber Asset. | 2024-04-01 |  |  |  |  | 220000000 | NPCC-NS
ST-2021-08-23-0000001 | RQ-2021-08-24-0000001 |  | 1. | RP-2021-08-24-0000001 | PRC-006-SERC-03 R2.1. | Have the capability of shedding at least 30 percent of the Peak Demand (MW) served from the Planning Coordinator’s transmission system. The Peak Demand may be either summer or winter as determined by the Planning Coordinator. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | 2022-04-01 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-23-0000001 | RQ-2021-08-24-0000001 |  | 2. | RP-2021-08-24-0000002 | PRC-006-SERC-03 R2.2. | Shed load with a minimum of three frequency set points. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | 2022-04-01 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-23-0000001 | RQ-2021-08-24-0000001 |  | 3. | RP-2021-08-24-0000003 | PRC-006-SERC-03 R2.3. | The highest frequency set point for relays used to arrest frequency decline shall be no lower than 59.3 Hz and not higher than 59.6 Hz. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | 2022-04-01 |  |  |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-23-0000001 | RQ-2021-08-24-0000001 |  | 3.1. | RP-2021-08-24-0000004 | PRC-006-SERC-03 R2.3.1. | This does not apply to UFLS relays with time delay of one second or longer and a higher frequency setpoint applied to prevent the frequency from stalling at less than 60 Hz when recovering from an underfrequency event. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | 2022-04-01 |  |  |  |  | 231000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-23-0000001 | RQ-2021-08-24-0000001 |  | 4. | RP-2021-08-24-0000005 | PRC-006-SERC-03 R2.4. | The lowest frequency set point shall be no lower than 58.2 Hz. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | 2022-04-01 |  |  |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-23-0000001 | RQ-2021-08-24-0000001 |  | 4.1. | RP-2021-08-24-0000006 | PRC-006-SERC-03 R2.4.1. | At least 30% of peak demand shall be set greater than or equal to 58.4 Hz |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | 2022-04-01 |  |  |  |  | 241000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-23-0000001 | RQ-2021-08-24-0000001 |  | 5. | RP-2021-08-24-0000007 | PRC-006-SERC-03 R2.5. | The difference between frequency set points shall be at least 0.2 Hz but no greater than 0.5 Hz. |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | 2022-04-01 |  |  |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-23-0000001 | RQ-2021-08-24-0000001 |  | 6. | RP-2021-08-24-0000008 | PRC-006-SERC-03 R2.6. | Time delay setting shall be at least six cycles (0.1 seconds). |  | DP-UFLS, PCPA |  |  | DP-UFLS | [6 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as reports or other documentation that the UFLS scheme for its area meets the design requirements specified in Requirement R2. | 2022-04-01 |  |  |  |  | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-23-0000001 | RQ-2021-08-24-0000003 |  | 1. | RP-2021-08-24-0000009 | PRC-006-SERC-03 R4.1. | The percent of load shedding to be implemented shall be based on either: A. The actual or estimated substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year’s actual Peak Demand in the season specified by the Planning Coordinator in R2. B. The forecasted substation or feeder demand (including losses) of the UFLS entities at the time coincident with the next year’s forecasted Peak Demand in the season specified by the Planning Coordinator in R2. |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | 2022-04-01 |  |  |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-23-0000001 | RQ-2021-08-24-0000003 |  | 2. | RP-2021-08-24-0000010 | PRC-006-SERC-03 R4.2. | The amount of load in each load shedding step shall be within -1.0 and +3.0 of the percentage specified by the Planning Coordinator (for example, if the specified percentage step load shed is 12%, the allowable range is 11 to 15%). |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | 2022-04-01 |  |  |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-23-0000001 | RQ-2021-08-24-0000003 |  | 3. | RP-2021-08-24-0000011 | PRC-006-SERC-03 R4.3. | The amount of total UFLS load of all steps combined shall be within -1.0 and +5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R4 (including all the data elements in Parts 4.1, 4.2, and 4.3) unless scheme changes per Requirement R6 are in process. | 2022-04-01 |  |  |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-23-0000001 | RQ-2021-08-24-0000004 |  | 1. | RP-2021-08-24-0000012 | PRC-006-SERC-03 R5.1. | The percent of load shedding to be implemented shall be based on either: A. The actual or estimated substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year’s actual Peak Demand in the season specified by the Planning Coordinator in R2. B. The forecasted substation or feeder demand (including losses) of the UFLS entities at the time coincident with the next year’s forecasted Peak Demand in the season specified by the Planning Coordinator in R2. |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  | Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R5 (including all the data elements in Parts 5.1and 5.2) unless scheme changes per Requirement R6 are in process. | 2022-04-01 |  |  |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-23-0000001 | RQ-2021-08-24-0000004 |  | 2. | RP-2021-08-24-0000013 | PRC-006-SERC-03 R5.2. | The amount of total UFLS load shall be within ± 5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. |  | DP, DP-UFLS, TO |  | DP | DP-UFLS | [14 empty] | TO |  |  |  | Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall have evidence such as reports or other documentation demonstrating that its implementation of the UFLS scheme on May 1 of each calendar year meets the requirements of Requirement R5 (including all the data elements in Parts 5.1and 5.2) unless scheme changes per Requirement R6 are in process. | 2022-04-01 |  |  |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-23-0000001 | RQ-2021-08-24-0000006 |  | 1. | RP-2021-08-24-0000014 | PRC-006-SERC-03 R8.1. | Generator protection automatic underfrequency and overfrequency trip set points (Hz). |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [16 empty] | Each Generator Owner shall have evidence such as reports or other documentation that data specified in Requirement R8 was provided to SERC as requested. | 2022-04-01 |  |  |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-23-0000001 | RQ-2021-08-24-0000006 |  | 2. | RP-2021-08-24-0000015 | PRC-006-SERC-03 R8.2. | Total clearing time associated with each set point (sec). This is defined as the time that begins when frequency reaches the set point and ends when the breaker opens. If inverse time underfrequency relays are used, provide the total clearing time at 59.0, 58.5, 58.0, and 57.0 Hz. |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [16 empty] | Each Generator Owner shall have evidence such as reports or other documentation that data specified in Requirement R8 was provided to SERC as requested. | 2022-04-01 |  |  |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2021-08-23-0000001 | RQ-2021-08-24-0000006 |  | 3. | RP-2021-08-24-0000016 | PRC-006-SERC-03 R8.3. | Maximum generator net MW that could be tripped automatically due to an underfrequency or overfrequency condition. |  | DP-UFLS, GO |  |  | DP-UFLS |  | GO | [16 empty] | Each Generator Owner shall have evidence such as reports or other documentation that data specified in Requirement R8 was provided to SERC as requested. | 2022-04-01 |  |  |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000001 |  | 1. | RP-2022-02-16-0000001 | CIP-014-3 R1.1. | Subsequent risk assessments shall be performed: - At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or - At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria in Applicability Section 4.1.1 as specified in Requirement R1. Additionally, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment as specified in Requirement R1, Part 1.2. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000001 |  | 2. | RP-2022-02-16-0000002 | CIP-014-3 R1.2. | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria in Applicability Section 4.1.1 as specified in Requirement R1. Additionally, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment as specified in Requirement R1, Part 1.2. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000002 |  | 1. | RP-2022-02-16-0000003 | CIP-014-3 R2.1. | Each Transmission Owner shall select an unaffiliated verifying entity that is either: - A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or - An entity that has transmission planning or analysis experience. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000002 |  | 2. | RP-2022-02-16-0000004 | CIP-014-3 R2.2. | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000002 |  | 3. | RP-2022-02-16-0000005 | CIP-014-3 R2.3. | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation: - Modify its identification under Requirement R1 consistent with the recommendation; or - Document the technical basis for not modifying the identification in accordance with the recommendation. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000002 |  | 4. | RP-2022-02-16-0000006 | CIP-014-3 R2.4. | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000003 |  | 1. | RP-2022-02-16-0000007 | CIP-014-3 R3.1. | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic notifications or communications that the Transmission Owner notified each Transmission Operator, as applicable, according to Requirement R3. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000004 |  | 1. | RP-2022-02-16-0000008 | CIP-014-3 R4.1. | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000004 |  | 2. | RP-2022-02-16-0000009 | CIP-014-3 R4.2. | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000004 |  | 3. | RP-2022-02-16-0000010 | CIP-014-3 R4.3. | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000005 |  | 1. | RP-2022-02-16-0000011 | CIP-014-3 R5.1. | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000005 |  | 2. | RP-2022-02-16-0000012 | CIP-014-3 R5.2. | Law enforcement contact and coordination information. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000005 |  | 3. | RP-2022-02-16-0000013 | CIP-014-3 R5.3. | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000005 |  | 4. | RP-2022-02-16-0000014 | CIP-014-3 R5.4. | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000006 |  | 1. | RP-2022-02-16-0000015 | CIP-014-3 R6.1. | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following: - An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification. - An entity or organization approved by the ERO. - A governmental agency with physical security expertise. - An entity or organization with demonstrated law enforcement, government, or military physical security expertise. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000006 |  | 2. | RP-2022-02-16-0000016 | CIP-014-3 R6.2. | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000006 |  | 3. | RP-2022-02-16-0000017 | CIP-014-3 R6.3. | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation: - Modify its evaluation or security plan(s) consistent with the recommendation; or - Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001 | RQ-2022-02-16-0000006 |  | 4. | RP-2022-02-16-0000018 | CIP-014-3 R6.4. | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | 2022-06-16 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000001-NS |  | 1. | RP-2022-02-16-0000001-NS | CIP-014-3 (Nova Scotia) R1.1. | Subsequent risk assessments shall be performed: - At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or - At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria in Applicability Section 4.1.1 as specified in Requirement R1. Additionally, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment as specified in Requirement R1, Part 1.2. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 110000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000001-NS |  | 2. | RP-2022-02-16-0000002-NS | CIP-014-3 (Nova Scotia) R1.2. | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the risk assessment of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria in Applicability Section 4.1.1 as specified in Requirement R1. Additionally, examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation of the identification of the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment as specified in Requirement R1, Part 1.2. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 120000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000002-NS |  | 1. | RP-2022-02-16-0000003-NS | CIP-014-3 (Nova Scotia) R2.1. | Each Transmission Owner shall select an unaffiliated verifying entity that is either: - A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or - An entity that has transmission planning or analysis experience. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 210000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000002-NS |  | 2. | RP-2022-02-16-0000004-NS | CIP-014-3 (Nova Scotia) R2.2. | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 220000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000002-NS |  | 3. | RP-2022-02-16-0000005-NS | CIP-014-3 (Nova Scotia) R2.3. | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation: - Modify its identification under Requirement R1 consistent with the recommendation; or - Document the technical basis for not modifying the identification in accordance with the recommendation. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 230000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000002-NS |  | 4. | RP-2022-02-16-0000006-NS | CIP-014-3 (Nova Scotia) R2.4. | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner completed an unaffiliated third party verification of the Requirement R1 risk assessment and satisfied all of the applicable provisions of Requirement R2, including, if applicable, documenting the technical basis for not modifying the Requirement R1 identification as specified under Part 2.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 2.4. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 240000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000003-NS |  | 1. | RP-2022-02-16-0000007-NS | CIP-014-3 (Nova Scotia) R3.1. | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. |  | TO | [17 empty] | TO |  |  |  | Examples of acceptable evidence may include, but are not limited to, dated written or electronic notifications or communications that the Transmission Owner notified each Transmission Operator, as applicable, according to Requirement R3. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 310000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000004-NS |  | 1. | RP-2022-02-16-0000008-NS | CIP-014-3 (Nova Scotia) R4.1. | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 410000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000004-NS |  | 2. | RP-2022-02-16-0000009-NS | CIP-014-3 (Nova Scotia) R4.2. | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 420000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000004-NS |  | 3. | RP-2022-02-16-0000010-NS | CIP-014-3 (Nova Scotia) R4.3. | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation that the Transmission Owner or Transmission Operator conducted an evaluation of the potential threats and vulnerabilities of a physical attack to their respective Transmission station(s), Transmission substation(s) and primary control center(s) as specified in Requirement R4. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 430000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000005-NS |  | 1. | RP-2022-02-16-0000011-NS | CIP-014-3 (Nova Scotia) R5.1. | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 510000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000005-NS |  | 2. | RP-2022-02-16-0000012-NS | CIP-014-3 (Nova Scotia) R5.2. | Law enforcement contact and coordination information. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 520000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000005-NS |  | 3. | RP-2022-02-16-0000013-NS | CIP-014-3 (Nova Scotia) R5.3. | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 530000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000005-NS |  | 4. | RP-2022-02-16-0000014-NS | CIP-014-3 (Nova Scotia) R5.4. | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated written or electronic documentation of its physical security plan(s) that covers their respective identified and verified Transmission station(s), Transmission substation(s), and primary control center(s) as specified in Requirement R5, and additional evidence demonstrating execution of the physical security plan according to the timeline specified in the physical security plan. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 540000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000006-NS |  | 1. | RP-2022-02-16-0000015-NS | CIP-014-3 (Nova Scotia) R6.1. | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following: - An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification. - An entity or organization approved by the ERO. - A governmental agency with physical security expertise. - An entity or organization with demonstrated law enforcement, government, or military physical security expertise. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 610000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000006-NS |  | 2. | RP-2022-02-16-0000016-NS | CIP-014-3 (Nova Scotia) R6.2. | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 620000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000006-NS |  | 3. | RP-2022-02-16-0000017-NS | CIP-014-3 (Nova Scotia) R6.3. | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation: - Modify its evaluation or security plan(s) consistent with the recommendation; or - Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 630000000 | NPCC-NS
ST-2022-02-16-0000001-NS | RQ-2022-02-16-0000006-NS |  | 4. | RP-2022-02-16-0000018-NS | CIP-014-3 (Nova Scotia) R6.4. | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO, TOP | [17 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, written or electronic documentation that the Transmission Owner or Transmission Operator had an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5 as specified in Requirement R6 including, if applicable, documenting the reasons for not modifying the evaluation or security plan(s) in accordance with a recommendation under Part 6.3. Additionally, examples of evidence may include, but are not limited to, written or electronic documentation of procedures to protect information under Part 6.4. | 2023-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria: 4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility. 4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. 4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. 4.1..2 Transmission Operator. | 640000000 | NPCC-NS
ST-2022-05-16-0000001 | RQ-2022-05-16-0000001 |  | 1. | RP-2022-05-16-0000001 | FAC-001-4 R1.1. | generation Facilities; |  | TO | [17 empty] | TO |  |  |  | M1. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | 2024-01-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-05-16-0000001 | RQ-2022-05-16-0000001 |  | 2. | RP-2022-05-16-0000002 | FAC-001-4 R1.2. | transmission Facilities; and |  | TO | [17 empty] | TO |  |  |  | M1.Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | 2024-01-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-05-16-0000001 | RQ-2022-05-16-0000001 |  | 3. | RP-2022-05-16-0000003 | FAC-001-4 R1.3. | end-user Facilities. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | 2024-01-01 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-05-16-0000001 | RQ-2022-05-16-0000004 |  | 1. | RP-2022-05-16-0000004 | FAC-001-4 R3.1. | Procedures for coordinated studies for new interconnections or existing interconnections seeking to make a qualified change as defined by the Planning Coordinator and their impacts on affected systems. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | 2024-01-01 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-05-16-0000001 | RQ-2022-05-16-0000004 |  | 2. | RP-2022-05-16-0000009 | FAC-001-4 R3.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections or existing interconnections seeking to make a qualified change. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | 2024-01-01 |  |  |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-05-16-0000001 | RQ-2022-05-16-0000004 |  | 3. | RP-2022-05-16-0000005 | FAC-001-4 R3.3. | Procedures for confirming with those responsible for the reliability of affected systems that new Facilities or existing Facilities seeking to make a qualified change are within a Balancing Authority Area. |  | TO | [17 empty] | TO |  |  |  | Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R3. | 2024-01-01 |  |  |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-05-16-0000001 | RQ-2022-05-16-0000005 |  | 1. | RP-2022-05-16-0000006 | FAC-001-4 R4.1. | Procedures for coordinated studies of new interconnections and their impacts on affected system(s). |  | GO |  |  |  |  | GO | [16 empty] | Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | 2024-01-01 |  |  |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-05-16-0000001 | RQ-2022-05-16-0000005 |  | 2. | RP-2022-05-16-0000007 | FAC-001-4 R4.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. |  | GO |  |  |  |  | GO | [16 empty] | Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | 2024-01-01 |  |  |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-05-16-0000001 | RQ-2022-05-16-0000005 |  | 3. | RP-2022-05-16-0000008 | FAC-001-4 R4.3. | Procedures for confirming with those responsible for the reliability of affected systems that new Facilities or existing Facilities seeking to make a qualified change as defined by the Planning Coordinator are within a Balancing Authority Area. |  | GO |  |  |  |  | GO | [16 empty] | Each applicable Generator Owner shall have evidence (such as dated, documented Facility interconnection requirements addressing the procedures) that it met all requirements in Requirement R4. | 2024-01-01 |  |  |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-05-16-0000002 | RQ-2022-05-16-0000006 |  | 1.1. | RP-2022-05-16-0000010 | FAC-002-4 R1.1.1. | The reliability impact of the new interconnection, or existing interconnection seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, on affected system(s); |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M1. Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | 2024-01-01 |  |  |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-05-16-0000002 | RQ-2022-05-16-0000006 |  | 1.2. | RP-2022-05-16-0000011 | FAC-002-4 R1.1.2. | Adherence to applicable NERC Reliability Standards; regional and Transmission Owner planning criteria; and Facility interconnection requirements; |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M1. Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | 2024-01-01 |  |  |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-05-16-0000002 | RQ-2022-05-16-0000006 |  | 1.3. | RP-2022-05-16-0000012 | FAC-002-4 R1.1.3. | Steady-state, short-circuit, and dynamics studies, as necessary, to evaluate system performance under both normal and contingency conditions; and |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M1. Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | 2024-01-01 |  |  |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-05-16-0000002 | RQ-2022-05-16-0000006 |  | 1.4. | RP-2022-05-16-0000013 | FAC-002-4 R1.1.4. | Study assumptions, system performance, alternatives considered, and coordinated recommendations. While these studies may be performed independently, the results shall be evaluated and coordinated by the entities involved. |  | PCPA, TP | [9 empty] | PCPA | [9 empty] | TP |  | M1. Each Transmission Planner or each Planning Coordinator shall have evidence (such as study reports, including documentation of reliability issues) that it met all requirements in Requirement R1. | 2024-01-01 |  |  |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 | RP-2022-12-05-0000001 | 1. | RP-2022-12-05-0000002 | CIP-003-9 R1.1.1. | Personnel and training (CIP‐004); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 | RP-2022-12-05-0000001 | 2. | RP-2022-12-05-0000003 | CIP-003-9 R1.1.2. | Electronic Security Perimeters (CIP‐005) including Interactive Remote Access; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 | RP-2022-12-05-0000001 | 3. | RP-2022-12-05-0000004 | CIP-003-9 R1.1.3. | Physical security of BES Cyber Systems (CIP‐006); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 | RP-2022-12-05-0000001 | 4. | RP-2022-12-05-0000005 | CIP-003-9 R1.1.4. | System security management (CIP‐007); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 | RP-2022-12-05-0000001 | 5. | RP-2022-12-05-0000006 | CIP-003-9 R1.1.5. | Incident reporting and response planning (CIP‐008); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 | RP-2022-12-05-0000001 | 7. | RP-2022-12-05-0000007 | CIP-003-9 R1.1.7. | Configuration change management and vulnerability assessments (CIP‐ 010); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  |  | 117000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 | RP-2022-12-05-0000001 | 8. | RP-2022-12-05-0000008 | CIP-003-9 R1.1.8. | Information protection (CIP‐011); and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  |  | 118000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 | RP-2022-12-05-0000001 | 9. | RP-2022-12-05-0000009 | CIP-003-9 R1.1.9. | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  |  | 119000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 | RP-2022-12-05-0000010 | 1. | RP-2022-12-05-0000011 | CIP-003-9 R1.2.1. | Cyber security awareness; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 | RP-2022-12-05-0000010 | 2. | RP-2022-12-05-0000012 | CIP-003-9 R1.2.2. | Physical security controls; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 | RP-2022-12-05-0000010 | 3. | RP-2022-12-05-0000013 | CIP-003-9 R1.2.3. | Electronic access controls; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 | RP-2022-12-05-0000010 | 4. | RP-2022-12-05-0000014 | CIP-003-9 R1.2.4. | Cyber Security Incident response; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  |  | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 | RP-2022-12-05-0000010 | 5. | RP-2022-12-05-0000015 | CIP-003-9 R1.2.5. | Transient Cyber Assets and Removable Media malicious code risk mitigation; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  |  | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 | RP-2022-12-05-0000010 | 6. | RP-2022-12-05-0000016 | CIP-003-9 R1.2.6. | Vendor electronic remote access security controls; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  |  | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 | RP-2022-12-05-0000010 | 7. | RP-2022-12-05-0000017 | CIP-003-9 R1.2.7. | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  |  | 127000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 |  | 1. | RP-2022-12-05-0000001 | CIP-003-9 R1.1. | For its high impact and medium impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-02-0000001 | RQ-2022-12-02-0000001 |  | 2. | RP-2022-12-05-0000010 | CIP-003-9 R1.2. | For its assets identified in CIP‐002 containing low impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, policy documents; revision history, records of review, or workflow evidence from a document management system that indicate review of each cyber security policy at least once every 15 calendar months; and documented approval by the CIP Senior Manager for each cyber security policy. | 2026-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-003-8: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000001 | RP-2022-12-21-0000002 | 1. | RP-2022-12-21-0000003 | EOP-011-3 R1.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | [5 empty] | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000001 | RP-2022-12-21-0000002 | 2. | RP-2022-12-21-0000004 | EOP-011-3 R1.2.2. | Cancellation or recall of Transmission and generation outages; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | [5 empty] | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000001 | RP-2022-12-21-0000002 | 3. | RP-2022-12-21-0000005 | EOP-011-3 R1.2.3. | Transmission system reconfiguration; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | [5 empty] | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000001 | RP-2022-12-21-0000002 | 4. | RP-2022-12-21-0000006 | EOP-011-3 R1.2.4. | Redispatch of generation request; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | [5 empty] | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000001 | RP-2022-12-21-0000002 | 5. | RP-2022-12-21-0000007 | EOP-011-3 R1.2.5. | Operator-controlled manual Load shedding during an Emergency that accounts for each of the following: |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | [5 empty] | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000001 | RP-2022-12-21-0000002 | 6. | RP-2022-12-21-0000012 | EOP-011-3 R1.2.6. | Provisions to determine reliability impacts of: |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | [5 empty] | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000001 | RP-2022-12-21-0000002 | 6.1 | RP-2022-12-21-0000013 | EOP-011-3 R1.2.6.1 | cold weather conditions; and |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | [5 empty] | 1261000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000001 | RP-2022-12-21-0000002 | 6.2. | RP-2022-12-21-0000014 | EOP-011-3 R1.2.6.2. | extreme weather conditions. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | [5 empty] | 1262000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000001 | RP-2022-12-21-0000007 | 1. | RP-2022-12-21-0000008 | EOP-011-3 R1.2.5.1. | Provisions for manual Load shedding capable of being implemented in a timeframe adequate for mitigating the Emergency; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | [5 empty] | 10250100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000001 | RP-2022-12-21-0000007 | 2. | RP-2022-12-21-0000009 | EOP-011-3 R1.2.5.2. | Provisions to minimize the overlap of circuits that are designated for manual Load shed and circuits that serve designated critical loads; |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | [5 empty] | 10250200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000001 | RP-2022-12-21-0000007 | 3. | RP-2022-12-21-0000010 | EOP-011-3 R1.2.5.3. | Provisions to minimize the overlap of circuits that are designated for manual Load shed and circuits that are utilized for underfrequency load shed (UFLS) or undervoltage load shed (UVLS); and |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | [5 empty] | 10250300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000001 | RP-2022-12-21-0000007 | 4. | RP-2022-12-21-0000011 | EOP-011-3 R1.2.5.4. | Provisions for limiting the utilization of UFLS or UVLS circuits for manual Load shed to situations where warranted by system conditions. |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | [5 empty] | 10230400 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000001 |  | 1. | RP-2022-12-21-0000001 | EOP-011-3 R1.1. | Roles and responsibilities for activating the Operating Plan(s); |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | [5 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000001 |  | 2. | RP-2022-12-21-0000002 | EOP-011-3 R1.2. | Processes to prepare for and mitigate Emergencies including: |  | TOP | [18 empty] | TOP |  |  | Each Transmission Operator will have a dated Operating Plan(s) developed in accordance with Requirement R1 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R1. | [5 empty] | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 1. | RP-2022-12-21-0000015 | EOP-011-3 R2.1. | Roles and responsibilities for activating the Operating Plan(s); |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2. | RP-2022-12-21-0000016 | EOP-011-3 R2.2. | Processes to prepare for and mitigate Emergencies including: |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2.1. | RP-2022-12-21-0000017 | EOP-011-3 R2.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; |  | RC | [11 empty] | RC | [9 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2.2. | RP-2022-12-21-0000018 | EOP-011-3 R2.2.2. | Requesting an Energy Emergency Alert, per Attachment 1; |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2.3. | RP-2022-12-21-0000019 | EOP-011-3 R2.2.3. | Managing generating resources in its Balancing Authority Area to address: |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2.3.1. | RP-2022-12-21-0000020 | EOP-011-3 R2.2.3.1. | capability and availability; |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 223100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2.3.2. | RP-2022-12-21-0000021 | EOP-011-3 R2.2.3.2. | fuel supply and inventory concerns; |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 223200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2.3.3. | RP-2022-12-21-0000022 | EOP-011-3 R2.2.3.3. | fuel switching capabilities; and |  | BA, RC | BA | [10 empty] | RC | [9 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 223300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2.3.4. | RP-2022-12-21-0000023 | EOP-011-3 R2.2.3.4. | environmental constraints. |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 223400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2.4. | RP-2022-12-21-0000024 | EOP-011-3 R2.2.4. | Public appeals for voluntary Load reductions; |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 224000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2.5. | RP-2022-12-21-0000025 | EOP-011-3 R2.2.5. | Requests to government agencies to implement their programs to achieve necessary energy reductions; |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 225000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2.6. | RP-2022-12-21-0000026 | EOP-011-3 R2.2.6. | Reduction of internal utility energy use; |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 226000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2.7. | RP-2022-12-21-0000027 | EOP-011-3 R2.2.7. | Use of Interruptible Load, curtailable Load and demand response; |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 227000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2.8. | RP-2022-12-21-0000028 | EOP-011-3 R2.2.8. | Provisions for Transmission Operators to implement operator-controlled manual Load shed in accordance with Requirement R1 Part 1.2.5; and |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 228000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2.9. | RP-2022-12-21-0000029 | EOP-011-3 R2.2.9. | Provisions to determine reliability impacts of: |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 229000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2.9.1. | RP-2022-12-21-0000030 | EOP-011-3 R2.2.9.1. | cold weather conditions; and |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 229100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000002 |  | 2.9.2. | RP-2022-12-21-0000031 | EOP-011-3 R2.2.9.2. | extreme weather conditions. |  | BA | BA | [20 empty] | Each Balancing Authority will have a dated Operating Plan(s) developed in accordance with Requirement R2 and reviewed by its Reliability Coordinator; evidence such as a review or revision history to indicate that the Operating Plan(s) has been maintained; and will have as evidence, such as operator logs or other operating documentation, voice recordings, or other communication documentation to show that its Operating Plan(s) was implemented for times when an Emergency has occurred, in accordance with Requirement R2. | [5 empty] | 229200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000003 | RP-2022-12-21-0000032 | 1. | RP-2022-12-21-0000033 | EOP-011-3 R3.1.1. | Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator will have documentation, such as dated emails or other correspondences that it reviewed, Transmission Operator and Balancing Authority Operating Plans, within 30 calendar days of submittal in accordance with Requirement R3. | [5 empty] | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000003 | RP-2022-12-21-0000032 | 2. | RP-2022-12-21-0000034 | EOP-011-3 R3.1.2. | Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator will have documentation, such as dated emails or other correspondences that it reviewed, Transmission Operator and Balancing Authority Operating Plans, within 30 calendar days of submittal in accordance with Requirement R3. | [5 empty] | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000003 | RP-2022-12-21-0000032 | 3. | RP-2022-12-21-0000035 | EOP-011-3 R3.1.3. | Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator will have documentation, such as dated emails or other correspondences that it reviewed, Transmission Operator and Balancing Authority Operating Plans, within 30 calendar days of submittal in accordance with Requirement R3. | [5 empty] | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000001 | RQ-2022-12-21-0000003 |  | 1. | RP-2022-12-21-0000032 | EOP-011-3 R3.1. | Within 30 calendar days of receipt, the Reliability Coordinator shall: |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator will have documentation, such as dated emails or other correspondences that it reviewed, Transmission Operator and Balancing Authority Operating Plans, within 30 calendar days of submittal in accordance with Requirement R3. | [5 empty] | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000009 | RP-2022-12-21-0000040 | .1 | RP-2022-12-21-0000041 | EOP-012-1 R3.5.1 | Generating unit(s) operating limitations in cold weather to include: |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | 2024-10-01 |  |  |  |  | 351000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000009 | RP-2022-12-21-0000040 | .2 | RP-2022-12-21-0000046 | EOP-012-1 R3.5.2 | Generating unit(s) minimum: - Design temperature; - Historical operating temperature; or - Current cold weather performance temperature determined by an engineering analysis. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | 2024-10-01 |  |  |  |  | 352000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000009 | RP-2022-12-21-0000041 | .1 | RP-2022-12-21-0000042 | EOP-012-1 R3.5.1.1 | Capability and availability; |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | 2024-10-01 |  |  |  |  | 30551100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000009 | RP-2022-12-21-0000041 | .2 | RP-2022-12-21-0000043 | EOP-012-1 R3.5.1.2 | Fuel supply and inventory concerns; |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | 2024-10-01 |  |  |  |  | 30551200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000009 | RP-2022-12-21-0000041 | .3 | RP-2022-12-21-0000044 | EOP-012-1 R3.5.1.3 | Fuel switching capabilities; and |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | 2024-10-01 |  |  |  |  | 30551300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000009 | RP-2022-12-21-0000041 | .4 | RP-2022-12-21-0000045 | EOP-012-1 R3.5.1.4 | Environmental constraints. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | 2024-10-01 |  |  |  |  | 30551400 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000009 |  | 1 | RP-2022-12-21-0000036 | EOP-012-1 R3.1 | The Extreme Cold Weather Temperature for their unit(s) including the calculation date and source of temperature data; |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | 2024-10-01 |  |  |  | 4.2.1 For purposes of this standard, the term “generating unit” subject to these requirements refers to the following Bulk Electric System (BES) resources: 4.2.1.1 A Bulk Electric System generating unit that commits or is obligated to serve a Balancing Authority load pursuant to a tariff obligation, state requirement as defined by the relevant electric regulatory authority, or other contractual arrangement, rule, or regulation, for a continuous run of four hours or more at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius); or 4.2.1.2 A Blackstart Resource 4.2.2 Exemptions: 4.2.2.1 Any Bulk Electric System generating unit included under Section 4.2.1 above that has a calculated Extreme Cold Weather Temperature exceeding 32 degrees Fahrenheit (zero degrees Celsius) under Requirement R3 Part 3.1 and as part of the required five year review in Requirement R4 Part 4.1 is exempt from further requirements in this standard. 4.2.2.2 A Bulk Electric System generating unit that is not committed or obligated to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius) for any continuous run of more than four hours, but is called upon to operate for more than four hours in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius). | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000009 |  | 2 | RP-2022-12-21-0000037 | EOP-012-1 R3.2 | Documentation identifying the Generator Cold Weather Critical Components; |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | 2024-10-01 |  |  |  | 4.2.1 For purposes of this standard, the term “generating unit” subject to these requirements refers to the following Bulk Electric System (BES) resources: 4.2.1.1 A Bulk Electric System generating unit that commits or is obligated to serve a Balancing Authority load pursuant to a tariff obligation, state requirement as defined by the relevant electric regulatory authority, or other contractual arrangement, rule, or regulation, for a continuous run of four hours or more at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius); or 4.2.1.2 A Blackstart Resource 4.2.2 Exemptions: 4.2.2.1 Any Bulk Electric System generating unit included under Section 4.2.1 above that has a calculated Extreme Cold Weather Temperature exceeding 32 degrees Fahrenheit (zero degrees Celsius) under Requirement R3 Part 3.1 and as part of the required five year review in Requirement R4 Part 4.1 is exempt from further requirements in this standard. 4.2.2.2 A Bulk Electric System generating unit that is not committed or obligated to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius) for any continuous run of more than four hours, but is called upon to operate for more than four hours in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius). | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000009 |  | 3 | RP-2022-12-21-0000038 | EOP-012-1 R3.3 | Documentation of freeze protection measures implemented on Generator Cold Weather Critical Components which may include measures used to reduce the cooling effects of wind determined necessary by the Generator Owner to protect against heat loss, and where applicable, the effects of freezing precipitation (e.g., sleet, snow, ice, and freezing rain); |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | 2024-10-01 |  |  |  | 4.2.1 For purposes of this standard, the term “generating unit” subject to these requirements refers to the following Bulk Electric System (BES) resources: 4.2.1.1 A Bulk Electric System generating unit that commits or is obligated to serve a Balancing Authority load pursuant to a tariff obligation, state requirement as defined by the relevant electric regulatory authority, or other contractual arrangement, rule, or regulation, for a continuous run of four hours or more at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius); or 4.2.1.2 A Blackstart Resource 4.2.2 Exemptions: 4.2.2.1 Any Bulk Electric System generating unit included under Section 4.2.1 above that has a calculated Extreme Cold Weather Temperature exceeding 32 degrees Fahrenheit (zero degrees Celsius) under Requirement R3 Part 3.1 and as part of the required five year review in Requirement R4 Part 4.1 is exempt from further requirements in this standard. 4.2.2.2 A Bulk Electric System generating unit that is not committed or obligated to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius) for any continuous run of more than four hours, but is called upon to operate for more than four hours in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius). | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000009 |  | 4 | RP-2022-12-21-0000039 | EOP-012-1 R3.4 | Annual inspection and maintenance of generating unit(s) freeze protection measures; and |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | 2024-10-01 |  |  |  | 4.2.1 For purposes of this standard, the term “generating unit” subject to these requirements refers to the following Bulk Electric System (BES) resources: 4.2.1.1 A Bulk Electric System generating unit that commits or is obligated to serve a Balancing Authority load pursuant to a tariff obligation, state requirement as defined by the relevant electric regulatory authority, or other contractual arrangement, rule, or regulation, for a continuous run of four hours or more at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius); or 4.2.1.2 A Blackstart Resource 4.2.2 Exemptions: 4.2.2.1 Any Bulk Electric System generating unit included under Section 4.2.1 above that has a calculated Extreme Cold Weather Temperature exceeding 32 degrees Fahrenheit (zero degrees Celsius) under Requirement R3 Part 3.1 and as part of the required five year review in Requirement R4 Part 4.1 is exempt from further requirements in this standard. 4.2.2.2 A Bulk Electric System generating unit that is not committed or obligated to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius) for any continuous run of more than four hours, but is called upon to operate for more than four hours in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius). | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000009 |  | 5 | RP-2022-12-21-0000040 | EOP-012-1 R3.5 | Generating unit(s) cold weather data, to include: |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R3. | 2024-10-01 |  |  |  | 4.2.1 For purposes of this standard, the term “generating unit” subject to these requirements refers to the following Bulk Electric System (BES) resources: 4.2.1.1 A Bulk Electric System generating unit that commits or is obligated to serve a Balancing Authority load pursuant to a tariff obligation, state requirement as defined by the relevant electric regulatory authority, or other contractual arrangement, rule, or regulation, for a continuous run of four hours or more at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius); or 4.2.1.2 A Blackstart Resource 4.2.2 Exemptions: 4.2.2.1 Any Bulk Electric System generating unit included under Section 4.2.1 above that has a calculated Extreme Cold Weather Temperature exceeding 32 degrees Fahrenheit (zero degrees Celsius) under Requirement R3 Part 3.1 and as part of the required five year review in Requirement R4 Part 4.1 is exempt from further requirements in this standard. 4.2.2.2 A Bulk Electric System generating unit that is not committed or obligated to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius) for any continuous run of more than four hours, but is called upon to operate for more than four hours in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius). | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000010 |  | 1 | RP-2022-12-21-0000047 | EOP-012-1 R4.1 | Calculate the Extreme Cold Weather Temperature, and update the cold weather preparedness plan if this temperature is now lower than the previous lowest calculation; |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have dated, documented evidence that it reviewed temperature data and updated its cold weather preparedness plan(s) in accordance with Requirement R4. | 2029-10-01 |  |  |  | 4.2.1 For purposes of this standard, the term “generating unit” subject to these requirements refers to the following Bulk Electric System (BES) resources: 4.2.1.1 A Bulk Electric System generating unit that commits or is obligated to serve a Balancing Authority load pursuant to a tariff obligation, state requirement as defined by the relevant electric regulatory authority, or other contractual arrangement, rule, or regulation, for a continuous run of four hours or more at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius); or 4.2.1.2 A Blackstart Resource 4.2.2 Exemptions: 4.2.2.1 Any Bulk Electric System generating unit included under Section 4.2.1 above that has a calculated Extreme Cold Weather Temperature exceeding 32 degrees Fahrenheit (zero degrees Celsius) under Requirement R3 Part 3.1 and as part of the required five year review in Requirement R4 Part 4.1 is exempt from further requirements in this standard. 4.2.2.2 A Bulk Electric System generating unit that is not committed or obligated to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius) for any continuous run of more than four hours, but is called upon to operate for more than four hours in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius). | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000010 |  | 2 | RP-2022-12-21-0000048 | EOP-012-1 R4.2 | Review its documented generating unit(s) minimum temperature contained within its cold weather preparedness plan(s), pursuant to Part 3.5.2; and |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have dated, documented evidence that it reviewed temperature data and updated its cold weather preparedness plan(s) in accordance with Requirement R4. | 2029-10-01 |  |  |  | 4.2.1 For purposes of this standard, the term “generating unit” subject to these requirements refers to the following Bulk Electric System (BES) resources: 4.2.1.1 A Bulk Electric System generating unit that commits or is obligated to serve a Balancing Authority load pursuant to a tariff obligation, state requirement as defined by the relevant electric regulatory authority, or other contractual arrangement, rule, or regulation, for a continuous run of four hours or more at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius); or 4.2.1.2 A Blackstart Resource 4.2.2 Exemptions: 4.2.2.1 Any Bulk Electric System generating unit included under Section 4.2.1 above that has a calculated Extreme Cold Weather Temperature exceeding 32 degrees Fahrenheit (zero degrees Celsius) under Requirement R3 Part 3.1 and as part of the required five year review in Requirement R4 Part 4.1 is exempt from further requirements in this standard. 4.2.2.2 A Bulk Electric System generating unit that is not committed or obligated to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius) for any continuous run of more than four hours, but is called upon to operate for more than four hours in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius). | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000010 |  | 3 | RP-2022-12-21-0000049 | EOP-012-1 R4.3 | Review whether its generating units have the freeze protection measures required to operate at the Extreme Cold Weather Temperature pursuant to R1 or R2 as applicable, and if not develop a CAP for the identified issues, including identification of any needed modifications to the cold weather preparedness plan required under Requirement R3. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have dated, documented evidence that it reviewed temperature data and updated its cold weather preparedness plan(s) in accordance with Requirement R4. | 2029-10-01 |  |  |  | 4.2.1 For purposes of this standard, the term “generating unit” subject to these requirements refers to the following Bulk Electric System (BES) resources: 4.2.1.1 A Bulk Electric System generating unit that commits or is obligated to serve a Balancing Authority load pursuant to a tariff obligation, state requirement as defined by the relevant electric regulatory authority, or other contractual arrangement, rule, or regulation, for a continuous run of four hours or more at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius); or 4.2.1.2 A Blackstart Resource 4.2.2 Exemptions: 4.2.2.1 Any Bulk Electric System generating unit included under Section 4.2.1 above that has a calculated Extreme Cold Weather Temperature exceeding 32 degrees Fahrenheit (zero degrees Celsius) under Requirement R3 Part 3.1 and as part of the required five year review in Requirement R4 Part 4.1 is exempt from further requirements in this standard. 4.2.2.2 A Bulk Electric System generating unit that is not committed or obligated to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius) for any continuous run of more than four hours, but is called upon to operate for more than four hours in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius). | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000012 |  | 1 | RP-2022-12-21-0000050 | EOP-012-1 R6.1 | A summary of the identified cause(s) for the Generator Cold Weather Reliability Event, where applicable, and any relevant associated data; |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have documented evidence that it developed a CAP in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): CAP(s) and updated cold weather preparedness plan(s) where indicated as needed by the CAP. | 2024-10-01 |  |  |  | 4.2.1 For purposes of this standard, the term “generating unit” subject to these requirements refers to the following Bulk Electric System (BES) resources: 4.2.1.1 A Bulk Electric System generating unit that commits or is obligated to serve a Balancing Authority load pursuant to a tariff obligation, state requirement as defined by the relevant electric regulatory authority, or other contractual arrangement, rule, or regulation, for a continuous run of four hours or more at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius); or 4.2.1.2 A Blackstart Resource 4.2.2 Exemptions: 4.2.2.1 Any Bulk Electric System generating unit included under Section 4.2.1 above that has a calculated Extreme Cold Weather Temperature exceeding 32 degrees Fahrenheit (zero degrees Celsius) under Requirement R3 Part 3.1 and as part of the required five year review in Requirement R4 Part 4.1 is exempt from further requirements in this standard. 4.2.2.2 A Bulk Electric System generating unit that is not committed or obligated to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius) for any continuous run of more than four hours, but is called upon to operate for more than four hours in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius). | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000012 |  | 2 | RP-2022-12-21-0000051 | EOP-012-1 R6.2 | A review of applicability to similar equipment at other generating units owned by the Generator Owner; |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have documented evidence that it developed a CAP in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): CAP(s) and updated cold weather preparedness plan(s) where indicated as needed by the CAP. | 2024-10-01 |  |  |  | 4.2.1 For purposes of this standard, the term “generating unit” subject to these requirements refers to the following Bulk Electric System (BES) resources: 4.2.1.1 A Bulk Electric System generating unit that commits or is obligated to serve a Balancing Authority load pursuant to a tariff obligation, state requirement as defined by the relevant electric regulatory authority, or other contractual arrangement, rule, or regulation, for a continuous run of four hours or more at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius); or 4.2.1.2 A Blackstart Resource 4.2.2 Exemptions: 4.2.2.1 Any Bulk Electric System generating unit included under Section 4.2.1 above that has a calculated Extreme Cold Weather Temperature exceeding 32 degrees Fahrenheit (zero degrees Celsius) under Requirement R3 Part 3.1 and as part of the required five year review in Requirement R4 Part 4.1 is exempt from further requirements in this standard. 4.2.2.2 A Bulk Electric System generating unit that is not committed or obligated to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius) for any continuous run of more than four hours, but is called upon to operate for more than four hours in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius). | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000012 |  | 3 | RP-2022-12-21-0000052 | EOP-012-1 R6.3 | An identification of any temporary operating limitations or impacts to the cold weather preparedness plan, that would apply until execution of the corrective action(s) identified in the CAP. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner will have documented evidence that it developed a CAP in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): CAP(s) and updated cold weather preparedness plan(s) where indicated as needed by the CAP. | 2024-10-01 |  |  |  | 4.2.1 For purposes of this standard, the term “generating unit” subject to these requirements refers to the following Bulk Electric System (BES) resources: 4.2.1.1 A Bulk Electric System generating unit that commits or is obligated to serve a Balancing Authority load pursuant to a tariff obligation, state requirement as defined by the relevant electric regulatory authority, or other contractual arrangement, rule, or regulation, for a continuous run of four hours or more at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius); or 4.2.1.2 A Blackstart Resource 4.2.2 Exemptions: 4.2.2.1 Any Bulk Electric System generating unit included under Section 4.2.1 above that has a calculated Extreme Cold Weather Temperature exceeding 32 degrees Fahrenheit (zero degrees Celsius) under Requirement R3 Part 3.1 and as part of the required five year review in Requirement R4 Part 4.1 is exempt from further requirements in this standard. 4.2.2.2 A Bulk Electric System generating unit that is not committed or obligated to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius) for any continuous run of more than four hours, but is called upon to operate for more than four hours in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius). | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000013 |  | 1 | RP-2022-12-21-0000053 | EOP-012-1 R7.1 | Implement each CAP developed pursuant to Requirements R2, R4, or R6, or explain in a declaration why corrective actions are not being implemented due to any technical, commercial, or operational constraints as defined by the Generator Owner. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables, or has explained in a declaration why corrective actions are not being implemented in accordance with Requirement R7. Acceptable evidence may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. Any declaration shall contain dated documentation to support constraints identified by the Generator Owner. | 2024-10-01 |  |  |  | 4.2.1 For purposes of this standard, the term “generating unit” subject to these requirements refers to the following Bulk Electric System (BES) resources: 4.2.1.1 A Bulk Electric System generating unit that commits or is obligated to serve a Balancing Authority load pursuant to a tariff obligation, state requirement as defined by the relevant electric regulatory authority, or other contractual arrangement, rule, or regulation, for a continuous run of four hours or more at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius); or 4.2.1.2 A Blackstart Resource 4.2.2 Exemptions: 4.2.2.1 Any Bulk Electric System generating unit included under Section 4.2.1 above that has a calculated Extreme Cold Weather Temperature exceeding 32 degrees Fahrenheit (zero degrees Celsius) under Requirement R3 Part 3.1 and as part of the required five year review in Requirement R4 Part 4.1 is exempt from further requirements in this standard. 4.2.2.2 A Bulk Electric System generating unit that is not committed or obligated to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius) for any continuous run of more than four hours, but is called upon to operate for more than four hours in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius). | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2022-12-21-0000002 | RQ-2022-12-21-0000013 |  | 2 | RP-2022-12-21-0000054 | EOP-012-1 R7.2 | Update each CAP if actions or timetables change, until completed. |  | GO |  |  |  |  | GO | [16 empty] | Each Generator Owner shall have dated evidence that demonstrates it implemented each CAP, including updating actions or timetables, or has explained in a declaration why corrective actions are not being implemented in accordance with Requirement R7. Acceptable evidence may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the implementation of each CAP and the completion of actions for each CAP including revision history of each CAP. Evidence may also include work management program records, work orders, and maintenance records. Any declaration shall contain dated documentation to support constraints identified by the Generator Owner. | 2024-10-01 |  |  |  | 4.2.1 For purposes of this standard, the term “generating unit” subject to these requirements refers to the following Bulk Electric System (BES) resources: 4.2.1.1 A Bulk Electric System generating unit that commits or is obligated to serve a Balancing Authority load pursuant to a tariff obligation, state requirement as defined by the relevant electric regulatory authority, or other contractual arrangement, rule, or regulation, for a continuous run of four hours or more at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius); or 4.2.1.2 A Blackstart Resource 4.2.2 Exemptions: 4.2.2.1 Any Bulk Electric System generating unit included under Section 4.2.1 above that has a calculated Extreme Cold Weather Temperature exceeding 32 degrees Fahrenheit (zero degrees Celsius) under Requirement R3 Part 3.1 and as part of the required five year review in Requirement R4 Part 4.1 is exempt from further requirements in this standard. 4.2.2.2 A Bulk Electric System generating unit that is not committed or obligated to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius) for any continuous run of more than four hours, but is called upon to operate for more than four hours in order to assist in the mitigation of BES Emergencies, Capacity Emergencies, or Energy Emergencies during periods at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius). | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000001 | RQ-2023-02-22-0000006 |  | 1. | RP-2023-02-22-0000001 | PRC-023-6 R6.1. | Maintain a list of circuits subject to PRC-023-6 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023- 6, Attachment B applies. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-6, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | 2024-04-01 |  |  |  | 4.1. Functional Entity: 4.1.1 Transmission Owner with load-responsive phase protection systems as describedin PRC-023-6 - Attachment A, applied at the terminals of the circuits defined in 4.2.1 (Circuits Subject to Requirements R1 – R5). 4.1.2 Generator Owner with load-responsive phase protection systems as described in PRC-023-6 - Attachment A, applied at the terminals of the circuits defined in 4.2.1 (Circuits Subject to Requirements R1 – R5). 4.1.3 Distribution Provider with load-responsive phase protection systems as described in PRC-023-6 - Attachment A, applied at the terminals of the circuits defined in 4.2.1 (Circuits Subject to Requirements R1 – R5), provided those circuits have bi- directional flow capabilities. 4.1.4 Planning Coordinator 4.2. Circuits: 4.2.1 Circuits Subject to Requirements R1 – R5: 4.2.1.1 Transmission lines operated at 200 kV and above, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plantloads. 4.2.1.2 Transmission lines operated at 100 kV to 200 kV selected by the Planning Coordinator in accordance with Requirement R6. 4.2.1.3 Transmission lines operated below 100 kV that are part of the BES and selected by the Planning Coordinator in accordance with RequirementR6. 4.2.1.4 Transformers with low voltage terminals connected at 200 kV and above. 4.2.1.5 Transformers with low voltage terminals connected at 100 kV to 200 kV selected by the Planning Coordinator in accordance with RequirementR6. 4.2.1.6 Transformers with low voltage terminals connected below 100 kV PRC-023-6 – Transmission Relay Loadability Page 4 of 18 that are part of the BES and selected by the Planning Coordinator in accordancewith Requirement R6. 4.2.2 Circuits Subject to Requirement R6: 4.2.2.1 Transmission lines operated at 100 kV to 200 kV and transformers withlow voltage terminals connected at 100 kV to 200 kV, except Elements that connect the GSU transformer(s) to the Transmission system that areused exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. 4.2.2.2 Transmission lines operated below 100 kV and transformers with low voltage terminals connected below 100 kV that are part of the BES,except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000001 | RQ-2023-02-22-0000006 |  | 2. | RP-2023-02-22-0000002 | PRC-023-6 R6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. |  | PCPA | [9 empty] | PCPA | [11 empty] | Each Planning Coordinator shall have evidence such as power flow results, calculation summaries, or study reports that it used the criteria established within PRC-023-6, Attachment B to determine the circuits in its Planning Coordinator area for which applicable entities must comply with the standard as described in Requirement R6. The Planning Coordinator shall have a dated list of such circuits and shall have evidence such as dated correspondence that it provided the list to the Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within the required timeframe. (R6) | 2024-04-01 |  |  |  | 4.1. Functional Entity: 4.1.1 Transmission Owner with load-responsive phase protection systems as describedin PRC-023-6 - Attachment A, applied at the terminals of the circuits defined in 4.2.1 (Circuits Subject to Requirements R1 – R5). 4.1.2 Generator Owner with load-responsive phase protection systems as described in PRC-023-6 - Attachment A, applied at the terminals of the circuits defined in 4.2.1 (Circuits Subject to Requirements R1 – R5). 4.1.3 Distribution Provider with load-responsive phase protection systems as described in PRC-023-6 - Attachment A, applied at the terminals of the circuits defined in 4.2.1 (Circuits Subject to Requirements R1 – R5), provided those circuits have bi- directional flow capabilities. 4.1.4 Planning Coordinator 4.2. Circuits: 4.2.1 Circuits Subject to Requirements R1 – R5: 4.2.1.1 Transmission lines operated at 200 kV and above, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plantloads. 4.2.1.2 Transmission lines operated at 100 kV to 200 kV selected by the Planning Coordinator in accordance with Requirement R6. 4.2.1.3 Transmission lines operated below 100 kV that are part of the BES and selected by the Planning Coordinator in accordance with RequirementR6. 4.2.1.4 Transformers with low voltage terminals connected at 200 kV and above. 4.2.1.5 Transformers with low voltage terminals connected at 100 kV to 200 kV selected by the Planning Coordinator in accordance with RequirementR6. 4.2.1.6 Transformers with low voltage terminals connected below 100 kV PRC-023-6 – Transmission Relay Loadability Page 4 of 18 that are part of the BES and selected by the Planning Coordinator in accordancewith Requirement R6. 4.2.2 Circuits Subject to Requirement R6: 4.2.2.1 Transmission lines operated at 100 kV to 200 kV and transformers withlow voltage terminals connected at 100 kV to 200 kV, except Elements that connect the GSU transformer(s) to the Transmission system that areused exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. 4.2.2.2 Transmission lines operated below 100 kV and transformers with low voltage terminals connected below 100 kV that are part of the BES,except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000014 |  | 1. | RP-2023-02-22-0000003 | PRC-002-4 R1.1. | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-4, Attachment 1. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner for Requirement R1, Part 1.1 has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-4, Attachment 1; has dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1, Part 1.2; and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1, Part 1.3. | 2024-04-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000014 |  | 2. | RP-2023-02-22-0000004 | PRC-002-4 R1.2. | Notify the other owners of BES Elements directly connected1 to those BES buses, that SER or FR data is required for those BES Elements, only if the Transmission Owner who identified the BES buses in Part 1.1 does not have SER or FR data. This notification is required within 90 calendar days of completion of Part 1.1. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner for Requirement R1, Part 1.1 has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-4, Attachment 1; has dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1, Part 1.2; and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1, Part 1.3. | 2024-04-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000014 |  | 3. | RP-2023-02-22-0000005 | PRC-002-4 R1.3. | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners in accordance with Part 1.2. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner for Requirement R1, Part 1.1 has a dated (electronic or hard copy) list of BES buses for which SER and FR data is required, identified in accordance with PRC-002-4, Attachment 1; has dated (electronic or hard copy) evidence that it notified other owners in accordance with Requirement R1, Part 1.2; and evidence that all BES buses have been re-evaluated within the required intervals under Requirement R1, Part 1.3. | 2024-04-01 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000016 | RP-2023-02-22-0000007 | 1. | RP-2023-02-22-0000032 | PRC-002-4 R3.2.1. | Transformers that have a low-side operating voltage of 100 kV or above. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000016 | RP-2023-02-22-0000007 | 2. | RP-2023-02-22-0000033 | PRC-002-4 R3.2.2. | Transmission Lines. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000016 |  | 1. | RP-2023-02-22-0000006 | PRC-002-4 R3.1. | Phase-to-neutral voltage for each phase of each specified BES bus. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings | 2024-04-01 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000016 |  | 2. | RP-2023-02-22-0000007 | PRC-002-4 R3.2. | Each phase current and the residual or neutral current for the following BES Elements: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of FR data that is sufficient to determine electrical quantities as specified in Requirement R3. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-04-01 |  |  |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000017 | RP-2023-02-22-0000010 | 1. | RP-2023-02-22-0000034 | PRC-002-4 R4.3.1. | Neutral (residual) overcurrent. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 431000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000017 | RP-2023-02-22-0000010 | 2. | RP-2023-02-22-0000035 | PRC-002-4 R4.3.2. | Phase undervoltage or overcurrent |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 432000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000017 |  | 1. | RP-2023-02-22-0000008 | PRC-002-4 R4.1. | A single record or multiple records that include: • A pre-trigger record length of at least two cycles and a total record length of at least 30 cycles for the same trigger point, or • At least two cycles of the pre-trigger data, the first three cycles of the posttrigger data, and the final cycle of the fault as seen by the fault recorder. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | 2024-04-01 |  |  |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000017 |  | 2. | RP-2023-02-22-0000009 | PRC-002-4 R4.2. | A minimum recording rate of 16 samples per cycle. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | 2024-04-01 |  |  |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000017 |  | 3. | RP-2023-02-22-0000010 | PRC-002-4 R4.3. | Trigger settings for at least the following: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that FR data meets Requirement R4. Evidence may include, but is not limited to: (1) documents describing the device specification (R4, Part 4.2) and device configuration or settings (R4, Parts 4.1 and 4.3), or (2) actual data recordings or derivations. | 2024-04-01 |  |  |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000018 | RP-2023-02-22-0000011 | 1. | RP-2023-02-22-0000036 | PRC-002-4 R5.1.1. | Generating resource(s) with: |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 511000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000018 | RP-2023-02-22-0000011 | 2. | RP-2023-02-22-0000041 | PRC-002-4 R5.1.2. | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-04-01 |  |  |  |  | 512000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000018 | RP-2023-02-22-0000011 | 3. | RP-2023-02-22-0000042 | PRC-002-4 R5.1.3. | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-04-01 |  |  |  |  | 513000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000018 | RP-2023-02-22-0000011 | 4. | RP-2023-02-22-0000043 | PRC-002-4 R5.1.4. | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-04-01 |  |  |  |  | 514000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000018 | RP-2023-02-22-0000011 | 5. | RP-2023-02-22-0000044 | PRC-002-4 R5.1.5. | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-04-01 |  |  |  |  | 515000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000018 | RP-2023-02-22-0000012 | 1. | RP-2023-02-22-0000039 | PRC-002-4 R5.2.1. | One BES Element; and |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 521000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000018 | RP-2023-02-22-0000012 | 2. | RP-2023-02-22-0000040 | PRC-002-4 R5.2.2. | One BES Element per 3,000 MW of the Reliability Coordinator’s historical simultaneous peak System Demand. |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 522000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000018 | RP-2023-02-22-0000036 | 1. | RP-2023-02-22-0000037 | PRC-002-4 R5.1.1.1. | Gross individual nameplate rating greater than or equal to 500 MVA. |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 50101100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000018 | RP-2023-02-22-0000036 | 2. | RP-2023-02-22-0000038 | PRC-002-4 R5.1.1.2. | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 50101200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000018 |  | 1. | RP-2023-02-22-0000011 | PRC-002-4 R5.1. | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-04-01 |  |  |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000018 |  | 2. | RP-2023-02-22-0000012 | PRC-002-4 R5.2. | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-04-01 |  |  |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000018 |  | 3. | RP-2023-02-22-0000013 | PRC-002-4 R5.3. | Notify all owners of identified BES Elements, within 90 calendar days of completion of Part 5.1, that their respective BES Elements require DDR data. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-04-01 |  |  |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000018 |  | 4. | RP-2023-02-22-0000014 | PRC-002-4 R5.4. | Re-evaluate all BES Elements within its Reliability Coordinator Area at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3. |  | RC | [11 empty] | RC | [9 empty] | The Reliability Coordinator has a dated (electronic or hard copy) list of BES Elements for which DDR data is required, developed in accordance with Requirement R5, Part 5.1 and Part 5.2; and re-evaluated in accordance with Part 5.4. The Reliability Coordinator has dated evidence (electronic or hard copy) that each Transmission Owner or Generator Owner has been notified in accordance with Requirement 5, Part 5.3. Evidence may include, but is not limited to: letters, emails, electronic files, or hard copy records demonstrating transmittal of information. | 2024-04-01 |  |  |  |  | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000019 |  | 1. | RP-2023-02-22-0000015 | PRC-002-4 R6.1. | One phase-to-neutral or positive sequence voltage. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-04-01 |  |  |  |  | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000019 |  | 2. | RP-2023-02-22-0000016 | PRC-002-4 R6.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-04-01 |  |  |  |  | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000019 |  | 3. | RP-2023-02-22-0000017 | PRC-002-4 R6.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-04-01 |  |  |  |  | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000019 |  | 4. | RP-2023-02-22-0000018 | PRC-002-4 R6.4. | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. |  | TO | [17 empty] | TO |  |  |  | The Transmission Owner has evidence (electronic or hard copy) of DDR data to determine electrical quantities as specified in Requirement R6. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings or derivations; or (3) station drawings. | 2024-04-01 |  |  |  |  | 640000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000020 |  | 1. | RP-2024-04-29-0000001 | PRC-002-4 R7.1. | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. |  | GO |  |  |  |  | GO | [17 empty] | 2024-04-01 |  |  |  |  | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000020 |  | 2. | RP-2024-04-29-0000002 | PRC-002-4 R7.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. |  | GO |  |  |  |  | GO | [17 empty] | 2024-04-01 |  |  |  |  | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000020 |  | 3. | RP-2024-04-29-0000003 | PRC-002-4 R7.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | GO |  |  |  |  | GO | [17 empty] | 2024-04-01 |  |  |  |  | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000020 |  | 4. | RP-2024-04-29-0000004 | PRC-002-4 R7.4. | Frequency of at least one of the voltages in Requirement R7, Part 7.1. |  | GO |  |  |  |  | GO | [17 empty] | 2024-04-01 |  |  |  |  | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000021 |  | 1. | RP-2023-02-22-0000019 | PRC-002-4 R8.1. | Triggered record lengths of at least three minutes. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | 2024-04-01 |  |  |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000021 |  | 2. | RP-2023-02-22-0000020 | PRC-002-4 R8.2. | At least one of the following three triggers: Off nominal frequency trigger set at: Low High o Eastern Interconnection <59.75 Hz >61.0 Hz o Western Interconnection <59.55 Hz >61.0 Hz o ERCOT Interconnection <59.35 Hz >61.0 Hz o Hydro-Quebec Interconnection <58.55 Hz >61.5 Hz • Rate of change of frequency trigger set at: o Eastern Interconnection < -0.03125 Hz/sec >0.125 Hz/sec o Western Interconnection < -0.05625 Hz/sec >0.125 Hz/sec o ERCOT Interconnection < -0.08125 Hz/sec >0.125 Hz/sec o Hydro-Quebec Interconnection < -0.18125 Hz/sec >0.1875 Hz/sec • Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | Each Transmission Owner and Generator Owner has dated evidence (electronic or hard copy) of data recordings and storage in accordance with Requirement R8. Evidence may include, but is not limited to: (1) documents describing the device specifications and configurations, which may include a single design standard as representative for common installations; or (2) actual data recordings. | 2024-04-01 |  |  |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000022 |  | 1. | RP-2023-02-22-0000021 | PRC-002-4 R9.1. | Input sampling rate of at least 960 samples per second. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | 2024-04-01 |  |  |  |  | 910000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000022 |  | 2. | RP-2023-02-22-0000022 | PRC-002-4 R9.2. | Output recording rate of electrical quantities of at least 30 times per second. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that DDR data meets Requirement R9. Evidence may include, but is not limited to: (1) documents describing the device specification, device configuration, or settings (R9, Part 9.1; R9, Part 9.2); or (2) actual data recordings (R9, Part 9.2). | 2024-04-01 |  |  |  |  | 920000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000023 |  | 1. | RP-2023-02-22-0000023 | PRC-002-4 R10.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings | 2024-04-01 |  |  |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000023 |  | 2. | RP-2023-02-22-0000024 | PRC-002-4 R10.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) of time synchronization described in Requirement R10. Evidence may include, but is not limited to: (1) documents describing the device specification, configuration, or setting; (2) time synchronization indication or status; or 3) station drawings. | 2024-04-01 |  |  |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000024 |  | 1. | RP-2023-02-22-0000025 | PRC-002-4 R11.1. | Data will be retrievable for the period of 10 calendar days, inclusive of the day the data was recorded. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | 2024-04-01 |  |  |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000024 |  | 2. | RP-2023-02-22-0000026 | PRC-002-4 R11.2. | Data subject to Part 11.1 will be provided within |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | 2024-04-01 |  |  |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000024 |  | 3. | RP-2023-02-22-0000027 | PRC-002-4 R11.3. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, | 2024-04-01 |  |  |  |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000024 |  | 4. | RP-2023-02-22-0000028 | PRC-002-4 R11.4. | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings. | 2024-04-01 |  |  |  |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000024 |  | 5. | RP-2023-02-22-0000029 | PRC-002-4 R11.5. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has evidence (electronic or hard copy) that data was submitted upon request in accordance with Requirement R11. Evidence may include, but is not limited to: (1) dated transmittals to the requesting entity with formatted records; (2) documents describing data storage capability, device specification, configuration or settings; or (3) actual data recordings | 2024-04-01 |  |  |  |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000026 |  | 1. | RP-2023-02-22-0000030 | PRC-002-4 R13.1. | Within three (3) calendar years of completing a re-evaluation or receiving notification under Requirement R1, Part 1.3, have SER or FR data as applicable for BES Elements directly connected to the identified BES buses. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R13. Evidence may include, but is not limited to: letters, emails, drawings, or settings files. | 2024-04-01 |  |  |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-02-22-0000002 | RQ-2023-02-22-0000026 |  | 2. | RP-2023-02-22-0000031 | PRC-002-4 R13.2. | Within three (3) calendar years of receiving notification under Requirement R5, Part 5.4, have DDR data for BES Elements identified during the re-evaluation. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  | The Transmission Owner or Generator Owner has dated evidence (electronic or hard copy) that meets Requirement R13. Evidence may include, but is not limited to: letters, emails, drawings, or settings files. | 2024-04-01 |  |  |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-11-0000001 | RQ-2023-08-11-0000001 |  | 1. | RP-2023-08-21-0000001 | PRC-002-4 (Saskatchewan) R1.1. | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-4, Attachment 1. |  | TO | [17 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 110000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000001 |  | 2. | RP-2023-08-21-0000002 | PRC-002-4 (Saskatchewan) R1.2. | Notify the other owners of BES Elements directly connected1 to those BES buses, that SER or FR data is required for those BES Elements, only if the Transmission Owner who identified the BES buses in Part 1.1 does not have SER or FR data. This notification is required within 90 calendar days of completion of Part 1.1. |  | TO | [17 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 120000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000001 |  | 3. | RP-2023-08-21-0000003 | PRC-002-4 (Saskatchewan) R1.3. | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners in accordance with Part 1.2. |  | TO | [17 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 130000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000003 | RP-2023-08-21-0000005 | 1. | RP-2023-08-21-0000006 | PRC-002-4 (Saskatchewan) R3.2.1. | Transformers that have a low-side operating voltage of 100 kV or above. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 321000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000003 | RP-2023-08-21-0000005 | 2. | RP-2023-08-21-0000007 | PRC-002-4 (Saskatchewan) R3.2.2. | Transmission Lines. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 322000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000003 |  | 1. | RP-2023-08-21-0000004 | PRC-002-4 (Saskatchewan) R3.1. | Phase-to-neutral voltage for each phase of each specified BES bus. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 310000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000003 |  | 2. | RP-2023-08-21-0000005 | PRC-002-4 (Saskatchewan) R3.2. | Each phase current and the residual or neutral current for the following BES Elements: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 320000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000004 | RP-2023-08-21-0000010 | 1. | RP-2023-08-21-0000011 | PRC-002-4 (Saskatchewan) R4.3.1. | Neutral (residual) overcurrent. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 431000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000004 | RP-2023-08-21-0000010 | 2. | RP-2023-08-21-0000012 | PRC-002-4 (Saskatchewan) R4.3.2. | Phase undervoltage or overcurrent. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 432000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000004 |  | 1. | RP-2023-08-21-0000008 | PRC-002-4 (Saskatchewan) R4.1. | A single record or multiple records that include: - A pre-trigger record length of at least two cycles and a total record length of at least 30 cycles for the same trigger point, or - At least two cycles of the pre-trigger data, the first three cycles of the post- trigger data, and the final cycle of the fault as seen by the fault recorder. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 410000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000004 |  | 2. | RP-2023-08-21-0000009 | PRC-002-4 (Saskatchewan) R4.2. | A minimum recording rate of 16 samples per cycle. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 420000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000004 |  | 3. | RP-2023-08-21-0000010 | PRC-002-4 (Saskatchewan) R4.3. | Trigger settings for at least the following: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 430000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000005 | RP-2023-08-21-0000013 | 1. | RP-2023-08-21-0000014 | PRC-002-4 (Saskatchewan) R5.1.1. | Generating resource(s) with: |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 511000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000005 | RP-2023-08-21-0000013 | 2. | RP-2023-08-21-0000017 | PRC-002-4 (Saskatchewan) R5.1.2. | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 512000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000005 | RP-2023-08-21-0000013 | 3. | RP-2023-08-21-0000018 | PRC-002-4 (Saskatchewan) R5.1.3. | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter. |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 513000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000005 | RP-2023-08-21-0000013 | 4. | RP-2023-08-21-0000019 | PRC-002-4 (Saskatchewan) R5.1.4. | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 514000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000005 | RP-2023-08-21-0000013 | 5. | RP-2023-08-21-0000020 | PRC-002-4 (Saskatchewan) R5.1.5. | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 515000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000005 | RP-2023-08-21-0000014 | 1. | RP-2023-08-21-0000015 | PRC-002-4 (Saskatchewan) R5.1.1.1. | Gross individual nameplate rating greater than or equal to 500 MVA. |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 50101100 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000005 | RP-2023-08-21-0000014 | 2. | RP-2023-08-21-0000016 | PRC-002-4 (Saskatchewan) R5.1.1.2. | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 50101200 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000005 | RP-2023-08-21-0000021 | 1. | RP-2023-08-21-0000022 | PRC-002-4 (Saskatchewan) R5.2.1. | One BES Element; and |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 521000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000005 | RP-2023-08-21-0000021 | 2. | RP-2023-08-21-0000023 | PRC-002-4 (Saskatchewan) R5.2.2. | One BES Element per 3,000 MW of the Reliability Coordinator’s historical simultaneous peak System Demand. |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 522000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000005 |  | 1. | RP-2023-08-21-0000013 | PRC-002-4 (Saskatchewan) R5.1. | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [5 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 510000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000005 |  | 2. | RP-2023-08-21-0000021 | PRC-002-4 (Saskatchewan) R5.2. | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 520000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000005 |  | 3. | RP-2023-08-21-0000024 | PRC-002-4 (Saskatchewan) R5.3. | Notify all owners of identified BES Elements, within 90 calendar days of completion of Part 5.1, that their respective BES Elements require DDR data. |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 530000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000005 |  | 4. | RP-2023-08-21-0000025 | PRC-002-4 (Saskatchewan) R5.4. | Re-evaluate all BES Elements within its Reliability Coordinator Area at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3. |  | RC | [11 empty] | RC | [10 empty] | 2024-04-01 |  |  |  |  | 540000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000006 |  | 1. | RP-2023-08-21-0000026 | PRC-002-4 (Saskatchewan) R6.1. | One phase-to-neutral or positive sequence voltage. |  | TO | [17 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 610000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000006 |  | 2. | RP-2023-08-21-0000027 | PRC-002-4 (Saskatchewan) R6.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. |  | TO | [17 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 620000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000006 |  | 3. | RP-2023-08-21-0000028 | PRC-002-4 (Saskatchewan) R6.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | TO | [17 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 630000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000006 |  | 4. | RP-2023-08-21-0000029 | PRC-002-4 (Saskatchewan) R6.4. | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. |  | TO | [17 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 640000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000007 |  | 1. | RP-2023-08-21-0000030 | PRC-002-4 (Saskatchewan) R7.1. | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. |  | GO |  |  |  |  | GO | [17 empty] | 2024-04-01 |  |  |  |  | 710000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000007 |  | 2. | RP-2023-08-21-0000031 | PRC-002-4 (Saskatchewan) R7.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. |  | GO |  |  |  |  | GO | [17 empty] | 2024-04-01 |  |  |  |  | 720000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000007 |  | 3. | RP-2023-08-21-0000032 | PRC-002-4 (Saskatchewan) R7.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | GO |  |  |  |  | GO | [17 empty] | 2024-04-01 |  |  |  |  | 730000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000007 |  | 4. | RP-2023-08-21-0000033 | PRC-002-4 (Saskatchewan) R7.4. | Frequency of at least one of the voltages in Requirement R7, Part 7.1. |  | GO |  |  |  |  | GO | [17 empty] | 2024-04-01 |  |  |  |  | 740000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000008 |  | 1. | RP-2023-08-21-0000034 | PRC-002-4 (Saskatchewan) R8.1. | Triggered record lengths of at least three minutes. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 810000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000008 |  | 2. | RP-2023-08-21-0000035 | PRC-002-4 (Saskatchewan) R8.2. | At least one of the following three triggers: - Off nominal frequency trigger set at: o Eastern Interconnection -<59.75 Hz >61.0 Hz o Western Interconnection-<59.75 Hz >61.0 Hz o ERCOT Interconnection -<59.75 Hz >61.0 Hz o Hydro-Quebec Interconnection-<59.75 Hz - Rate of change of frequency trigger set at: o Eastern Interconnection - < -0.03125 Hz/sec >0.125 Hz/sec o Western Interconnection - < -0.03125 Hz/sec >0.125 Hz/sec o ERCOT Interconnection - < -0.03125 Hz/sec >0.125 Hz/sec o Hydro-Quebec Interconnection - < -0.03125 Hz/sec >0.125 Hz/sec - Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. |  | GO |  |  |  |  | GO | [17 empty] | 2024-04-01 |  |  |  |  | 820000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000009 |  | 1. | RP-2023-08-21-0000036 | PRC-002-4 (Saskatchewan) R9.1. | Input sampling rate of at least 960 samples per second. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 910000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000009 |  | 2. | RP-2023-08-21-0000037 | PRC-002-4 (Saskatchewan) R9.2. | Output recording rate of electrical quantities of at least 30 times per second. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 920000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000010 |  | 1. | RP-2023-08-21-0000038 | PRC-002-4 (Saskatchewan) R10.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 101000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000010 |  | 2. | RP-2023-08-21-0000039 | PRC-002-4 (Saskatchewan) R10.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 102000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000011 |  | 1. | RP-2023-08-21-0000040 | PRC-002-4 (Saskatchewan) R11.1. | Data will be retrievable for the period of 10 calendar days, inclusive of the day the data was recorded. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 111000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000011 |  | 2. | RP-2023-08-21-0000041 | PRC-002-4 (Saskatchewan) R11.2. | Data subject to Part 11.1 will be provided within 30 calendar days of a request unless an extension is granted by the requestor. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 112000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000011 |  | 3. | RP-2023-08-21-0000042 | PRC-002-4 (Saskatchewan) R11.3. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 113000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000011 |  | 4. | RP-2023-08-21-0000043 | PRC-002-4 (Saskatchewan) R11.4. | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 114000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000011 |  | 5. | RP-2023-08-21-0000044 | PRC-002-4 (Saskatchewan) R11.5. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 115000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000013 |  | 1. | RP-2023-08-21-0000045 | PRC-002-4 (Saskatchewan) R13.1. | Within three (3) calendar years of completing a re-evaluation or receiving notification under Requirement R1, Part 1.3, have SER or FR data as applicable for BES Elements directly connected to the identified BES buses. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 131000000 | MRO-SK
ST-2023-08-11-0000001 | RQ-2023-08-11-0000013 |  | 2. | RP-2023-08-21-0000046 | PRC-002-4 (Saskatchewan) R13.2. | Within three (3) calendar years of receiving notification under Requirement R5, Part 5.4, have DDR data for BES Elements identified during the re-evaluation. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2024-04-01 |  |  |  |  | 132000000 | MRO-SK
ST-2023-08-11-0000002 | RQ-2023-08-11-0000018 |  | 1. | RP-2023-08-21-0000047 | PRC-023-6 (Saskatchewan) R6.1. | Maintain a list of circuits subject to PRC-023-6 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023- 6, Attachment B applies. |  | DP, GO, PCPA, TO |  | DP |  |  | GO |  |  |  |  | PCPA | [7 empty] | TO | [9 empty] | 610000000 | MRO-SK
ST-2023-08-11-0000002 | RQ-2023-08-11-0000018 |  | 2. | RP-2023-08-21-0000048 | PRC-023-6 (Saskatchewan) R6.2. | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. |  | DP, GO, PCPA, TO |  | DP |  |  | GO |  |  |  |  | PCPA | [7 empty] | TO | [9 empty] | 620000000 | MRO-SK
ST-2023-08-15-0000002 | RQ-2023-08-15-0000006 |  | 1. | RP-2023-08-15-0000001 | VAR-501-WECC-4 R3.1. | PSS shall be set to provide the measured, simulated, or calculated compensated Vt/Vref frequency response of the excitation system and synchronous machine such that the phase angle will not exceed ± 30 degrees through the frequency range from 0.2 Hertz to the lesser of 1.0 Hertz or the highest frequency at which the phase of the Vt/Vref frequency response does not exceed 90 degrees. |  | GO, GOP |  |  |  |  | GO | GOP | [16 empty] | 2024-04-01 |  |  |  |  | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-15-0000002 | RQ-2023-08-15-0000006 |  | 2. | RP-2023-08-15-0000002 | VAR-501-WECC-4 R3.2. | PSS output limits shall be set to provide at least ±5% of the synchronous machine’s nominal terminal voltage. |  | GO, GOP |  |  |  |  | GO | GOP | [16 empty] | 2024-04-01 |  |  |  |  | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-15-0000002 | RQ-2023-08-15-0000006 |  | 3. | RP-2023-08-15-0000003 | VAR-501-WECC-4 R3.3. | PSS gain shall be set to between 1/3 and 1/2 of maximum practical gain. |  | GO, GOP |  |  |  |  | GO | GOP | [16 empty] | 2024-04-01 |  |  |  |  | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-15-0000002 | RQ-2023-08-15-0000006 |  | 4. | RP-2023-08-15-0000004 | VAR-501-WECC-4 R3.4. | PSS washout time constant shall be no greater than 30 seconds. |  | GO, GOP |  |  |  |  | GO | GOP | [16 empty] | 2024-04-01 |  |  |  |  | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-15-0000002 | RQ-2023-08-15-0000006 |  | 5. | RP-2023-08-15-0000005 | VAR-501-WECC-4 R3.5. | Units that have an excitation system or PSS that is incapable of meeting the tuning requirements of Requirement R3 are exempt from Requirement R3 until the voltage regulator is either replaced or retrofitted such that the PSS becomes capable of meeting the tuning requirements. |  | GO, GOP |  |  |  |  | GO | GOP | [16 empty] | 2024-04-01 |  |  |  |  | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 | RP-2023-08-22-0000003 | 1. | RP-2023-08-22-0000004 | IRO-010-5 R1.3.1. | Operating limitations based on: |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 | RP-2023-08-22-0000003 | 2. | RP-2023-08-22-0000009 | IRO-010-5 R1.3.2. | Generating unit(s) minimum: |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 | RP-2023-08-22-0000004 | 1. | RP-2023-08-22-0000005 | IRO-010-5 R1.3.1.1. | capability and availability; |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 10301100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 | RP-2023-08-22-0000004 | 2. | RP-2023-08-22-0000006 | IRO-010-5 R1.3.1.2. | fuel supply and inventory concerns; |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 10301200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 | RP-2023-08-22-0000004 | 3. | RP-2023-08-22-0000007 | IRO-010-5 R1.3.1.3. | fuel switching capabilities; and |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 10301300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 | RP-2023-08-22-0000004 | 4. | RP-2023-08-22-0000008 | IRO-010-5 R1.3.1.4. | environmental constraints |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 10301400 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 | RP-2023-08-22-0000009 | 1. | RP-2023-08-22-0000010 | IRO-010-5 R1.3.2.1. | design temperature; or |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 10302100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 | RP-2023-08-22-0000009 | 2. | RP-2023-08-22-0000011 | IRO-010-5 R1.3.2.2. | historical operating temperature; or |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 10302200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 | RP-2023-08-22-0000009 | 3. | RP-2023-08-22-0000012 | IRO-010-5 R1.3.2.3. | current cold weather performance temperature determined by an engineering analysis. |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 10302300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 | RP-2023-08-22-0000014 | 1. | RP-2023-08-22-0000015 | IRO-010-5 R1.5.1. | Specific deadlines or periodicity in which data and information is to be provided; |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 | RP-2023-08-22-0000014 | 2. | RP-2023-08-22-0000016 | IRO-010-5 R1.5.2. | Performance criteria for the availability and accuracy of data and information, as applicable; |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 | RP-2023-08-22-0000014 | 3. | RP-2023-08-22-0000017 | IRO-010-5 R1.5.3. | Provisions to update or correct data and information, as applicable or necessary. |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 153000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 | RP-2023-08-22-0000014 | 4. | RP-2023-08-22-0000018 | IRO-010-5 R1.5.4. | A mutually agreeable format. |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 154000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 | RP-2023-08-22-0000014 | 5. | RP-2023-08-22-0000019 | IRO-010-5 R1.5.5. | A mutually agreeable method(s) for securely transferring data and information. |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 155000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 |  | 1. | RP-2023-08-22-0000001 | IRO-010-5 R1.1. | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real‐time monitoring, and Real‐ time Assessments including non‐BES data and information, external network data and information, and identification of the entities responsible for responding to the specification as deemed necessary by the Reliability Coordinator. |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 |  | 2. | RP-2023-08-22-0000002 | IRO-010-5 R1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 |  | 3. | RP-2023-08-22-0000003 | IRO-010-5 R1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 |  | 4. | RP-2023-08-22-0000013 | IRO-010-5 R1.4. | Identification of a mutually agreeable process for resolving conflicts. |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000002 | RQ-2023-08-22-0000001 |  | 5. | RP-2023-08-22-0000014 | IRO-010-5 R1.5. | Method(s) for the entity identified in Part 1.1 to provide data and information that includes, but is not limited to. |  | RC | [11 empty] | RC | [10 empty] | 2025-07-01 |  |  |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 | RP-2023-08-23-0000003 | 1. | RP-2023-08-23-0000004 | TOP-003-6 R1.3.1. | Operating limitations based on: |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 | RP-2023-08-23-0000003 | 2. | RP-2023-08-23-0000009 | TOP-003-6 R1.3.2. | Generating unit(s) minimum: |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 | RP-2023-08-23-0000004 | 1. | RP-2023-08-23-0000005 | TOP-003-6 R1.3.1.1. | capability and availability; |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 10301100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 | RP-2023-08-23-0000004 | 2. | RP-2023-08-23-0000006 | TOP-003-6 R1.3.1.2. | fuel supply and inventory concerns; |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 10301200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 | RP-2023-08-23-0000004 | 3. | RP-2023-08-23-0000007 | TOP-003-6 R1.3.1.3. | fuel switching capabilities; and |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 10301300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 | RP-2023-08-23-0000004 | 4. | RP-2023-08-23-0000008 | TOP-003-6 R1.3.1.4. | environmental constraints |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 10301400 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 | RP-2023-08-23-0000009 | 1. | RP-2023-08-23-0000010 | TOP-003-6 R1.3.2.1. | design temperature; or |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 10302100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 | RP-2023-08-23-0000009 | 2. | RP-2023-08-23-0000011 | TOP-003-6 R1.3.2.2. | historical operating temperature; or |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 10302200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 | RP-2023-08-23-0000009 | 3. | RP-2023-08-23-0000012 | TOP-003-6 R1.3.2.3. | current cold weather performance temperature determined by an engineering analysis. |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 10302300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 | RP-2023-08-23-0000014 | 1. | RP-2023-08-23-0000015 | TOP-003-6 R1.5.1. | Specified deadlines or periodicity which data and information is to be provided; |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 | RP-2023-08-23-0000014 | 2. | RP-2023-08-23-0000016 | TOP-003-6 R1.5.2. | Performance criteria for the availability and accuracy of data and information as applicable; |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 | RP-2023-08-23-0000014 | 3. | RP-2023-08-23-0000017 | TOP-003-6 R1.5.3. | Provisions to update or correct data and information, as applicable or necessary; |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 153000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 | RP-2023-08-23-0000014 | 4. | RP-2023-08-23-0000018 | TOP-003-6 R1.5.4. | A mutually agreeable format; |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 154000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 | RP-2023-08-23-0000014 | 5. | RP-2023-08-23-0000019 | TOP-003-6 R1.5.5. | Mutually agreeable method(s) for securely transferring data and information. |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 155000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 |  | 1. | RP-2023-08-23-0000001 | TOP-003-6 R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real‐time monitoring, and Real‐time Assessments including non‐BES data and information, external network data and information, and identification of the entities responsible for responding to the specification as deemed necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 |  | 2. | RP-2023-08-23-0000002 | TOP-003-6 R1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 |  | 3. | RP-2023-08-23-0000003 | TOP-003-6 R1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 |  | 4. | RP-2023-08-23-0000013 | TOP-003-6 R1.4. | Identification of a mutually agreeable process for resolving conflicts. |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000004 |  | 5. | RP-2023-08-23-0000014 | TOP-003-6 R1.5. | Method(s) for the entity identified in Part 1.1 to provide the data and information that includes at a minimum the following. |  | TOP | [18 empty] | TOP | [5 empty] | 2023-08-23 |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 | RP-2023-08-23-0000022 | 1. | RP-2023-08-23-0000023 | TOP-003-6 R2.3.1. | Operating limitations based on: |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 231000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 | RP-2023-08-23-0000022 | 2. | RP-2023-08-24-0000001 | TOP-003-6 R2.3.2. | Generating unit(s) minimum: |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 232000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 | RP-2023-08-23-0000023 | 1. | RP-2023-08-23-0000038 | TOP-003-6 R2.3.1.1. | capability and availability; |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 20301100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 | RP-2023-08-23-0000023 | 2. | RP-2023-08-23-0000039 | TOP-003-6 R2.3.1.2. | fuel supply and inventory concerns; |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 20301200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 | RP-2023-08-23-0000023 | 3. | RP-2023-08-23-0000040 | TOP-003-6 R2.3.1.3. | fuel switching capabilities; and |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 20301300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 | RP-2023-08-23-0000023 | 4. | RP-2023-08-23-0000041 | TOP-003-6 R2.3.1.4. | environmental constraints. |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 20301400 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 | RP-2023-08-23-0000032 | 1. | RP-2023-08-23-0000033 | TOP-003-6 R2.5.1. | Specific deadlines or periodicity in which data and information is to be provided; |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 251000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 | RP-2023-08-23-0000032 | 2. | RP-2023-08-23-0000034 | TOP-003-6 R2.5.2. | Performance criteria for the availability and accuracy of data and information, as applicable; |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 252000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 | RP-2023-08-23-0000032 | 3. | RP-2023-08-23-0000035 | TOP-003-6 R2.5.3. | Provisions to update or correct data and information, as applicable or necessary. |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 253000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 | RP-2023-08-23-0000032 | 4. | RP-2023-08-23-0000036 | TOP-003-6 R2.5.4. | A mutually agreeable format. |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 254000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 | RP-2023-08-23-0000032 | 5. | RP-2023-08-23-0000037 | TOP-003-6 R2.5.5. | A mutually agreeable methods for securely transferring data and information. |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 255000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 | RP-2023-08-24-0000001 | 1. | RP-2023-08-24-0000002 | TOP-003-6 R2.3.2.1. | design temperature; or |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 20302100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 | RP-2023-08-24-0000001 | 2. | RP-2023-08-24-0000003 | TOP-003-6 R2.3.2.2. | historical operating temperature; or |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 20302200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 | RP-2023-08-24-0000001 | 3. | RP-2023-08-24-0000004 | TOP-003-6 R2.3.2.3. | current cold weather performance temperature determined by an engineering analysis. |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 20302300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 |  | 1. | RP-2023-08-23-0000020 | TOP-003-6 R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real‐time monitoring including non‐Bulk Electric System data and information, and external network data and information, as deemed necessary by the Balancing Authority, and identification of the entity responsible for responding to the specification. |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 |  | 2. | RP-2023-08-23-0000021 | TOP-003-6 R2.2. | Provisions for notification of current Protection System and Remedial Action Scheme status or degradation that impacts System reliability. |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 |  | 3. | RP-2023-08-23-0000022 | TOP-003-6 R2.3. | Provisions for notification of BES generating unit(s) status during local forecasted cold weather to include: |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 |  | 4. | RP-2023-08-23-0000031 | TOP-003-6 R2.4. | Identification of a mutually agreeable process in resolving conflicts |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-08-22-0000005 | RQ-2023-08-22-0000005 |  | 5. | RP-2023-08-23-0000032 | TOP-003-6 R2.5. | Methods for the entity identified in Part 2.1 to provide data and information that includes at a minimum the following. |  | BA | BA | [23 empty] | 2023-08-23 |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000001 | RP-2023-09-13-0000003 | 1. | RP-2023-09-13-0000004 | TOP-003-6.1 R1.3.1. | Operating limitations based on: |  | TOP | [18 empty] | TOP |  |  |  | 2025-07-01 |  |  |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000001 | RP-2023-09-13-0000004 | 1. | RP-2023-09-13-0000005 | TOP-003-6.1 R1.3.1.1. | capability and availability; |  | TOP | [18 empty] | TOP |  |  |  | 2025-07-01 |  |  |  |  | 10301100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000001 | RP-2023-09-13-0000004 | 2. | RP-2023-09-13-0000006 | TOP-003-6.1 R1.3.1.2. | fuel supply and inventory concerns; |  | TOP | [18 empty] | TOP |  |  |  | 2025-07-01 |  |  |  |  | 10301200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000001 | RP-2023-09-13-0000004 | 3. | RP-2023-09-13-0000007 | TOP-003-6.1 R1.3.1.3. | fuel switching capabilities; and |  | TOP | [18 empty] | TOP |  |  |  | 2025-07-01 |  |  |  |  | 10301300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000001 | RP-2023-09-13-0000004 | 4. | RP-2023-09-13-0000008 | TOP-003-6.1 R1.3.1.4. | environmental constraints |  | TOP | [18 empty] | TOP |  |  |  | 2025-07-01 |  |  |  |  | 10301400 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000001 | RP-2023-09-13-0000010 | 1. | RP-2023-09-13-0000011 | TOP-003-6.1 R1.5.1. | Specified deadlines or periodicity which data and information is to be provided; |  | TOP | [18 empty] | TOP |  |  |  | 2025-07-01 |  |  |  |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000001 | RP-2023-09-13-0000010 | 2. | RP-2023-09-13-0000012 | TOP-003-6.1 R1.5.2. | Performance criteria for the availability and accuracy of data and information as applicable; |  | TOP | [18 empty] | TOP |  |  |  | 2025-07-01 |  |  |  |  | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000001 | RP-2023-09-13-0000010 | 3. | RP-2023-09-13-0000013 | TOP-003-6.1 R1.5.3. | Provisions to update or correct data and information, as applicable or necessary; |  | TOP | [18 empty] | TOP |  |  |  | 2025-07-01 |  |  |  |  | 153000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000001 | RP-2023-09-13-0000010 | 4. | RP-2023-09-13-0000014 | TOP-003-6.1 R1.5.4. | A mutually agreeable format; |  | TOP | [18 empty] | TOP |  |  |  | 2025-07-01 |  |  |  |  | 154000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000001 | RP-2023-09-13-0000010 | 5. | RP-2023-09-13-0000015 | TOP-003-6.1 R1.5.5. | Mutually agreeable method(s) for securely transferring data and information. |  | TOP | [18 empty] | TOP |  |  |  | 2025-07-01 |  |  |  |  | 155000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000001 |  | 1. | RP-2023-09-13-0000001 | TOP-003-6.1 R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and information, external network data and information, and identification of the entities responsible for responding to the specification as deemed necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2025-07-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000001 |  | 2. | RP-2023-09-13-0000002 | TOP-003-6.1 R1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. |  | TOP | [18 empty] | TOP |  |  |  | 2025-07-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000001 |  | 3. | RP-2023-09-13-0000003 | TOP-003-6.1 R1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: |  | TOP | [18 empty] | TOP |  |  |  | 2025-07-01 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000001 |  | 4. | RP-2023-09-13-0000009 | TOP-003-6.1 R1.4. | Identification of a mutually agreeable process for resolving conflicts. |  | TOP | [18 empty] | TOP |  |  |  | 2025-07-01 |  |  |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000001 |  | 5. | RP-2023-09-13-0000010 | TOP-003-6.1 R1.5. | Method(s) for the entity identified in Part 1.1 to provide the data and information that includes at a minimum the following. |  | TOP | [18 empty] | TOP |  |  |  | 2025-07-01 |  |  |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 | RP-2023-09-13-0000018 | 1. | RP-2023-09-13-0000019 | TOP-003-6.1 R2.3.1. | Operating limitations based on: |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 231000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 | RP-2023-09-13-0000018 | 2. | RP-2023-09-13-0000024 | TOP-003-6.1 R2.3.2. | Generating unit(s) minimum: |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 232000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 | RP-2023-09-13-0000019 | 1. | RP-2023-09-13-0000020 | TOP-003-6.1 R2.3.1.1. | capability and availability; |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 20301100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 | RP-2023-09-13-0000019 | 2. | RP-2023-09-13-0000021 | TOP-003-6.1 R2.3.1.2. | fuel supply and inventory concerns; |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 20301200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 | RP-2023-09-13-0000019 | 3. | RP-2023-09-13-0000022 | TOP-003-6.1 R2.3.1.3. | fuel switching capabilities; and |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 20301300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 | RP-2023-09-13-0000019 | 4. | RP-2023-09-13-0000023 | TOP-003-6.1 R2.3.1.4. | environmental constraints. |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 20301400 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 | RP-2023-09-13-0000024 | 1. | RP-2023-09-13-0000025 | TOP-003-6.1 R2.3.2.1. | design temperature; or |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 20302100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 | RP-2023-09-13-0000024 | 2. | RP-2023-09-13-0000026 | TOP-003-6.1 R2.3.2.2. | historical operating temperature; or |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 20302200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 | RP-2023-09-13-0000024 | 3. | RP-2023-09-13-0000027 | TOP-003-6.1 R2.3.2.3. | current cold weather performance temperature determined by an engineering analysis. |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 20302300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 | RP-2023-09-13-0000029 | 1. | RP-2023-09-13-0000030 | TOP-003-6.1 R2.5.1. | Specific deadlines or periodicity in which data and information is to be provided; |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 251000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 | RP-2023-09-13-0000029 | 2. | RP-2023-09-13-0000031 | TOP-003-6.1 R2.5.2. | Performance criteria for the availability and accuracy of data and information, as applicable; |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 252000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 | RP-2023-09-13-0000029 | 3. | RP-2023-09-13-0000032 | TOP-003-6.1 R2.5.3. | Provisions to update or correct data and information, as applicable or necessary. |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 253000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 | RP-2023-09-13-0000029 | 4. | RP-2023-09-13-0000033 | TOP-003-6.1 R2.5.4. | A mutually agreeable format. |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 254000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 | RP-2023-09-13-0000029 | 5. | RP-2023-09-13-0000034 | TOP-003-6.1 R2.5.5. | A mutually agreeable method(s) for securely transferring data and information. |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 255000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 |  | 1. | RP-2023-09-13-0000016 | TOP-003-6.1 R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring including non-Bulk Electric System data and information, and external network data and information, as deemed necessary by the Balancing Authority, and identification of the entity responsible for responding to the specification. |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 |  | 2. | RP-2023-09-13-0000017 | TOP-003-6.1 R2.2. | Provisions for notification of current Protection System and Remedial Action Scheme status or degradation that impacts System reliability. |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 |  | 3. | RP-2023-09-13-0000018 | TOP-003-6.1 R2.3. | Provisions for notification of BES generating unit(s) status during local forecasted cold weather to include: |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 |  | 4. | RP-2023-09-13-0000028 | TOP-003-6.1 R2.4. | Identification of a mutually agreeable process in resolving conflicts |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-09-13-0000001 | RQ-2023-09-13-0000002 |  | 5. | RP-2023-09-13-0000029 | TOP-003-6.1 R2.5. | Methods for the entity identified in Part 2.1 to provide data and information that includes at a minimum the following. |  | BA | BA | [21 empty] | 2025-07-01 |  |  |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000001 | RQ-2023-10-03-0000001 |  | 1. | RP-2023-10-03-0000001 | CIP-005-7 (Manitoba) R1.1. | All applicable Cyber Assets connected to a network via a routable protocol shall reside within a defined ESP. | High Impact BES Cyber Systems and their associated: • PCA Medium Impact BES Cyber Systems and their associated: • PCA | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | : For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator 4.1.4. Generator Owner CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 2 of 20 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 3 of 20 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 110000000 | MRO-MB
ST-2023-10-03-0000001 | RQ-2023-10-03-0000001 |  | 2. | RP-2023-10-03-0000002 | CIP-005-7 (Manitoba) R1.2. | All External Routable Connectivity must be through an identified Electronic Access Point (EAP) | High Impact BES Cyber Systems with External Routable Connectivity and their associated: • PCA Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: • PCA | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | : For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator 4.1.4. Generator Owner CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 2 of 20 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 3 of 20 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 120000000 | MRO-MB
ST-2023-10-03-0000001 | RQ-2023-10-03-0000001 |  | 3. | RP-2023-10-03-0000003 | CIP-005-7 (Manitoba) R1.3. | Require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default. | Electronic Access Points for High Impact BES Cyber Systems Electronic Access Points for Medium Impact BES Cyber Systems | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | : For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator 4.1.4. Generator Owner CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 2 of 20 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 3 of 20 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 130000000 | MRO-MB
ST-2023-10-03-0000001 | RQ-2023-10-03-0000001 |  | 4. | RP-2023-10-03-0000004 | CIP-005-7 (Manitoba) R1.4. | Where technically feasible, perform authentication when establishing Dialup Connectivity with applicable Cyber Assets. | High Impact BES Cyber Systems with Dial-up Connectivity and their associated: • PCA Medium Impact BES Cyber Systems with Dial-up Connectivity and their associated: • PCA | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | : For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator 4.1.4. Generator Owner CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 2 of 20 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 3 of 20 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 140000000 | MRO-MB
ST-2023-10-03-0000001 | RQ-2023-10-03-0000001 |  | 5. | RP-2023-10-03-0000005 | CIP-005-7 (Manitoba) R1.5. | Have one or more methods for detecting known or suspected malicious communications for both inbound and outbound communications | Electronic Access Points for High Impact BES Cyber Systems Electronic Access Points for Medium Impact BES Cyber Systems at Control Centers | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | : For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator 4.1.4. Generator Owner CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 2 of 20 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 3 of 20 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 150000000 | MRO-MB
ST-2023-10-03-0000001 | RQ-2023-10-03-0000002 |  | 1. | RP-2023-10-03-0000006 | CIP-005-7 (Manitoba) R2.1. | For all Interactive Remote Access, utilize an Intermediate System such that the Cyber Asset initiating Interactive Remote Access does not directly access an applicable Cyber Asset. | High Impact BES Cyber Systems and their associated: • PCA Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: • PCA | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | : For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator 4.1.4. Generator Owner CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 2 of 20 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 3 of 20 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 210000000 | MRO-MB
ST-2023-10-03-0000001 | RQ-2023-10-03-0000002 |  | 2. | RP-2023-10-03-0000007 | CIP-005-7 (Manitoba) R2.2. | For all Interactive Remote Access sessions, utilize encryption that terminates at an Intermediate System. | High Impact BES Cyber Systems and their associated: • PCA Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: • PCA | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | : For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator 4.1.4. Generator Owner CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 2 of 20 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 3 of 20 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 220000000 | MRO-MB
ST-2023-10-03-0000001 | RQ-2023-10-03-0000002 |  | 3. | RP-2023-10-03-0000008 | CIP-005-7 (Manitoba) R2.3. | Require multi-factor authentication for all Interactive Remote Access sessions. | High Impact BES Cyber Systems and their associated: • PCA Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: • PCA | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | : For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator 4.1.4. Generator Owner CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 2 of 20 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 3 of 20 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 230000000 | MRO-MB
ST-2023-10-03-0000001 | RQ-2023-10-03-0000002 |  | 4. | RP-2023-10-03-0000009 | CIP-005-7 (Manitoba) R2.4. | Have one or more methods for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access). | High Impact BES Cyber Systems and their associated: • PCA Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: • PCA | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | : For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator 4.1.4. Generator Owner CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 2 of 20 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 3 of 20 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 240000000 | MRO-MB
ST-2023-10-03-0000001 | RQ-2023-10-03-0000002 |  | 5. | RP-2023-10-03-0000010 | CIP-005-7 (Manitoba) R2.5. | Have one or more method(s) to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access). | High Impact BES Cyber Systems and their associated: • PCA Medium Impact BES Cyber Systems with External Routable Connectivity and their associated: • PCA | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | : For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator 4.1.4. Generator Owner CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 2 of 20 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 3 of 20 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 250000000 | MRO-MB
ST-2023-10-03-0000001 | RQ-2023-10-03-0000003 |  | 1. | RP-2023-10-03-0000011 | CIP-005-7 (Manitoba) R3.1. | Have one or more method(s) to determine authenticated vendorinitiated remote connections. | EACMS and PACS associated with High Impact BES Cyber Systems EACMS and PACS associated with Medium Impact BES Cyber Systems with External Routable Connectivity | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | : For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator 4.1.4. Generator Owner CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 2 of 20 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 3 of 20 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 310000000 | MRO-MB
ST-2023-10-03-0000001 | RQ-2023-10-03-0000003 |  | 2. | RP-2023-10-03-0000012 | CIP-005-7 (Manitoba) R3.2. | Have one or more method(s) to terminate authenticated vendorinitiated remote connections and control the ability to reconnect. | EACMS and PACS associated with High Impact BES Cyber Systems EACMS and PACS associated with Medium Impact BES Cyber Systems with External Routable Connectivity | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | : For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator 4.1.4. Generator Owner CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 2 of 20 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-005-7: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. CIP-005-7 — Cyber Security – Electronic Security Perimeter(s) Page 3 of 20 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 320000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 | RP-2023-10-03-0000013 | 1. | RP-2023-10-03-0000019 | CIP-010-4 (Manitoba) R1.1.1. | Operating system(s) (including version) or firmware where no independent operating system exists; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 111000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 | RP-2023-10-03-0000013 | 2. | RP-2023-10-03-0000020 | CIP-010-4 (Manitoba) R1.1.2. | Any commercially available or open-source application software (including version) intentionally installed; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 112000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 | RP-2023-10-03-0000013 | 3. | RP-2023-10-03-0000021 | CIP-010-4 (Manitoba) R1.1.3. | Any custom software installed; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 113000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 | RP-2023-10-03-0000013 | 4. | RP-2023-10-03-0000022 | CIP-010-4 (Manitoba) R1.1.4. | Any logical network accessible ports; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 114000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 | RP-2023-10-03-0000013 | 5. | RP-2023-10-03-0000023 | CIP-010-4 (Manitoba) R1.1.5. | Any security patches applied. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 115000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 | RP-2023-10-03-0000017 | 1. | RP-2023-10-03-0000027 | CIP-010-4 (Manitoba) R1.5.1. | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 151000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 | RP-2023-10-03-0000017 | 2. | RP-2023-10-03-0000028 | CIP-010-4 (Manitoba) R1.5.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 152000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 | RP-2023-10-03-0000018 | 1. | RP-2023-10-03-0000029 | CIP-010-4 (Manitoba) R1.6.1. | Verify the identity of the software source; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 161000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 | RP-2023-10-03-0000018 | 2. | RP-2023-10-03-0000030 | CIP-010-4 (Manitoba) R1.6.2. | Verify the integrity of the software obtained from the software source. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 162000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 | RP-2023-10-03-0000022 | 1. | RP-2023-10-03-0000024 | CIP-010-4 (Manitoba) R1.1.4.1. | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 10104100 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 | RP-2023-10-03-0000022 | 2. | RP-2023-10-03-0000025 | CIP-010-4 (Manitoba) R1.1.4.2. | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 10104200 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 | RP-2023-10-03-0000022 | 3. | RP-2023-10-03-0000026 | CIP-010-4 (Manitoba) R1.1.4.3. | Document the results of the verification. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 10104300 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 |  | 1. | RP-2023-10-03-0000013 | CIP-010-4 (Manitoba) R1.1. | Develop a baseline configuration, individually or by group, which shall include the following items: | High Impact BES Cyber Systems and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium Impact BES Cyber Systems and their associated: 1. EACMS; 2. PACS; and 3. PCA | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 2 of 32 4.1.4. Generator Owner 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-4: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 3 of 32 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 110000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 |  | 2. | RP-2023-10-03-0000014 | CIP-010-4 (Manitoba) R1.2. | Authorize and document changes that deviate from the existing baseline configuration. | High Impact BES Cyber Systems and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium Impact BES Cyber Systems and their associated: 1. EACMS; 2. PACS; and 3. PCA | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 2 of 32 4.1.4. Generator Owner 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-4: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 3 of 32 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 120000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 |  | 3. | RP-2023-10-03-0000015 | CIP-010-4 (Manitoba) R1.3. | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. | High Impact BES Cyber Systems and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium Impact BES Cyber Systems and their associated: 1. EACMS; 2. PACS; and 3. PCA | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 2 of 32 4.1.4. Generator Owner 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-4: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 3 of 32 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 130000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 |  | 4. | RP-2023-10-03-0000016 | CIP-010-4 (Manitoba) R1.4. | For a change that deviates from the existing baseline configuration: | High Impact BES Cyber Systems and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium Impact BES Cyber Systems and their associated: 1. EACMS; 2. PACS; and 3. PCA | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 2 of 32 4.1.4. Generator Owner 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-4: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 3 of 32 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 140000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 |  | 5. | RP-2023-10-03-0000017 | CIP-010-4 (Manitoba) R1.5. | Where technically feasible, for each change that deviates from the existing baseline configuration: | High Impact BES Cyber Systems | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 2 of 32 4.1.4. Generator Owner 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-4: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 3 of 32 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 150000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000004 |  | 6. | RP-2023-10-03-0000018 | CIP-010-4 (Manitoba) R1.6. | Prior to a change that deviates from the existing baseline configuration associated with baseline items in Parts 1.1.1, 1.1.2, and 1.1.5, and when the method to do so is available to the Responsible Entity from the software source: | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Medium Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PACS Note: Implementation does not require the Responsible Entity to renegotiate or abrogate existing contracts (including amendments to master agreements and purchase orders). Additionally, the following issues are beyond the scope of Part 1.6: (1) the actual terms and conditions of a procurement contract; and (2) vendor performance and adherence to a contract. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 2 of 32 4.1.4. Generator Owner 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-4: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 3 of 32 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 160000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000005 |  | 1. | RP-2023-10-03-0000031 | CIP-010-4 (Manitoba) R2.1. | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 2 of 32 4.1.4. Generator Owner 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-4: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 3 of 32 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 210000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000006 | RP-2023-10-03-0000033 | 1. | RP-2023-10-03-0000034 | CIP-010-4 (Manitoba) R3.2.1. | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 321000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000006 | RP-2023-10-03-0000033 | 2. | RP-2023-10-03-0000035 | CIP-010-4 (Manitoba) R3.2.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 322000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000006 |  | 1. | RP-2023-10-03-0000032 | CIP-010-4 (Manitoba) R3.1. | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A document listing the date of the assessment (performed at least once every 15 calendar months), the controls assessed for each BES Cyber System along with the method of assessment; or • A document listing the date of the assessment and the output of any tools used to perform the assessment. | 2023-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 2 of 32 4.1.4. Generator Owner 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-4: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 3 of 32 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 310000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000006 |  | 2. | RP-2023-10-03-0000033 | CIP-010-4 (Manitoba) R3.2. | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed at least once every 36 calendar months), the output of the tools used to perform the assessment, and a list of differences between the production and test environments with descriptions of how any differences were accounted for in conducting the assessment. | 2023-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 2 of 32 4.1.4. Generator Owner 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-4: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 3 of 32 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 320000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000006 |  | 3. | RP-2023-10-03-0000036 | CIP-010-4 (Manitoba) R3.3. | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset. | High Impact BES Cyber Systems and their associated: 1. EACMS; and 2. PCA | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed prior to the commissioning of the new Cyber Asset) and the output of any tools used to perform the assessment. | 2023-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 2 of 32 4.1.4. Generator Owner 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-4: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 3 of 32 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 330000000 | MRO-MB
ST-2023-10-03-0000002 | RQ-2023-10-03-0000006 |  | 4. | RP-2023-10-03-0000037 | CIP-010-4 (Manitoba) R3.4. | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. | High Impact BES Cyber Systems and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium Impact BES Cyber Systems and their associated: 1. EACMS; 2. PACS; and 3. PCA | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the results or the review or assessment, a list of action items, documented proposed dates of completion for the action plan, and records of the status of the action items (such as minutes of a status meeting, updates in a work order system, or a spreadsheet tracking the action items). | 2023-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.1.3. Generator Operator CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 2 of 32 4.1.4. Generator Owner 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-010-4: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. CIP-010-4 – Cyber Security — Configuration Change Management and Vulnerability Assessments Page 3 of 32 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. | 340000000 | MRO-MB
ST-2023-10-03-0000003 | RQ-2023-10-03-0000008 |  | 1. | RP-2023-10-03-0000038 | CIP-012-1 (Manitoba) R1.1. | Identification of security protection used to mitigate the risks posed by unauthorized disclosure and unauthorized modification of Real-time Assessment and Real-time monitoring data while being transmitted between Control Centers; |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 110000000 | MRO-MB
ST-2023-10-03-0000003 | RQ-2023-10-03-0000008 |  | 2. | RP-2023-10-03-0000039 | CIP-012-1 (Manitoba) R1.2. | Identification of where the Responsible Entity applied security protection for transmitting Real-time Assessment and Real-time monitoring data between Control Centers; and |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 120000000 | MRO-MB
ST-2023-10-03-0000003 | RQ-2023-10-03-0000008 |  | 3. | RP-2023-10-03-0000040 | CIP-012-1 (Manitoba) R1.3. | If the Control Centers are owned or operated by different Responsible Entities, identification of the responsibilities of each Responsible Entity for applying security protection to the transmission of Real-time Assessment and Real-time monitoring data between those Control Centers. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 130000000 | MRO-MB
ST-2023-10-03-0000004 | RQ-2023-10-03-0000009 | RP-2023-10-03-0000042 | 1. | RP-2023-10-03-0000043 | CIP-013-2(Manitoba) R1.2.1. | Notification by the vendor of vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 121000000 | MRO-MB
ST-2023-10-03-0000004 | RQ-2023-10-03-0000009 | RP-2023-10-03-0000042 | 2. | RP-2023-10-03-0000044 | CIP-013-2(Manitoba) R1.2.2. | Coordination of responses to vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 122000000 | MRO-MB
ST-2023-10-03-0000004 | RQ-2023-10-03-0000009 | RP-2023-10-03-0000042 | 3. | RP-2023-10-03-0000045 | CIP-013-2(Manitoba) R1.2.3. | Notification by vendors when remote or onsite access should no longer be granted to vendor representatives; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 123000000 | MRO-MB
ST-2023-10-03-0000004 | RQ-2023-10-03-0000009 | RP-2023-10-03-0000042 | 4. | RP-2023-10-03-0000046 | CIP-013-2(Manitoba) R1.2.4. | Disclosure by vendors of known vulnerabilities related to the products or services provided to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 124000000 | MRO-MB
ST-2023-10-03-0000004 | RQ-2023-10-03-0000009 | RP-2023-10-03-0000042 | 5. | RP-2023-10-03-0000047 | CIP-013-2(Manitoba) R1.2.5. | Verification of software integrity and authenticity of all software and patches provided by the vendor for use in the BES Cyber System and their associated EACMS and PACS; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 125000000 | MRO-MB
ST-2023-10-03-0000004 | RQ-2023-10-03-0000009 | RP-2023-10-03-0000042 | 6. | RP-2023-10-03-0000048 | CIP-013-2(Manitoba) R1.2.6. | Coordination of controls for vendor-initiated remote access. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 126000000 | MRO-MB
ST-2023-10-03-0000004 | RQ-2023-10-03-0000009 |  | 1. | RP-2023-10-03-0000041 | CIP-013-2(Manitoba) R1.1. | One or more process(es) used in planning for the procurement of BES Cyber Systems and their associated EACMS and PACS to identify and assess cyber security risk(s) to the Bulk Electric System from vendor products or services resulting from: (i) procuring and installing vendor equipment and software; and (ii) transitions from one vendor(s) to another vendor(s). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.3. Generator Operator 4.1.4. Generator Owner 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner CIP-013-2 – Cyber Security - Supply Chain Risk Management Page 2 of 10 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-013-2: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. CIP-013-2 – Cyber Security - Supply Chain Risk Management Page 3 of 10 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002 or any subsequent version of that Reliability Standard. | 110000000 | MRO-MB
ST-2023-10-03-0000004 | RQ-2023-10-03-0000009 |  | 2. | RP-2023-10-03-0000042 | CIP-013-2(Manitoba) R1.2. | One or more process(es) used in procuring BES Cyber Systems, and their associated EACMS and PACS, that address the following, as applicable: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly. 4.1.1. Balancing Authority 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that: 4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.1.3. Generator Operator 4.1.4. Generator Owner 4.1.5. Reliability Coordinator 4.1.6. Transmission Operator 4.1.7. Transmission Owner CIP-013-2 – Cyber Security - Supply Chain Risk Management Page 2 of 10 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly. 4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that: 4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more. 4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard. 4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. 4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities. 4.2.3. Exemptions: The following are exempt from Standard CIP-013-2: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54. CIP-013-2 – Cyber Security - Supply Chain Risk Management Page 3 of 10 4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. 4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002 or any subsequent version of that Reliability Standard. | 120000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000012 |  | 1. | RP-2023-10-03-0000049 | CIP-014-3 (Manitoba) R1.1. | Subsequent risk assessments shall be performed: • At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or • At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 110000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000012 |  | 2. | RP-2023-10-03-0000050 | CIP-014-3 (Manitoba) R1.2. | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 120000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000013 |  | 1. | RP-2023-10-03-0000051 | CIP-014-3 (Manitoba) R2.1. | Each Transmission Owner shall select an unaffiliated verifying entity that is either: • A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or • An entity that has transmission planning or analysis experience. |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 210000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000013 |  | 2. | RP-2023-10-03-0000052 | CIP-014-3 (Manitoba) R2.2. | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 220000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000013 |  | 3. | RP-2023-10-03-0000053 | CIP-014-3 (Manitoba) R2.3. | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation: • Modify its identification under Requirement R1 consistent with the recommendation; or • Document the technical basis for not modifying the identification in accordance with the recommendation. |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 230000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000013 |  | 4. | RP-2023-10-03-0000054 | CIP-014-3 (Manitoba) R2.4. | Each Transmission Owner shall implement procedures, such as the use of nondisclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 240000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000014 |  | 1. | RP-2023-10-03-0000055 | CIP-014-3 (Manitoba) R3.1. | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 310000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000015 |  | 1. | RP-2023-10-03-0000056 | CIP-014-3 (Manitoba) R4.1. | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 410000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000015 |  | 2. | RP-2023-10-03-0000057 | CIP-014-3 (Manitoba) R4.2. | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 420000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000015 |  | 3. | RP-2023-10-03-0000058 | CIP-014-3 (Manitoba) R4.3. | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 430000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000016 |  | 1. | RP-2023-10-03-0000059 | CIP-014-3 (Manitoba) R5.1. | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 510000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000016 |  | 2. | RP-2023-10-03-0000060 | CIP-014-3 (Manitoba) R5.2. | Law enforcement contact and coordination information. |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 520000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000016 |  | 3. | RP-2023-10-03-0000061 | CIP-014-3 (Manitoba) R5.3. | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 530000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000016 |  | 4. | RP-2023-10-03-0000062 | CIP-014-3 (Manitoba) R5.4. | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 540000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000017 |  | 2. | RP-2023-10-03-0000064 | CIP-014-3 (Manitoba) R6.2. | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 620000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000017 |  | 3. | RP-2023-10-03-0000065 | CIP-014-3 (Manitoba) R6.3. | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation: • Modify its evaluation or security plan(s) consistent with the recommendation; or • Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 630000000 | MRO-MB
ST-2023-10-03-0000005 | RQ-2023-10-03-0000017 |  | 4. | RP-2023-10-03-0000066 | CIP-014-3 (Manitoba) R6.4. | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO, TOP, TP | [17 empty] | TO | TOP | TP |  |  | 2023-07-01 |  |  |  |  | 640000000 | MRO-MB
ST-2023-10-03-0000006 | RQ-2023-10-03-0000019 | RP-2023-10-03-0000069 | 1. | RP-2023-10-03-0000070 | TOP-003-5 (Saskatchewan) R1.3.1. | Operating limitations based on: |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000019 | RP-2023-10-03-0000069 | 2. | RP-2023-10-03-0000075 | TOP-003-5 (Saskatchewan) R1.3.2. | Generating unit(s) minimum: |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000019 | RP-2023-10-03-0000070 | 1. | RP-2023-10-03-0000071 | TOP-003-5 (Saskatchewan) R1.3.1.1. | capability and availability; |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 10301100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000019 | RP-2023-10-03-0000070 | 2. | RP-2023-10-03-0000072 | TOP-003-5 (Saskatchewan) R1.3.1.2. | fuel supply and inventory concerns; |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 10301200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000019 | RP-2023-10-03-0000070 | 3. | RP-2023-10-03-0000073 | TOP-003-5 (Saskatchewan) R1.3.1.3. | fuel switching capabilities; and |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 10301300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000019 | RP-2023-10-03-0000070 | 4. | RP-2023-10-03-0000074 | TOP-003-5 (Saskatchewan) R1.3.1.4. | environmental constraints |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 10301400 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000019 | RP-2023-10-03-0000075 | 1. | RP-2023-10-03-0000076 | TOP-003-5 (Saskatchewan) R1.3.2.1. | design temperature; or |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 10302100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000019 | RP-2023-10-03-0000075 | 2. | RP-2023-10-03-0000077 | TOP-003-5 (Saskatchewan) R1.3.2.2. | historical operating temperature; or |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 10302200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000019 | RP-2023-10-03-0000075 | 3. | RP-2023-10-03-0000078 | TOP-003-5 (Saskatchewan) R1.3.2.3. | current cold weather performance temperature determined by an engineering analysis. |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 10302300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000019 |  | 1. | RP-2023-10-03-0000067 | TOP-003-5 (Saskatchewan) R1.1. | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000019 |  | 2. | RP-2023-10-03-0000068 | TOP-003-5 (Saskatchewan) R1.2. | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000019 |  | 3. | RP-2023-10-03-0000069 | TOP-003-5 (Saskatchewan) R1.3. | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000019 |  | 4. | RP-2023-10-03-0000079 | TOP-003-5 (Saskatchewan) R1.4. | A periodicity for providing data. |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000019 |  | 5. | RP-2023-10-03-0000080 | TOP-003-5 (Saskatchewan) R1.5. | The deadline by which the respondent is to provide the indicated data. |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000020 | RP-2023-10-03-0000083 | 1. | RP-2023-10-03-0000084 | TOP-003-5 (Saskatchewan) R2.3.1. | Operating limitations based on: |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  |  | 231000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000020 | RP-2023-10-03-0000083 | 2. | RP-2023-10-03-0000089 | TOP-003-5 (Saskatchewan) R2.3.2. | Generating unit(s) minimum: |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  |  | 232000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000020 | RP-2023-10-03-0000084 | 1. | RP-2023-10-03-0000085 | TOP-003-5 (Saskatchewan) R2.3.1.1. | capability and availability; |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  |  | 20301100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000020 | RP-2023-10-03-0000084 | 2. | RP-2023-10-03-0000086 | TOP-003-5 (Saskatchewan) R2.3.1.2. | fuel supply and inventory concerns; |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  |  | 20301200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000020 | RP-2023-10-03-0000084 | 3. | RP-2023-10-03-0000087 | TOP-003-5 (Saskatchewan) R2.3.1.3. | fuel switching capabilities; and |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  |  | 20301300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000020 | RP-2023-10-03-0000084 | 4. | RP-2023-10-03-0000088 | TOP-003-5 (Saskatchewan) R2.3.1.4. | environmental constraints. |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  |  | 20301400 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000020 | RP-2023-10-03-0000089 | 1. | RP-2023-10-03-0000090 | TOP-003-5 (Saskatchewan) R2.3.2.1. | design temperature; or |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  |  | 20302100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000020 | RP-2023-10-03-0000089 | 2. | RP-2023-10-03-0000091 | TOP-003-5 (Saskatchewan) R2.3.2.2. | historical operating temperature; or |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  |  | 20302200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000020 | RP-2023-10-03-0000089 | 3. | RP-2023-10-03-0000092 | TOP-003-5 (Saskatchewan) R2.3.2.3. | current cold weather performance temperature determined by an engineering analysis. |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  |  | 20302300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000020 |  | 1. | RP-2023-10-03-0000081 | TOP-003-5 (Saskatchewan) R2.1. | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  |  | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000020 |  | 2. | RP-2023-10-03-0000082 | TOP-003-5 (Saskatchewan) R2.2. | Provisions for notification of current Protection System and Remedial Action Scheme status or degradation that impacts System reliability. |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  |  | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000020 |  | 3. | RP-2023-10-03-0000083 | TOP-003-5 (Saskatchewan) R2.3. | Provisions for notification of BES generating unit(s) status during local forecasted cold weather to include: |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  |  | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000020 |  | 4. | RP-2023-10-03-0000093 | TOP-003-5 (Saskatchewan) R2.4. | A periodicity for providing data. |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  |  | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000020 |  | 5. | RP-2023-10-03-0000094 | TOP-003-5 (Saskatchewan) R2.5. | The deadline by which the respondent is to provide the indicated data. |  | BA | BA | [21 empty] | 2023-07-01 |  |  |  |  | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000023 |  | 1. | RP-2023-10-03-0000095 | TOP-003-5 (Saskatchewan) R5.1. | A mutually agreeable format |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000023 |  | 2. | RP-2023-10-03-0000096 | TOP-003-5 (Saskatchewan) R5.2. | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-03-0000006 | RQ-2023-10-03-0000023 |  | 3. | RP-2023-10-03-0000097 | TOP-003-5 (Saskatchewan) R5.3. | A mutually agreeable security protocol |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  |  | 2023-07-01 |  |  |  |  | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-04-0000001 | RQ-2023-10-04-0000001 |  | 1. | RP-2023-10-04-0000001 | PRC-002-2 (Manitoba) R1.1. | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-2, Attachment 1. |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 110000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000001 |  | 2. | RP-2023-10-04-0000002 | PRC-002-2 (Manitoba) R1.2. | Notify other owners of BES Elements connected to those BES buses, if any, within 90-calendar days of completion of Part 1.1, that those BES Elements require SER data and/or FR data. |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 120000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000001 |  | 3. | RP-2023-10-04-0000003 | PRC-002-2 (Manitoba) R1.3. | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners, if any, in accordance with Part 1.2, and implement the re-evaluated list of BES buses as per the Implementation Plan. |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 130000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000003 | RP-2023-10-04-0000005 | 1. | RP-2023-10-04-0000006 | PRC-002-2 (Manitoba) R3.2.1. | Transformers that have a low-side operating voltage of 100kV or above. |  | GO, PCPA, RC, TO |  |  |  |  | GO |  |  |  |  | PCPA |  | RC | [5 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 321000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000003 | RP-2023-10-04-0000005 | 2. | RP-2023-10-04-0000007 | PRC-002-2 (Manitoba) R3.2.2. | Transmission Lines. |  | GO, PCPA, RC, TO |  |  |  |  | GO |  |  |  |  | PCPA |  | RC | [5 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 322000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000003 |  | 1. | RP-2023-10-04-0000004 | PRC-002-2 (Manitoba) R3.1. | Phase-to-neutral voltage for each phase of each specified BES bus. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 310000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000003 |  | 2. | RP-2023-10-04-0000005 | PRC-002-2 (Manitoba) R3.2. | Each phase current and the residual or neutral current for the following BES Elements: |  | GO, PCPA, RC, TO |  |  |  |  | GO |  |  |  |  | PCPA |  | RC | [5 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 320000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000004 | RP-2023-10-04-0000010 | 1. | RP-2023-10-04-0000011 | PRC-002-2 (Manitoba) R4.3.1. | Neutral (residual) overcurrent. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 431000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000004 | RP-2023-10-04-0000010 | 2. | RP-2023-10-04-0000012 | PRC-002-2 (Manitoba) R4.3.2. | Phase undervoltage or overcurrent. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 432000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000004 |  | 1. | RP-2023-10-04-0000008 | PRC-002-2 (Manitoba) R4.1. | A single record or multiple records that include: • A pre-trigger record length of at least two cycles and a total record length of at least 30-cycles for the same trigger point, or • At least two cycles of the pre-trigger data, the first three cycles of the post- trigger data, and the final cycle of the fault as seen by the fault recorder. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 410000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000004 |  | 2. | RP-2023-10-04-0000009 | PRC-002-2 (Manitoba) R4.2. | A minimum recording rate of 16 samples per cycle. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 420000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000004 |  | 3. | RP-2023-10-04-0000010 | PRC-002-2 (Manitoba) R4.3. | Trigger settings for at least the following: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 430000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000005 | RP-2023-10-04-0000013 | 1. | RP-2023-10-04-0000014 | PRC-002-2 (Manitoba) R5.1.1. | Generating resource(s) with: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 511000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000005 | RP-2023-10-04-0000013 | 2. | RP-2023-10-04-0000018 | PRC-002-2 (Manitoba) R5.1.2. | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 512000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000005 | RP-2023-10-04-0000013 | 3. | RP-2023-10-04-0000019 | PRC-002-2 (Manitoba) R5.1.3. | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 513000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000005 | RP-2023-10-04-0000013 | 4. | RP-2023-10-04-0000020 | PRC-002-2 (Manitoba) R5.1.4. | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 514000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000005 | RP-2023-10-04-0000013 | 5. | RP-2023-10-04-0000021 | PRC-002-2 (Manitoba) R5.1.5. | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 515000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000005 | RP-2023-10-04-0000014 | 1. | RP-2023-10-04-0000015 | PRC-002-2 (Manitoba) R5.1.1.1. | Gross individual nameplate rating greater than or equal to 500 MVA. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 50101100 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000005 | RP-2023-10-04-0000014 | 2. | RP-2023-10-04-0000016 | PRC-002-2 (Manitoba) R5.1.1.2. | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 50101200 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000005 | RP-2023-10-04-0000017 | 1. | RP-2023-10-04-0000022 | PRC-002-2 (Manitoba) R5.2.1. | One BES Element; and |  | GO, PCPA, RC, TO |  |  |  |  | GO |  |  |  |  | PCPA |  | RC | [5 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 521000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000005 | RP-2023-10-04-0000017 | 2. | RP-2023-10-04-0000023 | PRC-002-2 (Manitoba) R5.2.2. | One BES Element per 3,000 MW of the Responsible Entity’s historical simultaneous peak System Demand. |  | GO, PCPA, RC, TO |  |  |  |  | GO |  |  |  |  | PCPA |  | RC | [5 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 522000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000005 |  | 1. | RP-2023-10-04-0000013 | PRC-002-2 (Manitoba) R5.1. | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 510000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000005 |  | 2. | RP-2023-10-04-0000017 | PRC-002-2 (Manitoba) R5.2. | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: |  | GO, PCPA, RC, TO |  |  |  |  | GO |  |  |  |  | PCPA |  | RC | [5 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 520000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000005 |  | 3. | RP-2023-10-04-0000024 | PRC-002-2 (Manitoba) R5.3. | Notify all owners of identified BES Elements, within 90-calendar days of completion of Part 5.1, that their respective BES Elements require DDR data when requested. |  | GO, PCPA, RC, TO |  |  |  |  | GO |  |  |  |  | PCPA |  | RC | [5 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 530000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000005 |  | 4. | RP-2023-10-04-0000025 | PRC-002-2 (Manitoba) R5.4. | Re-evaluate all BES Elements at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3 to implement the re-evaluated list of BES Elements as per the Implementation Plan. |  | GO, PCPA, RC, TO |  |  |  |  | GO |  |  |  |  | PCPA |  | RC | [5 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 540000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000006 |  | 1. | RP-2023-10-04-0000026 | PRC-002-2 (Manitoba) R6.1. | One phase-to-neutral or positive sequence voltage. |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 610000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000006 |  | 2. | RP-2023-10-04-0000027 | PRC-002-2 (Manitoba) R6.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 620000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000006 |  | 3. | RP-2023-10-04-0000028 | PRC-002-2 (Manitoba) R6.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 630000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000006 |  | 4. | RP-2023-10-04-0000029 | PRC-002-2 (Manitoba) R6.4. | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. |  | TO | [17 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 640000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000007 |  | 1. | RP-2023-10-04-0000030 | PRC-002-2 (Manitoba) R7.1. | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  |  | 710000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000007 |  | 2. | RP-2023-10-04-0000031 | PRC-002-2 (Manitoba) R7.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  |  | 720000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000007 |  | 3. | RP-2023-10-04-0000032 | PRC-002-2 (Manitoba) R7.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  |  | 730000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000007 |  | 4. | RP-2023-10-04-0000033 | PRC-002-2 (Manitoba) R7.4. | Frequency of at least one of the voltages in Requirement R7, Part 7.1. |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  |  | 740000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000008 |  | 1. | RP-2023-10-04-0000034 | PRC-002-2 (Manitoba) R8.1. | Triggered record lengths of at least three minutes. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-04-0000001 | RQ-2023-10-04-0000008 |  | 2. | RP-2023-10-04-0000035 | PRC-002-2 (Manitoba) R8.2. | At least one of the following three triggers: - Off nominal frequency trigger set at: Low High o Eastern Interconnection <59.75 Hz >61.0 Hz o Western Interconnection <59.55 Hz >61.0 Hz o ERCOT Interconnection <59.35 Hz >61.0 Hz o Hydro-Quebec Interconnection <58.55 Hz >61.5 Hz · Rate of change of frequency trigger set at: o Eastern Interconnection < -0.03125 Hz/sec > 0.125 Hz/sec o Western Interconnection < -0.05625 Hz/sec > 0.125 Hz/sec o ERCOT Interconnection < -0.08125 Hz/sec > 0.125 Hz/sec o Hydro-Quebec Interconnection < -0.18125 Hz/sec > 0.1875 Hz/sec - Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-04-0000001 | RQ-2023-10-04-0000010 |  | 1. | RP-2023-10-04-0000036 | PRC-002-2 (Manitoba) R10.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. |  | GO, PCPA, RC, TO |  |  |  |  | GO |  |  |  |  | PCPA |  | RC | [5 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 101000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000010 |  | 2. | RP-2023-10-04-0000037 | PRC-002-2 (Manitoba) R10.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. |  | GO, PCPA, RC, TO |  |  |  |  | GO |  |  |  |  | PCPA |  | RC | [5 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 102000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000011 |  | 1. | RP-2023-10-04-0000038 | PRC-002-2 (Manitoba) R11.1. | Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 111000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000011 |  | 2. | RP-2023-10-04-0000039 | PRC-002-2 (Manitoba) R11.2. | Data subject to Part 11.1 will be provided within 30-calendar days of a request unless an extension is granted by the requestor. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 112000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000011 |  | 3. | RP-2023-10-04-0000040 | PRC-002-2 (Manitoba) R11.3. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 113000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000011 |  | 4. | RP-2023-10-04-0000041 | PRC-002-2 (Manitoba) R11.4. | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 114000000 | MRO-MB
ST-2023-10-04-0000001 | RQ-2023-10-04-0000011 |  | 5. | RP-2023-10-04-0000042 | PRC-002-2 (Manitoba) R11.5. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. |  | GO, TO |  |  |  |  | GO | [12 empty] | TO |  |  |  |  | 2023-07-01 |  |  |  |  | 115000000 | MRO-MB
ST-2023-10-25-0000001 | RQ-2023-10-25-0000003 |  | 1. | RP-2023-10-25-0000001 | PRC-024-3 (Manitoba) R3.1. | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: - Identification of a regulatory or equipment limitation. - Repair of the equipment causing the limitation that removes the limitation. - Replacement of the equipment causing the limitation with equipment that removes the limitation. - Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. |  | GO |  |  |  |  | GO | [17 empty] | 2023-07-01 |  |  |  | 4.1.1 Generator Owners that apply protection listed in Section 4.2.1. 4.1.2 Transmission Owners (in the Quebec Interconnection only) that own a BES generator step-up (GSU) transformer or main power transformer (MPT)1 and apply protection listed in Section 4.2.1. 4.1.3 Planning Coordinators (in the Quebec Interconnection only) 4.2. Facilities2: 4.2.1 Frequency, voltage, and volts per hertz protection (whether provided by relaying or functions within associated control systems) that respond to electrical signals and: (i) directly trip the generating resource(s); or (ii) provide signals to the generating resource(s) to either trip or cease injecting current; and are applied to the following: 4.2.1.1 BES generating resource(s). 4.2.1.2 BES GSU transformer(s). 4.2.1.3 High side of the generator-connected unit auxiliary transformer3 (UAT) installed on BES generating resource(s). 4.2.1.4 Individual dispersed power producing resource(s) identified in the BES Definition, Inclusion I4. 4.2.1.5 Elements that are designed primarily for the delivery of capacity from the individual dispersed power producing resources identified in the BES Definition, Inclusion I4, to the point where those resources aggregate to greater than 75 MVA 4.2.1.6 MPT4 of resource(s) identified in the BES Definition, Inclusion I4. 4.2.2 Exemptions: Protection on all auxiliary equipment within the generating Facility. | 310000000 | MRO-MB
ST-2023-10-31-0000001 | RQ-2023-10-31-0000004 |  | 1. | RP-2023-10-31-0000001 | TOP-002-5 R4.1. | Expected generation resource commitment and dispatch; |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-31-0000001 | RQ-2023-10-31-0000004 |  | 2. | RP-2023-10-31-0000002 | TOP-002-5 R4.2. | Interchange scheduling; |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-31-0000001 | RQ-2023-10-31-0000004 |  | 3. | RP-2023-10-31-0000003 | TOP-002-5 R4.3. | Demand patterns; and |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-31-0000001 | RQ-2023-10-31-0000004 |  | 4. | RP-2023-10-31-0000004 | TOP-002-5 R4.4. | Capacity and energy reserve requirements, including deliverability capability. |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-31-0000001 | RQ-2023-10-31-0000008 | RP-2023-10-31-0000006 | 1. | RP-2023-10-31-0000007 | TOP-002-5 R8.2.1. | Capability and availability; |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 821000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-31-0000001 | RQ-2023-10-31-0000008 | RP-2023-10-31-0000006 | 2. | RP-2023-10-31-0000008 | TOP-002-5 R8.2.2. | Fuel supply and inventory concerns; |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 822000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-31-0000001 | RQ-2023-10-31-0000008 | RP-2023-10-31-0000006 | 3. | RP-2023-10-31-0000009 | TOP-002-5 R8.2.3. | Start-up issues; |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 823000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-31-0000001 | RQ-2023-10-31-0000008 | RP-2023-10-31-0000006 | 4. | RP-2023-10-31-0000010 | TOP-002-5 R8.2.4. | Fuel switching capabilities; and |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 824000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-31-0000001 | RQ-2023-10-31-0000008 | RP-2023-10-31-0000006 | 5. | RP-2023-10-31-0000011 | TOP-002-5 R8.2.5. | Environmental constraints. |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 825000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-31-0000001 | RQ-2023-10-31-0000008 | RP-2023-10-31-0000012 | 1. | RP-2023-10-31-0000013 | TOP-002-5 R8.3.1. | Expected generation resource commitment and dispatch; |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 831000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-31-0000001 | RQ-2023-10-31-0000008 | RP-2023-10-31-0000012 | 2. | RP-2023-10-31-0000014 | TOP-002-5 R8.3.2. | Demand patterns |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 832000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-31-0000001 | RQ-2023-10-31-0000008 | RP-2023-10-31-0000012 | 3. | RP-2023-10-31-0000015 | TOP-002-5 R8.3.3. | Capacity and energy reserve requirements, including deliverability capability; and |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 833000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-31-0000001 | RQ-2023-10-31-0000008 | RP-2023-10-31-0000012 | 4. | RP-2023-10-31-0000016 | TOP-002-5 R8.3.4. | Weather forecast. |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 834000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-31-0000001 | RQ-2023-10-31-0000008 |  | 1. | RP-2023-10-31-0000005 | TOP-002-5 R8.1. | A methodology for identifying an extreme cold weather period within each Balancing Authority Area; |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-31-0000001 | RQ-2023-10-31-0000008 |  | 2. | RP-2023-10-31-0000006 | TOP-002-5 R8.2. | A methodology to determine an adequate reserve margin during the extreme cold weather period considering the generating unit(s) operating limitations in previous extreme cold weather periods that includes, but is not limited to: |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-10-31-0000001 | RQ-2023-10-31-0000008 |  | 3. | RP-2023-10-31-0000012 | TOP-002-5 R8.3. | A methodology to determine a five-day hourly forecast during the identified extreme cold weather periods that includes, but is not limited to: |  | BA | BA | [21 empty] | 2025-10-01 |  |  |  |  | 830000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000001 | RP-2023-11-02-0000002 | 1. | RP-2023-11-02-0000003 | EOP-011-4 R1.2.1. | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; |  | BA, RC | BA | [10 empty] | RC | [15 empty] | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000001 | RP-2023-11-02-0000002 | 2. | RP-2023-11-02-0000004 | EOP-011-4 R1.2.2. | Cancellation or recall of Transmission and generation outages; |  | BA, RC | BA | [10 empty] | RC | [15 empty] | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000001 | RP-2023-11-02-0000002 | 3. | RP-2023-11-02-0000005 | EOP-011-4 R1.2.3. | Transmission system reconfiguration; |  | BA, RC | BA | [10 empty] | RC | [15 empty] | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000001 | RP-2023-11-02-0000002 | 4. | RP-2023-11-02-0000006 | EOP-011-4 R1.2.4. | Redispatch of generation request; |  | BA, RC | BA | [10 empty] | RC | [15 empty] | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000001 | RP-2023-11-02-0000002 | 5. | RP-2023-11-02-0000007 | EOP-011-4 R1.2.5. | Operator-controlled manual Load shed, undervoltage load shed (UVLS), or underfrequency load shed (UFLS) during an Emergency that accounts for each of the following: |  | BA, RC | BA | [10 empty] | RC | [15 empty] | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000001 | RP-2023-11-02-0000002 | 6. | RP-2023-11-02-0000013 | EOP-011-4 R1.2.6. | Provisions to determine reliability impacts of: |  | BA, RC | BA | [10 empty] | RC | [15 empty] | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000001 | RP-2023-11-02-0000007 | 1. | RP-2023-11-02-0000008 | EOP-011-4 R1.2.5.1. | Provisions for manual Load shedding capable of being implemented in a timeframe adequate for mitigating the Emergency; |  | BA, RC | BA | [10 empty] | RC | [15 empty] | 10205100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000001 | RP-2023-11-02-0000007 | 2. | RP-2023-11-02-0000009 | EOP-011-4 R1.2.5.2. | Provisions to minimize the overlap of circuits that are designated for manual Load shed, UVLS, or UFLS and circuits that serve designated critical loads which are essential to the reliability of the BES; |  | BA, RC | BA | [10 empty] | RC | [15 empty] | 10205200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000001 | RP-2023-11-02-0000007 | 3. | RP-2023-11-02-0000010 | EOP-011-4 R1.2.5.3. | Provisions to minimize the overlap of circuits that are designated for manual Load shed and circuits that are utilized for UFLS or UVLS; |  | BA, RC | BA | [10 empty] | RC | [15 empty] | 10205300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000001 | RP-2023-11-02-0000007 | 4. | RP-2023-11-02-0000011 | EOP-011-4 R1.2.5.4. | Provisions for limiting the utilization of UFLS or UVLS circuits for manual Load shed to situations where warranted by system conditions; |  | BA, RC | BA | [10 empty] | RC | [15 empty] | 10205400 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000001 | RP-2023-11-02-0000007 | 5. | RP-2023-11-02-0000012 | EOP-011-4 R1.2.5.5. | Provisions for the identification and prioritization of designated critical natural gas infrastructure loads which are essential to the reliability of the BES as defined by the Applicable Entity; and |  | BA, RC | BA | [10 empty] | RC | [15 empty] | 10205500 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000001 | RP-2023-11-02-0000013 | 1. | RP-2023-11-02-0000014 | EOP-011-4 R1.2.6.1. | Cold weather conditions; and |  | BA, RC | BA | [10 empty] | RC | [15 empty] | 10206100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000001 | RP-2023-11-02-0000013 | 2. | RP-2023-11-02-0000015 | EOP-011-4 R1.2.6.2. | Extreme weather conditions. |  | BA, RC | BA | [10 empty] | RC | [15 empty] | 10206200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000001 |  | 1. | RP-2023-11-02-0000001 | EOP-011-4 R1.1. | Roles and responsibilities for activating the Operating Plan(s); |  | BA, RC | BA | [10 empty] | RC | [15 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000001 |  | 2. | RP-2023-11-02-0000002 | EOP-011-4 R1.2. | Processes to prepare for and mitigate Emergencies including: |  | BA, RC | BA | [10 empty] | RC | [15 empty] | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000017 | 1. | RP-2023-11-02-0000018 | EOP-011-4 R2.2.1. | Notification to its Reliability Coordinator to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; |  | BA | BA | [26 empty] | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000017 | 10. | RP-2023-11-02-0000032 | EOP-011-4 R2.2.10. | Provisions to determine reliability impacts of: |  | BA | BA | [26 empty] | 221000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000017 | 2. | RP-2023-11-02-0000019 | EOP-011-4 R2.2.2. | Requesting an Energy Emergency Alert, per Attachment 1; |  | BA | BA | [26 empty] | 222000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000017 | 3. | RP-2023-11-02-0000021 | EOP-011-4 R2.2.3. | Managing generating resources in its Balancing Authority Area to address: |  | BA | BA | [26 empty] | 223000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000017 | 4. | RP-2023-11-02-0000026 | EOP-011-4 R2.2.4. | Public appeals for voluntary Load reductions; |  | BA | BA | [26 empty] | 224000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000017 | 5. | RP-2023-11-02-0000027 | EOP-011-4 R2.2.5. | Requests to government agencies to implement their programs to achieve necessary energy reductions; |  | BA | BA | [26 empty] | 225000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000017 | 6. | RP-2023-11-02-0000028 | EOP-011-4 R2.2.6. | Reduction of internal utility energy use; |  | BA | BA | [26 empty] | 226000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000017 | 7. | RP-2023-11-02-0000029 | EOP-011-4 R2.2.7. | Use of Interruptible Load, curtailable Load, and demand response; |  | BA | BA | [26 empty] | 227000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000017 | 8. | RP-2023-11-02-0000030 | EOP-011-4 R2.2.8. | Provisions for excluding critical natural gas infrastructure loads which are essential to the reliability of the BES, as defined by the Applicable Entity, as Interruptible Load, curtailable Load, and demand response during extreme cold weather periods within each Balancing Authority Area; |  | BA | BA | [26 empty] | 228000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000017 | 9. | RP-2023-11-02-0000031 | EOP-011-4 R2.2.9. | Provisions for Transmission Operators to implement operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding in accordance with Requirement R1 Part 1.2.5; and |  | BA | BA | [26 empty] | 229000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000021 | 1. | RP-2023-11-02-0000022 | EOP-011-4 R2.2.3.1. | Capability and availability; |  | BA | BA | [26 empty] | 20203100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000021 | 2. | RP-2023-11-02-0000023 | EOP-011-4 R2.2.3.2. | Fuel supply and inventory concerns; |  | BA | BA | [26 empty] | 20203200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000021 | 3. | RP-2023-11-02-0000024 | EOP-011-4 R2.2.3.3. | Fuel switching capabilities; and |  | BA | BA | [26 empty] | 20203300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000021 | 4. | RP-2023-11-02-0000025 | EOP-011-4 R2.2.3.4. | Environmental constraints. |  | BA | BA | [26 empty] | 20203400 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000032 | 1. | RP-2023-11-02-0000033 | EOP-011-4 R2.2.10.1. | Cold weather conditions; and |  | BA | BA | [26 empty] | 20210100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 | RP-2023-11-02-0000032 | 2. | RP-2023-11-02-0000034 | EOP-011-4 R2.2.10.2. | Extreme weather conditions. |  | BA | BA | [26 empty] | 20210200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 |  | 1. | RP-2023-11-02-0000016 | EOP-011-4 R2.1. | Roles and responsibilities for activating the Operating Plan(s); |  | BA | BA | [26 empty] | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000002 |  | 2. | RP-2023-11-02-0000017 | EOP-011-4 R2.2. | Processes to prepare for and mitigate Emergencies including: |  | BA | BA | [26 empty] | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000003 | RP-2023-11-02-0000035 | 1. | RP-2023-11-02-0000036 | EOP-011-4 R3.1.1. | Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [8 empty] | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000003 | RP-2023-11-02-0000035 | 2. | RP-2023-11-02-0000037 | EOP-011-4 R3.1.2. | Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [8 empty] | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000003 | RP-2023-11-02-0000035 | 3. | RP-2023-11-02-0000038 | EOP-011-4 R3.1.3. | Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [8 empty] | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000003 |  | 1. | RP-2023-11-02-0000035 | EOP-011-4 R3.1. | Within 30 calendar days of receipt, the Reliability Coordinator shall: |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [8 empty] | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000008 | RP-2023-11-02-0000039 | 1. | RP-2023-11-02-0000040 | EOP-011-4 R8.1.1. | Provisions for manual Load shedding capable of being implemented in a timeframe adequate for mitigating the Emergency |  | DP, DP-UFLS, TO, TOP |  | DP | DP-UFLS | [14 empty] | TO | TOP | [8 empty] | 811000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000008 | RP-2023-11-02-0000039 | 2. | RP-2023-11-02-0000041 | EOP-011-4 R8.1.2. | Provisions to minimize the overlap of circuits that are designated for manual, undervoltage, or underfrequency Load shed and circuits that serve designated critical loads which are essential to the reliability of the BES; |  | DP, DP-UFLS, TO, TOP |  | DP | DP-UFLS | [14 empty] | TO | TOP | [8 empty] | 812000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000008 | RP-2023-11-02-0000039 | 3. | RP-2023-11-02-0000042 | EOP-011-4 R8.1.3. | Provisions to minimize the overlap of circuits that are designated for manual Load shed and circuits that are utilized for UFLS or UVLS; |  | DP, DP-UFLS, TO, TOP |  | DP | DP-UFLS | [14 empty] | TO | TOP | [8 empty] | 813000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000008 | RP-2023-11-02-0000039 | 4. | RP-2023-11-02-0000043 | EOP-011-4 R8.1.4. | Provisions for limiting the utilization of UFLS or UVLS circuits for manual Load shed to situations where warranted by system conditions; and |  | DP, DP-UFLS, TO, TOP |  | DP | DP-UFLS | [14 empty] | TO | TOP | [8 empty] | 814000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000008 | RP-2023-11-02-0000039 | 5. | RP-2023-11-02-0000044 | EOP-011-4 R8.1.5. | Provisions for the identification and prioritization of designated critical natural gas infrastructure loads which are essential to the reliability of the BES as defined by the Applicable Entity. |  | DP, DP-UFLS, TO, TOP |  | DP | DP-UFLS | [14 empty] | TO | TOP | [8 empty] | 815000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000008 |  | 1. | RP-2023-11-02-0000039 | EOP-011-4 R8.1. | Operator-controlled manual Load shedding, undervoltage Load shedding, or underfrequency Load shedding during an Emergency that accounts for each of the following: |  | DP, DP-UFLS, TO, TOP |  | DP | DP-UFLS | [14 empty] | TO | TOP | [6 empty] | See Implementation Plan for Project 2021-07. As provided therein, each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner that receives notification from the Transmission Operator that it is required to assist in the mitigation of operating Emergencies in the Transmission Operator Area under Requirement R7 shall become compliant with Requirement R8 within 30 calendar months of the notification. |  | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-11-02-0000001 | RQ-2023-11-02-0000008 |  | 2. | RP-2023-11-02-0000045 | EOP-011-4 R8.2. | Provisions to provide the Load shedding plan to the Transmission Operator for review. |  | DP, DP-UFLS, TO, TOP |  | DP | DP-UFLS | [14 empty] | TO | TOP | [6 empty] | See Implementation Plan for Project 2021-07. As provided therein, each Distribution Provider, UFLS-Only Distribution Provider, and Transmission Owner that receives notification from the Transmission Operator that it is required to assist in the mitigation of operating Emergencies in the Transmission Operator Area under Requirement R7 shall become compliant with Requirement R8 within 30 calendar months of the notification. |  | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-12-18-0000001 | RQ-2023-12-18-0000001 |  | 1. | RP-2023-12-18-0000001 | CIP-012-2 R1.1. | 1.1. Identification of method(s) used to mitigate the risk(s) posed by unauthorized disclosure and unauthorized modification of data used in Real-time Assessment and Real-time monitoring while such data is being transmitted between Control Centers; |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-12-18-0000001 | RQ-2023-12-18-0000001 |  | 2. | RP-2023-12-18-0000002 | CIP-012-2 R1.2. | Identification of method(s) used to mitigate the risk(s) posed by the loss of the ability to communicate Real-time Assessment and Real-time monitoring data between Control Centers; |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-12-18-0000001 | RQ-2023-12-18-0000001 |  | 3. | RP-2023-12-18-0000003 | CIP-012-2 R1.3. | Identification of method(s) used to initiate the recovery of communication links used to transmit Real-time Assessment and Real-time monitoring data between Control Centers; |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-12-18-0000001 | RQ-2023-12-18-0000001 |  | 4. | RP-2023-12-18-0000004 | CIP-012-2 R1.4. | Identification of where the Responsible Entity implemented method(s) as required in Parts 1.1 and 1.2; and |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2023-12-18-0000001 | RQ-2023-12-18-0000001 |  | 5. | RP-2023-12-18-0000005 | CIP-012-2 R1.5. | If the Control Centers are owned or operated by different ResponsibleEntities, identification of the responsibilities of each Responsible Entity for implementing method(s) as required in Parts 1.1, 1.2, and 1.3. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000001 | RP-2024-02-22-0000001 | 1. | RP-2024-02-22-0000003 | EOP-012-2 R1.1.1. | If the re-calculated Extreme Cold Weather Temperature is lower than the previous Extreme Cold Weather Temperature, the entity shall review and update its cold weather preparedness plan(s) under Requirement R4 within six (6) months of the recalculation. If new corrective actions are needed to provide the required operational capability under Requirement R2 or R3, the entity shall develop a Corrective Action Plan within 6 months of the recalculation. |  | GO |  |  |  |  | GO | [22 empty] | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000001 | RP-2024-02-22-0000002 | 1. | RP-2024-02-22-0000004 | EOP-012-2 R1.2.1. | Generating unit(s) operating limitations in cold weather to include: |  | GO |  |  |  |  | GO | [22 empty] | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000001 | RP-2024-02-22-0000002 | 2. | RP-2024-02-22-0000010 | EOP-012-2 R1.2.2. | Generating unit(s) minimum: - Design temperature, and if available, the concurrent wind speed and precipitation; - Historical operating temperature at least one hour in duration, and if available, the concurrent wind speed and precipitation; or - Current cold weather performance temperature determined by an engineering analysis, which includes the concurrent wind speed and precipitation. |  | GO |  |  |  |  | GO | [22 empty] | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000001 | RP-2024-02-22-0000004 | 1. | RP-2024-02-22-0000005 | EOP-012-2 R1.2.1.1. | Capability and availability; |  | GO |  |  |  |  | GO | [22 empty] | 10201100 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000001 | RP-2024-02-22-0000004 | 2. | RP-2024-02-22-0000006 | EOP-012-2 R1.2.1.2. | Fuel supply and inventory concerns; |  | GO |  |  |  |  | GO | [22 empty] | 10201200 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000001 | RP-2024-02-22-0000004 | 3. | RP-2024-02-22-0000007 | EOP-012-2 R1.2.1.3. | Start-up issues; |  | GO |  |  |  |  | GO | [22 empty] | 10201300 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000001 | RP-2024-02-22-0000004 | 4. | RP-2024-02-22-0000008 | EOP-012-2 R1.2.1.4. | Fuel switching capabilities; and |  | GO |  |  |  |  | GO | [22 empty] | 10201400 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000001 | RP-2024-02-22-0000004 | 5. | RP-2024-02-22-0000009 | EOP-012-2 R1.2.1.5. | Environmental constraints. |  | GO |  |  |  |  | GO | [22 empty] | 10201500 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000001 |  | 1. | RP-2024-02-22-0000001 | EOP-012-2 R1.1. | Calculate the Extreme Cold Weather Temperature for each of its applicable unit(s) and identify the calculation date and source of temperature data; and |  | GO |  |  |  |  | GO | [22 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000001 |  | 2. | RP-2024-02-22-0000002 | EOP-012-2 R1.2. | Identify generating unit(s) cold weather data, to include: |  | GO |  |  |  |  | GO | [22 empty] | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000004 |  | 1. | RP-2024-02-22-0000011 | EOP-012-2 R4.1. | The lowest calculated Extreme Cold Weather Temperature for each unit, as determined in Requirement R1;3 |  | GO |  |  |  |  | GO | [22 empty] | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000004 |  | 2. | RP-2024-02-22-0000012 | EOP-012-2 R4.2. | The generating unit cold weather data, as determined in Requirement R1.2; |  | GO |  |  |  |  | GO | [22 empty] | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000004 |  | 3. | RP-2024-02-22-0000013 | EOP-012-2 R4.3. | Documentation identifying Generator Cold Weather Critical Components; |  | GO |  |  |  |  | GO | [22 empty] | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000004 |  | 4. | RP-2024-02-22-0000014 | EOP-012-2 R4.4. | Documentation of freeze protection measures implemented on Generator Cold Weather Critical Components which includes measures used to reduce the cooling effects of wind determined necessary by the Generator Owner to protect against heat loss, and where applicable, the effects of freezing precipitation (e.g., sleet, snow, ice, and freezing rain); and |  | GO |  |  |  |  | GO | [22 empty] | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000004 |  | 5. | RP-2024-02-22-0000015 | EOP-012-2 R4.5. | Annual inspection and maintenance of generating unit(s) freeze protection measures. |  | GO |  |  |  |  | GO | [22 empty] | 450000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000006 |  | 1. | RP-2024-02-22-0000016 | EOP-012-2 R6.1. | A summary of the identified cause(s) for the Generator Cold Weather Reliability Event, where applicable, and any relevant associated data; |  | GO |  |  |  |  | GO | [22 empty] | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000006 |  | 2. | RP-2024-02-22-0000017 | EOP-012-2 R6.2. | A review of applicability to similar equipment at generating units owned by the Generator Owner; and |  | GO |  |  |  |  | GO | [22 empty] | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000006 |  | 3. | RP-2024-02-22-0000018 | EOP-012-2 R6.3. | An identification of operating limitations or impacts to the cold weather preparedness plan that would apply until execution of the corrective action(s) identified in the Corrective Action Plan. |  | GO |  |  |  |  | GO | [22 empty] | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000007 | RP-2024-02-22-0000019 | 1. | RP-2024-02-22-0000020 | EOP-012-2 R7.1.1. | List the action(s) which address(es) existing equipment or freeze protection measures, if any, to be completed within 24 calendar months of completing development of the Corrective Action Plan; |  | GO |  |  |  |  | GO | [22 empty] | 711000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000007 | RP-2024-02-22-0000019 | 2. | RP-2024-02-22-0000021 | EOP-012-2 R7.1.2. | List the action(s) which require(s) new equipment or freeze protection measures, if any, to be completed within 48 calendar months of completing development of the Corrective Action Plan; and |  | GO |  |  |  |  | GO | [22 empty] | 712000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000007 | RP-2024-02-22-0000019 | 3. | RP-2024-02-22-0000022 | EOP-012-2 R7.1.3. | List the updates to the cold weather preparedness plan required under Requirement R4 to identify the updates or additions to the Generator Cold Weather Critical Components and their freeze protection measures; |  | GO |  |  |  |  | GO | [22 empty] | 713000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000007 |  | 1. | RP-2024-02-22-0000019 | EOP-012-2 R7.1. | Include a timetable for implementing the selected corrective action(s) that shall: |  | GO |  |  |  |  | GO | [22 empty] | 710000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000007 |  | 2. | RP-2024-02-22-0000023 | EOP-012-2 R7.2. | Implement the Corrective Action Plan in accordance with the specified timetables in Requirement R7 Part 7.1; |  | GO |  |  |  |  | GO | [22 empty] | 720000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000007 |  | 3. | RP-2024-02-22-0000024 | EOP-012-2 R7.3. | Update the Corrective Action Plan action(s) and timetable(s), with justification, if corrective action(s) change or timetable(s) exceed the timelines in Requirement R7 Part 7.1; and |  | GO |  |  |  |  | GO | [22 empty] | 730000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000007 |  | 4. | RP-2024-02-22-0000025 | EOP-012-2 R7.4. | Document in a declaration, with justification, any Generator Cold Weather Constraint that precludes the Generator Owner from implementing selected action(s) contained within the Corrective Action Plan. |  | GO |  |  |  |  | GO | [22 empty] | 740000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000008 |  | 1. | RP-2024-02-22-0000026 | EOP-012-2 R8.1. | Review the Generator Cold Weather Constraint declaration at least every five calendar years or as needed when a change of status to the Generator Cold Weather Constraint occurs; and |  | GO |  |  |  |  | GO | [22 empty] | 810000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-02-22-0000001 | RQ-2024-02-22-0000008 |  | 2. | RP-2024-02-22-0000027 | EOP-012-2 R8.2. | Update the operating limitations associated with capability and availability under Requirement R1 Part R1.2 if applicable. |  | GO |  |  |  |  | GO | [22 empty] | 820000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-09-0000001 | RQ-2024-05-09-0000001 |  | 1. | RP-2024-05-09-0000001 | CIP-015-1 R1.1. | Implement, using a risk-based rationale, network data feed(s) to monitor network activity; including connections, devices, and network communications. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-09-0000001 | RQ-2024-05-09-0000001 |  | 2. | RP-2024-05-09-0000002 | CIP-015-1 R1.2. | Implement one or more method(s) to detect anomalous network activity using the network data feed(s) from Part 1.1. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-09-0000001 | RQ-2024-05-09-0000001 |  | 3. | RP-2024-05-09-0000003 | CIP-015-1 R1.3. | Implement one or more method(s) to evaluate anomalous network activity detected in Part 1.2. to determine further action(s). |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-09-0000002 | RQ-2024-05-09-0000004 |  | 1. | RP-2024-05-09-0000004 | CIP-002-7 R1.1. | Identify each of the high impact BCS according to Attachment 1, Section 1, if any, at each asset; |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-09-0000002 | RQ-2024-05-09-0000004 |  | 2. | RP-2024-05-09-0000005 | CIP-002-7 R1.2. | Identify each of the medium impact BCS according to Attachment 1, Section 2, if any, at each asset; and |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-09-0000002 | RQ-2024-05-09-0000004 |  | 3. | RP-2024-05-09-0000006 | CIP-002-7 R1.3. | Identify each asset that contains a low impact BCS according to Attachment 1, Section 3, if any (a discrete list of low impact BCS is not required). |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-09-0000002 | RQ-2024-05-09-0000005 |  | 1. | RP-2024-05-09-0000007 | CIP-002-7 R2.1. | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-09-0000002 | RQ-2024-05-09-0000005 |  | 2. | RP-2024-05-09-0000008 | CIP-002-7 R2.2. | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000001 | 1. | RP-2024-05-10-0000011 | CIP-003-10 R1.1.1. | Personnel and training (CIP-004); | [29 empty] | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000001 | 2. | RP-2024-05-10-0000012 | CIP-003-10 R1.1.2. | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; | [29 empty] | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000001 | 3. | RP-2024-05-10-0000013 | CIP-003-10 R1.1.3. | Physical security of BCS (CIP-006); | [29 empty] | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000001 | 4. | RP-2024-05-10-0000014 | CIP-003-10 R1.1.4. | System security management (CIP-007); | [29 empty] | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000001 | 5. | RP-2024-05-10-0000015 | CIP-003-10 R1.1.5. | Incident reporting and response planning (CIP-008); | [29 empty] | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000001 | 6. | RP-2024-05-10-0000016 | CIP-003-10 R1.1.6. | Recovery plans for BCS (CIP-009); | [29 empty] | 116000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000001 | 7. | RP-2024-05-10-0000017 | CIP-003-10 R1.1.7. | Configuration change management and vulnerability assessments (CIP-010); | [29 empty] | 117000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000001 | 8. | RP-2024-05-10-0000018 | CIP-003-10 R1.1.8. | Information protection (CIP-011); and | [29 empty] | 118000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000001 | 9. | RP-2024-05-10-0000019 | CIP-003-10 R1.1.9. | Declaring and responding to CIP Exceptional Circumstances. | [29 empty] | 119000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000002 | 1. | RP-2024-05-10-0000021 | CIP-003-10 R1.2.1. | Cyber security awareness; | [29 empty] | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000002 | 2. | RP-2024-05-10-0000022 | CIP-003-10 R1.2.2. | Physical security controls; | [29 empty] | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000002 | 3. | RP-2024-05-10-0000023 | CIP-003-10 R1.2.3. | Electronic access controls; | [29 empty] | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000002 | 4. | RP-2024-05-10-0000024 | CIP-003-10 R1.2.4. | Cyber Security Incident response; | [29 empty] | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000002 | 5. | RP-2024-05-10-0000025 | CIP-003-10 R1.2.5. | Transient Cyber Assets (TCA) and Removable Media malicious code risk mitigation; | [29 empty] | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000002 | 6. | RP-2024-05-10-0000026 | CIP-003-10 R1.2.6. | Vendor electronic remote access security controls; and | [29 empty] | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000002 | 7. | RP-2024-05-10-0000027 | CIP-003-10 R1.2.7. | Declaring and responding to CIP Exceptional Circumstances. | [29 empty] | 127000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 | RP-2024-05-10-0000012 | 1. | RP-2024-05-10-0000020 | CIP-003-10 R1.1.2.1. | Cyber security awareness; | [29 empty] | 112100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 |  | 1. | RP-2024-05-10-0000001 | CIP-003-10 R1.1. | For its high impact and medium impact BCS, if any: |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000001 | RQ-2024-05-10-0000001 |  | 2. | RP-2024-05-10-0000002 | CIP-003-10 R1.2. | For its assets identified in CIP-002 containing low impact BCS, if any: |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000002 | RQ-2024-05-10-0000005 | RP-2024-05-10-0000004 | 1. | RP-2024-05-10-0000005 | CIP-013-3 R1.2.1. | Notification by the vendor of vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; | [29 empty] | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000002 | RQ-2024-05-10-0000005 | RP-2024-05-10-0000004 | 2. | RP-2024-05-10-0000006 | CIP-013-3 R1.2.2. | Coordination of responses to vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; | [29 empty] | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000002 | RQ-2024-05-10-0000005 | RP-2024-05-10-0000004 | 3. | RP-2024-05-10-0000007 | CIP-013-3 R1.2.3. | Notification by vendors when remote or onsite access should no longer be granted to vendor representatives; | [29 empty] | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000002 | RQ-2024-05-10-0000005 | RP-2024-05-10-0000004 | 4. | RP-2024-05-10-0000008 | CIP-013-3 R1.2.4. | Disclosure by vendors of known vulnerabilities related to the products or services provided to the Responsible Entity; | [29 empty] | 124000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000002 | RQ-2024-05-10-0000005 | RP-2024-05-10-0000004 | 5. | RP-2024-05-10-0000009 | CIP-013-3 R1.2.5. | Verification of software integrity and authenticity of all software and patches provided by the vendor; and | [29 empty] | 125000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000002 | RQ-2024-05-10-0000005 | RP-2024-05-10-0000004 | 6. | RP-2024-05-10-0000010 | CIP-013-3 R1.2.6. | Coordination of controls for vendor-initiated remote access. | [29 empty] | 126000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000002 | RQ-2024-05-10-0000005 |  | 1. | RP-2024-05-10-0000003 | CIP-013-3 R1.1. | One or more process(es) used in planning for the procurement of applicable systems listed in Requirement R1 to identify and assess cyber security risk(s) to the BES from vendor products or services resulting from: (i) procuring and installing vendor equipment and software; and (ii) transitions from one vendor(s) to another vendor(s). |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000002 | RQ-2024-05-10-0000005 |  | 2. | RP-2024-05-10-0000004 | CIP-013-3 R1.2. | One or more process(es) used in procuring applicable systems listed in Requirement R1 that address the following, as applicable: |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000003 | RQ-2024-05-10-0000008 |  | 1. | RP-2024-05-10-0000028 | CIP-011-4 R1.1. | Method(s) to identify BCSI. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000003 | RQ-2024-05-10-0000008 |  | 2. | RP-2024-05-10-0000029 | CIP-011-4 R1.2. | Method(s) to protect and securely handle BCSI to mitigate risks of compromising confidentiality. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000003 | RQ-2024-05-10-0000009 |  | 1. | RP-2024-05-10-0000030 | CIP-011-4 R2.1. | Methods to prevent the unauthorized retrieval of BCSI from Applicable Systems containing BCSI, prior to their disposal or reuse (except for reuse within other systems identified in the Applicable Systems column). |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000010 |  | 1. | RP-2024-05-10-0000031 | CIP-004-8 R1.1. | Security awareness that, at least once each calendar quarter, reinforces cyber security practices (which may include associated physical security practices) for the Responsible Entity’s personnel who have authorized electronic or authorized unescorted physical access to Applicable Systems. | High impact BCS Medium impact BCS Shared Cyber Infrastructure (SCI) supporting an Applicable System in this Part. | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation that the quarterly reinforcement has been provided. Examples of evidence of reinforcement may include, but are not limited to, dated copies of information used to reinforce security awareness, as well as evidence of distribution, such as: - direct communications (for example, e-mails, memos, computer-based training); or - indirect communications (for example, posters, intranet, or brochures); or - management support and reinforcement (for example, presentations or meetings). | [5 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000011 | RP-2024-05-10-0000032 | 1. | RP-2024-05-10-0000051 | CIP-004-8 R2.1.1. | Cyber security policies; | [29 empty] | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000011 | RP-2024-05-10-0000032 | 2. | RP-2024-05-10-0000052 | CIP-004-8 R2.1.2. | Physical access controls; | [29 empty] | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000011 | RP-2024-05-10-0000032 | 3. | RP-2024-05-10-0000053 | CIP-004-8 R2.1.3. | Electronic access controls; | [29 empty] | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000011 | RP-2024-05-10-0000032 | 4. | RP-2024-05-10-0000054 | CIP-004-8 R2.1.4. | The visitor control program; | [29 empty] | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000011 | RP-2024-05-10-0000032 | 5. | RP-2024-05-10-0000055 | CIP-004-8 R2.1.5. | Handling of BES Cyber System Information (BCSI) and its storage; | [29 empty] | 215000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000011 | RP-2024-05-10-0000032 | 6. | RP-2024-05-10-0000056 | CIP-004-8 R2.1.6. | Identification of a Cyber Security Incident and initial notifications in accordance with the entity’s incident response plan; | [29 empty] | 216000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000011 | RP-2024-05-10-0000032 | 7. | RP-2024-05-10-0000057 | CIP-004-8 R2.1.7. | Recovery plans for BCS; | [29 empty] | 217000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000011 | RP-2024-05-10-0000032 | 8. | RP-2024-05-10-0000058 | CIP-004-8 R2.1.8. | Response to Cyber Security Incidents; and | [29 empty] | 218000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000011 | RP-2024-05-10-0000032 | 9. | RP-2024-05-10-0000059 | CIP-004-8 R2.1.9. | Cyber security risks associated with a BCS electronic interconnectivity and interoperability with other Cyber Systems, including Transient Cyber Assets (TCA), and with Removable Media. | [29 empty] | 219000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000011 |  | 1. | RP-2024-05-10-0000032 | CIP-004-8 R2.1. | Training content on: | High impact BCS and their associated: 1. Electronic Access Control or Monitoring Systems (EACMS); and 2. Physical Access Control Systems (PACS) Medium impact BCS with External Routable Connectivity (ERC) and their associated: 1. EACMS; and 2. PACS Medium impact BCS with Interactive Remote Access (IRA) SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | [5 empty] | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000011 |  | 2. | RP-2024-05-10-0000033 | CIP-004-8 R2.2. | Require completion of the training specified in Part 2.1 prior to granting authorized electronic access and authorized unescorted physical access to Applicable Systems, except during CIP Exceptional Circumstances. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PACS Medium impact BCS with IRA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training records and documentation of when CIP Exceptional Circumstances were invoked. | [5 empty] | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000011 |  | 3. | RP-2024-05-10-0000034 | CIP-004-8 R2.3. | Require completion of the training specified in Part 2.1 at least once every 15 calendar months. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PACS Medium impact BCS with IRA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated individual training records. | [5 empty] | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000012 | RP-2024-05-10-0000036 | 1. | RP-2024-05-10-0000060 | CIP-004-8 R3.2.1. | current residence, regardless of duration; and | [29 empty] | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000012 | RP-2024-05-10-0000036 | 2. | RP-2024-05-10-0000061 | CIP-004-8 R3.2.2. | other locations where, during the seven years immediately prior to the date of the criminal history records check, the subject has resided for six consecutive months or more. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. | [29 empty] | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000012 |  | 1. | RP-2024-05-10-0000035 | CIP-004-8 R3.1. | Process to confirm identity. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PACS Medium impact BCS with IRA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to confirm identity. | [5 empty] | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000012 |  | 2. | RP-2024-05-10-0000036 | CIP-004-8 R3.2. | Process to perform a seven year criminal history records check as part of each personnel risk assessment that includes: | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PACS Medium impact BCS with IRA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. | [5 empty] | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000012 |  | 3. | RP-2024-05-10-0000037 | CIP-004-8 R3.3. | Criteria or process to evaluate criminal history records checks for authorizing access. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PACS Medium impact BCS with IRA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s criteria or process to evaluate criminal history records checks. | [5 empty] | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000012 |  | 4. | RP-2024-05-10-0000038 | CIP-004-8 R3.4. | Criteria or process for verifying that personnel risk assessments performed for contractors or service vendors are conducted according to Parts 3.1 through 3.3. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PACS Medium impact BCS with IRA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the Responsible Entity’s criteria or process for verifying contractors or service vendors personnel risk assessments. | [5 empty] | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000012 |  | 5. | RP-2024-05-10-0000039 | CIP-004-8 R3.5. | Process to ensure that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed, except during CIP Exceptional Circumstances, according to Parts 3.1 through 3.4 within the last seven years. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PACS Medium impact BCS with IRA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the Responsible Entity’s process for ensuring that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed within the last seven years. | [5 empty] | 350000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000013 | RP-2024-05-10-0000040 | 1. | RP-2024-05-10-0000062 | CIP-004-8 R4.1.1. | Electronic access; and | [29 empty] | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000013 | RP-2024-05-10-0000040 | 2. | RP-2024-05-10-0000063 | CIP-004-8 R4.1.2. | Unescorted physical access into a Physical Security Perimeter (PSP) (except for medium impact BCS without ERC). | [29 empty] | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000013 |  | 1. | RP-2024-05-10-0000040 | CIP-004-8 R4.1. | Process to authorize based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PACS Medium impact BCS with IRA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of the process to authorize electronic access, and unescorted physical access in a PSP. | [5 empty] | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000013 |  | 2. | RP-2024-05-10-0000041 | CIP-004-8 R4.2. | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PACS Medium impact BCS with IRA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: - Dated documentation of the verification between the system generated list of individuals who have been authorized for access (i.e., workflow database) and a system generated list of personnel who have access (i.e., user account listing), or - Dated documentation of the verification between a list of individuals who have been authorized for access (i.e., authorization forms) and a list of individuals provisioned for access (i.e., provisioning forms or shared account listing). | [5 empty] | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000013 |  | 3. | RP-2024-05-10-0000042 | CIP-004-8 R4.3. | For electronic access, verify at least once every 15 calendar months that all user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and are those that the Responsible Entity determines are necessary. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PACS Medium impact BCS with IRA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the review that includes all of the following: 1. A dated listing of all accounts/account groups or roles within the system; 2. A summary description of privileges associated with each group or role; 3. Accounts assigned to the group or role; and 4. Dated evidence showing verification of the privileges for the group are authorized and appropriate to the work function performed by people assigned to each account. | [5 empty] | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000014 |  | 1. | RP-2024-05-10-0000043 | CIP-004-8 R5.1. | A process to initiate removal of an individual’s ability for unescorted physical access (except for medium impact BCS without ERC) and Interactive Remote Access (IRA) upon a termination action, and complete the removals within 24 hours of the termination action (Removal of the ability for access may be different than deletion, disabling, revocation, or removal of all access rights). | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PACS Medium impact BCS with IRA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of all of the following: 1. Dated workflow or sign-off form verifying access removal associated with the termination action; and 2. Logs or other demonstration showing such persons no longer have access. | [5 empty] | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000014 |  | 2. | RP-2024-05-10-0000044 | CIP-004-8 R5.2. | For reassignments or transfers, revoke the individual’s authorized electronic access to individual accounts; and authorized unescorted physical access (except for medium impact BCS without ERC) that the Responsible Entity determines are not necessary by the end of the next calendar day following the date that the Responsible Entity determines that the individual no longer requires retention of that access. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PACS Medium impact BCS with IRA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of all of the following: 1. Dated workflow or sign-off form showing a review of logical and physical access; and 2. Logs or other demonstration showing such persons no longer have access that the Responsible Entity determines is not necessary. | [5 empty] | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000014 |  | 3. | RP-2024-05-10-0000045 | CIP-004-8 R5.3. | For termination actions, revoke the individual’s non-shared user accounts (unless already revoked according to Part 5.1) within 30 calendar days of the effective date of the termination action. | High impact BCS and their associated EACMS SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, workflow or sign-off form showing access removal for any individual BES Cyber Assets and software applications as determined necessary to completing the revocation of access and dated within thirty calendar days of the termination actions. | [5 empty] | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000014 |  | 4. | RP-2024-05-10-0000047 | CIP-004-8 R5.4. | For termination actions, change passwords for shared account(s) known to the user within 30 calendar days of the termination action. For reassignments or transfers, change passwords for shared account(s) known to the user within 30 calendar days following the date that the Responsible Entity determines that the individual no longer requires retention of that access. If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances. | High impact BCS and their associated EACMS SCI supporting an Applicable System in this Part. | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: - Workflow or sign-off form showing password reset within 30 calendar days of the termination action; - Workflow or sign-off form showing password reset within 30 calendar days of the reassignments or transfers; or - Documentation of the extenuating operating circumstance and workflow or sign-off form showing password reset within 10 calendar days following the end of the operating circumstance. | [5 empty] | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000015 | RP-2024-05-10-0000048 | 1. | RP-2024-05-10-0000064 | CIP-004-8 R6.1.1. | Provisioned electronic access to electronic BCSI; and | [29 empty] | 611000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000015 | RP-2024-05-10-0000048 | 2. | RP-2024-05-10-0000065 | CIP-004-8 R6.1.2. | Provisioned physical access to physical BCSI (except for BCSI at a medium impact BCS without ERC). | [29 empty] | 612000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000015 | RP-2024-05-10-0000049 | 1. | RP-2024-05-10-0000066 | CIP-004-8 R6.2.1. | have an authorization record; and | [29 empty] | 621000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000015 | RP-2024-05-10-0000049 | 2. | RP-2024-05-10-0000067 | CIP-004-8 R6.2.2. | still need the provisioned access to perform their current work functions, as determined by the Responsible Entity. | [29 empty] | 622000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000015 |  | 1. | RP-2024-05-10-0000048 | CIP-004-8 R6.1. | Prior to provisioning, authorize (unless already authorized according to Part 4.1) based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PACS Medium impact BCS with IRA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, individual records or lists that include who is authorized, the date of the authorization, and the justification of business need for the provisioned access | [5 empty] | 610000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000015 |  | 2. | RP-2024-05-10-0000049 | CIP-004-8 R6.2. | Verify at least once every 15 calendar months that all individuals with provisioned access to BCSI: | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PACS Medium impact BCS with IRA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, the documentation of the review that includes all of the following: - List of authorized individuals; - List of individuals who have been provisioned access; - Verification that provisioned access is appropriate based on need; and - Documented reconciliation actions, if any. | [5 empty] | 620000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000004 | RQ-2024-05-10-0000015 |  | 3. | RP-2024-05-10-0000050 | CIP-004-8 R6.3. | For termination actions, remove the individual’s ability to use provisioned access to BCSI (unless already revoked according to Part 5.1) (except for BCSI at a medium impact BCS without ERC) by the end of the next calendar day following the effective date of the termination action. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PACS Medium impact BCS with IRA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of dated evidence may include, but are not limited to, access revocation records associated with the terminations and dated within the next calendar day of the termination action. | [5 empty] | 630000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000005 | RQ-2024-05-10-0000016 |  | 1. | RP-2024-05-10-0000068 | CIP-005-8 R1.1. | Applicable Systems connected to a network via a routable protocol must be protected by an ESP. | High impact BCS and their associated PCA Medium impact BCS and their associated PCA | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but is not limited to, a list of all ESPs with all uniquely identifiable applicable Cyber Systems connected via a routable protocol within each ESP. | [5 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000005 | RQ-2024-05-10-0000016 |  | 2. | RP-2024-05-10-0000069 | CIP-005-8 R1.2. | Permit only needed routable protocol communications, documenting the reason, and deny all other routable protocol communications, through the ESP; excluding time sensitive communications of Protection Systems. | High impact BCS with ERC and their associated PCA Medium impact BCS with ERC and their associated PCA | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation that includes the configuration of system and documented reason, such as: - Electronic Access Point (EAP) configuration; - Network infrastructure configuration (e.g., technical policies, ACL, VLAN, VXLAN, MPLS, VRF, multi-context, or multi-tenant environment); or - SCI configuration or settings (e.g., technical policies, hypervisor, fabric, back-plane, or SAN configuration). | [5 empty] | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000005 | RQ-2024-05-10-0000016 |  | 3. | RP-2024-05-10-0000070 | CIP-005-8 R1.3. | Protect ESP and SCI configurations by implementing methods to permit only needed network accessibility to Management Interfaces of Applicable Systems, per system capability. | SCI supporting an Applicable System from Part 1.1.EACMS, and their supporting SCI, that control an ESP for an Applicable System in Part 1.1 | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods implemented to permit only needed network accessibility to Management Interfaces, including documented reasons such as: - Logical configuration or settings (e.g., technical Policies, ACL, VLAN, VXLAN, MPLS, VRF, multi-context, or multi-tenant environment); - Physically isolated or out-of-band network for dedicated Management Interfaces; or - SCI configuration or settings showing the isolation of the Management Interfaces (e.g., technical policies, hypervisor, fabric back-plane, or SAN configuration). | [5 empty] | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000005 | RQ-2024-05-10-0000016 |  | 4. | RP-2024-05-10-0000071 | CIP-005-8 R1.4. | Perform authentication when establishing Dial-up Connectivity with Applicable Systems, if any, and per system capability. | High impact BCS and their associated PCA Medium impact BCS and their associated PCA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, configuration, settings, or documented process that describes how the Responsible Entity is providing authenticated access through each dial-up connection. | [5 empty] | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000005 | RQ-2024-05-10-0000016 |  | 5. | RP-2024-05-10-0000072 | CIP-005-8 R1.5. | Have one or more methods for detecting known or suspected malicious routable protocol communications entering or leaving an ESP. | High impact BCS Medium impact BCS at Control Centers | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation that malicious routable protocol communications detection methods (e.g., intrusion detection system, application layer firewall, etc.) are implemented. | [5 empty] | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000005 | RQ-2024-05-10-0000016 |  | 6. | RP-2024-05-10-0000073 | CIP-005-8 R1.6. | Protect the data traversing communication links used to span a single ESP between PSPs through the use of: - Confidentiality and integrity controls, or - Physical controls that restrict access to the cabling and other non-programmable communication components in those instances when such cabling and components are located outside of a PSP, Excluding: i. Real-time Assessment and Real-time monitoring data while being transmitted between Control Centers subject to CIP-012; and ii.Time-sensitive communication of Protection Systems. | High impact BCS and their associated PCA Medium impact BCS at Control Centers and their associated PCA | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of methods used to protect the confidentiality and integrity of the data, such as: - Configurations or settings used to enforce encryption; or - The physical access restrictions (e.g., cabling and components secured through conduit or secured cable trays). | [5 empty] | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000005 | RQ-2024-05-10-0000017 |  | 1. | RP-2024-05-10-0000074 | CIP-005-8 R2.1. | Permit Interactive Remote Access (IRA), if any, only through an Intermediate System. | High impact BCS and their associated PCA Medium impact BCS and their associated PCA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, network diagrams, architecture documents, configuration, or settings that show all IRA is through an Intermediate System. | [5 empty] | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000005 | RQ-2024-05-10-0000017 |  | 2. | RP-2024-05-10-0000075 | CIP-005-8 R2.2. | Protect the confidentiality and integrity of IRA communications between the initiating Cyber Asset or Virtual Cyber Asset and the Intermediate System. | Intermediate System(s) used to access an Applicable System in Part 2.1 | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, architecture documents, configuration or settings detailing where confidentiality and integrity controls (e.g., encryption) initiate and terminate. | [5 empty] | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000005 | RQ-2024-05-10-0000017 |  | 3. | RP-2024-05-10-0000076 | CIP-005-8 R2.3. | Require multi-factor authentication to the Intermediate System for IRA communications between the initiating Cyber Asset or Virtual Cyber Asset and the Intermediate System. | Intermediate System(s) used to access an Applicable System in Part 2.1 | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Example of evidence may include, but are not limited to, architecture documents, configuration or settings detailing the authentication factors used. Examples of authenticators may include, but are not limited to, - Something the individual knows such as passwords or PINs. This does not include User ID; - Something the individual has such as tokens, digital certificates, or smart cards; or - Something the individual is such as fingerprints, iris scans, or other biometric characteristic | [5 empty] | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000005 | RQ-2024-05-10-0000017 |  | 4. | RP-2024-05-10-0000077 | CIP-005-8 R2.4. | Have one or more methods for determining active vendor remote access sessions (including IRA and system-to-system remote access). | High impact BCS and their associated PCA Medium impact BCS and their associated PCA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods used to determine active vendor remote access, including IRA and system-to-system remote access, such as: - Methods for accessing logged or monitoring information to determine active vendor remote access sessions; - Methods for monitoring activity (e.g., connection tables or rule hit counters in a firewall, or user activity monitoring) or open ports (e.g., netstat or related commands to display currently active ports) to determine active system to system remote access sessions; or - Methods that control vendor initiation of remote access such as vendors calling and requesting a second factor in order to initiate remote access. | [5 empty] | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000005 | RQ-2024-05-10-0000017 |  | 5. | RP-2024-05-10-0000078 | CIP-005-8 R2.5. | Have one or more method(s) to disable active vendor remote access (including IRA and system-to-system remote access). | High impact BCS and their associated PCA Medium impact BCS and their associated PCA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include,but are not limited to, documentation of the methods(s) used to disable active vendor remote access (including IRA and system-to-system remote access). | [5 empty] | 250000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000005 | RQ-2024-05-10-0000017 |  | 6. | RP-2024-05-10-0000079 | CIP-005-8 R2.6. | Prevent Intermediate System(s) from sharing CPU resources and memory resources with any part of a high or medium impact BCS or associated PCAs. | Intermediate System(s) used to access an Applicable System in Part 2.1 | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation that includes the following: - Intermediate System architecture; or - Configuration or settings of each Intermediate System and supporting Cyber Systems | [5 empty] | 260000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000005 | RQ-2024-05-10-0000017 |  | 7. | RP-2024-05-10-0000080 | CIP-005-8 R2.7. | Intermediate System(s) used to access an Applicable System in Part 2.1 | Intermediate System(s) used to access an Applicable System in Part 2.1 | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation that includes the following: - Network diagrams of Intermediate Systems architecture; or - Configuration, settings, or policy of the EAP which controls routable protocol communications of IRA through the ESP. | [5 empty] | 270000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000005 | RQ-2024-05-10-0000018 |  | 1. | RP-2024-05-10-0000081 | CIP-005-8 R3.1. | Have one or more method(s) to determine authenticated vendor-initiated remote connections. | EACMS and PACS associated with high impact BCS. EACMS and PACS associated with medium impact BCS with ERC. SCI supporting an Applicable System in this Part. | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods(s) used to terminate authenticated vendor-initiated remote connections to applicable systems. Examples include terminating an active vendor-initiated shell/process/session or dropping an active vendor-initiated connection in a firewall. Methods to control the ability to reconnect, if necessary, could be: disabling an Active Directory account; disabling a security token; restricting IP addresses from vendor sources in a firewall; or physically disconnecting a network cable to prevent a reconnection. | [5 empty] | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000005 | RQ-2024-05-10-0000018 |  | 2. | RP-2024-05-10-0000082 | CIP-005-8 R3.2. | Have one or more method(s) to terminate authenticated vendor-initiated remote connections and control the ability to reconnect. | EACMS and PACS associated with high impact BCS. EACMS and PACS associated with medium impact BCS with ERC. SCI supporting an Applicable System in this Part. | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods(s) used to terminate authenticated vendor-initiated remote connections to applicable systems. Examples include terminating an active vendor-initiated shell/process/session or dropping an active vendor-initiated connection in a firewall. Methods to control the ability to reconnect, if necessary, could be: disabling an Active Directory account; disabling a security token; restricting IP addresses from vendor sources in a firewall; or physically disconnecting a network cable to prevent a reconnection. | [5 empty] | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000006 | RQ-2024-05-10-0000019 |  | 1. | RP-2024-05-10-0000083 | CIP-006-7 R1.1. | Define operational or procedural controls to restrict physical access. | Medium impact BCS without External Routable Connectivity (ERC) Physical Access Control Systems (PACS) associated with: - High impact BCS, or - Medium impact BCS with ERC SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation that operational or procedural controls exist. | [5 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000006 | RQ-2024-05-10-0000019 |  | 2. | RP-2024-05-10-0000084 | CIP-006-7 R1.2. | Utilize at least one physical access control to allow unescorted physical access into each applicable PSP to only those individuals who have authorized unescorted physical access. | Medium impact BCS with ERC and their associated: 1. Electronic Access Control and Monitoring Systems (EACMS); and 2. Protected Cyber Asset (PCA) SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, language in the physical security plan that describes each PSP and how unescorted physical access is controlled by one or more different methods and proof that unescorted physical access is restricted to only authorized individuals, such as a list of authorized individuals accompanied by access logs. | [5 empty] | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000006 | RQ-2024-05-10-0000019 |  | 3. | RP-2024-05-10-0000085 | CIP-006-7 R1.3. | Utilize two or more different physical access controls (this does not require two completely independent PACS) to collectively allow unescorted physical access into PSPs to only those individuals who have authorized unescorted physical access, per system capability. | High impact BCS and their associated: 1. EACMS; and 2. PCA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, language in the physical security plan that describes each PSP and how unescorted physical access is controlled by two or more different methods and proof that unescorted physical access is restricted to only authorized individuals, such as a list of authorized individuals accompanied by access logs. | [5 empty] | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000006 | RQ-2024-05-10-0000019 |  | 4. | RP-2024-05-10-0000086 | CIP-006-7 R1.4. | Monitor for unauthorized access through a physical access point into a PSP. | High impact BCS and their associated: 1. EACMS; and 2. PCA Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PCA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of controls that monitor for unauthorized access through a physical access point into a PSP. | [5 empty] | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000006 | RQ-2024-05-10-0000019 |  | 5. | RP-2024-05-10-0000087 | CIP-006-7 R1.5. | Issue an alarm or alert in response to detected unauthorized access through a physical access point into a PSP to the personnel identified in the Cyber Security Incident response plan within 15 minutes of detection. | High impact BCS and their associated: 1. EACMS; and 2. PCA Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PCA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, language in the physical security plan that describes the issuance of an alarm or alert in response to unauthorized access through a physical access control into a PSP and additional evidence that the alarm or alert was issued and communicated as identified in the Cyber Security Incident Response Plan, such as manual or electronic alarm or alert logs, cell phone or pager logs, or other evidence that documents that the alarm or alert was generated and communicated. | [5 empty] | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000006 | RQ-2024-05-10-0000019 |  | 6. | RP-2024-05-10-0000088 | CIP-006-7 R1.6. | Monitor each PACS for unauthorized physical access to a PACS. | Physical Access Control Systems (PACS) associated with: - High impact BCS, or - Medium impact BCS with ERC SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of controls that monitor for unauthorized physical access to a PACS. | [5 empty] | 160000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000006 | RQ-2024-05-10-0000019 |  | 7. | RP-2024-05-10-0000089 | CIP-006-7 R1.7. | Issue an alarm or alert in response to detected unauthorized physical access to a PACS to the personnel identified in the Cyber Security Incident response plan within 15 minutes of the detection. | - High impact BCS, or - Medium impact BCS with ERC SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, language in the physical security plan that describes the issuance of an alarm or alert in response to unauthorized physical access to PACS and additional evidence that the alarm or alerts was issued and communicated as identified in the Cyber Security Incident Response Plan, such as alarm or alert logs, cell phone or pager logs, or other evidence that the alarm or alert was generated and communicated. | [5 empty] | 170000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000006 | RQ-2024-05-10-0000019 |  | 8. | RP-2024-05-10-0000090 | CIP-006-7 R1.8. | Log (through automated means or by personnel who control entry) entry of each individual with authorized unescorted physical access into each PSP, with information to identify the individual and date and time of entry. | High impact BCS and their associated: 1. EACMS; and 2. PCA Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PCA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, language in the physical security plan that describes logging and recording of physical entry into each PSP and additional evidence to demonstrate that this logging has been implemented, such as logs of physical access into each PSP that show the individual and the date and time of entry into each PSP. | [5 empty] | 180000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000006 | RQ-2024-05-10-0000019 |  | 9. | RP-2024-05-10-0000091 | CIP-006-7 R1.9. | Retain physical access logs of entry of individuals with authorized unescorted physical access into each PSP for at least 90 calendar days. | High impact BCS and their associated: 1. EACMS; and 2. PCA Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PCA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation such as logs of physical access into each PSP that show the date and time of entry into each PSP. | [5 empty] | 190000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000006 | RQ-2024-05-10-0000020 |  | 1. | RP-2024-05-10-0000092 | CIP-006-7 R2.1. | Require continuous escorted access of visitors (individuals who are provided access but are not authorized for unescorted physical access) within each PSP. | High impact BCS and their associated: 1. EACMS; and 2. PCA Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PCA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, language in a visitor control program that requires continuous escorted access of visitors within each PSP and additional evidence to demonstrate that the process was implemented, such as visitor logs. | [5 empty] | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000006 | RQ-2024-05-10-0000020 |  | 2. | RP-2024-05-10-0000093 | CIP-006-7 R2.2. | Require manual or automated logging of visitor entry into and exit from each PSP that includes date and time of the initial entry and last exit, the visitor’s name, and the name of an individual point of contact responsible for the visitor. | High impact BCS and their associated: 1. EACMS; and 2. PCA Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PCA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, language in a visitor control program that requires continuous escorted access of visitors within each PSP and additional evidence to demonstrate that the process was implemented, such as dated visitor logs that include the required information. | [5 empty] | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000006 | RQ-2024-05-10-0000020 |  | 3. | RP-2024-05-10-0000094 | CIP-006-7 R2.3. | Retain visitor logs for at least 90 calendar days. | High impact BCS and their associated: 1. EACMS; and 2. PCA Medium impact BCS with ERC and their associated: 1. EACMS; and 2. PCA SCI supporting an Applicable System in this Part | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [7 empty] | An example of evidence may include, but is not limited to, documentation showing logs have been retained for at least 90 calendar days. | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000006 | RQ-2024-05-10-0000021 |  | 1. | RP-2024-05-10-0000095 | CIP-006-7 R3.1. | Maintenance and testing of each PACS and locally mounted hardware or devices at each PSP at least once every 24 calendar months to ensure they function properly. | PACS associated with: · High impact BCS, or - Medium impact BCS with ERC - Locally mounted hardware or devices at the PSP associated with: - High impact BCS, or - Medium impact BCS with ERC | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, a maintenance and testing program that provides for testing each PACS and locally mounted hardware or devices associated with each applicable each PSP at least once every 24 calendar months and additional evidence to demonstrate that this testing was done, such as dated maintenance records, or other documentation showing testing and maintenance has been performed on each applicable device or system at least once every 24 calendar months. | [5 empty] | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000022 |  | 1. | RP-2024-05-10-0000096 | CIP-007-7 R1.1. | Disable or prevent unneeded routable protocol network accessibility on each Applicable System, per system capability. | High impact BCS and their associated: 1. Electronic Access Control and Monitoring Systems (EACMS); 2. Physical Access Control Systems (PACS); and 3. Protected Cyber Asset (PCA) Medium impact BCS with ERC and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: - Documentation of the need for all enabled network accessible logical ports or network accessible logical services, individually or by group; - Listings of the listening ports, individually or by group, from either configuration files or settings, command output (such as netstat), or network scans of open ports; - Configuration or settings of host-based firewalls or other device level mechanisms that disable or prevent unneeded network accessible logical ports or network accessible logical services; or - Identity or process based access policy or workload configuration demonstrating needed network accessibility. | [5 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000022 |  | 2. | RP-2024-05-10-0000097 | CIP-007-7 R1.2. | Protect against the use of unnecessary physical input/output ports used for network connectivity, console commands, or Removable Media. | High impact BCS and their associated: 1. PCA; and 2. Nonprogrammable communication components located inside both a PSP and an ESP. Medium impact BCS at Control Centers and their associated: 1. PCA; and 2. Nonprogrammable communication components located inside both a PSP and an ESP. SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation showing types of protection of physical input/output ports, either logically through system configuration or physically using a port lock or signage. | [5 empty] | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000022 |  | 3. | RP-2024-05-10-0000098 | CIP-007-7 R1.3. | Mitigate the risk of CPU or memory vulnerabilities by preventing the sharing of CPU resources and memory resources, excluding storage resources, between VCAs that are, or are associated with, a medium or high impact BCS, and VCAs that are not, or are not associated with, a medium or high impact BCS. | SCI supporting either: High impact BCS or their associated PCA. Medium impact BCS or their associated PCA. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the configuration or settings showing that the CPU and memory cannot be shared, such as: - Virtualization affinity rules; or - Hardware partitioning of physical Cyber Assets. | [5 empty] | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000023 |  | 1. | RP-2024-05-10-0000099 | CIP-007-7 R2.1. | A patch management process for tracking, evaluating, and installing cyber security patches. The tracking portion shall include the identification of a source or sources that the Responsible Entity tracks for the release of cyber security patches for Applicable Systems that are updateable and for which a patching source exists | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of a patch management process and documentation or lists of sources that are monitored. | [5 empty] | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000023 |  | 2. | RP-2024-05-10-0000100 | CIP-007-7 R2.2. | At least once every 35 calendar days, evaluate cyber security patches for applicability that have been released since the last evaluation from the source or sources identified in Part 2.1. | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, an evaluation conducted by, referenced by, or on behalf of a Responsible Entity of cyber security patches released by the documented sources at least once every 35 calendar days. | [5 empty] | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000023 |  | 3. | RP-2024-05-10-0000101 | CIP-007-7 R2.3. | For applicable patches identified in Part 2.2, within 35 calendar days of the evaluation completion, take one of the following actions: - Apply the applicable patches; - Create a dated mitigation plan; or - Revise an existing mitigation plan. Mitigation plans shall include the Responsible Entity’s planned actions to mitigate the vulnerabilities addressed by each cyber security patch and a timeframe to complete these mitigations. | High impact BES Cyber Systems and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BES Cyber Systems and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: - Records of the installation of the cyber security patch (e.g., exports from automated patch management tools that provide installation date, verification of component software revision, or registry exports that show software has been installed); or - A dated plan showing when and how the vulnerability will be addressed, to include documentation of the actions to be taken by the Responsible Entity to mitigate the vulnerabilities addressed by the cyber security patch and a timeframe for the completion of these mitigations. | [5 empty] | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000023 |  | 4. | RP-2024-05-10-0000102 | CIP-007-7 R2.4. | For each mitigation plan created or revised in Part 2.3, implement the plan within the timeframe specified in the plan, unless a revision to the plan or an extension to the timeframe specified in Part 2.3 is approved by the CIP Senior Manager or delegate. | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, records of implementation of mitigations, and any approval records for mitigation plan revisions or extensions | [5 empty] | 240000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000024 |  | 1. | RP-2024-05-10-0000103 | CIP-007-7 R3.1. | Deploy method(s) to deter, detect, or prevent malicious code. | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, records of the Responsible Entity’s performance of these processes (e.g., through traditional antivirus, system hardening, policies, etc.). | [5 empty] | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000024 |  | 2. | RP-2024-05-10-0000104 | CIP-007-7 R3.2. | Mitigate the threat of detected malicious code. | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: - Records of response processes for malicious code detection - Records of the performance of these processes when malicious code is detected. | [5 empty] | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000024 |  | 3. | RP-2024-05-10-0000105 | CIP-007-7 R3.3. | For those methods identified in Part 3.1 that use signatures or patterns, have a process for the update of the signatures or patterns. The process must address testing and installing the signatures or patterns. | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation showing the process used for the update of signatures or patterns | [5 empty] | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000025 | RP-2024-05-10-0000106 | 1. | RP-2024-05-10-0000110 | CIP-007-7 R4.1.1. | Detected successful login attempts; | [29 empty] | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000025 | RP-2024-05-10-0000106 | 2. | RP-2024-05-10-0000111 | CIP-007-7 R4.1.2. | Detected failed access attempts and failed login attempts; and | [29 empty] | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000025 | RP-2024-05-10-0000106 | 3. | RP-2024-05-10-0000112 | CIP-007-7 R4.1.3. | Detected malicious code. | [29 empty] | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000025 | RP-2024-05-10-0000107 | 1. | RP-2024-05-10-0000113 | CIP-007-7 R4.2.1. | Detected malicious code from Part 4.1; and | [29 empty] | 421000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000025 | RP-2024-05-10-0000107 | 2. | RP-2024-05-10-0000114 | CIP-007-7 R4.2.2. | Detected failure of Part 4.1 event logging. | [29 empty] | 422000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000025 |  | 1. | RP-2024-05-10-0000106 | CIP-007-7 R4.1. | Log security events, per system capability, for identification of, and after-the-fact investigations of, Cyber Security Incidents that include, at a minimum, each of the following types of events: | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, a paper or system generated listing of event types for which the Applicable System is capable of detecting and, for generated events, is configured to log. This listing must include the required types of events. | [5 empty] | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000025 |  | 2. | RP-2024-05-10-0000107 | CIP-007-7 R4.2. | Generate alerts for security events that the Responsible Entity determines necessitates an alert that includes, as a minimum, each of the following types of events, per system capability: | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS with ERC and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, paper or system-generated listing of security events that the Responsible Entity determined necessitate alerts, including paper or system generated list showing how alerts are configured. | [5 empty] | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000025 |  | 3. | RP-2024-05-10-0000108 | CIP-007-7 R4.3. | Retain applicable security event logs identified in Part 4.1 for at least the last 90 consecutive calendar days, per system capability, except under CIP Exceptional Circumstances. | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS at Control Centers and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the event log retention process and paper or system generated reports showing log retention configuration set at 90 calendar days or greater. | [5 empty] | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000025 |  | 4. | RP-2024-05-10-0000109 | CIP-007-7 R4.4. | Review a summarization or sampling of logged security events as determined by the Responsible Entity at intervals no greater than 15 calendar days to identify undetected Cyber Security Incidents. | High impact BCS and their associated: 1. EACMS; and 2. PCA SCI supporting an Applicable System in this Part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation describing the review, findings from the review (if any), and dated documentation showing the review occurred. | [5 empty] | 440000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000026 | RP-2024-05-10-0000119 | 1. | RP-2024-05-10-0000120 | CIP-007-7 R5.5.1. | Password length that is, at least, the lesser of eight characters or the maximum length supported by the Applicable Systems; and | [29 empty] | 551000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000026 | RP-2024-05-10-0000119 | 2. | RP-2024-05-10-0000121 | CIP-007-7 R5.5.2. | Minimum password complexity that is the lesser of three or more different types of characters (e.g., uppercase alphabetic, lowercase alphabetic, numeric, non-alphanumeric) or the maximum complexity supported by the Applicable System. | [29 empty] | 552000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000026 |  | 1. | RP-2024-05-10-0000115 | CIP-007-7 R5.1. | Have a method(s) to enforce authentication of interactive user access, per system capability. | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS at Control Centers and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS with ERC and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation describing how access is authenticated | [5 empty] | 510000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000026 |  | 2. | RP-2024-05-10-0000116 | CIP-007-7 R5.2. | Identify and inventory all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, a listing of accounts by account types showing the enabled default or generic account types in use. | [5 empty] | 520000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000026 |  | 3. | RP-2024-05-10-0000117 | CIP-007-7 R5.3. | Identify individuals who have authorized access to shared accounts. | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS with ERC and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, listing of shared accounts and the individuals who have authorized access to each shared account. | [5 empty] | 530000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000026 |  | 4. | RP-2024-05-10-0000118 | CIP-007-7 R5.4. | Change known default passwords, per system capability | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: - Records of a procedure that passwords are changed when new devices are in production; or - Documentation in system manuals or other vendor documents showing default vendor passwords were generated pseudo-randomly and are thereby unique to the device. | [5 empty] | 540000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000026 |  | 5. | RP-2024-05-10-0000119 | CIP-007-7 R5.5. | For password-only authentication for interactive user access, either technically or procedurally enforce the following password parameters: | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: - System-generated reports or screenshots of the system-enforced password parameters, including length and complexity; or - Attestations that include a reference to the documented procedures that were followed. | [5 empty] | 550000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000026 |  | 6. | RP-2024-05-10-0000122 | CIP-007-7 R5.6. | For password-only authentication for interactive user access, either technically or procedurally enforce password changes or an obligation to change the password at least once every 15 calendar months, per system capability. | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS with ERC and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: - System-generated reports or screenshots of the system-enforced periodicity of changing passwords; or - Attestations that include a reference to the documented procedures that were followed. | [5 empty] | 560000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000007 | RQ-2024-05-10-0000026 |  | 7. | RP-2024-05-10-0000123 | CIP-007-7 R5.7. | Limit the number of unsuccessful authentication attempts or generate alerts after a threshold of unsuccessful authentication attempts, per system capability. | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS at Control Centers and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: - Documentation of the account-lockout parameters; or - Rules in the alerting configuration or settings showing how the system notified individuals after a determined number of unsuccessful login attempts. | [5 empty] | 570000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000027 | RP-2024-05-10-0000125 | 1. | RP-2024-05-10-0000126 | CIP-008-7 R1.2.1. | That include criteria to evaluate and define attempts to compromise;V | [29 empty] | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000027 | RP-2024-05-10-0000125 | 2. | RP-2024-05-10-0000127 | CIP-008-7 R1.2.2. | To determine if an identified Cyber Security Incident is: - A Reportable Cyber Security Incident; or - An attempt to compromise, as determined by applying the criteria from Part 1.2.1, one or more systems identified in the Applicable Systems column for this Part; and | [29 empty] | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000027 | RP-2024-05-10-0000125 | 3. | RP-2024-05-10-0000128 | CIP-008-7 R1.2.3. | To provide notification per Requirement R4. | [29 empty] | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000027 |  | 1. | RP-2024-05-10-0000124 | CIP-008-7 R1.1. | One or more processes to identify, classify, and respond to Cyber Security Incidents. | High impact BCS and their associated Electronic Access Control and Monitoring Systems (EACMS) Medium impact BCS and their associated EACMS Shared Cyber Infrastructure (SCI) supporting an Applicable System in this Part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of Cyber Security Incident response plan(s) that include the process(es) to identify, classify, and respond to Cyber Security Incidents | [5 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000027 |  | 2. | RP-2024-05-10-0000125 | CIP-008-7 R1.2. | One or more processes: | High impact BCS and their associated EACMS Medium impact BCS and their associated EACMS SCI supporting an Applicable System in this Part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of Cyber Security Incident response plan(s) that provide guidance or thresholds for determining which Cyber Security Incidents are also Reportable Cyber Security Incidents or a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the Applicable Systems column including justification for attempt determination criteria and documented processes for notification. | [5 empty] | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000027 |  | 3. | RP-2024-05-10-0000129 | CIP-008-7 R1.3. | The roles and responsibilities of Cyber Security Incident response groups or individuals. | High impact BCS and their associated EACMS Medium impact BCS and their associated EACMS SCI supporting an Applicable System in this Part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated Cyber Security Incident response process(es) or procedure(s) that define roles and responsibilities (e.g., monitoring, reporting, initiating, documenting, etc.) of Cyber Security Incident response groups or individuals. | [5 empty] | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000027 |  | 4. | RP-2024-05-10-0000130 | CIP-008-7 R1.4. | Incident handling procedures for Cyber Security Incidents. | High impact BCS and their associated EACMS Medium impact BCS and their associated EACMS SCI supporting an Applicable System in this Part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated Cyber Security Incident response process(es) or procedure(s) that address incident handling (e.g., containment, eradication, recovery/incident resolution). | [5 empty] | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000028 |  | 1. | RP-2024-05-10-0000131 | CIP-008-7 R2.1. | Test each Cyber Security Incident response plan(s) at least once every 15 calendar months: - By responding to an actual Reportable Cyber Security Incident; - With a paper drill or tabletop exercise of a Reportable Cyber Security Incident; or - With an operational exercise of a Reportable Cyber Security Incident. | High impact BCS and their associated EACMS Medium impact BCS and their associated EACMS SCI supporting an Applicable System in this Part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated evidence of a lessons-learned report that includes a summary of the test or a compilation of notes, logs, and communication resulting from the test. Types of exercises may include discussion or operations based exercises | [5 empty] | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000028 |  | 2. | RP-2024-05-10-0000132 | CIP-008-7 R2.2. | Use the Cyber Security Incident response plan(s) under Requirement R1 when responding to a Reportable Cyber Security Incident, responding to a Cyber Security Incident that attempted to compromise a system identified in the Applicable Systems column for this Part, or performing an exercise of a Reportable Cyber Security Incident. Document deviations from the plan(s) taken during the response to the incident or exercise | High impact BCS and their associated EACMS Medium impact BCS and their associated EACMS SCI supporting an Applicable System in this Part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, incident reports, logs, and notes that were kept during the incident response process, and follow-up documentation that describes deviations taken from the plan during the incident response or exercise. | [5 empty] | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000028 |  | 3. | RP-2024-05-10-0000133 | CIP-008-7 R2.3. | Retain records related to Reportable Cyber Security Incidents and Cyber Security Incidents that attempted to compromise a system identified in the Applicable Systems column for this Part as per the Cyber Security Incident response plan(s) under Requirement R1. | High impact BCS and their associated EACMS Medium impact BCS and their associated EACMS SCI supporting an Applicable System in this Part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation, such as security logs, police reports, emails, response forms or checklists, forensic analysis results, restoration records, and post-incident review notes related to Reportable Cyber Security Incidents and a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the Applicable Systems column. | [5 empty] | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000029 | RP-2024-05-10-0000134 | 1. | RP-2024-05-10-0000135 | CIP-008-7 R3.1.1. | Document any lessons learned or document the absence of any lessons learned; | [29 empty] | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000029 | RP-2024-05-10-0000134 | 2. | RP-2024-05-10-0000136 | CIP-008-7 R3.1.2. | Update the Cyber Security Incident response plan based on any documented lessons learned associated with the plan; and | [29 empty] | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000029 | RP-2024-05-10-0000134 | 3. | RP-2024-05-10-0000137 | CIP-008-7 R3.1.3. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates to the Cyber Security Incident response plan based on any documented lessons learned | [29 empty] | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000029 | RP-2024-05-10-0000138 | 1. | RP-2024-05-10-0000139 | CIP-008-7 R3.2.1. | Update the Cyber Security Incident response plan(s); and | [29 empty] | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000029 | RP-2024-05-10-0000138 | 2. | RP-2024-05-10-0000140 | CIP-008-7 R3.2.2. | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates. | [29 empty] | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000029 |  | 1. | RP-2024-05-10-0000134 | CIP-008-7 R3.1. | No later than 90 calendar days after completion of a Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response: | High impact BCS and their associated EACMS Medium impact BCS and their associated EACMS SCI supporting an Applicable System in this Part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, all of the following: 1. Dated documentation of post incident(s) review meeting notes or follow-up report showing lessons learned associated with the Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response or dated documentation stating there were no lessons learned; 2. Dated and revised Cyber Security Incident response plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: - Emails; - USPS or other mail service; - Electronic distribution system; or - Training sign-in sheets. | [5 empty] | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000029 |  | 2. | RP-2024-05-10-0000138 | CIP-008-7 R3.2. | No later than 60 calendar days after a change to the roles or responsibilities, Cyber Security Incident response groups or individuals, or technology that the Responsible Entity determines would impact the ability to execute the plan: | High impact BCS and their associated EACMS Medium impact BCS and their associated EACMS SCI supporting an Applicable System in this Part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: 1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and 2. Evidence of plan update distribution including, but not limited to: - Emails; - USPS or other mail service; - Electronic distribution system; or - Training sign-in sheets. | [5 empty] | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000030 | RP-2024-05-10-0000141 | 1. | RP-2024-05-10-0000142 | CIP-008-7 R4.1.1. | The functional impact; | [29 empty] | 411000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000030 | RP-2024-05-10-0000141 | 2. | RP-2024-05-10-0000143 | CIP-008-7 R4.1.2. | The attack vector used; and | [29 empty] | 412000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000030 | RP-2024-05-10-0000141 | 3. | RP-2024-05-10-0000144 | CIP-008-7 R4.1.3. | The level of intrusion that was achieved or attempted. | [29 empty] | 413000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000030 |  | 1. | RP-2024-05-10-0000141 | CIP-008-7 R4.1. | Initial notifications and updates shall include the following attributes, at a minimum, to the extent known: | High impact BCS and their associated EACMS Medium impact BCS and their associated EACMS SCI supporting an Applicable System in this Part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of initial notifications and updates to the E-ISAC and CISA, or their successors. | [5 empty] | 410000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000030 |  | 2. | RP-2024-05-10-0000145 | CIP-008-7 R4.2. | After the Responsible Entity’s determination made pursuant to documented process(es) in Requirement R1, Part 1.2, provide initial notification within the following timelines: - One hour after the determination of a Reportable Cyber Security Incident. - By the end of the next calendar day after determination that a Cyber Security Incident was an attempt to compromise a system identified in the Applicable Systems column for this Part | High impact BCS and their associated EACMS Medium impact BCS and their associated EACMS SCI supporting an Applicable System in this Part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of notices to the E-ISAC and CISA, or their successors. | [5 empty] | 420000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000008 | RQ-2024-05-10-0000030 |  | 3. | RP-2024-05-10-0000146 | CIP-008-7 R4.3. | Provide updates, if any, within seven calendar days of determination of new or changed attribute information required in Part 4.1. | High impact BCS and their associated EACMS Medium impact BCS and their associated EACMS SCI supporting an Applicable System in this Part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of submissions to the E-ISAC and CISA, or their successors. | [5 empty] | 430000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000009 | RQ-2024-05-10-0000031 |  | 1. | RP-2024-05-10-0000147 | CIP-009-7 R1.1. | Conditions for activation of the recovery plan(s). | High impact BCS and their associated: 1. Electronic Access Control and Monitoring Systems (EACMS); and 2. Physical Access Control Systems (PACS) Medium impact BCS and their associated: 1. EACMS; and PACS | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, one or more plans that include language identifying conditions for activation of the recovery plan(s). | [5 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000009 | RQ-2024-05-10-0000031 |  | 2. | RP-2024-05-10-0000148 | CIP-009-7 R1.2. | Roles and responsibilities of responders. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS and their associated: 1. EACMS; and PACS | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, one or more recovery plans that include language identifying the roles and responsibilities of responders. | [5 empty] | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000009 | RQ-2024-05-10-0000031 |  | 3. | RP-2024-05-10-0000149 | CIP-009-7 R1.3. | One or more processes for the backup and storage of information required to recover Applicable System functionality. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS and their associated: 1. EACMS; and PACS | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation of specific processes for the backup and storage of information required to recover Applicable System functionality. | [5 empty] | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000009 | RQ-2024-05-10-0000031 |  | 4. | RP-2024-05-10-0000150 | CIP-009-7 R1.4. | One or more processes to verify the successful completion of the backup processes in Part 1.3 and to address any backup failures. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS at Control Centers and their associated: 1. EACMS; and PACS | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, logs, workflow or other documentation confirming that the backup process completed successfully and backup failures, if any, were addressed. | [5 empty] | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000009 | RQ-2024-05-10-0000031 |  | 5. | RP-2024-05-10-0000151 | CIP-009-7 R1.5. | One or more processes to preserve data, per system capability, for determining the cause of a Cyber Security Incident that triggers activation of the recovery plan(s). Data preservation should not impede or restrict recovery. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS and their associated: 1. EACMS; and 2. PACS SCI supporting an Applicable System in this part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, procedures to preserve data, such as preserving a corrupted drive or making a data mirror of the system before proceeding with recovery. | [5 empty] | 150000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000009 | RQ-2024-05-10-0000032 |  | 1. | RP-2024-05-10-0000152 | CIP-009-7 R2.1. | Test each of the recovery plans referenced in Requirement R1 at least once every 15 calendar months: - By recovering from an actual incident; - With a paper drill or tabletop exercise; or - With an operational exercise. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS at Control Centers and their associated: 1. EACMS; and PACS | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated evidence of a test (by recovering from an actual incident, with a paper drill or tabletop exercise, or with an operational exercise) of the recovery plan at least once every 15 calendar months. For the paper drill or full operational exercise, evidence may include meeting notices, minutes, or other records of exercise findings. | [5 empty] | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000009 | RQ-2024-05-10-0000032 |  | 2. | RP-2024-05-10-0000153 | CIP-009-7 R2.2. | Test a representative sample of information used to recover Applicable System functionality at least once every 15 calendar months to ensure that the information is useable and is compatible with current configurations. An actual recovery that incorporates the information used to recover Applicable System functionality substitutes for this test. | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS at Control Centers and their associated: 1. EACMS; and PACS | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, operational logs or test results with criteria for testing the usability (e.g., sample tape load, browsing tape contents) and compatibility with current system configurations (e.g., manual, or automated comparison checkpoints between backup media contents and current configuration). | [5 empty] | 220000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000009 | RQ-2024-05-10-0000032 |  | 3. | RP-2024-05-10-0000154 | CIP-009-7 R2.3. | Test each of the recovery plans referenced in Requirement R1 at least once every 36 calendar months through an operational exercise of the recovery plans in an environment representative of the production environment. An actual recovery response may substitute for an operational exercise. | High impact BCS | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of: - An operational exercise at least once every 36 calendar months between exercises, that demonstrates recovery in a representative environment; or - An actual recovery response that occurred within the 36 calendar month timeframe that exercised the recovery plans. | [5 empty] | 230000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000009 | RQ-2024-05-10-0000033 | RP-2024-05-10-0000155 | 1. | RP-2024-05-10-0000156 | CIP-009-7 R3.1.1. | Document any lessons learned associated with a recovery plan test or actual recovery or document the absence of any lessons learned; | [29 empty] | 311000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000009 | RQ-2024-05-10-0000033 | RP-2024-05-10-0000155 | 2. | RP-2024-05-10-0000157 | CIP-009-7 R3.1.2. | Update the recovery plan based on any documented lessons learned associated with the plan; and | [29 empty] | 312000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000009 | RQ-2024-05-10-0000033 | RP-2024-05-10-0000155 | 3. | RP-2024-05-10-0000158 | CIP-009-7 R3.1.3. | Notify each person or group with a defined role in the recovery plan of the updates to the recovery plan based on any documented lessons learned. | [29 empty] | 313000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000009 | RQ-2024-05-10-0000033 | RP-2024-05-10-0000159 | 1. | RP-2024-05-10-0000160 | CIP-009-7 R3.2.1. | Update the recovery plan; and | [29 empty] | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000009 | RQ-2024-05-10-0000033 | RP-2024-05-10-0000159 | 2. | RP-2024-05-10-0000161 | CIP-009-7 R3.2.2. | Notify each person or group with a defined role in the recovery plan of the updates. | [29 empty] | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000009 | RQ-2024-05-10-0000033 |  | 1. | RP-2024-05-10-0000155 | CIP-009-7 R3.1. | No later than 90 calendar days after completion of a recovery plan test or actual recovery: | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS at Control Centers and their associated: 1. EACMS; and 2. PACS | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, all of the following: 1. Dated documentation of identified deficiencies or lessons learned for each recovery plan test or actual incident recovery or dated documentation stating there were no lessons learned; 2. Dated and revised recovery plan showing any changes based on the lessons learned; and 3. Evidence of plan update distribution including, but not limited to: - Emails; - USPS or other mail service; - Electronic distribution system; or - Training sign-in sheets. | [5 empty] | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000009 | RQ-2024-05-10-0000033 |  | 2. | RP-2024-05-10-0000159 | CIP-009-7 R3.2. | No later than 60 calendar days after a change to the roles or responsibilities, responders, or technology that the Responsible Entity determines would impact the ability to execute the recovery plan: | High impact BCS and their associated: 1. EACMS; and 2. PACS Medium impact BCS at Control Centers and their associated: 1. EACMS; and 2. PACS | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, all of the following: 1. Dated and revised recovery plan with changes to the roles or responsibilities, responders, or technology; and 2. Evidence of plan update distribution including, but not limited to: - Emails; - USPS or other mail service; - Electronic distribution system; or - Training sign-in sheets. | [5 empty] | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000034 | RP-2024-05-10-0000163 | 1. | RP-2024-05-11-0000001 | CIP-010-5 R1.2.1. | Prior to implementing any change from Part 1.1 in the production environment, except during a CIP Exceptional Circumstance, test the changes in a test environment that minimizes differences with the production environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and | [29 empty] | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000034 | RP-2024-05-10-0000163 | 2. | RP-2024-05-11-0000002 | CIP-010-5 R1.2.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. | [29 empty] | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000034 | RP-2024-05-11-0000003 | 1. | RP-2024-05-11-0000004 | CIP-010-5 R1.3.1. | Verify the identity of the software source; and | [29 empty] | 131000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000034 | RP-2024-05-11-0000003 | 2. | RP-2024-05-11-0000005 | CIP-010-5 R1.3.2. | Verify the integrity of the software obtained from the software source. | [29 empty] | 132000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000034 |  | 1. | RP-2024-05-10-0000162 | CIP-010-5 R1.1. | Authorize changes that affect Applicable Systems where those changes alter the behavior of one or more cyber security controls, excluding procedural and physical controls, serving one or more requirement parts in CIP-005 or CIP-007, as defined by the Responsible Entity. | High impact BCS and their associated: 1. Electronic Access Control or Monitoring Systems (EACMS); 2. Physical Access Control Systems (PACS); and 3. Protected Cyber Asset (PCA) Medium impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, one or more documented process(es) that authorize changes that affect Applicable Systems where those changes alter the behavior of one or more cyber security controls, excluding procedural and physical controls, serving one or more requirement parts in CIP-005 or CIP-007, as defined by the Responsible Entity, such as: - Change records documenting the authorization. - Change records authorizing systems to automate changes to Applicable Systems. Examples of changes that may alter the behavior of one or more cyber security controls may include, but are not limited to: - Installation, removal, or update of operating system, firmware, software, or cyber security patches, including changes to VCA parent images from which Applicable Systems will be instantiated (CIP-007 R1.1, R2) - Configuration changes that affect routable protocol network accessibility (CIP-007 R1.1) - Configuration changes affecting the establishment of, or access control through, an ESP (CIP-005 R1, R2) - Configuration of malicious code prevention methods (CIP-007 R3) - Configuration of security event logging/alerting (CIP-007 R4) - Configuration changes to authentication methods (e.g., a password enforcement policy change, but not users changing their password) (CIP-007 R5) - Configuration changes to CPU/memory sharing of VCAs on SCI (CIP-007 R1.3) | [5 empty] | 110000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000034 |  | 2. | RP-2024-05-10-0000163 | CIP-010-5 R1.2. | High impact BCS |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls tested along with successful test results and a list of differences between the production and test environments with descriptions of how any differences were accounted for, including the date of the test, or logs from systems that automatically remediate deviations in required cyber security controls in CIP-005 and CIP-007. | [5 empty] | 120000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000034 |  | 3. | RP-2024-05-11-0000003 | CIP-010-5 R1.3. | Prior to the installation of operating systems, firmware, software, or software patches and when the method to do so is available to the Responsible Entity from the software source: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [8 empty] | 130000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000034 |  | 4. | RP-2024-05-11-0000006 | CIP-010-5 R1.4. | As a part of the changes authorized per Part 1.1, verify that the behavior(s) of the altered cyber security controls were not adversely affected. | High impact BCS and their associated: EACMS; PACS; and PCA Medium impact BCS and their associated: EACMS; PACS; and PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to: - System generated evidence of automated verification of required behaviors. - Records from a verification process showing that, as a part of the change process, the required behavior(s) of the altered security controls remain effective, were corrected, or the change was reversed. | [5 empty] | 140000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000035 | RP-2024-05-11-0000007 | 1. | RP-2024-05-11-0000008 | CIP-010-5 R2.1.1. | Configuration on each Applicable System that affects its routable protocol network accessibility; | [29 empty] | 211000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000035 | RP-2024-05-11-0000007 | 2. | RP-2024-05-11-0000009 | CIP-010-5 R2.1.2. | Configuration of CPU or memory sharing of VCAs on SCI; | [29 empty] | 212000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000035 | RP-2024-05-11-0000007 | 3. | RP-2024-05-11-0000010 | CIP-010-5 R2.1.3. | Installation, removal, and update of operating system, firmware, software, and cyber security patches. | [29 empty] | 213000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000035 | RP-2024-05-11-0000007 | 4. | RP-2024-05-11-0000011 | CIP-010-5 R2.1.4. | Configuration of malicious code protection methods; | [29 empty] | 214000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000035 | RP-2024-05-11-0000007 | 5. | RP-2024-05-11-0000012 | CIP-010-5 R2.1.5. | Configuration of security event logging or alerting; | [29 empty] | 215000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000035 | RP-2024-05-11-0000007 | 6. | RP-2024-05-11-0000013 | CIP-010-5 R2.1.6. | Configuration of authentication methods; and | [29 empty] | 216000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000035 | RP-2024-05-11-0000007 | 7. | RP-2024-05-11-0000014 | CIP-010-5 R2.1.7. | Changes to the enabled or disabled status of accounts. Document and investigate detected unauthorized changes. | [29 empty] | 217000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000035 |  | 1. | RP-2024-05-11-0000007 | CIP-010-5 R2.1. | Methods to monitor, per system capability, at least once every 35 calendar days, for unauthorized changes that affect Applicable Systems, where those changes alter the behavior of one or more cyber security controls, excluding procedural and physical controls, serving one or more requirement parts in CIP-007, as defined by the Responsible Entity; that include at least one cyber security control for each of the following: | High impact BES Cyber Systems and their associated: 1. EACMS; and 2. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documented methods to monitor at least once every 35 calendar days. Monitoring system configuration or procedural controls demonstrating monitoring of at least one cyber security control for 2.1.1 through 2.1.7. Examples of evidence may include, but are not limited to, reports generated from automated tools or manual reviews along with records of investigation for any unauthorized changes that were detected. Note: monitoring of VCA parent images from which Applicable Systems will be instantiated is an example of an automated control for 2.1.3. | [5 empty] | 210000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000036 | RP-2024-05-11-0000016 | 1. | RP-2024-05-11-0000019 | CIP-010-5 R3.2.1. | Perform an active vulnerability assessment in a test environment that minimizes differences with the production environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects; and | [29 empty] | 321000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000036 | RP-2024-05-11-0000016 | 2. | RP-2024-05-11-0000018 | CIP-010-5 R3.2.2. | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. | [29 empty] | 322000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000036 |  | 1. | RP-2024-05-11-0000015 | CIP-010-5 R3.1. | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. | High impact BES Cyber Systems and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BES Cyber Systems and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: - A document listing the date of the assessment (performed at least once every 15 calendar months), the controls assessed for each BES Cyber System along with the method of assessment; or - A document listing the date of the assessment and the output of any tools used to perform the assessment. | [5 empty] | 310000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000036 |  | 2. | RP-2024-05-11-0000016 | CIP-010-5 R3.2. | At least once every 36 calendar months, per system capability: | High impact BES Cyber Systems. SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed at least once every 36 calendar months), the output of the tools used to perform the assessment, and a list of differences between the production and test environments with descriptions of how any differences were accounted for in conducting the assessment. | [5 empty] | 320000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000036 |  | 3. | RP-2024-05-11-0000020 | CIP-010-5 R3.3. | Prior to becoming a new Applicable System, perform an active vulnerability assessment of the new Applicable System, except for: - Like replacements or additions with a previously assessed configuration of an existing Applicable System; or - CIP Exceptional Circumstances. | High impact BCS and their associated: 1. EACMS; and 2. PCA SCI supporting an Applicable System in this Part | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to: - The output of tools used to perform the assessment; or - Reports from automated assessment and remediation mechanisms (remediation VLANs, quarantine systems, 802.1x mechanisms that assess and remediate, etc.) that documents the date of the assessment performed prior to becoming a new Applicable System. | [5 empty] | 330000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
ST-2024-05-10-0000010 | RQ-2024-05-10-0000036 |  | 4. | RP-2024-05-11-0000021 | CIP-010-5 R3.4. | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. | High impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA Medium impact BCS and their associated: 1. EACMS; 2. PACS; and 3. PCA SCI supporting an Applicable System in this Part. | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: - Reports or logs from automated mechanisms that perform remediation of VCAs at instantiation; or - Documentation listing the results or the review or assessment, a list of action items, documented proposed dates of completion for the action plan, and records of the status of the action items (such as minutes of a status meeting, updates in a work order system, or a spreadsheet tracking the action items). | [5 empty] | 340000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US