## non-CIP SNOPs
Filed_Date | NOC_ID | Region | Registered_Entity_Name | NCR | Reliability_Functions | Notice_of_Confirmed_Violation_or_Settlement_Agreement | Admits_OR_Agrees_and_Stipulates_OR_Neither_Admits_nor_Denies_OR_Does_Not_Contest | Total_Penalty | NERC_Violation_ID | Reliability_Standard | Requirement | Risk_Assessment | Violation_Risk_Factor | Violation_Severity_Level | Discovery_Method | Reported_to_Region_Date | Noncompliance_Start_Date | Noncompliance_End_Date | Mitigation_Expected_Completion_Date | Mitigation_Completion_Date | Date_Regional_Entity_Verified_Completion_of_Mitigation | Description_of_Noncompliance | Description_of_Risk_Assessment | Description_of_Mitigation | Other_Factors_and_Compliance_History_Discussion
2025-01-30 | NOC-2852 | RF | City of Lansing by its Board of Water and Light | NCR00718 | TO | Settlement Agreement | Admits | 40000 | RFC2020024314 | FAC-008-3 | R6. | Moderate | Medium | Lower | Compliance Audit | 2020-12-11 | 2011-06-30 | 2024-03-08 |  | 2024-03-08 | 2024-11-07 | On December 11, 2020, ReliabilityFirst identified as part of a Compliance Audit that the entity, as a Transmission Owner, was in violation of FAC-008-3 R6. ReliabilityFirst subsequently determined that the violation dated back to FAC-009-1 R1. The Compliance Audit was conducted from December 7, 2020, through December 11, 2020. This violation involves the entity’s failure to establish Facility Ratings consistent with its Facility Ratings Methodology (FRM). The entity’s FRM provided that, for emergency ratings, all transmission lines, including any vertical clearance thereof, should be capable of safely operating at 160C. However, the entity only had evidence to support design to a safe operating temperature of 100C, despite basing its emergency ratings off an operating temperature of 160C. The cause of the discrepancy was a software issue. As part of mitigation, the entity changed its FRM (a) to determine normal and emergency ratings based on a safe operating temperature of 100C and (b) to more clearly account for sag limited ratings based on the minimum allowable clearance to ground or other objects as dictated by the National Electric Safety Code (NESC). Following the changes, the entity was required to remediate thermal rating inconsistencies based on vertical clearance limits for two transmission lines: the Enterprise-Wise line and the Northeast-Willow line. The Enterprise-Wise Transmission Line remained noncompliant with the entity’s methodology for both emergency and normal ratings even after adjusting to a safe operating temperature of 100C and considering the NESC. Therefore, the entity performed fieldwork to assign the line a higher sag limited rating than its interim rating. The average percent derate required was 39%. The Northeast-Willow Transmission Line remained noncompliant with the entity’s methodology for both emergency and normal ratings even after adjusting to a safe operating temperature of 100C and considering the NESC. Therefore, the entity performed fieldwork to assign the line a higher sag limited rating than its interim rating. The average percent derate required was 83%. The root cause of this violation is multifaceted. First, as to the original audit finding (i.e., the incorrect software setting), the entity failed to implement adequate verification controls. Second, as to the derates required to remediate the thermal violations, the entity’s procedures did not sufficiently account for the particular attributes of field conditions around the Northeast-Willow and Enterprise-Wise lines. The violation began on June 30, 2011, when the entity registered as a TO and was required to comply with FAC-009-1, and ended on March 8, 2024, when the entity updated its FRM and completed the necessary fieldwork to remediate the incorrect Facility Rating for the Enterprise-Wise line. | This violation posed a moderate risk to the reliability of the bulk power system (BPS). The risk posed by having an incorrect basis or documented methodology for determining Facility Ratings is incorrectly or incompletely determining Facility Ratings. Entities rely on accurate Facility Ratings for a variety of reliability focused activities, including, without limitation, relay loadability, modeling/analysis, data specifications, operations, and planning. Facility Ratings errors can result in compounding risks to the reliability of the BPS. The risk here is not minimal because of the duration of the violation, the size of derates on the Enterprise-Wise and Northeast-Willow lines (averages of 39% and 83%, respectively), and the nature of the discovery of the noncompliance (i.e., through a Compliance Audit, indicating a failure of the entity’s preventative and detective controls). The risk here is not serious because, for the Enterprise-Wise and Northeast-Willow lines, the entity never exceeded the corrected Facility Ratings or operated the affected transmission lines within 10% of the corrected Facility Ratings. Additionally, these lines were not tie lines with International Transmission Company. No harm is known to have occurred. | To complete its Mitigation Plan, the entity: 1) revised its documentation for its Facility Ratings software to ensure that staff use the entity’s current emergency ratings for new project analysis; 2) engaged a consultant to review and update its FRM; 3) reviewed and updated its FRM to reflect consistency with its new methodology (basing emergency ratings off of a safe operating temperature of 100C); 4) documented its internal controls related to the review of emergency ratings for use in designing new projects; 5) committed to work with an outside vendor to design and document the scope of a study of its transmission lines; 6) entered into a contract with an outside vendor for a LIDAR scan (and formal report based on the same); 7) confirmed its vendor commitment to complete a draft report, which the entity committed to review prior to its finalization; 8) received and reviewed the final transmission line sag clearance study (initiated in no. 5) and used this information to update its Facility Ratings and FRM; 9) updated its FRM to reflect its use of an exception in the NESC which provides for a reduced clearance requirements when a transmission line and distribution line (or other support structure) are owned by the same entity; 10) calculated temporary Facility Ratings for transmission lines that were identified in the transmission line sag clearance study and provided these ratings to its ISO, MISO study; 11) completed the necessary field work to bring the Northeast-Willow transmission line into compliance with the entity’s FRM; 12) completed the necessary field work to bring the Enterprise-Wise transmission line into compliance with the entity’s FRM; and 13) updated its Facility Ratings and FRM based on the results of the transmission line sag clearance study | ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. ReliabilityFirst recognizes that the cooperation of Registered Entities is vital to maintaining and strengthening the reliability of the BPS. Throughout the lifecycle of this noncompliance, the entity was cooperative and responsive. As such, cooperating credit is being awarded to the entity.