## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits" "Neither Admits nor Denies" "Agrees and Stipulates to the Facts" or "Does Not Contest" | Factors Affecting the Penalty and Other Considerations
Midwest Reliability Organization (MRO) | Alliant Energy - East (ALTE) | NCR00961 | MRO201000211 | Notice of Confirmed Violation | On July 16, 2010, ALTE, as a Distribution Provider (DP) and Generator Owner (GO), self-certified noncompliance with PRC-005-1 R1 because its Protection System maintenance and testing procedure did not address DC Control Circuitry. ALTE revised its Protection System maintenance and testing procedure on March 1, 2009. The revision omitted a reference to conducting functional testing (DC control circuitry) of the Protection System which was included in the previous program dated May 21, 2007. | PRC-005-1 | R1.1; R1.2 | High | High | This violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because it presented a documentation issue only. ALTE had conducted maintenance and testing and provided testing records to MRO for all of its DC control circuitry. | 3/1/2009 (when ALTE revised its maintenance and testing procedure) | 11/7/2011 (Mitigation Plan completion) | $40,000 (for MRO201000211 and MRO201000228) | Self-Certification | ALTE revised its Protection System maintenance and testing procedure to include DC Control Circuitry. | 2011-11-07 | 2011-11-08 | Admits | ALTE had an internal compliance program (ICP) at the time of the violation but it was considered a neutral factor in determining the penalty amount.
Midwest Reliability Organization (MRO) | Alliant Energy - East (ALTE) | NCR00961 | MRO201000228 | Notice of Confirmed Violation | On October 21, 2010, ALTE, as a Distribution Provider (DP) and Generator Owner (GO), self-reported noncompliance with PRC-005-1 R2 because it failed to maintain and test 17 station batteries. Upon receiving the Self-Report, MRO requested a full inventory of ALTE's Protection System maintenance and testing records. ALTE reported that it has 1,527 Protection System devices subject to PRC-005-1 R2. Of the 1,527 devices, ALTE failed to provide annual maintenance and testing records for 17 station batteries, or approximately 1% of its devices. ALTE has 20 total batteries and missed records for 17 batteries, which represent 85% of the total. | PRC-005-1 | R2.1; R2.2 | High | Lower | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because ALTE failed to provide maintenance and testing records for 17 station batteries located at several generating units, including two black-start units. The generating units at issue produce approximately 2,200 MW. Several large units did not have annual station battery test records for two to three years in a row, and a subset of these units had no visual check of station battery performed. ALTE has fourteen 345 kV BPS tie lines, two 161 kV BPS tie lines, thirty-four 138 kV BPS tie lines, and three 115 kV BPS tie lines. Therefore, considering some of the high voltage ties and the size of the generating units involved, MRO determined that this violation posed a moderate risk to the BPS. However, MRO determined that this was not a serious or substantial risk to the BPS because ALTE performed an analysis at each station to determine the impact on the BPS if a battery failed and the backup Protection System would have been required to operate, removing the generator substation bus from the BPS. At all of the generating stations where this analysis was completed, there were no branch overloads or voltage violations. Additionally, ALTE monitors the battery voltage at the generating sites which includes a low battery voltage alarm, and ALTE reported that all of the devices tested performed as expected without any issues. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/1/2011 (Mitigation Plan completion) | $40,000 (for MRO201000211 and MRO201000228) | Self-Report | ALTE performed the following actions to mitigate this violation: (1) performed a full survey of maintenance and testing records; (2) developed standard job plans for uniform application across the generating fleet to ensure that inspections are being performed consistently for all applicable battery banks; (3) developed and performed training regarding the PRC-005 Standard and the inspection requirements for the generating fleet, as well as documentation and record keeping; (4) developed an internal control plan to review a percentage of the Protection System components maintained and tested each year to ensure consistency, completeness and compliance to the program; and (5) maintained and tested Protection System equipment with missing records. | 2011-12-01 | 2012-02-14 | Admits | ALTE had an internal compliance program (ICP) at the time of the violation but it was considered a neutral factor in determining the penalty amount.
Midwest Reliability Organization (MRO) | Alliant Energy - West (ALTW) | NCR00962 | MRO201000210 | Notice of Confirmed Violation | On July 16, 2010, ALTW, as a Distribution Provider (DP) and Generator Owner (GO), self-certified noncompliance with PRC-005-1 R1 because its Protection System maintenance and testing procedure did not address DC Control Circuitry. ALTW revised its Protection System maintenance and testing procedure on March 1, 2009. The revision omitted a reference to conducting functional testing (DC control circuitry) of the Protection System which was included in the program dated May 21, 2007. ALTW has 455 DC Control Circuitry and 1333 Protection System devices total. | PRC-005-1 | R1.1; R1.2 | High | High | This violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because it presented a documentation issue only. ALTW had conducted maintenance and testing and provided testing records to MRO for all of its DC control circuitry. | 3/1/2009 (when ALTW revised its maintenance and testing procedure) | 11/7/2011 (Mitigation Plan completion) | $40,000 (for MRO201000210 and MRO201000190) | Self-Certification | ALTW revised its Protection System maintenance and testing procedure to include DC Control Circuitry. | 2011-11-07 | 2011-11-08 | Admits | ALTW had an internal compliance program (ICP) at the time of the violation but it was considered a neutral factor in determining the penalty amount.
Midwest Reliability Organization (MRO) | Alliant Energy - West (ALTW) | NCR00962 | MRO201000190 | Notice of Confirmed Violation | On May 7, 2010, ALTW, as a Distribution Provider (DP) and Generator Owner (GO), self-reported noncompliance with PRC-005-1 R2 because it failed to maintain and test station batteries. Upon receiving the Self-Report, MRO requested a full inventory of ALTW's Protection System maintenance and testing records. ALTW reported that it has 1,333 Protection System devices subject to PRC-005-1 R2. Of the 1,333 devices, ALTW failed to provide annual maintenance and testing records for 15 station batteries, or approximately 1% of its total devices. ALTW has 19 total batteries and missed records for 15 batteries, which represent 78.95% of the total. | PRC-005-1 | R2.1; R2.2 | High | Lower | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because ALTW failed to provide maintenance and testing records for 15 station batteries located at several generating units, including two black-start units. The generating units at issue produce approximately 2,100 MW. Several large units did not have annual station battery test records for two to three years in a row and a subset of these units had no visual check of station battery performed. ALTW has sixteen 345 kV BPS tie lines, forty-one 161 kV BPS tie lines, one 138 kV BPS tie line, and two 115 kV BPS tie lines. Therefore, considering some of the high voltage tie lines and the size of the generating units, MRO determined that this violation posed a moderate risk to the BPS. However, MRO determined that this was not a serious or substantial risk to the BPS because ALTW performed an analysis at each station to determine the impact on the BPS if a battery failed and the backup Protection System would have been required to operate, removing the generator substation bus from the BPS. At all of the generating stations where this analysis was completed, there were no branch overloads or voltage violations. Additionally, ALTW monitors the battery voltage at the generating site which included a low battery voltage alarm and ALTW reported that all of the devices tested performed as expected without any issues. | 6/18/2007 (when the Standard became mandatory and enforceable) | 12/1/2011 (Mitigation Plan completion) | $40,000 (for MRO201000210 and MRO201000190) | Self-Report | ALTW performed the following actions to mitigate this violation: (1) performed a full survey of maintenance and testing records; (2) developed standard job plans for uniform application across the generating fleet to ensure that inspections are being performed consistently for all applicable battery banks; (3) developed and performed training regarding the PRC-005 Standard and the inspection requirements for the generating fleet, as well as documentation and record keeping; (4) developed an internal control plan to review a percentage of the Protection System components maintained and tested each year to ensure consistency, completeness and compliance to the program; and (5) maintained and tested Protection System equipment with missing records. | 2011-12-01 | 2012-02-14 | Admits | ALTW had an internal compliance program (ICP) at the time of the violation but it was considered a neutral factor in determining the penalty amount.
ReliabilityFirst Corporation (ReliabilityFirst) | Wolf Hills Energy, LLC (Wolf Hills) | NCR00953 | RFC2011001115 | Settlement Agreement | On September 16, 2011, Wolf Hills, as a Generation Owner, self-reported a possible violation of PRC-005-1 R1 to ReliabilityFirst. Prior to November 3, 2011, Wolf Hills did not have a documented maintenance and testing program for its Protection System devices. Wolf Hills has 123 total Protection System devices, consisting of 11 relays, 96 voltage and current sensing devices, five battery banks, and 11 DC Control Circuits. ReliabilityFirst determined that since November 3, 2011 Wolf Hills has had a documented maintenance and testing program for its protection system devices pursuant to PRC-005-1, R1. | PRC-005-1 | R1 | High | Severe | ReliabilityFirst determined that this violation posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. Despite the lack of a documented Program, Wolf Hills represents it performed routine maintenance on all of its Protection System devices within the last two years. This routine maintenance included maintenance and testing on all of Wolf Hills' relays, voltage and current sensing devices. battery banks, and DC control circuits. Additionally, Wolf Hills reviewed all plant events and determined it has not had any Protection System misoperations to date. | 6/18/2007 (date standard became mandatory and enforceable) | 11/3/2011 (when Wolf Hills documented its maintenance and testing program) | 5000 | Self-Report | On November 3, 2011 Wolf Hills documented its maintenance and testing program for its Protection System devices. The program includes, as required, a summary of maintenance and testing procedures including maintenance and testing intervals, and basis for each of the intervals. | 2011-11-03 | 2012-06-14 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of Wolf Hills' internal compliance program (ICP) as mitigating factors. For instance, Wolf Hills has an ICP in place that addresses each applicable Reliability Standard. Wolf Hills distributed copies of the ICP to all appropriate personnel. Wolf Hills has those operating and managing its ICP work independently of those that are directly responsible for compliance with Reliability Standards. Additionally, Wolf Hills provides annual training to all employees with direct and indirect responsibility for compliance with Reliability Standards. ReliabilityFirst also considered that Wolf Hills Self-Reported the violation as a mitigating factor. A Settlement Agreement covering a violation of PRC-005-1 R2.1 for Lincoln Generating Facility, LLC, an affiliate of Wolf Hills, was filed with FERC on July 6, 2010 under NP10-126-000. On August 5, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering a violation of PRC-005-1 R2 for Troy Energy, LLC, an affiliate of Wolf Hills, was filed with FERC on June 29, 2011, under NP11-207-000. On July 29, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering a violation of PRC-005-1 R1 for New Covert Generating Company, LLC, an affiliate of Wolf Hills, was filed with FERC on July 28, 2011 under NP11-235-000. On August 29, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. ReliabilityFirst determined Wolf Hills' alleged violation of PRC-005-1, R1 evidenced conduct similar to prior alleged violations of its affiliated companies. Therefore, ReliabilityFirst considered Wolf Hills' compliance history as an aggravating factor.
SERC Reliability Corporation (SERC) | ExxonMobil - Baton Rouge (ExxonMobil) | NCR00128 | SERC201000531 | Settlement Agreement | On May 11, 2010, ExxonMobil, as a registered Generator Owner (GO) and Transmission Owner (TO), self-reported a violation of PRC-005-1 R2. ExxonMobil indicated that it had failed to test and calibrate several relays within the defined four-year interval, lacked documentation for battery testing for approximately four months in 2007, and failed to test batteries on a monthly basis in accordance with its procedure from October 2007 to January 2009. SERC staff reviewed the spreadsheets prepared by ExxonMobil, which included each Protection System device, the applicable defined maintenance and testing intervals, the most recent test date, and the previous test date for each device. SERC staff reviewed test dates for all test periods back to the beginning of the enforceable period. SERC staff verified that the listed intervals provided in the spreadsheets and those included in ExxonMobil’s procedures were consistent. For its GO function, ExxonMobil adopted the Generator Operator's Protection System maintenance and testing procedures. For its TO function, ExxonMobil utilized internal ExxonMobil procedures. SERC staff determined that ExxonMobil tested the following out of interval: 16 out of 158 protective relays (10.1%), 276 out of 337 voltage and current sensing devices (81.9%), and 1 out of 19 station batteries (5.3%). In addition, SERC staff determined that ExxonMobil lacked previous test records for the following: 2 out of 158 protective relays (1.2%), 1 out of 2 associated communication systems (50%), 22 out of 337 voltage and current sensing devices (6.5%), and 76 out of 82 DC control circuitry devices (92.7%). SERC staff determined that ExxonMobil was in violation of PRC-005-1 R2 for failing to have documentation that its Protection System devices were maintained and tested within the defined intervals or failing to have previous test records for 394 of its 598 Protection System devices, which make up approximately 66% of the Protection System devices. | PRC-005-1 | R2 | High | High | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. ExxonMobil's Protection Systems are designed with redundancy to minimize the risk of a failure of any one device; 2. ExxonMobil and the Generator Operator monitor system status 24 hours a day, 7 days a week to prompt a quick response in the event of an unexpected change. ExxonMobil’s battery systems are monitored 24 hours a day, seven days a week. ExxonMobil has indicator lights for Protection System devices to alert personnel that there is an issue with such devices. ExxonMobil also conducts visual inspections of Protection System devices on a monthly basis. No alarms sounded during the period of the violation. 3. ExxonMobil is an industrial complex that owns a co-generation plant, considered to be a Qualifying Facility under the Public Utility Regulatory Policies Act of 1978 (PURPA), with roughly 30 MW of surplus generation capacity. 4. ExxonMobil found no issues with the Protection System devices during the most recent testing. | 8/28/2008 (when ExxonMobil registered as a GO) | 4/2/2012 (Mitigation Plan completion) | $7,000 (for SERC201000531 and SERC201000545) | Self-Report | ExxonMobil tested all devices according to its Protection System maintenance and testing procedures and documented the results. ExxonMobil confirmed that the required personnel are aware of the Protection System maintenance and testing Reliability Standard and the actions required to comply with the Standard. | 2012-04-02 | 2012-05-17 | Neither Admits nor Denies | ExxonMobil had not implemented a sufficient internal compliance program (ICP) prior to the start of this violation. Accordingly, SERC considered ExxonMobil's ICP a neutral factor in the penalty determination. An ExxonMobil affiliate, ExxonMobil Oil Corporation - Beaumont Refinery (ExxonMobil-BR), had a prior violation of PRC-005-1 R2, which was filed with FERC under NP10-90-000 on March 31, 2010. SERC considered ExxonMobil-BR's prior violation of PRC-005-1 R2 an aggravating factor in the penalty determination.
SERC Reliability Corporation (SERC) | ExxonMobil - Baton Rouge (ExxonMobil) | NCR00128 | SERC201000545 | Settlement Agreement | On May 28, 2010, ExxonMobil, as a registered Generator Owner (GO) and Transmission Owner (TO), self-reported a violation of PRC-005-1 R1. ExxonMobil indicated that it did not include voltage and current sensing devices nor DC control circuitry in its maintenance and testing program as required prior to August 2009. ExxonMobil’s TO and GO functions did not utilize the same Protection System maintenance and testing procedures. For its GO function, ExxonMobil adopted the Generator Operator's Protection System maintenance and testing procedures. For its TO function, ExxonMobil utilized internal procedures based on the NERC document, "Protection System Maintenance: A Technical Reference." SERC staff determined that the maintenance and testing procedures ExxonMobil associated with its GO function listed the testing intervals for relays, potential transformers, current transformers, and DC control circuitry, but did not list the interval basis or summary of maintenance and testing procedures for these devices. Additionally, the maintenance and testing procedures addressed neither the battery maintenance and testing prior to June 2, 2009, nor the associated communications systems (ACS) maintenance and testing prior to February 22, 2011. SERC staff determined that the initial maintenance and testing procedures ExxonMobil associated with its TO function were approved on November 12, 2009, approximately eight months after ExxonMobil’s registration as a TO. The procedure included maintenance intervals and a summary of maintenance and testing for the Protection System devices. The procedure also stated that ExxonMobil did not have ACS devices and did not include the interval basis for the Protection System devices. SERC staff determined that ExxonMobil failed to provide evidence that it had a compliant Protection System maintenance and testing program that included maintenance and testing intervals and their basis and a summary of maintenance and testing procedures in place on August 28, 2008, the date of its registration as a GO, and on March 11, 2009, the date of its registration as a TO. | PRC-005-1 | R1 | High | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. ExxonMobil's Protection Systems are designed with redundancy to minimize the risk of a failure of any one device; 2. ExxonMobil and the Generator Operator monitor system status 24 hours a day, 7 days a week to prompt a quick response in the event of an unexpected change. ExxonMobil’s battery systems are monitored 24 hours a day, seven days a week. ExxonMobil has indicator lights for Protection System devices to alert personnel that there is an issue with such devices. ExxonMobil also conducts visual inspections of Protection System devices on a monthly basis. No alarms sounded during the period of the violation. 3. ExxonMobil is an industrial complex that owns a co-generation plant, considered to be a Qualifying Facility under the Public Utility Regulatory Policies Act of 1978 (PURPA), with roughly 30 MW of surplus generation capacity. 4. ExxonMobil found no issues with the Protection System devices during the most recent testing. | 8/28/2008 (when ExxonMobil registered as a GO) | 4/2/2012 (Mitigation Plan completion) | $7,000 (for SERC201000531 and SERC201000545) | Self-Report | ExxonMobil updated its Protection System maintenance and testing procedures to meet all of the requirements of PRC-005-1 R1 as a GO. The updates include the maintenance and testing intervals and their basis, and a summary of maintenance and testing procedures. ExxonMobil also updated its Protection System maintenance and testing procedures to meet all of the requirements of PRC-005-1 R1 as a TO, to include the maintenance and testing intervals and their basis, and a summary of maintenance and testing procedures. | 2012-04-02 | 2012-05-17 | Neither Admits nor Denies | ExxonMobil had not implemented a sufficient internal compliance program (ICP) prior to the start of this violation. Accordingly, SERC considered ExxonMobil's ICP a neutral factor in the penalty determination. An ExxonMobil affiliate, ExxonMobil Oil Corporation - Beaumont Refinery (ExxonMobil-BR), had a prior violation of PRC-005-1 R2, which was filed with FERC under NP10-90-000 on March 31, 2010. SERC considered ExxonMobil-BR's prior violation of PRC-005-1 R2 an aggravating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Louisiana Generating LLC (LaGen) | NCR01265 | SERC2011008220 | Settlement Agreement | On September 26, 2011, LaGen self-reported a violation of PRC-005-1 R2, stating that it discovered that direct current (DC) functional trip checks exceeded the interval designated in LaGen’s transmission Protection System maintenance and testing program for three devices. On November 18, 2011, LaGen submitted a second Self-Report indicating that DC functional trip checks with the associated bushing current transformer (CT) saturation tests and station battery test also exceeded the intervals designated in LaGen’s transmission Protection System maintenance and testing program. SERC considered the incidents detailed in the November 18, 2011 Self-Report to be an expansion of the scope of the September 26, 2011 Self-Report. During its assessment of the violation, SERC discovered additional Protection System devices that exceeded the defined intervals in LaGen's generation and transmission Protection System maintenance and testing programs. SERC determined that LaGen, as a Generator Owner and Transmission Owner, tested 3 out of 583 protective relays (0.5%), 81 out of 776 voltage and current sensing devices (10.4%), 16 out of 54 station batteries (29.6%), and 89 out of 660 DC control circuitry devices (13.5%) outside of the defined intervals. In total, LaGen tested 189 out of 2,103 Protection System devices (8.99%) outside of the defined intervals. | PRC-005-1 | R2; R2.1 | High | Lower | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1. LaGen’s staff continuously monitors its protective relay systems, DC control circuit and CT functionality, and associated battery systems with alarms via SCADA and manual inspections. No alarms sounded during the period of the violation. If a protective device had alarmed, LaGen procedures require the operator, in coordination with on-call supervisors, to dispatch appropriate personnel to investigate and address the problem, thereby reducing the chance that failures would go undetected; 2. LaGen subsequently tested all of its relays, CTs, DC control circuits, and battery banks that were outside of the defined interval and found no problems; and 3. LaGen reported that no misoperations of the self-reported devices occurred during the pendency of the violation. | 8/13/2007 (the day after the first missed testing interval) | 1/7/2012 (Mitigation Plan completion) | 3500 | Self-Report | To mitigate this violation, LaGen tested all Protection System devices that were not tested according to their scheduled intervals. To ensure this does not happen in the future, LaGen's parent company, NRG Energy Inc., has: a. Restructured the engineering department such that all substation and relay engineering and field services now report up through a newly-developed engineer supervisor position. This revised structure allows for additional oversight and management of all Protection System testing activities. Front line responsibilities associated with the development and administration of Protection System relay testing and scheduling have been reassigned within the department; b. Committed to, in accordance with its Regulatory Compliance and Investigation Policy, assess discipline for a violation to responsible employees for failures to follow policy; c. Re-trained employees responsible for implementing and following the LaGen Protection System maintenance and testing program on the program and the importance of compliance with the NERC Reliability Standards; d. Added a column to the trip check tracking spreadsheet to indicate the previous trip check test date; e. Placed all elements in the LaGen Protection System maintenance and testing program into a workflow management program, which will provide timely reminder notifications of testing to be performed and tracking of completed tests; and f. Increased the number of activities in the corporate compliance tracking program and tasked the responsible person quarterly to verify that all elements in the LaGen Protection System maintenance and testing program are scheduled to be completed according to their prescribed intervals. | 2012-01-07 | 2012-04-09 | Neither Admits nor Denies | LaGen was operating under its parent company's, NRG Energy Inc.'s, internal compliance program (ICP) at the time of the violation. SERC considered the ICP to be a mitigating factor in the penalty determination. The ICP is managed by the Regulatory Compliance group, which has been led by either a named Chief Compliance Officer or Regulatory Compliance Officer who has full independent access to the CEO, COO, CAO, CFO, and the Board of Directors of NRG Energy, Inc. The Regulatory Compliance group is responsible for implementation of the ICP, is sufficiently resourced, and fully supported by management. The ICP includes training for employees and possible disciplinary action for employees involved in violations.
Southwest Power Pool Regional Entity (SPP RE) | Flat Ridge Wind Energy, LLC (Flat Ridge) | NCR10312 | SPP201100458 | Settlement Agreement | On January 14, 2011, Flat Ridge, as a Generator Owner (GO), self-certified a possible violation of PRC-005-1 R2 (2.1-2.2). Subsequently, on March 10, 2011, Flat Ridge supplemented its original Self-Certification with a Self-Report. Two of Flat Ridge's 24 Protection System devices (8.3%) were not tested according to Flat Ridge's maintenance and testing intervals. The first device tested outside the prescribed interval was the battery bank. The assessment matrix contained in Flat Ridge's maintenance and testing program specified semi-annual impedance checks on batteries and battery chargers. However, the only historical impedance check recorded was performed on March 16, 2010. As a result, Flat Ridge could not substantiate impedance checks occurring within the established interval. According to Flat Ridge, it was not Flat Ridge’s intention to perform impedance testing of its batteries on a semi-annual basis. At the time of the violation, the only documentation referencing impedance checks was the interval matrix attached to the Flat Ridge High Voltage Condition Assessment Procedure (HVCA) (a precursor to the current Flat Ridge PRC-005 Protection System Maintenance Program, which went into effect on April 16, 2010). Impedance checks were not referenced or described within the body of the HVCA or referenced on the corresponding semi-annual battery assessment form attached to the HVCA. Flat Ridge indicated that the inclusion of the impedance testing interval on the interval matrix attached to Flat Ridge’s HVCA was a documentation error. Flat Ridge was conducting all other battery maintenance and testing required by its procedure, including visual inspections, electrolyte level inspections, battery charger voltage and current levels, and semi-annual battery voltage checks. The second device tested outside the prescribed interval was the Universal Power Line Carrier (UPLC) system. On January 13, 2011, Flat Ridge technicians de-energized the Flat Ridge facility to perform maintenance on circuit breakers, including a capacitor bank circuit breaker. After completing the maintenance, as the technicians were attempting to re-energize the facility, the capacitor bank main circuit breaker tripped due to the failure of an associated current transformer and insulator, which caused the breaker to trip on undervoltage. The technicians attempted a second time to re-energize the capacitor bank by closing the circuit breaker, and the breaker tripped again, this time on both undervoltage and instantaneous overcurrent/alternating current time current. The first trip of the capacitor bank circuit breaker caused a circuit breaker at the 138 kV Medicine Lodge substation to open. The second trip of the capacity bank circuit breaker caused a circuit breaker at the 138 kV Harper substation to open. The opening of the Medicine Lodge and Harper circuit breakers resulted in an outage of the Medicine Lodge-Harper 138 kV transmission line and the isolation of the Flat Ridge facility. The Medicine Lodge-Harper line serves as the bulk power system (BPS) interconnection point for the Flat Ridge facility. Upon investigation, the technicians discovered that an antenna cable in the UPLC system associated with the Flat Ridge capacitor bank circuit breaker—a PRC-005 communication system device—was disconnected. The UPLC is utilized to transmit trip-blocking signals to the Medicine Lodge and Harper circuit breakers when a fault is isolated by the Flat Ridge capacitor bank circuit breaker. Had the UPLC device operated properly, it would have prevented the outage of the Medicine Lodge-Harper transmission line by preventing the operation of the Medicine Lodge and Harper circuit breakers. It was determined that the antenna cable had been disconnected on March 13, 2009, the month during which the Flat Ridge facility entered commercial operations. Flat Ridge provided the following explanations for why the antenna cable was disconnected: (1) the antenna cable may have originally been fastened incorrectly and become disconnected on its own, or (2) a contractor performing relay adjustments during March 2009 may have disconnected the antenna and failed to reconnect it when the adjustments were complete. Section 6.4 of the Flat Ridge protection system maintenance program calls for continuous monitoring of communication system alarms. Thus, the disconnection of the antenna cable should have produced an alarm, immediately detectable by operations staff. However, it was determined that Flat Ridge had not installed the necessary data collection point and software to ensure continuous monitoring of its communication systems. Therefore, the Flat Ridge operators were unaware of a problem which persisted for 22 months and resulted in the outage of approximately 30 miles of 138 kV transmission infrastructure, as well as the isolation of the Flat Ridge facility. The Flat Ridge facility was inspected by technicians between January 17, 2011 and January 19, 2011, following the January 13, 2011 misoperation. The technicians performed a visual inspection of the UPLC on January 17, 2011, and reconnected the antenna on that date. The Flat Ridge facility was returned to service on January 19, 2011, following satisfactory testing of the UPLC system. | PRC-005-1 | R2 (2.1, 2.2) | High | Lower | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the BPS. The failure to continuously monitor the UPLC resulted in a 27-minute outage of the 138 kV Medicine Lodge-Harper transmission line, but did not result in loss of load. Flat Ridge is not deemed a "critical asset" for system support or restoration by the Southwest Power Pool Reliability Coordinator (SPP RC). It is a wind-powered variable energy facility with a maximum capacity of 50 MW, and at the time of the communication failure, the facility was off-line and not supporting load. Had the facility been online at the time of the violation, the risk would have remained moderate since it is a variable energy facility and is offsetting some of the work of the base load generation in the area. Because the output is variable, an adequate amount of base load generation would always be available to ramp up and support load. Regarding its batteries, while Flat Ridge failed to perform battery and charger impedance testing within its defined interval, SPP RE found that the violation was mitigated by Flat Ridge’s technicians’ visual inspection of batteries and chargers on a weekly basis. Additionally, Flat Ridge continuously monitors its batteries for low voltage, which triggers local and remote alarms that by policy require the immediate response of a technician. | 3/18/2009 (when Flat Ridge became subject to PRC-005-1) | 12/1/2011 (Mitigation Plan completion) | 8000 | Self-certification | To mitigate the violation, Flat Ridge successfully installed and tested Distributed Network Protocol (DNP) software, which allows for continuous monitoring of its UPLC system via a centralized data collection point. The DNP system provides a communications checkback signal that indicates to operators whether the UPLC communication system is functioning and communicating properly between sites, and will trigger an alarm within the control center upon an antenna disconnection. Further, Flat Ridge verified that the UPLC communication signal was being transmitted between the Flat Ridge, Medicine Lodge, and Harper substations, and formal visual inspections of the UPLC antenna cable, which was moved to a more visible location after the event, were added to the weekly and monthly substation inspection checklists. Additionally, Flat Ridge updated its PRC-005 maintenance and testing procedure (PSMP) to only require impedance checks as necessary and removed the matrix calling for impedance checks during semi-annual maintenance. Instead, under the PSMP, impedance checks are optional and only required upon a request by BP Wind Energy’s engineering department to obtain more detailed information in the event fault conditions have occurred. Because battery impedance checks are viewed as above and beyond activity in the industry, SPP RE views this testing interval as reasonable. | 2011-12-01 | 2012-02-15 | Neither Admits nor Denies | SPP RE considered the fact that Flat Ridge self-certified the instant violation to be a mitigating factor in the penalty determination. Additionally, SPP RE took into account the fact that neither Flat Ridge, nor its affiliates, had prior violations of the same or similar Standard and requirement. Further, SPP RE considered the quality of the Flat Ridge compliance program, and the cooperation of the Flat Ridge staff during the violation review as mitigating factors in the penalty determination. Specifically, the BP Wind Energy business unit organization is responsible for managing and maintaining Flat Ridge's ICP. In 2011, BP Wind adopted a formal ICP, appointed a compliance officer, and hired a regulatory compliance specialist to support the regulatory compliance manager. The BP Wind regulatory compliance manager is assigned responsibility for supporting compliance with NERC reliability standards. With approval and oversight of the Flat Ridge asset manager and support and guidance from the BP Wind regulatory compliance manager and regulatory compliance specialist, the Flat Ridge facility manager is responsible for compliance with NERC reliability standards. The BP Wind regulatory compliance manager reports directly to BP Wind’s vice president of asset management and also reports indirectly to the BP Wind energy regulatory attorney and compliance officer on matters of regulatory compliance, including compliance with NERC reliability standards. The compliance officer and regulatory compliance manager have direct access to senior management of BP Alternative Energy North America, Inc. as well as senior management of other parent organizations, as necessary to resolve regulatory compliance issues. Flat Ridge’s ICP requires all employees to notify management of actual or potential non-compliance. Any employee act of ignoring, concealing, or misrepresenting requirements, procedures, or errors is subject to disciplinary action.
Western Electricity Coordinating Council (WECC) | GenOn California 2 (GCAII) | NCR11149 | WECC201103012 | Settlement Agreement | On September 20, 2011, GCAII submitted a Self-Certification identifying a potential violation of VAR-002-1.1b R1. WECC determined that GCAII, as a Generator Operator, did not operate one of its units in the proper mode. Specifically, GCAII operated its Mandalay generating unit #2 in the manual mode rather than automatic voltage control mode for brief periods during unit start-up on May 28, 2011 (28 minutes) and June 1, 2011 (one minute). The employee operator did not notify the Transmission Operator prior to operating the unit in manual mode. | VAR-002-1.1b | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) for the following reasons. First, although the generating unit is rated at 215 MW, the periods of operation in manual mode occurred when the unit was operating well below its rating. Second, the periods of operation in the incorrect mode were of short duration (28 minutes on May 28, 2011 and one minute on June 1, 2011) before GCAII switched the automatic voltage regulator (AVR) into the correct mode. Third, the amount of generation is a fraction of the generation available at the plant and an even smaller fraction of the generation available to the Transmission Operator. The Mandalay generating station has approximately 560 MW of capacity (from three total units), and GCAII owns approximately 5,000 MW of generation capacity in California. | 5/28/2011 (First Instance) 6/1/2011 (Second Instance) (when the generating unit was operated in incorrect mode) | 5/28/2011 (First Instance) 6/1/2011 (Second Instance) (when the generating unit resumed operation in the correct mode) | $1,500 (for WECC201103012 and WECC201103013) | Self-Certification | On February 21, 2012, GCAII submitted to WECC a Mitigation Plan to address the violation of VAR-002-1.1b R1. In accordance with the Mitigation Plan, GCAII has completed the following: (1) Trained operations employees on the requirements of the Standard and the existing operating procedures; (2) Trained employees on unit syncing procedures; (3) Clearly marked instructions on control panel; and (4) Included operations personnel on AVR and power system stabilizer (PSS) status changes by leveraging its real-time data and events management system. | 2011-07-29 | 2012-05-31 | Does Not Contest
Western Electricity Coordinating Council (WECC) | GenOn California 2 (GCAII) | NCR11149 | WECC201103013 | Settlement Agreement | On September 20, 2011, GCAII submitted a Self-Certification addressing a violation of VAR-002-1.1b R3. WECC determined that GCAII, as a Generator Operator, did not notify its Transmission Operator within thirty minutes of a status or capability change in GCAII's Reactive Power resource, as required by the Standard. Specifically, for brief periods during unit start-up on May 28, 2011 (28 minutes) and June 1, 2011 (one minute), GCAII operated its Mandalay generating unit #2 in the manual mode rather than automatic voltage control mode and did not notify its Transmission Operator of the changes in status. | VAR-002-1.1b | R3 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) for the following reasons. First, although the generating unit is rated at 215 MW, the periods of operation in manual mode occurred when the unit was operating well below its rating. Second, the periods of operation in the incorrect mode were of short duration (28 minutes on May 28, 2011 and one minute on June 1, 2011) before GCAII switched the automatic voltage regulator into the correct mode. Third, the amount of generation is a fraction of the generation available at the plant and an even smaller fraction of the generation available to the Transmission Operator. The Mandalay generating station has approximately 560 MW of capacity (from three total units), and GCAII owns approximately 5,000 MW of generation capacity in California. | 5/28/2011 (First Instance) 6/1/2011 (Second Instance) (when GCAII failed to notify its Transmission Operator of a change in status) | 5/28/2011(First Instance) 6/1/2011 (Second Instance) (when the generating unit resumed operation in the correct mode) | $1,500 (for WECC201103012 and WECC201103013) | Self-Certification | On February 21, 2012, GCAII submitted to WECC a Mitigation Plan to address the violation of VAR-002-1.1b R3. In accordance with the Mitigation Plan, GCAII trained its desk operations personnel on VAR-002 requirements and timing associated with Reactive Power resource status changes. | 2011-07-29 | 2012-05-31 | Does Not Contest
Western Electricity Coordinating Council (WECC) | Los Angeles Department of Water and Power (LDWP) | NCR05223 | WECC2011008662 | Settlement Agreement | On November 24, 2011, LDWP submitted a Self-Report to WECC indicating that, as a Balancing Authority (BA), it was in violation of BAL-004-0 R3.1. LDWP stated that the WECC Vancouver Reliability Coordinator (RC) requested LDWP to participate in a manual Time Error Correction on November 20, 2011, effective at 0300 hours, to correct for slow time error. In addition, the RC requested all BAs to schedule frequency to 60.02 Hz and thus over-generate by 0.02 Hz. On January 13, 2012, WECC reviewed LDWP's Self-Report and evidence documenting the start time, end time and date of the Time Error Correction. WECC determined that the Time Error Correction lasted a total of 7.5 hours. In addition, LDWP provided its Manual Time Error Procedure, which stated "the BA offsets its frequency schedule by 0.02 Hz while leaving its Frequency Bias Setting normal." LDWP had the procedure and process in place to comply with time correction error directives from its RC. However, it failed to participate in the time error correction event until 0311 hours, 11 minutes (2.4% of the time error correction timeframe) after the Time Error Correction start time. Based on the record, WECC determined that LDWP violated BAL-004-0 R3.1 for failing to immediately offset its frequency schedule by 0.02 Hz and leaving its Frequency Bias Setting normal for 11 minutes. | BAL-004-0 | R3.1 | Lower | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by the short duration of the violation during the Time Error Correction event, and the size of the entity. LDWP participated in the 7.5 hour long Time Error Correction event and only failed to participate for 11 minutes, or 2.4% of the event's duration. In addition, LDWP's BA footprint is of limited size relative to the entire Interconnection, thus reducing the risk to the BPS posed by LDWP's incorrect frequency schedule during the 11 minutes at issue. Also, the Time Error Correction event involved multiple BAs, one of which was LDWP. During the event, LDWP helped boost the frequency in the interconnection and as a result contributed to the success of the event. Further, the risk to the BPS was mitigated by the fact that the RC relied on several BAs to boost the frequency during the event, and therefore LDWP's limited size posed minimal risk in the context of this Interconnection-wide Time Error Correction event because several other BAs were also participating at the time of the violation. | 11/20/2011 (when LDWP failed to participate in the Time Error Correction event) | 11/20/2011 (when LDWP began participation in the Time Error Correction event) | 1500 | Self-Report | According to its Mitigation Plan, LDWP completed the following actions: 1. Performed an internal investigation of the facts of the event in accordance with civil service due process rules and procedures; 2. Investigated further coordination enhancements with the neighboring BAs and the WECC RC regarding participation in a Time Error Correction; 3. Evaluated regional practices and made recommendations; 4. Evaluated its policies and procedures that involve participation in a Time Error Correction to identify enhancements or changes; 5. Developed and implemented enhanced policies and procedures; and 6. Provided re-training of its personnel on the enhanced policies and procedures. | 2012-03-29 | 2012-05-31 | Does Not Contest | WECC considered LDWP's compliance history as an aggravating factor in determining the penalty amount. WECC also considered LDWP's internal compliance program ICP) as a mitigating factor when determining the penalty amount. WECC has reviewed LDWP’s ICP on four occasions and notes LDWP has shown continuous improvement and commitment to its ICP. WECC found that: LDWP’s ICP is documented; the ICP is disseminated throughout its operations; LDWP has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the CEO and/or board of directors; LDWP operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards; LDWP has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; LDWP reviews and modifies its ICP regularly; LDWP’s ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and LDWP’s ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable.