## PUBLIC_Non_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Florida Reliability Coordinating Council, Inc. (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2013013120 | Settlement Agreement | On October 31, 2013, NSB submitted a Self-Report stating that, as a Transmission Owner, it was in violation of FAC-009-1 R1. NSB failed to establish Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings Methodology. NSB’s initial Facility Ratings did not consider current transformers. When NSB considered current transformers, three 115 kV transmission line metering current transformers were incorrectly rated and one 115 kV ring bus Facility Rating was reduced. The three 115 kV transmission line Facility Ratings were reduced when the associated metering current transformer tap ratios were identified and applied. | FAC-009-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, not having the correct Facility Ratings precludes operating the BPS to proper limits, determining accurate contingencies, and performing functional studies. Three of the incorrect Facility Ratings were for tie lines which could cause neighboring Transmission Operators to operate to the incorrect limits. The risk was reduced because NSB owns less than one percent of the Regional transmission system with a peak load of less than 100 MW. Additionally, only NSB equipment would be damaged from an overload and only its load was subject to being de-energized. No actual harm is known to have occurred. | 6/19/2009 (when the oldest revision of NSB Facility Ratings manual was reviewed) | 5/10/2013 (when NSB corrected its Facility Ratings) | $0 (for FRCC2013013120, FRCC2013013163, FRCC2013013164, FRCC2013013165, FRCC2013013166, FRCC2013013167, FRCC2013013168, FRCC2013013169, FRCC2013013170, FRCC2013013171, FRCC2013013172, and FRCC2013013173) | Self-Report | To mitigate this violation NSB: 1) validated and updated its Facility Ratings to ensure compliance with its Facility Ratings Methodology; 2) verified that all component Facility Ratings are correct; 3) updated the alarming points in its energy management system to the verified Facility Ratings; 4) notified its Reliability Coordinator and neighboring Transmission Operators of the updated Facility Ratings and System Operating Limits; 5) updated and verified its System Operating Limits for the associated Facility Ratings changes; 6) revised its procedures for changes in Facility Ratings to include appropriate identification of changes, procedures, processes and studies to be updated, and notifications to be made for changes; and 7) trained the operating personnel on the updated Facility Ratings, operating limits, and procedural changes. | 8/2/2014 | TBD | Neither Admits nor Denies | FRCC reviewed NSB's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is reviewed twice per year, is widely disseminated throughout NSB, has designated operation and maintenance accounts dedicated to compliance, and has the support and participation of senior management. NSB has identified its director of system operations and generation as the ICP oversight position, who is supervised by the general manager and has independent access to the utilities commission. NSB did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. FRCC considered NSB's relative size and location to have a minimal impact to the reliability of the BPS and to be a mitigating factor in the penalty determination. FRCC considered NSB’s FAC-009-1 compliance history to be an aggravating factor in the penalty determination. FRCC considered a $0 penalty appropriate because NSB committed to additional reliability expenditures beyond those required to mitigate the instant violation: 1) NSB will install and commission an Inter Control Center Protocol (ICCP) data link at primary control center for the transfer of reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 2) NSB will complete an inventory of functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards and compare the functions to those that have been established at its backup control center; 3) NSB will update and implement processes at its backup control center to ensure that the functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards can be performed independently at its backup control center; 4) NSB will install and commission an ICCP data link at its backup control center for the transfer of Reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 5) NSB will create/update its procedures relating to 1) transmitting/receiving Reliability data in real-time; 2) plans for loss of control center functionality; and 3) other operating and planning processes impacted in the above actions; and F. NSB will train its system operating personnel on the procedural and process changes implemented in the above actions.
Florida Reliability Coordinating Council, Inc. (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2013013163 | Settlement Agreement | On November 20, 2013, NSB submitted a Self-Report stating that, as a Planning Authority, it was in violation of TPL-001-0.1 R1.3. NSB failed to demonstrate through a valid assessment that its portion of the interconnected transmission system was planned under the conditions defined in Category A of Table I (no contingencies) in TPL-001-0.1. NSB’s annual study results were invalid because the thermal ratings used in the studies were not consistent with the Facility Ratings established by the Transmission Owner. | TPL-001-0.1 | R1; R1.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, not having a valid assessment produces inaccurate study results used to plan the BPS. Inaccurate studies may not predict potential instability or contingencies that can pose a risk when operating the BPS in real-time. The risk was reduced because NSB owns less than one percent of the Regional transmission system and has a peak load of less than 100 MW. Additionally, only NSB equipment would be damaged from an overload and only its load was subject to being de-energized. No actual harm is known to have occurred. | 5/10/2013 (when NSB failed to perform a valid assessment) | 1/10/2014 (when the updated studies were supplied to the Reliability Coordinator) | $0 (for FRCC2013013120, FRCC2013013163, FRCC2013013164, FRCC2013013165, FRCC2013013166, FRCC2013013167, FRCC2013013168, FRCC2013013169, FRCC2013013170, FRCC2013013171, FRCC2013013172, and FRCC2013013173) | Self-Report | To mitigate this violation NSB: 1) completed the required studies using its updated Facility Ratings and System Operating Limit; 2) notified its Reliability Coordinator and neighboring Transmission Operators of the updated Facility Ratings; 3) revised its procedures for changes in Facility Ratings to include appropriate identification of changes, procedures, processes and studies to be updated, and notifications to be made for changes; and 4) trained the planning personnel on the proper reporting procedures. | 2014-07-31 | TBD | Neither Admits nor Denies | FRCC reviewed NSB's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is reviewed twice per year, is widely disseminated throughout NSB, has designated operation and maintenance accounts dedicated to compliance, and has the support and participation of senior management. NSB has identified its director of system operations and generation as the ICP oversight position, who is supervised by the general manager and has independent access to the utilities commission. NSB did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. FRCC considered NSB's relative size and location to have a minimal impact to the reliability of the BPS and to be a mitigating factor in the penalty determination. A Settlement Agreement covering a violation of TPL-001-0 R1 for NSB was filed with FERC under NP10-2-000 on October 14, 2009. On November 13, 2009, FERC issued an order stating it would not engage in further review of the Notice of Penalty. FRCC determined that NSB's compliance history should not serve as a basis for aggravating the penalty. While the violations were of the same Standard and Requirement, the facts and circumstances for the violations were different. The prior violation was due to NSB's failure to conduct annual assessments, while the instant violation was due to NSB's failure to perform a valid assessment. Additionally, the prior violation was fully mitigated four years before the start date of the instant violation. FRCC considered a $0 penalty appropriate because NSB committed to additional reliability expenditures beyond those required to mitigate the instant violation: 1) NSB will install and commission an Inter Control Center Protocol (ICCP) data link at primary control center for the transfer of reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 2) NSB will complete an inventory of functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards and compare the functions to those that have been established at its backup control center; 3) NSB will update and implement processes at its backup control center to ensure that the functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards can be performed independently at its backup control center; 4) NSB will install and commission an ICCP data link at its backup control center for the transfer of Reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 5) NSB will create/update its procedures relating to 1) transmitting/receiving Reliability data in real-time; 2) plans for loss of control center functionality; and 3) other operating and planning processes impacted in the above actions; and F. NSB will train its system operating personnel on the procedural and process changes implemented in the above actions.
Florida Reliability Coordinating Council, Inc. (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2013013164 | Settlement Agreement | On November 20, 2013, NSB submitted a Self-Report stating that, as a Planning Authority, it was in violation of TPL-002-0b R1.3. NSB failed to demonstrate through a valid assessment that its portion of the interconnected transmission system was planned under the conditions defined in Category B of Table I (single contingencies) in TPL-002-0b. NSB’s annual study results were invalid because the thermal ratings used in the studies were not consistent with the Facility Ratings established by the Transmission Owner. | TPL-002-0b | R1; R1.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, not having a valid assessment produces inaccurate study results used to plan the BPS. Inaccurate studies may not predict potential instability or contingencies that can pose a risk when operating the BPS in real-time. The risk was reduced because NSB owns less than one percent of the Regional transmission system and has a peak load of less than 100 MW. Additionally, only NSB equipment would be damaged from an overload and only its load was subject to being de-energized. No actual harm is known to have occurred. | 5/10/2013 (failed to perform a valid assessment) | 1/10/2014 (when the updated studies were supplied to the Reliability Coordinator) | $0 (for FRCC2013013120, FRCC2013013163, FRCC2013013164, FRCC2013013165, FRCC2013013166, FRCC2013013167, FRCC2013013168, FRCC2013013169, FRCC2013013170, FRCC2013013171, FRCC2013013172, and FRCC2013013173) | Self-Report | To mitigate this violation NSB: 1) completed the required studies using its updated Facility Ratings and System Operating Limit; 2) notified its Reliability Coordinator and neighboring Transmission Operators of the updated Facility Ratings; 3) revised its procedures for changes in Facility Ratings to include appropriate identification of changes, procedures, processes and studies to be updated, and notifications to be made for changes; and 4) trained the planning personnel on the proper reporting procedures. | 2014-07-31 | TBD | Neither Admits nor Denies | FRCC reviewed NSB's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is reviewed twice per year, is widely disseminated throughout NSB, has designated operation and maintenance accounts dedicated to compliance, and has the support and participation of senior management. NSB has identified its director of system operations and generation as the ICP oversight position, who is supervised by the general manager and has independent access to the utilities commission. NSB did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. FRCC considered NSB's relative size and location to have a minimal impact to the reliability of the BPS and to be a mitigating factor in the penalty determination. A Settlement Agreement covering a violation of TPL-002-0 R1 for NSB was filed with FERC under NP10-2-000 on October 14, 2009. On November 13, 2009, FERC issued an order stating it would not engage in further review of the Notice of Penalty. FRCC determined that NSB's compliance history should not serve as a basis for aggravating the penalty. While the violations were of the same Standard and Requirement, the facts and circumstances for the violations were different. The prior violation was due to NSB's failure to conduct annual assessments, while the instant violation was due to NSB's failure to perform a valid assessment. Additionally, the prior violation was fully mitigated four years before the start date of the instant violation. FRCC considered a $0 penalty appropriate because NSB committed to additional reliability expenditures beyond those required to mitigate the instant violation: 1) NSB will install and commission an Inter Control Center Protocol (ICCP) data link at primary control center for the transfer of reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 2) NSB will complete an inventory of functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards and compare the functions to those that have been established at its backup control center; 3) NSB will update and implement processes at its backup control center to ensure that the functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards can be performed independently at its backup control center; 4) NSB will install and commission an ICCP data link at its backup control center for the transfer of Reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 5) NSB will create/update its procedures relating to 1) transmitting/receiving Reliability data in real-time; 2) plans for loss of control center functionality; and 3) other operating and planning processes impacted in the above actions; and F. NSB will train its system operating personnel on the procedural and process changes implemented in the above actions.
Florida Reliability Coordinating Council, Inc. (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2013013165 | Settlement Agreement | On November 20, 2013, NSB submitted a Self-Report stating that, as a Planning Authority, it was in violation of TPL-003-0b R1.3. NSB failed to demonstrate through a valid assessment that its portion of the interconnected transmission system was planned under the conditions defined in Category C of Table I (multiple contingencies) in TPL-003-0b. NSB’s annual study results were invalid because the thermal ratings used in the studies were not consistent with the Facility Ratings established by the Transmission Owner. | TPL-003-0a | R1; R1.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, not having a valid assessment produces inaccurate study results used to plan the BPS. Inaccurate studies may not predict potential instability or contingencies that can pose a risk when operating the BPS in real-time. The risk was reduced because NSB owns less than one percent of the Regional transmission system and has a peak load of less than 100MW. Additionally, only NSB equipment would be damaged from an overload and only its load was subject to being de-energized. No actual harm is known to have occurred. | 5/10/2013 (failed to perform a valid assessment) | 1/10/2014 (when the updated studies were supplied to the Reliability Coordinator) | $0 (for FRCC2013013120, FRCC2013013163, FRCC2013013164, FRCC2013013165, FRCC2013013166, FRCC2013013167, FRCC2013013168, FRCC2013013169, FRCC2013013170, FRCC2013013171, FRCC2013013172, and FRCC2013013173) | Self-Report | To mitigate this violation NSB: 1) completed the required studies using its updated Facility Ratings; 2) notified its Reliability Coordinator and neighboring Transmission Operators of the updated Facility Ratings; 3) revised its procedures for changes in Facility Ratings to include appropriate identification of changes, procedures, processes and studies to be updated, and notifications to be made for changes; and 4) trained the planning personnel on the proper reporting procedures. | 2014-07-31 | TBD | Neither Admits nor Denies | FRCC reviewed NSB's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is reviewed twice per year, is widely disseminated throughout NSB, has designated operation and maintenance accounts dedicated to compliance, and has the support and participation of senior management. NSB has identified its director of system operations and generation as the ICP oversight position, who is supervised by the general manager and has independent access to the utilities commission. NSB did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. FRCC considered NSB's relative size and location to have a minimal impact to the reliability of the BPS and to be a mitigating factor in the penalty determination. A Settlement Agreement covering a violation of TPL-003-0 R1 for NSB was filed with FERC under NP10-2-000 on October 14, 2009. On November 13, 2009, FERC issued an order stating it would not engage in further review of the Notice of Penalty. FRCC determined that NSB's compliance history should not serve as a basis for aggravating the penalty. While the violations were of the same Standard and Requirement, the facts and circumstances for the violations were different. The prior violation was due to NSB's failure to conduct annual assessments, while the instant violation was due to NSB's failure to perform a valid assessment. Additionally, the prior violation was fully mitigated four years before the start date of the instant violation. FRCC considered a $0 penalty appropriate because NSB committed to additional reliability expenditures beyond those required to mitigate the instant violation: 1) NSB will install and commission an Inter Control Center Protocol (ICCP) data link at primary control center for the transfer of reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 2) NSB will complete an inventory of functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards and compare the functions to those that have been established at its backup control center; 3) NSB will update and implement processes at its backup control center to ensure that the functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards can be performed independently at its backup control center; 4) NSB will install and commission an ICCP data link at its backup control center for the transfer of Reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 5) NSB will create/update its procedures relating to 1) transmitting/receiving Reliability data in real-time; 2) plans for loss of control center functionality; and 3) other operating and planning processes impacted in the above actions; and F. NSB will train its system operating personnel on the procedural and process changes implemented in the above actions.
Florida Reliability Coordinating Council, Inc. (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2013013166 | Settlement Agreement | On November 21, 2013, NSB submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of IRO-005-3.1a R10. NSB failed to operate the Bulk Electric System to the most limiting parameter in an instance where there was a difference in derived limits. For 43 minutes during an event that loaded one of its tie-lines (the Cassadaga to Smyrna 115 kV line) to greater than the Facility Rating derived by NSB (80 MVA), it failed to operate to the most limiting parameter when its limit was less than that of the adjacent TOP (211 MVA). The methodology used by NSB at the time did not account for the Facility Rating factor of the current transformers, and therefore, the actual rating that should have been in effect was 159 MVA, thus reducing the amount of the overload, as well as the time spent in the overload. | IRO-005-3.1a | R10 | Pending | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because overloading Facilities greater than the derived ratings has the potential to cause cascading outages and Facility damage, thus delaying recovery and reducing system reliability. The risk was reduced because NSB owns less than one percent of the Regional transmission system and has a peak load of less than 100 MW. The NSB system loads rarely exceed the value of the revised limiting elements, and has never exceeded the revised rating. In addition, the NSB system is at or near the end of the interconnection with neighboring TOPs reducing the likelihood of an adverse impact on those systems. Additionally, only NSB equipment would be damaged from an overload and only its load was subject to being de-energized. No actual harm is known to have occurred. | 8/1/2013 (when the Facility loading exceeded its NSB derived rating) | 8/2/2013 (when the Facility loading returned to below its NSB derived rating) | $0 (for FRCC2013013120, FRCC2013013163, FRCC2013013164, FRCC2013013165, FRCC2013013166, FRCC2013013167, FRCC2013013168, FRCC2013013169, FRCC2013013170, FRCC2013013171, FRCC2013013172, and FRCC2013013173) | Self-Report | To mitigate this violation NSB: 1) validated and updated its Facility Ratings to ensure compliance with its Facility Ratings Methodology; 2) verified that all component Facility Ratings are correct; 3) updated the alarming points in its energy management system to the verified Facility Ratings; 4) notified its Reliability Coordinator (RC) and neighboring TOPs of the updated Facility Ratings and System Operating Limits (SOLs); 5) updated and verified its SOLs for the associated Facility Ratings changes; 6) revised its procedures for changes in Facility Ratings to include identification of the most limiting parameter or SOL, steps to take when a limit is exceeded, and notifications to the RC and TOPs for exceedances of a limit; and 7) trained the planning personnel on the SOL procedures and reporting requirements. | 8/2/2014 | TBD | Neither Admits nor Denies | FRCC reviewed NSB's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is reviewed twice per year, is widely disseminated throughout NSB, has designated operation and maintenance accounts dedicated to compliance, and has the support and participation of senior management. NSB has identified its director of system operations and generation as the ICP oversight position, who is supervised by the general manager and has independent access to the utilities commission. NSB did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. FRCC considered NSB's relative size and location to have a minimal impact to the reliability of the BPS and to be a mitigating factor in the penalty determination. FRCC considered NSB's compliance history and determined there were no relevant instances of noncompliance. FRCC considered a $0 penalty appropriate because NSB committed to additional reliability expenditures beyond those required to mitigate the instant violation: 1) NSB will install and commission an Inter Control Center Protocol (ICCP) data link at primary control center for the transfer of reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 2) NSB will complete an inventory of functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards and compare the functions to those that have been established at its backup control center; 3) NSB will update and implement processes at its backup control center to ensure that the functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards can be performed independently at its backup control center; 4) NSB will install and commission an ICCP data link at its backup control center for the transfer of Reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 5) NSB will create/update its procedures relating to 1) transmitting/receiving Reliability data in real-time; 2) plans for loss of control center functionality; and 3) other operating and planning processes impacted in the above actions; and F. NSB will train its system operating personnel on the procedural and process changes implemented in the above actions.
Florida Reliability Coordinating Council, Inc. (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2013013167 | Settlement Agreement | On November 21, 2013, NSB submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of TOP-004-2 R1. NSB failed to operate within its established System Operating Limits (SOLs). For 43 minutes during an event, one of its 115 kV lines and a substation bus were loaded to greater than the SOL derived by NSB. The methodology used by NSB at the time did not account for the Facility Rating factor of the current transformers, and therefore, the actual rating that should have been in effect was 159 MVA, thus reducing the amount of the overload, as well as the time spent in the overload. | TOP-004-2 | R1 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because overloading Facilities greater than the SOL has the potential to cause cascading outages and Facility damage, thus delaying recovery and reducing system reliability. The risk was reduced because NSB owns less than one percent of the Regional transmission system and has a peak load of less than 100 MW. Additionally, only NSB equipment would be damaged from an overload and only its load was subject to being de-energized. No actual harm is known to have occurred. | 8/1/2013 (when the Facility loading exceeded its NSB derived rating) | 8/2/2013 (when the Facility loading returned to below its NSB derived rating) | $0 (for FRCC2013013120, FRCC2013013163, FRCC2013013164, FRCC2013013165, FRCC2013013166, FRCC2013013167, FRCC2013013168, FRCC2013013169, FRCC2013013170, FRCC2013013171, FRCC2013013172, and FRCC2013013173) | Self-Report | To mitigate this violation NSB: 1) validated and updated its Facility Ratings to ensure compliance with its Facility Ratings Methodology; 2) verified that all component Facility Ratings are correct; 3) updated the alarming points in its energy management system to the verified Facility Ratings; 4) notified its Reliability Coordinator (RC) and neighboring TOPs of the updated Facility Ratings and SOLs; 5) updated and verified its SOLs for the associated Facility Ratings changes; 6) revised its procedures for changes in Facility Ratings to include identification of the most limiting parameter or SOL, steps to take when a limit is exceeded, and notifications to the RC and TOPs for exceedances of a limit; and 7) trained the planning personnel on the SOL procedures and reporting requirements. | 8/2/2014 | TBD | Neither Admits nor Denies | FRCC reviewed NSB's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is reviewed twice per year, is widely disseminated throughout NSB, has designated operation and maintenance accounts dedicated to compliance, and has the support and participation of senior management. NSB has identified its director of system operations and generation as the ICP oversight position, who is supervised by the general manager and has independent access to the utilities commission. NSB did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. FRCC considered NSB's relative size and location to have a minimal impact to the reliability of the BPS and to be a mitigating factor in the penalty determination. A Settlement Agreement covering a violation of TOP-004-1 R6 for NSB was filed with FERC under NP10-2-000 on October 14, 2009. On November 13, 2009, FERC issued an order stating it would not engage in further review of the Notice of Penalty. FRCC determined that NSB's compliance history should not serve as a basis for aggravating the penalty. While the violations were of the same Standard, the Requirements, facts and circumstances for the violations were different. The prior violation was due to NSB’s failure to have a process to coordinate the monitoring and controlling of voltages and power flows with other TOPs. The instant violation was different because NSB did operate within its established SOLs. Additionally, the prior violation was fully mitigated more than four years before the start date of the instant violation. FRCC considered a $0 penalty appropriate because NSB committed to additional reliability expenditures beyond those required to mitigate the instant violation: 1) NSB will install and commission an Inter Control Center Protocol (ICCP) data link at primary control center for the transfer of reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 2) NSB will complete an inventory of functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards and compare the functions to those that have been established at its backup control center; 3) NSB will update and implement processes at its backup control center to ensure that the functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards can be performed independently at its backup control center; 4) NSB will install and commission an ICCP data link at its backup control center for the transfer of Reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 5) NSB will create/update its procedures relating to 1) transmitting/receiving Reliability data in real-time; 2) plans for loss of control center functionality; and 3) other operating and planning processes impacted in the above actions; and F. NSB will train its system operating personnel on the procedural and process changes implemented in the above actions.
Florida Reliability Coordinating Council, Inc. (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2013013168 | Settlement Agreement | On November 21, 2013, NSB submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of TOP-008-1 R2. NSB failed to operate the Bulk Electric System to the most limiting parameter in an instance where there was a difference in derived limits. For 43 minutes during an event that loaded one of its tie-lines (the Cassadaga to Smyrna 115 kV line) to greater than the Facility Rating derived by NSB (80 MVA), it failed to operate to the most limiting parameter when its limit was less than that of the adjacent TOP (211 MVA). The methodology used by NSB at the time did not account for the Facility Rating factor of the current transformers, and therefore, the actual rating that should have been in effect was 159 MVA, thus reducing the amount of the overload, as well as the time spent in the overload. | TOP-008-1 | R2 | High | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because overloading multiple Facilities greater than the derived ratings has the potential to cause cascading outages and Facility damage, thus delaying recovery and reducing system reliability. The risk was reduced because NSB owns less than one percent of the Regional transmission system and has a peak load of less than 100 MW. Additionally, only NSB equipment would be damaged from an overload and only its load was subject to being de-energized. No actual harm is known to have occurred. | 8/1/2013 (when the Facility loading exceeded its NSB derived rating) | 8/2/2013 (when the Facility loading returned to below its NSB derived rating) | $0 (for FRCC2013013120, FRCC2013013163, FRCC2013013164, FRCC2013013165, FRCC2013013166, FRCC2013013167, FRCC2013013168, FRCC2013013169, FRCC2013013170, FRCC2013013171, FRCC2013013172, and FRCC2013013173) | Self-Report | To mitigate this violation NSB: 1) validated and updated its Facility Ratings to ensure compliance with its Facility Ratings Methodology; 2) verified that all component Facility Ratings are correct; 3) updated the alarming points in its energy management system to the verified Facility Ratings; 4) notified its Reliability Coordinator (RC) and neighboring TOPs of the updated Facility Ratings and SOLs; 5) updated and verified its SOLs for the associated Facility Ratings changes; 6) revised its procedures for changes in Facility Ratings to include identification of the most limiting parameter or SOL, steps to take when a limit is exceeded, and notifications to the RC and TOPs for exceedances of a limit; and 7) trained the planning personnel on the SOL procedures and reporting requirements. | 8/2/2014 | TBD | Neither Admits nor Denies | FRCC reviewed NSB's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is reviewed twice per year, is widely disseminated throughout NSB, has designated operation and maintenance accounts dedicated to compliance, and has the support and participation of senior management. NSB has identified its director of system operations and generation as the ICP oversight position, who is supervised by the general manager and has independent access to the utilities commission. NSB did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. FRCC considered NSB's relative size and location to have a minimal impact to the reliability of the BPS and to be a mitigating factor in the penalty determination. FRCC considered NSB's compliance history and determined there were no relevant instances of noncompliance. FRCC considered a $0 penalty appropriate because NSB committed to additional reliability expenditures beyond those required to mitigate the instant violation: 1) NSB will install and commission an Inter Control Center Protocol (ICCP) data link at primary control center for the transfer of reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 2) NSB will complete an inventory of functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards and compare the functions to those that have been established at its backup control center; 3) NSB will update and implement processes at its backup control center to ensure that the functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards can be performed independently at its backup control center; 4) NSB will install and commission an ICCP data link at its backup control center for the transfer of Reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 5) NSB will create/update its procedures relating to 1) transmitting/receiving Reliability data in real-time; 2) plans for loss of control center functionality; and 3) other operating and planning processes impacted in the above actions; and F. NSB will train its system operating personnel on the procedural and process changes implemented in the above actions.
Florida Reliability Coordinating Council, Inc. (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2013013169 | Settlement Agreement | On November 22, 2013, NSB submitted a Self-Report stating that, as a Planning Authority (PA) and Transmission Operator (TOP), it was in violation of FAC-014-2 R5, R5.2, and R5.3. NSB failed to provide its System Operating Limits (SOLs) to those entities that have a reliability-related need. NSB developed three SOLs (transmission lines) through the application of its SOL Methodology for the Planning Horizon, which were not communicated to those entities that have a reliability-related need. | FAC-014-2 | R5; R5.2; R5.3 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a minimal risk because the SOLs that were not provided were established for the Planning Horizon. The risk was reduced because NSB owns less than one percent of the Regional transmission system and has a peak load of less than 100 MW. Additionally, only NSB equipment would be damaged from an overload and only its load was subject to being de-energized. No actual harm is known to have occurred. | 5/10/2013 (when NSB updated its Facility Ratings) | 1/3/2014 (when the SOLs were provided to those entities with a reliability related need) | $0 (for FRCC2013013120, FRCC2013013163, FRCC2013013164, FRCC2013013165, FRCC2013013166, FRCC2013013167, FRCC2013013168, FRCC2013013169, FRCC2013013170, FRCC2013013171, FRCC2013013172, and FRCC2013013173) | Self-Report | To mitigate this violation NSB: 1) validated and updated its Facility Ratings to ensure compliance with its Facility Ratings Methodology; 2) verified that all component Facility Ratings are correct; 3) updated the alarming points in its energy management system to the verified Facility Ratings; 4) notified its Reliability Coordinator and neighboring TOPs of the updated Facility Ratings and SOLs; 5) updated and verified its SOLs for the associated Facility Ratings changes; 6) revised its procedures for changes in Facility Ratings to include appropriate identification of changes, procedures, processes and studies to be updated, and notifications to be made for changes; and 7) trained the operating personnel on the updated ratings, operating limits, and procedural changes. | 8/2/2014 | TBD | Neither Admits nor Denies | FRCC reviewed NSB's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is reviewed twice per year, is widely disseminated throughout NSB, has designated operation and maintenance accounts dedicated to compliance, and has the support and participation of senior management. NSB has identified its director of system operations and Generation as the ICP oversight position, who is supervised by the General Manager and has independent access to the utilities commission. NSB did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. FRCC considered NSB's relative size and location to have a minimal impact to the reliability of the BPS and to be a mitigating factor in the penalty determination. FRCC considered NSB's compliance history and determined there were no relevant instances of noncompliance. FRCC considered a $0 penalty appropriate because NSB committed to additional reliability expenditures beyond those required to mitigate the instant violation: 1) NSB will install and commission an Inter Control Center Protocol (ICCP) data link at primary control center for the transfer of reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 2) NSB will complete an inventory of functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards and compare the functions to those that have been established at its backup control center; 3) NSB will update and implement processes at its backup control center to ensure that the functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards can be performed independently at its backup control center; 4) NSB will install and commission an ICCP data link at its backup control center for the transfer of Reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 5) NSB will create/update its procedures relating to 1) transmitting/receiving Reliability data in real-time; 2) plans for loss of control center functionality; and 3) other operating and planning processes impacted in the above actions; and F. NSB will train its system operating personnel on the procedural and process changes implemented in the above actions.
Florida Reliability Coordinating Council, Inc. (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2013013170 | Settlement Agreement | On November 22, 2013, NSB submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of TOP-002-2.1b R11. NSB failed to update its Bulk Electric System (BES) studies as necessary to reflect current system conditions. | TOP-002-2.1b | R11 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was reduced because NSB owns less than one percent of the Regional transmission system and has a peak load of less than 100 MW. Additionally, only NSB equipment would be damaged from an overload and only its load was subject to being de-energized. No actual harm is known to have occurred. | 5/10/2013 (when NSB updated its Facility Ratings and failed to update its BES studies) | 2/10/2014 (when the System Operating Limits (SOLs) were updated to reflect system conditions) | $0 (for FRCC2013013120, FRCC2013013163, FRCC2013013164, FRCC2013013165, FRCC2013013166, FRCC2013013167, FRCC2013013168, FRCC2013013169, FRCC2013013170, FRCC2013013171, FRCC2013013172, and FRCC2013013173) | Self-Report | To mitigate this violation NSB: 1) validated and updated its Facility Ratings to ensure compliance with its Facility Ratings Methodology; 2) verified that all component Facility Ratings are correct; 3) updated the alarming points in its energy management system to the verified Facility Ratings; 4) notified its Reliability Coordinator and neighboring TOPs of the updated Facility Ratings and SOLs; 5) updated and verified its SOLs for the associated Facility Ratings changes; 6) revised its procedures for changes in Facility Ratings to include appropriate identification of changes, procedures, processes and studies to be updated, and notifications to be made for changes; and 7) trained the operating personnel on the updated ratings, operating limits, and procedural changes. | 8/2/2014 | TBD | Neither Admits nor Denies | FRCC reviewed NSB's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is reviewed twice per year, is widely disseminated throughout NSB, has designated operation and maintenance accounts dedicated to compliance, and has the support and participation of senior management. NSB has identified its director of system operations and generation as the ICP oversight position, who is supervised by the general manager and has independent access to the utilities commission. NSB did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. FRCC considered NSB's relative size and location to have a minimal impact to the reliability of the BPS and to be a mitigating factor in the penalty determination. FRCC considered NSB's compliance history and determined there were no relevant instances of noncompliance. FRCC considered a $0 penalty appropriate because NSB committed to additional reliability expenditures beyond those required to mitigate the instant violation: 1) NSB will install and commission an Inter Control Center Protocol (ICCP) data link at primary control center for the transfer of reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 2) NSB will complete an inventory of functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards and compare the functions to those that have been established at its backup control center; 3) NSB will update and implement processes at its backup control center to ensure that the functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards can be performed independently at its backup control center; 4) NSB will install and commission an ICCP data link at its backup control center for the transfer of Reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 5) NSB will create/update its procedures relating to 1) transmitting/receiving Reliability data in real-time; 2) plans for loss of control center functionality; and 3) other operating and planning processes impacted in the above actions; and F. NSB will train its system operating personnel on the procedural and process changes implemented in the above actions.
Florida Reliability Coordinating Council, Inc. (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2013013171 | Settlement Agreement | On November 22, 2013, NSB submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of TOP-007-0 R1. NSB failed to inform its Reliability Coordinator (RC) when a System Operating Limit (SOL) had been exceeded. For 43 minutes during an event that loaded one of its 115 kV lines and a substation bus to greater than the Facility Rating derived by NSB, it did not inform its RC that a SOL had been exceeded. | TOP-007-0 | R1 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because failure to notify the RC of exceeding SOLs can delay event recovery reducing system reliability. The risk was reduced because NSB owns less than one percent of the Regional transmission system and has a peak load of less than 100 MW. Additionally, only NSB equipment would be damaged from an overload and only its load was subject to being de-energized. No actual harm is known to have occurred. | 8/1/2013 (when the SOL exceeded its NSB derived rating) | 8/2/2013 (when the SOL returned to below its NSB derived rating) | $0 (for FRCC2013013120, FRCC2013013163, FRCC2013013164, FRCC2013013165, FRCC2013013166, FRCC2013013167, FRCC2013013168, FRCC2013013169, FRCC2013013170, FRCC2013013171, FRCC2013013172, and FRCC2013013173) | Self-Report | To mitigate this violation NSB: 1) validated and updated its Facility Ratings to ensure compliance with its Facility Ratings Methodology; 2) verified that all component Facility Ratings are correct; 3) updated the alarming points in its energy management system to the verified Facility Ratings; 4) notified its RC and neighboring TOPs of the updated Facility Ratings and SOLs; 5) updated and verified its SOLs for the associated Facility Ratings changes; 6) revised its procedures for changes in Facility Ratings to include identification of the most limiting parameter or SOL, steps to take when a limit is exceeded, and notifications to the RC and TOPs for exceedances of a limit; and 7) trained the planning personnel on the SOL procedures and reporting requirements. | 8/2/2014 | TBD | Neither Admits nor Denies | FRCC reviewed NSB's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is reviewed twice per year, is widely disseminated throughout NSB, has designated operation and maintenance accounts dedicated to compliance, and has the support and participation of senior management. NSB has identified its director of system operations and generation as the ICP oversight position, who is supervised by the general manager and has independent access to the utilities commission. NSB did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. FRCC considered NSB's relative size and location to have a minimal impact to the reliability of the BPS and to be a mitigating factor in the penalty determination. FRCC considered NSB's compliance history and determined there were no relevant instances of noncompliance. FRCC considered a $0 penalty appropriate because NSB committed to additional reliability expenditures beyond those required to mitigate the instant violation: 1) NSB will install and commission an Inter Control Center Protocol (ICCP) data link at primary control center for the transfer of reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 2) NSB will complete an inventory of functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards and compare the functions to those that have been established at its backup control center; 3) NSB will update and implement processes at its backup control center to ensure that the functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards can be performed independently at its backup control center; 4) NSB will install and commission an ICCP data link at its backup control center for the transfer of Reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 5) NSB will create/update its procedures relating to 1) transmitting/receiving Reliability data in real-time; 2) plans for loss of control center functionality; and 3) other operating and planning processes impacted in the above actions; and F. NSB will train its system operating personnel on the procedural and process changes implemented in the above actions.
Florida Reliability Coordinating Council, Inc. (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2013013172 | Settlement Agreement | On November 22, 2013, NSB submitted a Self-Report stating that, as a Planning Authority, it was in violation of FAC-010-2.1 R2.1. NSB failed to provide evidence that was sufficient to demonstrate that its System Operating Limit (SOL) Methodology included a requirement that its SOLs provided Bulk Electric System (BES) performance in the pre-contingency state and with all Facilities in service. In its determination of SOLs, the BES condition used by NSB did not reflect expected system conditions and did not reflect changes to its system topology including line outages. | FAC-010-2.1 | R2; R2.1 | High | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a minimal risk because Planning Horizon SOLs have little impact in the operating horizon. The risk was reduced because NSB owns less than one percent of the Regional transmission system and has a peak load of less than 100 MW. Additionally, only NSB equipment would be damaged from an overload and only its load was subject to being de-energized. No actual harm is known to have occurred. | 5/10/2013 (when NSB updated its Facility Ratings but did not ensure its SOL Methodology included a requirement that SOLs provide BES performance consistent with FAC-010-2.a R2.1) | 5/5/2014 (Mitigation Plan completion) | $0 (for FRCC2013013120, FRCC2013013163, FRCC2013013164, FRCC2013013165, FRCC2013013166, FRCC2013013167, FRCC2013013168, FRCC2013013169, FRCC2013013170, FRCC2013013171, FRCC2013013172, and FRCC2013013173) | Self-Report | To mitigate this violation NSB has updated its SOL Methodology to include a requirement that all SOLs provide BES performance in the pre-contingency state and with all Facilities in service. | 2014-05-05 | TBD | Neither Admits nor Denies | FRCC reviewed NSB's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is reviewed twice per year, is widely disseminated throughout NSB, has designated operation and maintenance accounts dedicated to compliance, and has the support and participation of senior management. NSB has identified its director of system operations and generation as the ICP oversight position, who is supervised by the general manager and has independent access to the utilities commission. NSB did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. FRCC considered NSB's relative size and location to have a minimal impact to the reliability of the BPS and to be a mitigating factor in the penalty determination. A Settlement Agreement covering a violation of FAC-010-1 R1 for NSB was filed with FERC under NP10-73-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. FRCC determined that NSB's compliance history should not serve as a basis for aggravating the penalty. While the violations were of the same Standard, the Requirements, facts and circumstances for the violations were different. The prior violation was due to NSB failing to ensure that SOLs used in the reliable planning of the BES were determined based on an established methodology. The instant violation was different because in its determination of SOLs, NSB did not consider all changes to system topology. Additionally, the prior violation was fully mitigated four years before the start date of the instant violation. FRCC considered a $0 penalty appropriate because NSB committed to additional reliability expenditures beyond those required to mitigate the instant violation: 1) NSB will install and commission an Inter Control Center Protocol (ICCP) data link at primary control center for the transfer of reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 2) NSB will complete an inventory of functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards and compare the functions to those that have been established at its backup control center; 3) NSB will update and implement processes at its backup control center to ensure that the functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards can be performed independently at its backup control center; 4) NSB will install and commission an ICCP data link at its backup control center for the transfer of Reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 5) NSB will create/update its procedures relating to 1) transmitting/receiving Reliability data in real-time; 2) plans for loss of control center functionality; and 3) other operating and planning processes impacted in the above actions; and F. NSB will train its system operating personnel on the procedural and process changes implemented in the above actions.
Florida Reliability Coordinating Council, Inc. (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2013013173 | Settlement Agreement | On November 22, 2013, NSB submitted a Self-Report stating that, as a Planning Authority (PA), it was in violation FAC-014-2 R3. NSB failed to establish System Operating Limits (SOLs), for its PA Area that were consistent with its SOL Methodology. One SOL (Ring Bus) established did not provide the Bulk Electric System (BES) performance that is required by its SOL Methodology for the Planning Horizon. Following a single contingency, all Facilities would not be operating within its applicable Facility Ratings. | FAC-014-2 | R3 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a minimal risk because Planning Horizon SOLs have little impact in the operating horizon. The risk was reduced because NSB owns less than one percent of the Regional transmission system and has a peak load of less than 100 MW. Additionally, only NSB equipment would be damaged from an overload and only its load was subject to being de-energized. No actual harm is known to have occurred. | 5/10/2013 (when NSB updated its Facility Ratings but failed to establish SOLs consistent with its SOL Methodology) | 2/10/2014 (when the SOLs were correctly established) | $0 (for FRCC2013013120, FRCC2013013163, FRCC2013013164, FRCC2013013165, FRCC2013013166, FRCC2013013167, FRCC2013013168, FRCC2013013169, FRCC2013013170, FRCC2013013171, FRCC2013013172, and FRCC2013013173) | Self-Report | To mitigate this violation NSB: 1) validated and updated its Facility Ratings to ensure compliance with its Facility Ratings Methodology; 2) verified that all component Facility Ratings are correct; 3) updated the alarming points in its energy management system to the verified Facility Ratings; 4) notified its Reliability Coordinator and neighboring Transmission Operators of the updated Facility Ratings and SOLs; 5) updated and verified its SOLs for the associated Facility Ratings changes; 6) revised its procedures for changes in Facility Ratings to include appropriate identification of changes, procedures, processes and studies to be updated, and notifications to be made for changes; and 7) trained the operating personnel on the updated ratings, operating limits, and procedural changes. | 2014-08-02 | TBD | Neither Admits nor Denies | FRCC reviewed NSB's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The ICP is reviewed twice per year, is widely disseminated throughout NSB, has designated operation and maintenance accounts dedicated to compliance, and has the support and participation of senior management. NSB has identified its director of system operations and generation as the ICP oversight position, who is supervised by the general manager and has independent access to the utilities commission. NSB did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. FRCC considered NSB's relative size and location to have a minimal impact to the reliability of the BPS and to be a mitigating factor in the penalty determination. FRCC considered NSB's compliance history and determined there were no relevant instances of noncompliance. FRCC considered a $0 penalty appropriate because NSB committed to additional reliability expenditures beyond those required to mitigate the instant violation: 1) NSB will install and commission an Inter Control Center Protocol (ICCP) data link at primary control center for the transfer of reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 2) NSB will complete an inventory of functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards and compare the functions to those that have been established at its backup control center; 3) NSB will update and implement processes at its backup control center to ensure that the functions performed at its primary control center that are necessary to comply with all approved NERC Reliability Standards can be performed independently at its backup control center; 4) NSB will install and commission an ICCP data link at its backup control center for the transfer of Reliability related data in real-time to and from the RCs, BAs and applicable TOPs; 5) NSB will create/update its procedures relating to 1) transmitting/receiving Reliability data in real-time; 2) plans for loss of control center functionality; and 3) other operating and planning processes impacted in the above actions; and F. NSB will train its system operating personnel on the procedural and process changes implemented in the above actions.
Northeast Power Coordinating Council (NPCC) | Essential Power Newington, LLC (EP Newington) | NCR00540 | NPCC2013011695 | Settlement Agreement | On January 2, 2013, EP Newington submitted a Self-Report stating that, as a Generator Owner, it was in violation of PRC-005-1 R2.1 and R2.2. During an internal self-assessment that was conducted on December 17, 2012 of EP Newington’s PRC-005 Protection System maintenance and testing records, EP Newington discovered that its testing documents for the GT1, GT2, balance of plant, and switchyard batteries were missing. EP Newington was missing testing documents for a total of four battery banks, including testing documents for two months in 2010 and for six months in 2011. After undertaking a complete review of all the available records, EP Newington personnel notified the director of compliance that, although they had conducted periodic visual inspections of the battery banks during the period in question, there was no documented maintenance and testing of the batteries as per EP Newington's Protection System maintenance and testing program (Program). In addition, while collecting information for this data request, EP Newington's compliance group discovered that several current and potential transformers (CT/PT) and DC control circuits were not tested per EP Newington’s Program. EP Newington failed to test 15 of 27 PTs (55.6%), 81 of 132 CTs (61.4%), and 18 of 22 DC Control Circuitry (81.8%) per its Program. | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This violation created a moderate risk because EP Newington's failure to test most of their DC Control circuitry including some PTs and CTs increased the potential that these devices might not have operated as intended. However, the risk was mitigated in part because EP Newington personnel did conduct some periodic visual inspections of the battery banks during the violation period. In addition, during the violation period, real-time relay operations operated as per design and a review determined there were no relay mis-operations. Finally, testing was completed on all devices, and all test results were satisfactory. | 7/14/2008 (when EP Newington registered as a GO) | 1/31/2014 (when remaining CT/PT and DC control circuitry testing was completed) | $20,000 | Self-Report | To mitigate the violation, EP Newington: 1) reviewed and corrected the battery related maintenance and testing tasks in the EP Newington maintenance database so compliance can monitor the tasks; 2) updated the EP Newington PRC-005 Program to ensure it clearly defines the testing intervals; 3) tested all missed DC control circuitry in accordance with the revised Program; 4) tested all missed CTs/PTs in accordance with the revised Program; 5) retrained employees on the new Program and process; and 6) performed an additional internal self assessment on PRC-005 requirements. | 2014-04-22 | 2014-06-10 | Does Not Contest | NPCC reviewed EP Newington's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The chief compliance officer and general counsel, reports directly to the chief executive officer and has independent access to the board of managers and to the board’s audit and risk committee. The compliance program at EP Newington is adequately staffed and is fully supported by senior management. EP Newington utilizes a compliance management software solution as well as web-based training for certain aspects of NERC compliance. EP Newington also reviews the applicable compliance Policies, Programs, and Procedures as part of its ongoing continuous improvement efforts, and revises them on an as needed basis. NPCC considered that EP Newington self reported the violation as a mitigating factors in assessing the penalty. NPCC also considered EP Newington's cooperation as a mitigating factor. EP Newington's compliance specialist was made available to provide information necessary in processing the violations. NPCC reviewed EP Newington's previously submitted Self-Certifications submitted and found that in 2010 EP Newington self-certified indicating compliant when its Self-Report submitted for these violations indicated it was not compliant. NPCC considered this an aggravating factor. A Spreadsheet Notice of Penalty covering violations of PRC-005 R1 and R2 for Essential Power OPP, LLC, an EP Newington affiliate, was filed with FERC under NP13-5-000 on October 31, 2012. On November 19, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Spreadsheet Notice of Penalty covering violations of PRC-005 R1 and R2 for Essential Power Rock Springs LLC an EP Newington affiliate, was filed with FERC under NP13-12-000 on December 31, 2012. On January 30, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005 R1 and R2 for Lakewood Cogeneration LP, an EP Newington affiliate, was filed with FERC under NP14-4-000 on October 30, 2013. On November 29, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. NPCC determined that the affiliate compliance history should not serve as a basis for aggravating the penalty. The violations for Essential Power OPP, LLC under NP13-5-000 were discovered during a Compliance Audit conducted by ReliabilityFirst in late 2011. Similarly, the violations for Essential Power Rock Springs, LLC under NP13-12-000 were discovered during a Compliance Audit conducted by ReliabilityFirst in late 2011. The Mitigation Plan under the NP13-12 violation required EP Rock Springs, LLC to update its Protection System maintenance and testing program and implement the new program. That Mitigation Plan was completed in March 2013. Since all Essential Power LLC affiliated facilities are subject to the same compliance program, and therefore operate to a common set of policies and procedure, updating and implementing its Protection System maintenance and testing program at all of its facilities resulted in the identification of violations at EP’s other facilities. This included the Lakewood Cogeneration LP violations under NP14-4-000 and the present violation , which was self-reported to NPCC in January 2013.
Western Electricity Coordinating Council (WECC) | El Paso Electric Company (EPE) | NCR05140 | WECC2013012984 | Settlement Agreement | During a Spot Check conducted on September 27, 2013, WECC determined that EPE, as a Transmission Owner, Generator Owner, and Distribution Provider, was in violation of PRC-005-1 R1. While EPE has a Protection System Maintenance and Testing Program (Program), portions for associated communications were missing or incomplete. Specifically, WECC determined that EPE failed to include a maintenance and testing interval in its Program for its associated communication devices and failed to include a summary of maintenance and testing procedures for EPE's associated communications system. | PRC-005-1 | R1; R1.1; R1.2. | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While EPE does not explicitly have an interval-based maintenance schedule for associated communications and does not have a summary of such testing in its Program, EPE effectively has an interval-based maintenance schedule for associated communications. When EPE performs end-to-end maintenance on relays, which are done on an interval schedule, EPE utilizes its associated communications system. In this manner, EPE effectively tests the associated communications system on the same interval schedule as its relay maintenance. The failure to document the maintenance and testing interval for associated communication devices did not cause actual harm. | 6/18/2007 (when the Standard became mandatory and enforceable) | 8/26/2014 (Mitigation Plan completion) | $0 | Spot Check | To mitigate this violation, EPE modified its Program to include maintenance and testing intervals and their basis and a summary of maintenance and testing procedures for EPE's associated communications devices. | 2014-08-26 | 2014-09-02 | Neither Admits nor Denies | WECC reviewed EPE's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. EPE’s program demonstrates a commitment to maintaining a strong corporate compliance culture and the highest of ethical standards. WECC did not find deficiencies in EPE’s program. Rather, WECC found several areas of the ICP which provide exemplary and best practices for entities with similar characteristics. Specifically, EPE has developed a NERC compliance awareness program that aims to provide an understanding of the development, implementation, and importance of the NERC Reliability Standards. EPE's ICP contains monthly, quarterly, and annual performance targets for employees, including employee incentives. In two previous Compliance Audits, WECC reviewed EPE's maintenance and testing program and associated evidence and did not find possible violations of PRC-005 R1. WECC is assessing a zero-dollar penalty for this violation based on the prior history of compliance monitoring. WECC considered EPE's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Imperial Irrigation District (IID) | NCR05195 | WECC2013013178 | Settlement Agreement | On November 27, 2013, IID submitted a Self-Report stating that, as a Transmission Owner, it was in violation of FAC-003-1 R1. WECC Enforcement reviewed the Self-Report, evidence provided at a subsequent Compliance Audit conducted from December 1, 2013 through December, 13, 2013 and the interview notes, and determined that IID had a violation of FAC-003-1 R1, for its failure to include one 230 kV line in the schedule for right-of-way (ROW) vegetation inspections, as set forth in IID’s transmission vegetation management program (TVMP). The line was commissioned in June 2011. Upon commission, IID failed to add the line to its TVMP which resulted in six quarterly cycles of missed inspections. The line is a radially fed line between Midway substation and Hudson Rand Geothermal Plant. The root cause of the violation was human error related to IID's lack of process practices. | FAC-003-1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this case, IID failed to include a 230 kV line as a required element in its TVMP, which could lead to IID’s failure to manage the vegetation under that line on a regular basis. As compensating measures, IID’s vegetation inspection schedules contained all required elements for its other transmission lines, but were not updated to include the single new line in question, so only that single line was at risk, as opposed to widespread deficiencies in vegetation practices. The transmission line associated with this violation is a radial transmission line to a single power plant, and the worst case situation of a vegetation-caused outage would not result in interruption to multiple customers or overloads on other transmission lines, but only to that power plant. The vegetation in the ROW under the transmission line associated with this violation consists of desert and low growing vegetation that is unlikely to cause any vegetation risk and IID has never had a vegetation-related outage. The ROW was determined to be free of vegetation on commissioning, and regular inspections commenced 17 months later. Although IID resumed regular inspections, IID has not yet revised its TVMP and inspection schedules to include the new line. IID has included this line in an inspection schedule for 2014, but for 30 months after it was commissioned, IID could not ensure that the line was inspected according to the inspection schedule. However, it is unlikely that wild vegetation in this area would seed and grow to reach a Clearance 2 limit of 10 feet from the conductors during this time frame. | 6/7/2011 (when the 230 kV line was energized and placed in service without including scheduled ROW vegetation inspections) | 1/22/2013 (when IID added the 230 kV line in question to the inspection schedule and resumed regular quarterly vegetation inspection) | $40,000 (for WECC2013013178, WECC2013012453, WECC2013012454, and WECC2012012956) | Self-Report | To mitigate this violation, IID: 1) updated its TVMP to include the 230 kiva Line and to participate in system outage committee meetings; 2) created controls to address gaps in its current TVMP and meet compliance with FAC-003-3; and 3) trained its staff on its vegetation management control program. | 2014-05-28 | 2014-07-28 | Agrees | WECC reviewed IID's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that IID has a comprehensive, established, and documented program; that IID has identified and assigned responsibility and accountability to a compliance officer or other high ranking official who has independent access to the chief executive officer or equivalent; and IID's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards. A Settlement Agreement covering a violation of FAC-003-1 R1 for IID was filed with FERC under NP11-128-000. On March 25, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC considered IID's FAC-003-1 R1 compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Imperial Irrigation District (IID) | NCR05195 | WECC2013012453 | Settlement Agreement | On June 3, 2013, IID submitted a Self-Report stating that, as a Generator Owner, it was in violation of FAC-008-3 R1. WECC Enforcement reviewed the Self-Report, and determined that IID had a violation of FAC-008-3 R1, for its failure to have documentation for determining the Facility Ratings of its solely and jointly owned generator facilities up to the high side terminals of the main step up transformer. The root cause of this violation was human error. IID’s Generation group assumed that since the Facility Ratings are to be determined between the high side of the transformer and the point of interconnection, that the Transmission group would have included the Facility Ratings for this equipment in the Transmission Facility Ratings methodology, while the Transmission group assumed that the Facility Ratings of the equipment from the high side of the transformer to the interconnection point were included in the Generation Facility Rating methodology. | FAC-008-3 | R1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this case, although IID had documentation for determining its Facility Ratings, the documentation did not adequately determine the ratings of each component in the generating stations up to the high side of the main step up transformer. IID failed to have the processes and documentation in place to determine if its Facility Ratings exceeded the most limiting equipment ratings for its generating stations. As compensating measures, IID states that the generators have not been run beyond generator index testing results since the Standard became enforceable. Prior to the Self-Report, one hour performance (index) testing was the Facility Ratings Methodology used by the Generator Owner at IID until a third-party mock audit discovered that the methodology did not comply with the new standard FAC-008-3. The methodology limited the facility output (rating) to what the generator component system could safely produce for a continuous hour without tripping the units or damaging equipment. This test was performed every three years as part of the generator real and reactive power testing with the units connected to the BPS, thus, testing and ensuring safe limits for the generator system and generator interconnection facilities in the process. | 1/1/2013 (when the Standard became mandatory and enforceable) | 10/4/2013 (Mitigation Plan completion) | $40,000 (for WECC2013013178, WECC2013012453, WECC2013012454, and WECC2012012956) | Self-Report | To mitigate this violation, IID: 1) assembled documentation for determining Facility Ratings; 2) implemented controls requiring the retention of documentation used to develop Facility Ratings for the IID Bulk Electric System generating facilities; 3) assigned responsibility for the work within IID:; and 4) ensured through validity checks that the work was completed according to the implemented controls. | 2013-10-04 | 2013-10-08 | Agrees | WECC reviewed IID's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that IID has a comprehensive, established, and documented program; that IID has identified and assigned responsibility and accountability to a compliance officer or other high ranking official who has independent access to the chief executive officer or equivalent; and IID's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards. WECC considered IID's voluntary corrective action to remediate this violation to be a mitigating factor.
Western Electricity Coordinating Council (WECC) | Imperial Irrigation District (IID) | NCR05195 | WECC2013012454 | Settlement Agreement | On June 3, 2013, IID submitted a Self-Report stating that, as a Generator Owner, it was in violation of FAC-008-3 R2. WECC Enforcement reviewed the Self-Report, and determined that IID had a violation of FAC-008-3 R2, for its failure to have a documented methodology for determining Facility Ratings of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner. The root cause of this violation was human error. IID's Generation group assumed that since the Facility Ratings are to be determined between the high side of the transformer and the point of interconnection, that the Transmission group would have included the Facility Ratings for this equipment in the Transmission Facility Ratings methodology, while the Transmission group assumed that the Facility Ratings of the equipment from the high side of the transformer to the interconnection point were included in the Generation Facility Rating methodology. | FAC-008-3 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this case, IID failed to have a documented methodology for determining Facility Ratings of its solely owned equipment connected from the high side of the transformer to the point of the interconnection. As a compensating measure, the devices that were not included in developing a methodology for determining Facility Ratings of it solely owned equipment are not likely to change the most limiting device of the facility. In the Mitigation Plan completion review process, IID confirmed that the most limiting device did not change after applying the updated Facility Ratings Methodology. | 1/1/2013 (when the Standard became mandatory and enforceable) | 10/4/2013 (Mitigation Plan completion) | $40,000 (for WECC2013013178, WECC2013012453, WECC2013012454, and WECC2012012956) | Self-Report | To mitigate this violation, IID: 1) drafted the methodology for determining Facility Ratings of the interconnection equipment between the high side of the step up transformer to the point of interconnection; 2) implemented controls that include the ratings methodology; 3) assigned responsibility for the work within IID; 4) clearly defined the interconnection equipment between the high side of the step up transformer to the point of interconnection; and 5) ensured through validity checks that the work was completed according to the implemented controls. | 2014-10-04 | 2013-10-08 | Agrees | WECC reviewed IID's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that IID has a comprehensive, established, and documented program; that IID has identified and assigned responsibility and accountability to a compliance officer or other high ranking official who has independent access to the chief executive officer or equivalent; and IID's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards. WECC considered IID's voluntary corrective action to remediate this violation to be a mitigating factor.
Western Electricity Coordinating Council (WECC) | Imperial Irrigation District (IID) | NCR05195 | WECC2013012956 | Settlement Agreement | On September 20, 2013, IID submitted a Self-Report stating that, as a Transmission Owner, Generator Owner, and Distribution Provider, it was in violation of PRC-023-1 R1. IID stated that on September 1, 2011, IID added 23 relays to the Protection System and did not update the relay settings so that they were compliant with PRC-023-1. WECC Enforcement reviewed the Self-Report and determined that IID had a violation of PRC-023-1 R1, for its failure to use the applicable criteria from the Standard for 23 relays, to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the Bulk Electric System for all fault conditions. There are 23 relays in scope spread across IID’s identified 230 kiva transmission system that affect the Protection System operations of five substations. Fifteen relays failed to meet PRC-023-1 R1.1, which states that the transmission relays are not to operate at or below 150% of the highest seasonal Facility Rating of a circuit for the available defined loading duration nearest four hours. Four relays failed to meet PRC-023-1 R1.6, which states that the transmission line relays applied on transmission lines connected to generation stations remote to load so they do not operate at or below 230% of the aggregated generation nameplate capacity. Four relays fail to meet PRC-023-1 R1 through R7, which states that transmission line relays applied at the load center terminal, remote from generation stations, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration. The root cause of the violation was IID's lack of process. | PRC-023-1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A failure to follow the criteria for these 26 relays could result in premature loss of up to 500 MW of load, or approximately half of IID’s available substations. IID implemented preventative and detective controls. IID has real-time monitoring and alarming set to notify a system operator of an abnormal condition. If an event were not an immediate threat, the operator would be allowed to respond to the situation prior to the Protection System operating. If an event were to happen quickly, IID would be able to use the real-time monitoring to detect the Protection System operations and respond appropriately to restore the system to normal operating conditions. IID implemented corrective controls. If the Protection System operated prematurely, IID’s personnel are trained on the Protection System schemes applied in its system. In addition, the operators are trained to respond to abnormal system conditions through training on emergency procedures. | 9/1/2011 (when IID added 23 relays to its protection system without updating the relay settings) | 5/7/2014 (Mitigation Plan completion) | $40,000 (for WECC2013013178, WECC2013012453, WECC2013012454, and WECC2012012956) | Self-Report | To mitigate this violation, IID: 1) revised the spreadsheet (IID’s 230 kV Transmission Lines Loadability) that ensures each relay applicable under PRC-023 is verified for having the appropriate settings to meet PRC-023 criteria; 2) IID corrected 14 relay settings to meet the PRC-023 R1 criteria 1, with the exception of the four relays set to protect a radial generation line with a maximum generation contribution; 3) completed the WECC Reliability Coordinator PRC-023 Agreement Process to implement the use of criteria six and seven for the four relays set to protect a radial generation line with a maximum generation contribution; and 4) IID implemented procedural controls. | 2014-05-07 | 2014-08-28 | Agrees | WECC reviewed IID's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC found that IID has a comprehensive, established, and documented program; that IID has identified and assigned responsibility and accountability to a compliance officer or other high ranking official who has independent access to the chief executive officer or equivalent; and IID's ICP is operated and managed so it is independent of those responsible for compliance with NERC Reliability Standards. WECC considered IID's voluntary corrective action to remediate this violation to be a mitigating factor.
Western Electricity Coordinating Council (WECC) | La Paloma Generating Company LLC (LPGC) | NCR05210 | WECC2014013511 | Settlement Agreement | On March 3, 2014, LPGC submitted a Self-Certification stating that, as a Generator Owner, it was in violation of PRC-005-1 R1. A WECC subject matter expert (SME) reviewed the Self-Certification and conducted an interview with LPGC personnel. According to the SME's findings, LPGC failed to update its Protection System maintenance and testing documentation to include battery chargers. On April 1, 2013, NERC's revisions to the NERC Glossary of Terms became effective and the definition added the inclusion of battery chargers within the definition of Protection Systems. LPGC did not update the Protection System maintenance and testing documentation to include all battery chargers at that time. LPGC has total of ten battery chargers. Eight are located in LPGC’s generation plant and the remaining two are located in the switchyard. All of the battery chargers are installed redundantly and have redundant AC power supplies. While LPGC’s Protection System maintenance and testing program (Program) did not include battery chargers, LPGC performed battery charger maintenance. The SME also determined that the root cause of the violation was a lack of compliance understanding. During the WECC SME’s review of the Self-Certification documents, the SME also discovered that LPGC did not have sufficient basis information for maintenance intervals of semi-annual or less for the battery chargers. Specifically, LPGC has a grace period included in its Program. The grace period specified in LPGC’s Program lacked clear application language. After review of the Program with LPGC personnel, the SME learned that the grace period was intended to apply to maintenance intervals longer than one year. LPGC uses the Institute of Electrical and Electronics Engineers (IEEE) 450-2002 standard for the basis of battery maintenance. The IEEE standard specifies monthly, quarterly, and annual maintenance. The IEEE standard does not provide for an adequate period of time to allow for LPGC’s grace period. Although this is the standard listed in LPGC’s Program, LPGC has not utilized the grace period for maintenance conducted at intervals of annual or less. Nonetheless, LPGC’s does not have a basis for its battery charger interval. As a result of these findings, WECC determined that LPGC was in possible violation of PRC-005-1 R1. The SME forwarded the Self-Certification and these findings to WECC Enforcement for review. | PRC-005-1 | R1; R1.1; R1.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. LPGC failed to include battery chargers in its Program and did not have sufficient basis for maintenance intervals of semi-annual and less which could potentially result in the loss of generating stations and switchyard battery systems. Without the battery systems, both the generation stations and the switchyard Protection Systems would potentially be lost resulting in a loss of both facilities and up to 1,048 MW of generation. To prevent the loss of the generating stations, switchyard Protection Systems, and up to 1,048 MW of generation, LPGC implemented a periodic maintenance program for the battery chargers and equipped them with redundant power sources for both the generation plant and the switchyard. To detect the loss of generating stations or switchyard battery systems, LPGC implemented a Digital Control System (DCS) that is monitored 24 hours a day, seven days a week by a plant dispatcher which provides analog quantities for the AC and DC bus voltages. LPGC also has a roving operator which makes daily inspections of the battery chargers and the battery chargers have two outputs to the DCS which activate on the following faults: high and low DC voltage, DC output failure, AC input failure, and ground fault detection on both the positive and negative buses. Relays external to the chargers also provide an alarm contact to the DCS for DC output failure and AC failure for detection purposes. Additionally, LPGC implemented fully redundant battery chargers, so that if one battery charger fails, the standby charger would carry the full DC load. The battery chargers are also fed from redundant AC power sources. No harm is known to have occurred. | 6/18/2007 (when the Standard became mandatory and enforceable) | 4/15/2014 (Mitigation Plan completion) | $12,500 (for WECC2014013511 and WECC2014013512) | Self-Certification | To mitigate this violation, LPGC: 1) confirmed the original equipment manufacturer’s maintenance requirements for the battery chargers; 2) updated the Protection System maintenance and testing attachment documentation; 3) scheduled maintenance via the computerized maintenance management system according to the determined intervals; and 4) performed any newly created scheduled maintenance at the scheduled intervals. | 2014-04-15 | TBD | Does Not Contest | WECC considered LPGC's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | La Paloma Generating Company LLC (LPGC) | NCR05210 | WECC2014013512 | Settlement Agreement | On March 3, 2014, LPGC submitted a Self-Certification stating that, as a Generator Owner, it was in violation of PRC-005-1a R2.1. A WECC subject matter expert (SME) reviewed the Self-Certification and conducted an interview with LPGC personnel. According to the SME findings, LPGC personnel failed to perform battery maintenance and testing as prescribed by its Protection System maintenance and testing program (Program). In its report, LPGC stated that it was its original intent to perform the load test according to the Institute of Electrical and Electronics Engineers (IEEE) standard interval, not yearly as stated in its Program. The Standard IEEE 450 Section 6.3 b calls for load testing at an interval of 25% of the expected life of the battery. For LPGC this equates to approximately 3.75 years. As a result of this discrepancy, LPGC failed to perform the load test on all eight of the generation station batteries within the amount of time specified. The earliest due date for the missed maintenance to be performed and the start date for this violation is December 7, 2011. The SME also determined that the root cause of the violation was human error. A WECC SME issued data requests to LPGC and conducted a review of LPGC’s responses. As a result of the review of the data requests responses, the SME also found that two of LPGC’s batteries semi-annual maintenance intervals had exceeded the listed six-month interval. WECC Enforcement reviewed the Self-Certification, the data request responses, and the SME’s findings and determined that LPGC had a violation of PRC-005-1a R2 for its failure to perform battery maintenance and testing as specified in its Program. | PRC-005-1a | R2; R2.1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. LPGC failed to perform battery maintenance and testing for all of its generation plant batteries according to its Program. By not performing maintenance and testing on a prescribed interval, the battery systems may experience problems leading to the inability to provide power over the expected amount of time. The result is that power for the plant DC buses would decay prematurely. While a loss of all LPGC’s battery systems at the same time would be extremely remote, the potential impact would result in a loss of the entity's peak generation amount of 1,048 MW. LPGC implemented strong preventative controls to prevent the loss of battery systems. Specifically, each battery has a redundant battery. Should one battery fail, the other battery would provide sufficient DC power for the facility. Redundant battery chargers are also employed with redundant AC power sources. Additionally, LPGC implemented maintenance and testing on the battery systems for intervals, other than those missed, which included monthly inspections and semi-annual checks. LPGC also implemented strong detective controls to detect any loss of battery systems. It implements a DCS that is monitored 24 hours a day, seven days a week by a plant dispatcher which provides analog quantities for the AC and DC bus voltages. LPGC also has a roving operator which makes daily inspections of the battery systems. Additionally, the battery chargers have two outputs to the DCS which will activate on the following faults: high and low DC voltage; DC output failure; AC input failure; and ground fault detection on both the positive and negative buses. Relays external to the chargers provide an alarm contact to the DCS for DC output failure and AC failure. In addition, LPGC implemented strong compensating controls. Specifically, LPGC implemented fully redundant battery chargers, so that if one battery charger fails, the standby charger would carry the full DC load. Additionally, the battery chargers are fed from redundant AC power sources. Each generator and switchyard utilizes redundant batteries connected in parallel. This ensures that if a failure of one of the battery systems occurs, the other battery system would continue to carry the load. Finally, the interval specified in the maintenance and testing program was more aggressive than the interval specified in the IEEE standard. No harm is known to have occurred. | 12/7/2011 (when LPGC failed to perform battery maintenance and testing as prescribed by its Program) | 4/15/2014 (Mitigation Plan completion) | $12,500 (for WECC2014013511 and WECC2014013512) | Self-Certification | To mitigate this violation, LPGC: 1) updated the Protection System maintenance and testing attachment documentation; 2) scheduled maintenance via the computerized maintenance management system according to the determined intervals; and 3) performed any newly created scheduled maintenance at the scheduled intervals. | 2014-04-15 | TBD | Does Not Contest | WECC considered LPGC's compliance history and determined there were no relevant instances of noncompliance.