## Public CIP SNOP Posting
Region | Registered EntityName | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015015404 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R2.2. WECC_URE1 failed to adequately implement security controls testing on two Physical Access Control Systems (PACS) servers as required for CIP-007-3 R1 pursuant to CIP-006-3c R2.2. The PACS system was upgraded to allow continued functioning in a fully supported NERC-compliant environment. As a consequence of the change, system event logs from the two PACS servers were not being transmitted to WECC_URE1's daily security report for periodic review. As part of routine maintenance activity on the hardware supporting the PACS software, WECC_URE1's IT department detected that daily security event reports did not include electronic access event information from two local PACS servers. Logs were being created and maintained by the PACS servers; however, the electronic access event information was not transmitted to WECC_URE1's daily security event reporting and therefore not being reviewed timely. This reporting failure was not noticed during the routine log reviews because the daily PACS security report typically contains only information from the PACS client workstations. Electronic access events on the client workstations occurred many times each day, whereas the electronic access events on PACS servers occurred approximately once a month. WECC_URE1 began an initial review of the server logs and found no security events issues or malware issues on the logs. Subsequent to the log review, WECC_URE1 performed a root cause analysis and determined that system testing and documentation for the upgrade on the two PACS servers per CIP-007-R1.1 were incomplete. Specifically, WECC_URE1's test plan called for “system integration testing” (SIT) and “user acceptance testing” (UAT) but the plan did not indicate what steps the tests were to include, nor did available documentation provide information as to the content of the tests. The SIT and UAT focused on functional testing and did not include testing of security controls related to the security event report. The configuration of electronic access events on the two PACS servers to the daily security event report did not occur. Prior to the upgrade, the two PACS servers had been reporting system logs, to include electronic access events, to WECC_URE1's security event report that were reviewed as required. The root cause of this violation was the failure of WECC_URE1 to adequately implement security controls testing as required by CIP-007-3 R1. | CIP-006-3c | R2; R2.2 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to perform adequate testing during an upgrade of the PACS servers which resulted in the system event logs of the two PACS servers not being reviewed for 258 days. Failure to perform adequate testing on Cyber Assets could lead to future changes being conducted without a clear understanding of the current configuration, leading to potential device failures as new changes are applied. PACS server logs were generated and maintained by the servers. WECC_URE1 reviewed the PACS server logs for system events related to electronic access attempts once the logs were configured correctly to appear on the security event report, and confirmed that no security events related to electronic access attempts occurred during the violation period. Additionally, the risk was further minimized by the fact that electronic and unescorted physical access to the devices was restricted to a small number of trained and authorized personnel. Each server was installed in a lock-box, controlled by card key and pin-pad access. Electronic access was controlled by Active Directory and restricted by both firewalls and network configuration. The only data that was not reported on the daily security event report was access attempts to the two PACS servers. WECC_URE1 had performed both operational and functional testing during the upgrade, and all physical access controls at WECC_URE1 continued to perform as required and expected during the upgrade. No harm is known to have occurred. | when WECC_URE1 failed to adequately implement security controls testing on two PACS servers | when WECC_URE1's PACS IT team developed and implemented an interim change management test script that specifically identified security testing | 17000 | Self-Report | To mitigate this violation, WECC_URE1: 1) developed and implemented an interim change management test script that specifically identified security testing; 2) comprehensively revised its test procedure for changes that deviate from the existing baseline configuration as part of the overall transition of cyber security practices from CIP Version 3 to CIP Version 5; and 3) trained all applicable personnel on the new procedures and controls. | 2016-06-16 | 2016-10-12 | Agrees/Stipulates | WECC_URE1 discovered this violation and self-reported nearly four months after discovery. WECC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted nearly four months after the noncompliance was discovered. WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Although WECC_URE1 has a documented ICP that has been provided to WECC, had the ICP been implemented properly, with appropriate internal controls in place, WECC_URE1 would have been able to identify, assess, and correct this violation in a timely manner. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015014872 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-006-1 R1.8. Specifically, WECC_URE2 stated that as part of its management effort to develop detailed roles and responsibilities within its IT department, WECC_URE2 discovered that security patches for its Physical Access Control System (PACS) had not been assessed in over a year. WECC_URE2 conducted a full extent of condition review to identify any other areas of possible noncompliance as per CIP-006-1 R1.8. As a result of the review, WECC_URE2 identified noncompliance with CIP-003-3 R5 (R5.1.2, R5.2, and R5.3), CIP-004-3a R4.1, CIP-007-1 R1 (R1.1 and R1.2), R2, and R5.2.3, CIP-007-3a R3, R5 (R5.1.3, R5.2.3, R5.3, and R5) and R9, CIP-008-3 R1.5, and CIP-009-3 R1 and R5, as it relates to PACS. WECC_URE2 failed to ensure 29 PACS devices were provided the protections as required by CIP-006-1 R1.8. The devices in scope were PACS Node Controllers, a PACS server, a PACS database server, a virtual host, and virtual workstations, affecting Critical Assets. The root causes of this issue were failure of WECC_URE2 to communicate and coordinate between lines of business and to provide sufficient controls to ensure periodic compliance activities were completed when individuals left WECC_URE2. | CIP-006-1 | R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, WECC_URE2 failed to ensure PACS devices were provided the protections as required by CIP-006-1 R1.8. Failing to provide multiple security controls for PACS could result in two areas of unexpected vulnerabilities and disruptions: 1) disruption of the intended function and operation of the PACS technologies, which includes changes, modifications or disabling existing PACS at Critical Assets; and 2) introducing vulnerabilities, such as unauthorized system accounts, malware or removal of monitoring controls on the PACS themselves. The result of these can be unauthorized personnel accessing Critical Assets and Critical Cyber Assets, resulting in damage to equipment, power cycling, or shutting down critical systems, thus potentially affecting the BPS. WECC_URE2 implemented good internal controls to eliminate potential unauthorized physical access. This included administrative, technical, and physical controls such as: 1) electronic badge card reader systems to control physical access to the PSPs; 2) 24x7 security monitoring of the PSPs; 3) personnel risk assessments for both role separation and function and 4) authentication systems to control access to Critical Assets. In addition, WECC_URE2 implemented a visitor control program and a contractor screening process, thereby reducing the risk of actions that could negatively affect the BPS. | when the Standard became mandatory and enforceable on WECC_URE2 | when WECC_URE2 provided the protections of CIP-006-3a R2.2 to the last remaining PACS device in scope | 55000 | Self-Certification | To mitigate this violation, WECC_URE2: 1) brought the devices in scope into compliance. Specifically, WECC_URE2: a. CIP-003-3 R5.1.2: completed the annual review of designated personnel responsible for authorizing access to protected information. b. CIP-003-3 R5.2: completed the annual review of access to protected information. c. CIP-003-3 R5.3: completed the annual review of the CIP-003 R5 procedure. d. CIP-004-3a R4.1: completed the quarterly reviews of the lists of personnel who have cyber access to the PACS. e. CIP-007-3a R3: completed security patch assessments and applied, where applicable. f. CIP-007-3a R5.1.3: completed the annual review of user accounts with access to the PACS. g. CIP-007-1 R5.2.3: began using a tool to manage its administrator and admin accounts. h. CIP-007-3a R5.3: began using a tool to manage the passwords for the administrator and admin accounts. i. CIP-007-3a R9: completed the annual review of the procedures required by CIP-007-3a R1 through R8. j. CIP-008-3 R1.5: completed the annual review of the Cyber Security Incident Response Plan. k. CIP-009-3 R1: completed the annual review of the recovery plan. l. CIP-009-3 R5: completed all backup media testing. m. CIP-007-1 R1.1 and R1.2: updated procedures to include language on how WECC_URE2 tests. n. CIP-007-1 R2: documented a process related to ports and services. o. CIP-007-3a R5: documented controls to enforce access authentications. 2) added events to a centralized group calendar to remind WECC_URE2 IT OpsNet staff of the required reviews; 3) engaged WECC_URE2's Enterprise Risk team to assist IT with the quarterly and annual review events and dates by performing spot checks and monitoring WECC_URE2's adherence to the review cycles; and 4) deployed a new PACS and configured all shared accounts used in the PACS environment to be managed through a password management tool. | 7/1/2015 | 6/28/2016 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Although WECC_URE2 has a documented ICP that has been provided to WECC, had the ICP been implemented properly, WECC_URE2 would have been able to identify, assess, and correct this violation in a timely manner. WECC applied an aggravating factor and escalated the disposition treatment with a penalty because of the duration of the violation. WECC considered WECC_URE2's CIP-006-1 R1.8 compliance history to be an aggravating factor in the penalty determination.