## Main Data Entry
Unit Information & Characteristics | [6 empty] | 11111109
Contributor Name:
Contributor Phone Number:
Contributor Email:
Generator Operator:
EIA 860 Plant Name (US Only):
EIA 860 Plant Code (US Only):
EIA 860 Generator ID (US Only):
GADS Generator Unit ID:
Planning Case Bus Number:
| Interconnection: | Eastern
Balancing Authority:
Generator Type:
Generator Machine Base (MBASE)(MVA):
Inertia Constant (H):
| Unit Droop Setting @ Time of Event: |  | %
| Unit Deadband Setting @ Time of Event: |  | Hz
| Unit Operating Mode @ Time of Event: |  |  | Hz Span | 3 | Hz
| Maximum Operating Level (Pmax)(HSL) @ Time of Event: | 0 | MW | Hz Span (dB) | 2.964 | Hz
| Minimum Operating Level (Pmin)(LSL) @ Time of Event: | 0 | MW | Turbine NDC | 0 | MW
| Expected Droop Setting: | 5%
| Expected Deadband Setting: | 0.036 | Hz
System & Event Characteristics
| Time of Frequency Event (UTC): | 2019-07-26 22:11 | Date | Time
| Grid Nominal Frequency: | 60 | 2019-07-26 22:11 | 43672.9244
Report Options
| Data Source: | Historian
| Time Zone of Historian Data: | UTC
Manual Data Entry
|  | Pre-Perturbation Average Frequency [T(-16) to T(-2)] |  | Hz
|  | Post-Perturbation Average Frequency [T(+20 to T(+52)] |  | Hz
|  | Post-Perturbation Frequency [(T+46)] |  | Hz
|  | Pre-Perturbation Average MW [T(-2 ) to T(-16)] |  | MW
|  | Post-Perturbation Average MW [T(+20 to T(+52)] |  | MW
|  | Maximum MW Response [T(+46) to T(+60)] |  | MW
|  | MW Output [T(-4)] |  | MW
|  | MW Output [T(-60)] |  | MW
Read Historian Data

## Results
Results
|  | P.U. Primary Frequency Response Performance (PUPFR): | Offline
|  | P.U. Sustained Primary Frequency Response Performance (PUSPFR): | Offline
|  | Overall Unit Performance: | Offline
|  | Minimum Acceptable Score (PU): | 75%
For Generators between Pmin and % of Pmax and eligible to provide PFR; -Generators who provide response in the proper direction and sustained it for the lessor of the event duration or for 1 minute: J -Generators whose MW output remained unchanged or was in the wrong direction: L
Reason for Performance (optional)
comments
Calculate

## Historian Data
|  |  | Start (2mins before T(0)) | 2019-07-26 22:09
|  |  | Offset | -1
-Data should be pulled for NO LESS THAN 1 minute before t(0) and NO LESS THAN 2 minutes after t(0).
-Data may be pulled at any sample interval from 1s to 8s, as long as it is in the proper format.
-Note that the resulting Primary Frequency Response (PFR) calculations are a product of the Data provided. Faster sampled data will provide a result most representative of the units response.
-Any data beyond Row 4000 of this sheet will not be sampled or used in the calculation.
Timestamp | Unit Frequency | MW Output
Read Historian Data

## Calculations
Offset (s) | 0 |  |  |  | Date (UTC): | [9 empty] | 2019-07-26 22:11
*Offset should not be more than +/-38s |  |  |  |  | Time of T(0) (UTC) | [9 empty] | 43672.9244 | [12 empty] | min frequency | 59.9
[28 empty] | max frequency | 60.025
Calculated using Generator provided Historian Data | [17 empty] | Calculated using Generator provided manually calculated data |  |  |  |  | Raw Input Data |  |  | Interpolated Values |  | frequency major unit | 0.025
[5 empty] | Pre-Perturbation Average Frequency [T(-16) to T(-2)] | [9 empty] | 59.9855 |  |  |  | Pre-Perturbation Average Frequency [T(-16) to T(-2)] | 0 | [7 empty] | frequency units | 5
[5 empty] | Post-Perturbation Average Frequency [T(+20 to T(+52)] | [9 empty] | 59.9508 |  |  |  | Post-Perturbation Average Frequency [T(+20 to T(+52)] | 0 |  |  | Timestamp | Raw Frequency (Hz) | Raw Generator Output (MW) | Raw Frequency (Hz) | Raw Generator Output (MW) | min response | 440
[5 empty] | Pre to Post Perturbation Delta Frequency Actual | [9 empty] | -0.034734 |  |  |  | Pre to Post Perturbation Delta Frequency Actual | 0 | [7 empty] | max response | 470
[5 empty] | Post-Perturbation Frequency (T+46) | [9 empty] | 59.9568 |  |  |  | Post-Perturbation Frequency (T+46) | 0 | [7 empty] | response major unit | 6
[5 empty] | Pre to Post-Event Delta Frequency Actual (T+46) | [9 empty] | -0.028693 |  |  |  | Pre to Post-Event Delta Frequency Actual (T+46) | 0
[5 empty] | High or Low Frequency Event? | [9 empty] | Low |  |  |  | High or Low Frequency Event? | Low
[23 empty] | 43672.9231 |  |  | 0 | 0
[5 empty] | Pre-Perturbation Average MW [T(-2 ) to T(-16)] | [9 empty] | 448.1995 | Headroom Available: | -448.1995 |  | Pre-Perturbation Average MW [T(-2 ) to T(-16)] | 0 | Headroom Available: | 0 | 43672.9231 | 60.0085 | 448.6598 | 60.0085 | 448.6598
[5 empty] | Post-Perturbation Average MW [T(+20 to T(+52)] | [9 empty] | 454.2995 | Footroom Available: | 448.1995 |  | Post-Perturbation Average MW [T(+20 to T(+52)] | 0 | Footroom Available: | 0 | 43672.9231 |  |  | 60.0085 | 448.6598
[5 empty] | Pre to Post-Perturbation Delta MW Actual | [9 empty] | 6.1 | Adequate Margin? | No |  | Pre to Post-Perturbation Delta MW Actual | 0 | Adequate Margin? | No | 43672.9231 | 60.0083 | 448.6791 | 60.0083 | 448.6791
[23 empty] | 43672.9231 |  |  | 60.0083 | 448.6791
[5 empty] | RampMagnitude_initial | [9 empty] | -0.22172 |  |  |  | RampMagnitude_initial | 0 |  |  | 43672.9231 | 60.0081 | 448.6984 | 60.0081 | 448.6984
[5 empty] | Actual Primary Frequency Response (adjusted) | [9 empty] | 6.3217 |  |  |  | Actual Primary Frequency Response (adjusted) | 0 |  |  | 43672.9232 |  |  | 60.0081 | 448.6984
[5 empty] | Expected Primary Frequency Response (Pre) | [9 empty] | 0 |  |  |  | Expected Primary Frequency Response (Pre) | 0 |  |  | 43672.9232 | 60.0079 | 448.7177 | 60.0079 | 448.7177
[5 empty] | Expected Primary Frequency Response (Post) | [9 empty] | 0 |  |  |  | Expected Primary Frequency Response (Post) | 0 |  |  | 43672.9232 |  |  | 60.0079 | 448.7177
[5 empty] | Expected Primary Frequency Response (Ideal) | [9 empty] | 0 |  |  |  | Expected Primary Frequency Response (Ideal) | 0 |  |  | 43672.9232 | 60.0074 | 448.737 | 60.0074 | 448.737
[5 empty] | Expected Primary Frequency Response (Final) | [9 empty] | 0 |  |  |  | Expected Primary Frequency Response (Final) | 0 |  |  | 43672.9232 |  |  | 60.0074 | 448.737
[23 empty] | 43672.9232 | 60.007 | 448.7563 | 60.007 | 448.7563
[5 empty] | PUPFR Performance | [9 empty] | 0% | Final PUPFR Performance | No Evaluation |  | PUPFR Performance | 0% | Final PUPFR Performance | No Evaluation | 43672.9232 |  |  | 60.007 | 448.7563
[23 empty] | 43672.9232 | 60.0065 | 448.7756 | 60.0065 | 448.7756
[5 empty] | Maximum MW Response [T(+46) to T(+60)] | [9 empty] | 454.029 |  |  |  | Maximum MW Response [T(+46) to T(+60)] | 0 |  |  | 43672.9233 |  |  | 60.0065 | 448.7756
[5 empty] | Actual Sustained Primary Frequency Response | [9 empty] | 5.8295 |  |  |  | Actual Sustained Primary Frequency Response | 0 |  |  | 43672.9233 | 60.0027 | 448.3638 | 60.0027 | 448.3638
[5 empty] | RampMagnitude_sustained | [9 empty] | -0.30853 |  |  |  | RampMagnitude_sustained | 0 |  |  | 43672.9233 |  |  | 60.0027 | 448.3638
[5 empty] | Actual Sustained Primary Frequency Response (adjusted) | [9 empty] | 6.1381 |  |  |  | Actual Sustained Primary Frequency Response (adjusted) | 0 |  |  | 43672.9233 | 59.9989 | 448.3148 | 59.9989 | 448.3148
[5 empty] | Expected Sustained Primary Frequency Response [T(+46)] | [9 empty] | 0 |  |  |  | Expected Sustained Primary Frequency Response [T(+46)] | 0 |  |  | 43672.9233 |  |  | 59.9989 | 448.3148
[5 empty] | Expected Sustained Primary Frequency Response (Ideal) | [9 empty] | 0 |  |  |  | Expected Sustained Primary Frequency Response (Ideal) | 0 |  |  | 43672.9233 | 59.9951 | 448.2659 | 59.9951 | 448.2659
[5 empty] | Expected Sustained Primary Frequency Response (Final) | [9 empty] | 0 |  |  |  | Expected Sustained Primary Frequency Response (Final) | 0 |  |  | 43672.9233 |  |  | 59.9951 | 448.2659
[23 empty] | 43672.9233 | 59.9951 | 448.2169 | 59.9951 | 448.2169
[5 empty] | PUSPFR Performance | [9 empty] | 0% | Final PUSPFR Performance | No Evaluation |  | PUSPFR Performance | 0% | Final PUSPFR Performance | No Evaluation | 43672.9233 |  |  | 59.9951 | 448.2169
[23 empty] | 43672.9234 | 59.9951 | 448.1679 | 59.9951 | 448.1679
[23 empty] | 43672.9234 |  |  | 59.9951 | 448.1679
[23 empty] | 43672.9234 | 59.9813 | 447.9287 | 59.9813 | 447.9287
[23 empty] | 43672.9234 |  |  | 59.9813 | 447.9287
[23 empty] | 43672.9234 | 59.9773 | 448.16 | 59.9773 | 448.16
| Pre-Event Period |  |  |  |  | Chart Values | [16 empty] | 43672.9234 |  |  | 59.9773 | 448.16
| T(0) | [21 empty] | 43672.9234 | 59.9734 | 448.6617 | 59.9734 | 448.6617
| Post-Event Period | [21 empty] | 43672.9234 |  |  | 59.9734 | 448.6617
| Input Data | Interpolated |  | *Note that all times are in UTC time |  |  | Pre and Post-Perturbation Average Values |  |  |  | PFR Values | [11 empty] | 43672.9234 | 59.9734 | 448.6634 | 59.9734 | 448.6634
|  |  |  | *Note that the first few rows in this might be blank depending on data provided. | [18 empty] | 43672.9235 |  |  | 59.9734 | 448.6634
T | Offset Timestamp | Offset Frequency (Hz) | Offset Generator Output (MW) | Average Frequency (Hz) | Average Output (MW) | Proxy | Pre-Perturbation Frequency (Hz) | Post-Perturbation Frequency (Hz) | Pre-Perturbation Output (MW) | Post-Perturbation Output (MW) | Measured Initial Response (MW) | Expected Initial PFR (MW) | Measured Sustained Response (MW) | Expected Sustained PFR (MW) | HSL (MW) | Ideal Expected Primary Frequency Response (EPFR) (MW) | Average EPFR (MW) | 36 mHz Deadband |  |  |  |  | 43672.9235 | 59.9734 | 448.6634 | 59.9734 | 448.6634
[23 empty] | 43672.9235 |  |  | 59.9734 | 448.6634
[23 empty] | 43672.9235 | 59.9734 | 448.6631 | 59.9734 | 448.6631
[23 empty] | 43672.9235 |  |  | 59.9734 | 448.6631
[23 empty] | 43672.9235 | 59.9717 | 448.126 | 59.9717 | 448.126
T-72s | 43672.9235 | 59.9717 | 448.126 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9235 |  |  | 59.9717 | 448.126
T-71s | 43672.9235 | 59.9717 | 448.1247 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9235 | 59.9717 | 448.1247 | 59.9717 | 448.1247
T-70s | 43672.9236 | 59.9717 | 448.1247 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9236 |  |  | 59.9717 | 448.1247
T-69s | 43672.9236 | 59.9717 | 448.1247 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9236 | 59.9717 | 448.1247 | 59.9717 | 448.1247
T-68s | 43672.9236 | 59.9717 | 448.1247 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9236 |  |  | 59.9717 | 448.1247
T-67s | 43672.9236 | 59.9717 | 448.1247 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9236 | 59.9717 | 448.1247 | 59.9717 | 448.1247
T-66s | 43672.9236 | 59.9717 | 448.1247 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9236 |  |  | 59.9717 | 448.1247
T-65s | 43672.9236 | 59.9699 | 448.457 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9236 | 59.9699 | 448.457 | 59.9699 | 448.457
T-64s | 43672.9236 | 59.9699 | 448.457 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9236 |  |  | 59.9699 | 448.457
T-63s | 43672.9236 | 59.9709 | 447.9988 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9236 | 59.9709 | 447.9988 | 59.9709 | 447.9988
T-62s | 43672.9236 | 59.9709 | 447.9988 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9236 |  |  | 59.9709 | 447.9988
T-61s | 43672.9237 | 59.9705 | 448.6846 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9237 | 59.9705 | 448.6846 | 59.9705 | 448.6846
T-60s | 43672.9237 | 59.9705 | 448.6846 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9237 |  |  | 59.9705 | 448.6846
T-59s | 43672.9237 | 59.9701 | 448.6867 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9237 | 59.9701 | 448.6867 | 59.9701 | 448.6867
T-58s | 43672.9237 | 59.9701 | 448.6867 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9237 |  |  | 59.9701 | 448.6867
T-57s | 43672.9237 | 59.9698 | 448.6867 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9237 | 59.9698 | 448.6867 | 59.9698 | 448.6867
T-56s | 43672.9237 | 59.9698 | 448.6867 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9237 |  |  | 59.9698 | 448.6867
T-55s | 43672.9237 | 59.9711 | 448.3689 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9237 | 59.9711 | 448.3689 | 59.9711 | 448.3689
T-54s | 43672.9237 | 59.9711 | 448.3689 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9237 |  |  | 59.9711 | 448.3689
T-53s | 43672.9237 | 59.971 | 448.5578 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9237 | 59.971 | 448.5578 | 59.971 | 448.5578
T-52s | 43672.9238 | 59.971 | 448.5578 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9238 |  |  | 59.971 | 448.5578
T-51s | 43672.9238 | 59.9709 | 448.5578 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9238 | 59.9709 | 448.5578 | 59.9709 | 448.5578
T-50s | 43672.9238 | 59.9709 | 448.5578 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9238 |  |  | 59.9709 | 448.5578
T-49s | 43672.9238 | 59.9708 | 448.5578 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9238 | 59.9708 | 448.5578 | 59.9708 | 448.5578
T-48s | 43672.9238 | 59.9708 | 448.5578 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9238 |  |  | 59.9708 | 448.5578
T-47s | 43672.9238 | 59.9707 | 448.5578 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9238 | 59.9707 | 448.5578 | 59.9707 | 448.5578
T-46s | 43672.9238 | 59.9707 | 448.5578 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9238 |  |  | 59.9707 | 448.5578
T-45s | 43672.9238 | 59.9726 | 448.2818 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9238 | 59.9726 | 448.2818 | 59.9726 | 448.2818
T-44s | 43672.9239 | 59.9726 | 448.2818 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9239 |  |  | 59.9726 | 448.2818
T-43s | 43672.9239 | 59.9745 | 448.5201 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9239 | 59.9745 | 448.5201 | 59.9745 | 448.5201
T-42s | 43672.9239 | 59.9745 | 448.5201 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9239 |  |  | 59.9745 | 448.5201
T-41s | 43672.9239 | 59.9745 | 448.1342 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9239 | 59.9745 | 448.1342 | 59.9745 | 448.1342
T-40s | 43672.9239 | 59.9745 | 448.1342 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9239 |  |  | 59.9745 | 448.1342
T-39s | 43672.9239 | 59.9745 | 448.1341 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9239 | 59.9745 | 448.1341 | 59.9745 | 448.1341
T-38s | 43672.9239 | 59.9745 | 448.1341 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9239 |  |  | 59.9745 | 448.1341
T-37s | 43672.9239 | 59.9745 | 448.1341 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9239 | 59.9745 | 448.1341 | 59.9745 | 448.1341
T-36s | 43672.9239 | 59.9745 | 448.1341 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9239 |  |  | 59.9745 | 448.1341
T-35s | 43672.924 | 59.9745 | 448.1341 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.924 | 59.9745 | 448.1341 | 59.9745 | 448.1341
T-34s | 43672.924 | 59.9745 | 448.1341 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.924 |  |  | 59.9745 | 448.1341
T-33s | 43672.924 | 59.978 | 448.3268 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.924 | 59.978 | 448.3268 | 59.978 | 448.3268
T-32s | 43672.924 | 59.978 | 448.3268 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.924 |  |  | 59.978 | 448.3268
T-31s | 43672.924 | 59.978 | 448.3268 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.924 | 59.978 | 448.3268 | 59.978 | 448.3268
T-30s | 43672.924 | 59.978 | 448.3268 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.924 |  |  | 59.978 | 448.3268
T-29s | 43672.924 | 59.978 | 448.3268 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.924 | 59.978 | 448.3268 | 59.978 | 448.3268
T-28s | 43672.924 | 59.978 | 448.3268 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.924 |  |  | 59.978 | 448.3268
T-27s | 43672.9241 | 59.978 | 448.3268 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9241 | 59.978 | 448.3268 | 59.978 | 448.3268
T-26s | 43672.9241 | 59.978 | 448.3268 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9241 |  |  | 59.978 | 448.3268
T-25s | 43672.9241 | 59.9841 | 447.9363 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9241 | 59.9841 | 447.9363 | 59.9841 | 447.9363
T-24s | 43672.9241 | 59.9841 | 447.9363 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9241 |  |  | 59.9841 | 447.9363
T-23s | 43672.9241 | 59.9859 | 447.8957 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9241 | 59.9859 | 447.8957 | 59.9859 | 447.8957
T-22s | 43672.9241 | 59.9859 | 447.8957 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9241 |  |  | 59.9859 | 447.8957
T-21s | 43672.9241 | 59.9859 | 447.8565 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9241 | 59.9859 | 447.8565 | 59.9859 | 447.8565
T-20s | 43672.9241 | 59.9859 | 447.8565 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9241 |  |  | 59.9859 | 447.8565
T-19s | 43672.9241 | 59.9859 | 447.8173 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9241 | 59.9859 | 447.8173 | 59.9859 | 447.8173
T-18s | 43672.9242 | 59.9859 | 447.8173 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9242 |  |  | 59.9859 | 447.8173
T-17s | 43672.9242 | 59.9859 | 447.7781 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9242 | 59.9859 | 447.7781 | 59.9859 | 447.7781
T-16s | 43672.9242 | 59.9859 | 447.7781 | 59.9855 | 448.1995 |  | 59.9855 |  | 448.1995 | [5 empty] | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9242 |  |  | 59.9859 | 447.7781
T-15s | 43672.9242 | 59.9859 | 447.9904 | 59.9855 | 448.1995 |  | 59.9855 |  | 448.1995 | [5 empty] | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9242 | 59.9859 | 447.9904 | 59.9859 | 447.9904
T-14s | 43672.9242 | 59.9859 | 447.9904 | 59.9855 | 448.1995 |  | 59.9855 |  | 448.1995 | [5 empty] | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9242 |  |  | 59.9859 | 447.9904
T-13s | 43672.9242 | 59.9856 | 448.2034 | 59.9855 | 448.1995 |  | 59.9855 |  | 448.1995 | [5 empty] | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9242 | 59.9856 | 448.2034 | 59.9856 | 448.2034
T-12s | 43672.9242 | 59.9856 | 448.2034 | 59.9855 | 448.1995 |  | 59.9855 |  | 448.1995 | [5 empty] | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9242 |  |  | 59.9856 | 448.2034
T-11s | 43672.9242 | 59.9853 | 448.2303 | 59.9855 | 448.1995 |  | 59.9855 |  | 448.1995 | [5 empty] | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9242 | 59.9853 | 448.2303 | 59.9853 | 448.2303
T-10s | 43672.9242 | 59.9853 | 448.2303 | 59.9855 | 448.1995 |  | 59.9855 |  | 448.1995 | [5 empty] | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9242 |  |  | 59.9853 | 448.2303
T-9s | 43672.9243 | 59.9851 | 448.2565 | 59.9855 | 448.1995 |  | 59.9855 |  | 448.1995 | [5 empty] | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9243 | 59.9851 | 448.2565 | 59.9851 | 448.2565
T-8s | 43672.9243 | 59.9851 | 448.2565 | 59.9855 | 448.1995 |  | 59.9855 |  | 448.1995 | [5 empty] | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9243 |  |  | 59.9851 | 448.2565
T-7s | 43672.9243 | 59.9848 | 448.2827 | 59.9855 | 448.1995 |  | 59.9855 |  | 448.1995 | [5 empty] | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9243 | 59.9848 | 448.2827 | 59.9848 | 448.2827
T-6s | 43672.9243 | 59.9848 | 448.2827 | 59.9855 | 448.1995 |  | 59.9855 |  | 448.1995 | [5 empty] | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9243 |  |  | 59.9848 | 448.2827
T-5s | 43672.9243 | 59.9845 | 448.3088 | 59.9855 | 448.1995 |  | 59.9855 |  | 448.1995 | [5 empty] | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9243 | 59.9845 | 448.3088 | 59.9845 | 448.3088
T-4s | 43672.9243 | 59.9845 | 448.3088 | 59.9855 | 448.1995 |  | 59.9855 |  | 448.1995 | [5 empty] | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9243 |  |  | 59.9845 | 448.3088
T-3s | 43672.9243 | 59.987 | 448.335 | 59.9855 | 448.1995 |  | 59.9855 |  | 448.1995 | [5 empty] | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9243 | 59.987 | 448.335 | 59.987 | 448.335
T-2s | 43672.9243 | 59.987 | 448.335 | 59.9855 | 448.1995 |  | 59.9855 |  | 448.1995 | [5 empty] | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9243 |  |  | 59.987 | 448.335
T-1s | 43672.9244 | 59.987 | 448.3612 |  |  | -1000000000 | [8 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9244 | 59.987 | 448.3612 | 59.987 | 448.3612
T=0 | 43672.9244 | 59.987 | 448.3612 |  |  | 60 | [8 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9244 |  |  | 59.987 | 448.3612
T+1s | 43672.9244 | 59.987 | 448.3874 |  |  | 1000000000 | [8 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9244 | 59.987 | 448.3874 | 59.987 | 448.3874
T+2s | 43672.9244 | 59.987 | 448.3874 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9244 |  |  | 59.987 | 448.3874
T+3s | 43672.9244 | 59.987 | 448.4135 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9244 | 59.987 | 448.4135 | 59.987 | 448.4135
T+4s | 43672.9244 | 59.987 | 448.4135 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9244 |  |  | 59.987 | 448.4135
T+5s | 43672.9244 | 59.9887 | 448.4397 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9244 | 59.9887 | 448.4397 | 59.9887 | 448.4397
T+6s | 43672.9244 | 59.9887 | 448.4397 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9244 |  |  | 59.9887 | 448.4397
T+7s | 43672.9244 | 59.9883 | 448.2621 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9244 | 59.9883 | 448.2621 | 59.9883 | 448.2621
T+8s | 43672.9245 | 59.9883 | 448.2621 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9245 |  |  | 59.9883 | 448.2621
T+9s | 43672.9245 | 59.988 | 448.2619 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9245 | 59.988 | 448.2619 | 59.988 | 448.2619
T+10s | 43672.9245 | 59.988 | 448.2619 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9245 |  |  | 59.988 | 448.2619
T+11s | 43672.9245 | 59.9877 | 448.2619 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9245 | 59.9877 | 448.2619 | 59.9877 | 448.2619
T+12s | 43672.9245 | 59.9877 | 448.2619 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9245 |  |  | 59.9877 | 448.2619
T+13s | 43672.9245 | 59.9874 | 448.2619 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9245 | 59.9874 | 448.2619 | 59.9874 | 448.2619
T+14s | 43672.9245 | 59.9874 | 448.2619 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9245 |  |  | 59.9874 | 448.2619
T+15s | 43672.9245 | 59.9691 | 448.7764 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9245 | 59.9691 | 448.7764 | 59.9691 | 448.7764
T+16s | 43672.9245 | 59.9691 | 448.7764 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9245 |  |  | 59.9691 | 448.7764
T+17s | 43672.9246 | 59.9509 | 450.35 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9246 | 59.9509 | 450.35 | 59.9509 | 450.35
T+18s | 43672.9246 | 59.9509 | 450.35 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9246 |  |  | 59.9509 | 450.35
T+19s | 43672.9246 | 59.9447 | 453.3483 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9246 | 59.9447 | 453.3483 | 59.9447 | 453.3483
T+20s | 43672.9246 | 59.9447 | 453.3483 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9246 |  |  | 59.9447 | 453.3483
T+21s | 43672.9246 | 59.9451 | 453.3483 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9246 | 59.9451 | 453.3483 | 59.9451 | 453.3483
T+22s | 43672.9246 | 59.9451 | 453.3483 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9246 |  |  | 59.9451 | 453.3483
T+23s | 43672.9246 | 59.9454 | 453.3483 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9246 | 59.9454 | 453.3483 | 59.9454 | 453.3483
T+24s | 43672.9246 | 59.9454 | 453.3483 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9246 |  |  | 59.9454 | 453.3483
T+25s | 43672.9247 | 59.9458 | 454.1004 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9247 | 59.9458 | 454.1004 | 59.9458 | 454.1004
T+26s | 43672.9247 | 59.9458 | 454.1004 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9247 |  |  | 59.9458 | 454.1004
T+27s | 43672.9247 | 59.9461 | 454.853 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9247 | 59.9461 | 454.853 | 59.9461 | 454.853
T+28s | 43672.9247 | 59.9461 | 454.853 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9247 |  |  | 59.9461 | 454.853
T+29s | 43672.9247 | 59.9465 | 454.853 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9247 | 59.9465 | 454.853 | 59.9465 | 454.853
T+30s | 43672.9247 | 59.9465 | 454.853 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9247 |  |  | 59.9465 | 454.853
T+31s | 43672.9247 | 59.9468 | 455.1813 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9247 | 59.9468 | 455.1813 | 59.9468 | 455.1813
T+32s | 43672.9247 | 59.9468 | 455.1813 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9247 |  |  | 59.9468 | 455.1813
T+33s | 43672.9247 | 59.9472 | 455.1825 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9247 | 59.9472 | 455.1825 | 59.9472 | 455.1825
T+34s | 43672.9248 | 59.9472 | 455.1825 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9248 |  |  | 59.9472 | 455.1825
T+35s | 43672.9248 | 59.9475 | 455.1825 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9248 | 59.9475 | 455.1825 | 59.9475 | 455.1825
T+36s | 43672.9248 | 59.9475 | 455.1825 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9248 |  |  | 59.9475 | 455.1825
T+37s | 43672.9248 | 59.9503 | 454.8202 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9248 | 59.9503 | 454.8202 | 59.9503 | 454.8202
T+38s | 43672.9248 | 59.9503 | 454.8202 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9248 |  |  | 59.9503 | 454.8202
T+39s | 43672.9248 | 59.9531 | 454.8627 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9248 | 59.9531 | 454.8627 | 59.9531 | 454.8627
T+40s | 43672.9248 | 59.9531 | 454.8627 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9248 |  |  | 59.9531 | 454.8627
T+41s | 43672.9248 | 59.9531 | 454.9066 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9248 | 59.9531 | 454.9066 | 59.9531 | 454.9066
T+42s | 43672.9248 | 59.9531 | 454.9066 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9248 |  |  | 59.9531 | 454.9066
T+43s | 43672.9249 | 59.9531 | 454.9505 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9249 | 59.9531 | 454.9505 | 59.9531 | 454.9505
T+44s | 43672.9249 | 59.9531 | 454.9505 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9249 |  |  | 59.9531 | 454.9505
T+45s | 43672.9249 | 59.9568 | 454.029 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 |  |  | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9249 | 59.9568 | 454.029 | 59.9568 | 454.029
T+46s | 43672.9249 | 59.9568 | 454.029 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 | 454.029 | 448.1995 | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9249 |  |  | 59.9568 | 454.029
T+47s | 43672.9249 | 59.9605 | 453.1071 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 | 454.029 | 448.1995 | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9249 | 59.9605 | 453.1071 | 59.9605 | 453.1071
T+48s | 43672.9249 | 59.9605 | 453.1071 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 | 454.029 | 448.1995 | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9249 |  |  | 59.9605 | 453.1071
T+49s | 43672.9249 | 59.9605 | 453.1043 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 | 454.029 | 448.1995 | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9249 | 59.9605 | 453.1043 | 59.9605 | 453.1043
T+50s | 43672.9249 | 59.9605 | 453.1043 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 | 454.029 | 448.1995 | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.9249 |  |  | 59.9605 | 453.1043
T+51s | 43672.925 | 59.9574 | 453.4373 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 | 454.029 | 448.1995 | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.925 | 59.9574 | 453.4373 | 59.9574 | 453.4373
T+52s | 43672.925 | 59.9574 | 453.4373 | 59.9508 | 454.2995 |  |  | 59.9508 |  | 454.2995 | 454.5212 | 448.1995 | 454.029 | 448.1995 | 0 | 0 | 0 | 59.964 |  |  |  |  | 43672.925 |  |  | 59.9574 | 453.4373
T+53s | 43672.925 | 59.9574 | 453.4163 | [9 empty] | 454.029 | 448.1995 | 0 | 0 |  | 59.964 |  |  |  |  | 43672.925 | 59.9574 | 453.4163 | 59.9574 | 453.4163
T+54s | 43672.925 | 59.9574 | 453.4163 | [9 empty] | 454.029 | 448.1995 | 0 | 0 |  | 59.964 |  |  |  |  | 43672.925 |  |  | 59.9574 | 453.4163
T+55s | 43672.925 | 59.9574 | 453.3942 | [9 empty] | 454.029 | 448.1995 | 0 | 0 |  | 59.964 |  |  |  |  | 43672.925 | 59.9574 | 453.3942 | 59.9574 | 453.3942
T+56s | 43672.925 | 59.9574 | 453.3942 | [9 empty] | 454.029 | 448.1995 | 0 | 0 |  | 59.964 |  |  |  |  | 43672.925 |  |  | 59.9574 | 453.3942
T+57s | 43672.925 | 59.9589 | 453.3721 | [9 empty] | 454.029 | 448.1995 | 0 | 0 |  | 59.964 |  |  |  |  | 43672.925 | 59.9589 | 453.3721 | 59.9589 | 453.3721
T+58s | 43672.925 | 59.9589 | 453.3721 | [9 empty] | 454.029 | 448.1995 | 0 | 0 |  | 59.964 |  |  |  |  | 43672.925 |  |  | 59.9589 | 453.3721
T+59s | 43672.925 | 59.959 | 453.35 | [9 empty] | 454.029 | 448.1995 | 0 | 0 |  | 59.964 |  |  |  |  | 43672.925 | 59.959 | 453.35 | 59.959 | 453.35
T+60s | 43672.9251 | 59.959 | 453.35 | [9 empty] | 454.029 | 448.1995 | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9251 |  |  | 59.959 | 453.35
T+61s | 43672.9251 | 59.959 | 453.3268 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9251 | 59.959 | 453.3268 | 59.959 | 453.3268
T+62s | 43672.9251 | 59.959 | 453.3268 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9251 |  |  | 59.959 | 453.3268
T+63s | 43672.9251 | 59.9591 | 452.8253 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9251 | 59.9591 | 452.8253 | 59.9591 | 452.8253
T+64s | 43672.9251 | 59.9591 | 452.8253 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9251 |  |  | 59.9591 | 452.8253
T+65s | 43672.9251 | 59.9592 | 452.8238 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9251 | 59.9592 | 452.8238 | 59.9592 | 452.8238
T+66s | 43672.9251 | 59.9592 | 452.8238 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9251 |  |  | 59.9592 | 452.8238
T+67s | 43672.9251 | 59.9584 | 453.4404 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9251 | 59.9584 | 453.4404 | 59.9584 | 453.4404
T+68s | 43672.9252 | 59.9584 | 453.4404 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9252 |  |  | 59.9584 | 453.4404
T+69s | 43672.9252 | 59.9576 | 453.4423 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9252 | 59.9576 | 453.4423 | 59.9576 | 453.4423
T+70s | 43672.9252 | 59.9576 | 453.4423 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9252 |  |  | 59.9576 | 453.4423
T+71s | 43672.9252 | 59.9585 | 453.0394 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9252 | 59.9585 | 453.0394 | 59.9585 | 453.0394
T+72s | 43672.9252 | 59.9585 | 453.0394 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9252 |  |  | 59.9585 | 453.0394
T+73s | 43672.9252 | 59.9595 | 453.039 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9252 | 59.9595 | 453.039 | 59.9595 | 453.039
T+74s | 43672.9252 | 59.9595 | 453.039 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9252 |  |  | 59.9595 | 453.039
T+75s | 43672.9252 | 59.9564 | 453.7148 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9252 | 59.9564 | 453.7148 | 59.9564 | 453.7148
T+76s | 43672.9252 | 59.9564 | 453.7148 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9252 |  |  | 59.9564 | 453.7148
T+77s | 43672.9253 | 59.9564 | 453.7185 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9253 | 59.9564 | 453.7185 | 59.9564 | 453.7185
T+78s | 43672.9253 | 59.9564 | 453.7185 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9253 |  |  | 59.9564 | 453.7185
T+79s | 43672.9253 | 59.9593 | 453.159 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9253 | 59.9593 | 453.159 | 59.9593 | 453.159
T+80s | 43672.9253 | 59.9593 | 453.159 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9253 |  |  | 59.9593 | 453.159
T+81s | 43672.9253 | 59.9594 | 453.1584 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9253 | 59.9594 | 453.1584 | 59.9594 | 453.1584
T+82s | 43672.9253 | 59.9594 | 453.1584 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9253 |  |  | 59.9594 | 453.1584
T+83s | 43672.9253 | 59.9596 | 453.1584 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9253 | 59.9596 | 453.1584 | 59.9596 | 453.1584
T+84s | 43672.9253 | 59.9596 | 453.1584 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9253 |  |  | 59.9596 | 453.1584
T+85s | 43672.9253 | 59.9598 | 452.4332 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9253 | 59.9598 | 452.4332 | 59.9598 | 452.4332
T+86s | 43672.9254 | 59.9598 | 452.4332 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9254 |  |  | 59.9598 | 452.4332
T+87s | 43672.9254 | 59.9599 | 452.6827 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9254 | 59.9599 | 452.6827 | 59.9599 | 452.6827
T+88s | 43672.9254 | 59.9599 | 452.6827 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9254 |  |  | 59.9599 | 452.6827
T+89s | 43672.9254 | 59.9601 | 452.6827 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9254 | 59.9601 | 452.6827 | 59.9601 | 452.6827
T+90s | 43672.9254 | 59.9601 | 452.6827 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9254 |  |  | 59.9601 | 452.6827
T+91s | 43672.9254 | 59.9603 | 452.9782 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9254 | 59.9603 | 452.9782 | 59.9603 | 452.9782
T+92s | 43672.9254 | 59.9603 | 452.9782 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9254 |  |  | 59.9603 | 452.9782
T+93s | 43672.9254 | 59.9604 | 452.9789 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9254 | 59.9604 | 452.9789 | 59.9604 | 452.9789
T+94s | 43672.9255 | 59.9604 | 452.9789 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9255 |  |  | 59.9604 | 452.9789
T+95s | 43672.9255 | 59.9606 | 452.9789 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9255 | 59.9606 | 452.9789 | 59.9606 | 452.9789
T+96s | 43672.9255 | 59.9606 | 452.9789 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9255 |  |  | 59.9606 | 452.9789
T+97s | 43672.9255 | 59.9608 | 452.7513 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9255 | 59.9608 | 452.7513 | 59.9608 | 452.7513
T+98s | 43672.9255 | 59.9608 | 452.7513 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9255 |  |  | 59.9608 | 452.7513
T+99s | 43672.9255 | 59.958 | 452.9529 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9255 | 59.958 | 452.9529 | 59.958 | 452.9529
T+100s | 43672.9255 | 59.958 | 452.9529 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9255 |  |  | 59.958 | 452.9529
T+101s | 43672.9255 | 59.958 | 452.9539 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9255 | 59.958 | 452.9539 | 59.958 | 452.9539
T+102s | 43672.9255 | 59.958 | 452.9539 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9255 |  |  | 59.958 | 452.9539
T+103s | 43672.9256 | 59.958 | 452.955 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9256 | 59.958 | 452.955 | 59.958 | 452.955
T+104s | 43672.9256 | 59.958 | 452.955 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9256 |  |  | 59.958 | 452.955
T+105s | 43672.9256 | 59.9551 | 453.7267 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9256 | 59.9551 | 453.7267 | 59.9551 | 453.7267
T+106s | 43672.9256 | 59.9551 | 453.7267 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9256 |  |  | 59.9551 | 453.7267
T+107s | 43672.9256 | 59.9574 | 454.0114 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9256 | 59.9574 | 454.0114 | 59.9574 | 454.0114
T+108s | 43672.9256 | 59.9574 | 454.0114 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9256 |  |  | 59.9574 | 454.0114
T+109s | 43672.9256 | 59.9578 | 454.0517 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9256 | 59.9578 | 454.0517 | 59.9578 | 454.0517
T+110s | 43672.9256 | 59.9578 | 454.0517 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9256 |  |  | 59.9578 | 454.0517
T+111s | 43672.9256 | 59.9582 | 454.0912 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9256 | 59.9582 | 454.0912 | 59.9582 | 454.0912
T+112s | 43672.9257 | 59.9582 | 454.0912 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9257 |  |  | 59.9582 | 454.0912
T+113s | 43672.9257 | 59.9585 | 454.1308 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9257 | 59.9585 | 454.1308 | 59.9585 | 454.1308
T+114s | 43672.9257 | 59.9585 | 454.1308 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9257 |  |  | 59.9585 | 454.1308
T+115s | 43672.9257 | 59.9579 | 454.7443 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9257 | 59.9579 | 454.7443 | 59.9579 | 454.7443
T+116s | 43672.9257 | 59.9579 | 454.7443 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9257 |  |  | 59.9579 | 454.7443
T+117s | 43672.9257 | 59.9572 | 454.7557 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9257 | 59.9572 | 454.7557 | 59.9572 | 454.7557
T+118s | 43672.9257 | 59.9572 | 454.7557 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9257 |  |  | 59.9572 | 454.7557
T+119s | 43672.9257 | 59.9585 | 454.7652 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9257 | 59.9585 | 454.7652 | 59.9585 | 454.7652
T+120s | 43672.9258 | 59.9585 | 454.7652 | [11 empty] | 0 | 0 |  | 59.964 |  |  |  |  | 43672.9258 |  |  | 59.9585 | 454.7652
[23 empty] | 43672.9258 | 59.9599 | 454.7747 | 59.9599 | 454.7747
[23 empty] | 43672.9258 |  |  | 59.9599 | 454.7747
[23 empty] | 43672.9258 | 59.9613 | 453.9813 | 59.9613 | 453.9813
[23 empty] | 43672.9258 |  |  | 59.9613 | 453.9813
[23 empty] | 43672.9258 | 59.9622 | 453.9789 | 59.9622 | 453.9789
[23 empty] | 43672.9258 |  |  | 59.9622 | 453.9789
[23 empty] | 43672.9258 | 59.9631 | 453.4534 | 59.9631 | 453.4534
[23 empty] | 43672.9258 |  |  | 59.9631 | 453.4534
[23 empty] | 43672.9259 | 59.9641 | 453.4526 | 59.9641 | 453.4526
[23 empty] | 43672.9259 |  |  | 59.9641 | 453.4526
[23 empty] | 43672.9259 | 59.965 | 453.2342 | 59.965 | 453.2342
[23 empty] | 43672.9259 |  |  | 59.965 | 453.2342
[23 empty] | 43672.9259 | 59.965 | 453.2303 | 59.965 | 453.2303
[23 empty] | 43672.9259 |  |  | 59.965 | 453.2303
[23 empty] | 43672.9259 | 59.965 | 453.227 | 59.965 | 453.227
[23 empty] | 43672.9259 |  |  | 59.965 | 453.227
[23 empty] | 43672.9259 | 59.9703 | 453.2236 | 59.9703 | 453.2236
[23 empty] | 43672.926 |  |  | 59.9703 | 453.2236
[23 empty] | 43672.926 | 59.9703 | 453.2203 | 59.9703 | 453.2203
[23 empty] | 43672.926 |  |  | 59.9703 | 453.2203
[23 empty] | 43672.926 | 59.9703 | 453.2169 | 59.9703 | 453.2169
[23 empty] | 43672.926 |  |  | 59.9703 | 453.2169
[23 empty] | 43672.926 | 59.973 | 453.2884 | 59.973 | 453.2884
[23 empty] | 43672.926 |  |  | 59.973 | 453.2884
[23 empty] | 43672.926 | 59.973 | 453.3601 | 59.973 | 453.3601
[23 empty] | 43672.9261 |  |  | 59.973 | 453.3601
[23 empty] | 43672.9261 | 59.9706 | 453.2917 | 59.9706 | 453.2917
[23 empty] | 43672.9261 |  |  | 59.9706 | 453.2917
[23 empty] | 43672.9261 | 59.9706 | 453.2226 | 59.9706 | 453.2226
[23 empty] | 43672.9261 |  |  | 59.9706 | 453.2226
[23 empty] | 43672.9261 | 59.9678 | 453.2844 | 59.9678 | 453.2844
[23 empty] | 43672.9261 |  |  | 59.9678 | 453.2844
[23 empty] | 43672.9261 | 59.9678 | 453.3469 | 59.9678 | 453.3469
[23 empty] | 43672.9261 |  |  | 59.9678 | 453.3469
[23 empty] | 43672.9262 | 59.9648 | 452.9274 | 59.9648 | 452.9274
[23 empty] | 43672.9262 |  |  | 59.9648 | 452.9274
[23 empty] | 43672.9262 | 59.965 | 453.3084 | 59.965 | 453.3084
[23 empty] | 43672.9262 |  |  | 59.965 | 453.3084
Calculate
Note on P2: Observe first change in frequency that identifies the beginning of the event. Edit the formula in this cell to reference that row number in the "Data" sheet that this occurs.

## Chart
Alignment Chart for Historian Data
-Users may use this chart to align their frequency and MW data to the t(0) of the event provided by NERC staff. |  |  | 2019-07-26 22:11
-Chart will not be available for manually entered data.
| OFFSET (s): | 0
This line should align with the interval immediately before the first frequency excursion.
Adjust offset of data here.