## 2020-1
Generator Catagory/Classification | Start | End | # Units | Unit-Years | NMC | NDC | Attempts | Actual | SH | RSH | # RSH | Pump Hr | SCH | AH | FOH | # FOH | POH | # POH | SEPO | # SEPO | MOH | # MOH | SEMO | # SEMO | UAH | PH | EFDH | ESDH | EFDHRS | EDOH | POF | MOF | ART | SR | NCF | NOF | SF | AF | EAF | FOR | EFOR | EFORd | SOF | FOF | UOF | EUOF | EUOR | WSF | WAF | WEAF | WFOR | WEFOR | WSOF | WFOF
FOSSIL All Fuel Types All Sizes | 2020 | 2020 | 799 | 801 | 340 | 339 | 31.63 | 31.37 | 4050.4 | 2658.74 | 13.08 | 0 | 0 | 6709.14 | 506.88 | 4.97 | 643.74 | 1.27 | 36.03 | 0.12 | 325 | 2.47 | 7.15 | 0.04 | 1518.8 | 8227.94 | 139.91 | 45.42 | 36.76 | 185.33 | 8.26 | 4.04 | 129.12 | 99.18 | 34.47 | 64.38 | 49.23 | 81.54 | 78.92 | 11.12 | 14.08 | 10.35 | 12.3 | 6.16 | 10.2 | 12.12 | 20.22 | 53.54 | 81.43 | 78.98 | 9.49 | 12.23 | 12.96 | 5.61
FOSSIL All Fuel Types 001-099 | 2020 | 2020 | 173 | 173 | 51 | 51 | 32.13 | 31.99 | 3247.33 | 2882.12 | 13.39 | 0 | 0 | 6129.45 | 604.44 | 4.06 | 485.87 | 1.05 | 36.71 | 0.08 | 367.16 | 1.69 | 0 | 0 | 1494.18 | 7623.63 | 127.99 | 46.68 | 26.46 | 174.67 | 6.85 | 4.82 | 101.51 | 99.56 | 27.45 | 63.85 | 42.6 | 80.4 | 77.18 | 15.69 | 18.89 | 12.57 | 11.67 | 7.93 | 12.74 | 14.54 | 26.1 | 42.99 | 80.58 | 77.51 | 15.41 | 18.87 | 11.59 | 7.83
FOSSIL All Fuel Types 100-199 | 2020 | 2020 | 143 | 143 | 138 | 137 | 88.24 | 88.13 | 3168.13 | 3299.44 | 16.64 | 0 | 0 | 6467.56 | 507.61 | 4.08 | 600.08 | 1.31 | 9.28 | 0.08 | 277.32 | 1.97 | 0.6 | 0.01 | 1394.9 | 7862.46 | 130.54 | 27.87 | 56.61 | 158.41 | 7.75 | 3.53 | 35.95 | 99.88 | 24.56 | 58.71 | 40.29 | 82.26 | 79.94 | 13.81 | 17.1 | 10.03 | 11.29 | 6.46 | 9.99 | 11.94 | 23.28 | 41.84 | 81.99 | 79.62 | 13.77 | 16.88 | 11.33 | 6.68
FOSSIL All Fuel Types 200-299 | 2020 | 2020 | 82 | 82 | 232 | 231 | 15.79 | 15.4 | 4863.89 | 2307.27 | 12.79 | 0 | 0 | 7171.16 | 363.85 | 5.72 | 599.03 | 1.16 | 33.7 | 0.13 | 284.47 | 3.33 | 6.59 | 0.09 | 1287.65 | 8458.81 | 138.85 | 43.24 | 40.41 | 182.09 | 7.48 | 3.44 | 315.84 | 97.53 | 35.24 | 61.71 | 57.5 | 84.78 | 82.28 | 6.96 | 9.54 | 7.97 | 10.92 | 4.3 | 7.74 | 9.69 | 14.73 | 57.11 | 84.85 | 82.38 | 6.93 | 9.49 | 10.9 | 4.25
FOSSIL All Fuel Types 300-399 | 2020 | 2020 | 80 | 81 | 337 | 336 | 20.81 | 20.27 | 3613.3 | 3173.41 | 19.36 | 0 | 0 | 6786.71 | 446.39 | 5.31 | 860.22 | 1.49 | 51.67 | 0.15 | 273.38 | 2.9 | 20.53 | 0.07 | 1652.19 | 8438.9 | 150.74 | 45.42 | 37.83 | 196.16 | 10.81 | 3.48 | 178.26 | 97.41 | 24.15 | 56.34 | 42.82 | 80.42 | 77.97 | 11 | 14.57 | 10.68 | 14.29 | 5.29 | 8.77 | 10.85 | 20.72 | 42.87 | 80.32 | 78 | 10.91 | 14.45 | 14.43 | 5.25
FOSSIL All Fuel Types 400-599 | 2020 | 2020 | 158 | 158 | 479 | 478 | 15.02 | 14.75 | 4619.98 | 2272.9 | 11.5 | 0 | 0 | 6892.88 | 567.55 | 6 | 676.98 | 1.49 | 48.41 | 0.13 | 340.37 | 2.85 | 2.91 | 0.03 | 1636.23 | 8529.11 | 161.16 | 57.07 | 43.72 | 218.23 | 8.5 | 4.02 | 313.22 | 98.2 | 34.41 | 63.2 | 54.17 | 80.82 | 78.09 | 10.94 | 13.93 | 11.51 | 12.53 | 6.65 | 10.68 | 12.71 | 19.44 | 54.46 | 81.18 | 78.49 | 10.25 | 13.17 | 12.6 | 6.22
FOSSIL All Fuel Types 600-799 | 2020 | 2020 | 106 | 106 | 662 | 660 | 10.62 | 10.31 | 5041 | 2073.26 | 7.54 | 0 | 0 | 7114.26 | 402.89 | 5.43 | 771.69 | 1.2 | 39.76 | 0.14 | 306.03 | 2.62 | 28.12 | 0.1 | 1548.48 | 8662.74 | 151.15 | 51.28 | 24.19 | 202.43 | 9.37 | 3.86 | 488.94 | 97.08 | 40.58 | 69.37 | 58.19 | 82.12 | 79.51 | 7.4 | 10.13 | 8.7 | 13.22 | 4.65 | 8.51 | 10.44 | 15.58 | 58.5 | 81.98 | 79.34 | 7.4 | 10.18 | 13.34 | 4.68
FOSSIL All Fuel Types 800-999 | 2020 | 2020 | 49 | 49 | 829 | 829 | 12.43 | 12.18 | 4817.33 | 2322.72 | 9.98 | 0 | 0 | 7140.05 | 527.58 | 4.65 | 655 | 1.18 | 48.32 | 0.24 | 308.22 | 2.55 | 0 | 0 | 1539.11 | 8679.16 | 108.22 | 47.09 | 17.22 | 155.3 | 8.1 | 3.55 | 395.51 | 97.99 | 35.68 | 63.93 | 55.5 | 82.27 | 80.45 | 9.87 | 11.86 | 9.89 | 11.65 | 6.08 | 9.63 | 11.38 | 17.41 | 55.81 | 82.51 | 80.72 | 9.58 | 11.55 | 11.57 | 5.92
FOSSIL All Fuel Types 1000 Plus | 2020 | 2020 | 8 | 8 | 1279 | 1279 | 8.38 | 8 | 4705.39 | 1567.89 | 6.5 | 0 | 0 | 6273.28 | 534.24 | 4.88 | 699.51 | 0.88 | 0 | 0 | 1276.97 | 5.63 | 0 | 0 | 2510.72 | 8784 | 106.46 | 42.29 | 7.39 | 148.75 | 7.96 | 14.54 | 588.17 | 95.47 | 37.31 | 67.47 | 53.57 | 71.42 | 69.69 | 10.2 | 12.21 | 10.77 | 22.5 | 6.08 | 20.62 | 22.3 | 30 | 55.3 | 71.28 | 69.51 | 10.18 | 12.18 | 22.45 | 6.27
FOSSIL Coal Primary All Sizes | 2020 | 2020 | 443 | 440 | 426 | 425 | 28.25 | 28.01 | 4847.5 | 1868.48 | 6.48 | 0 | 0 | 6715.97 | 502.67 | 5.43 | 590.65 | 1.06 | 32.23 | 0.12 | 283.74 | 2.51 | 4.77 | 0.05 | 1414.06 | 8130.04 | 115.7 | 43.87 | 14.33 | 159.57 | 7.66 | 3.55 | 173.06 | 99.15 | 41.37 | 67.1 | 59.62 | 82.61 | 80.31 | 9.4 | 11.53 | 9.4 | 11.21 | 6.18 | 9.73 | 11.4 | 16.38 | 61.66 | 82.2 | 79.92 | 8.45 | 10.59 | 12.1 | 5.69
FOSSIL Coal Primary 001-099 | 2020 | 2020 | 49 | 46.08 | 56 | 56 | 7.2 | 7.01 | 3268.61 | 2546.79 | 4.67 | 0 | 0 | 5815.4 | 632.94 | 4.36 | 504.32 | 0.85 | 14.76 | 0.07 | 228.87 | 1.48 | 0 | 0 | 1380.89 | 7196.29 | 34.89 | 15.85 | 0 | 50.73 | 7.21 | 3.18 | 466.28 | 97.36 | 33.42 | 72.58 | 45.42 | 80.81 | 79.43 | 16.22 | 17.12 | 14.21 | 10.39 | 8.8 | 11.98 | 12.59 | 21.94 | 46.05 | 82.01 | 80.52 | 14.89 | 15.81 | 9.94 | 8.06
FOSSIL Coal Primary 100-199 | 2020 | 2020 | 61 | 60.17 | 148 | 147 | 140.38 | 140.28 | 3915.24 | 1729.92 | 6.15 | 0 | 0 | 5645.17 | 556.84 | 4.4 | 380.64 | 1.1 | 12.51 | 0.12 | 167.53 | 1.73 | 1.42 | 0.03 | 1118.94 | 6764.11 | 91.82 | 17.31 | 11.28 | 109.13 | 5.81 | 2.5 | 27.91 | 99.93 | 39.49 | 67.47 | 57.88 | 83.46 | 81.26 | 12.45 | 14.47 | 10.69 | 8.31 | 8.23 | 10.73 | 12.25 | 17.79 | 58.52 | 82.97 | 80.72 | 12.81 | 14.83 | 8.44 | 8.6
FOSSIL Coal Primary 200-299 | 2020 | 2020 | 53 | 53 | 232 | 231 | 11.21 | 10.87 | 5084.38 | 1946.44 | 6.19 | 0 | 0 | 7030.82 | 402.38 | 6.32 | 512.37 | 1.08 | 29.17 | 0.13 | 295.93 | 3.25 | 10.2 | 0.13 | 1250.05 | 8280.87 | 122.07 | 44.09 | 31.31 | 166.16 | 6.54 | 3.7 | 467.74 | 96.97 | 38.34 | 63.28 | 61.4 | 84.9 | 82.43 | 7.33 | 9.5 | 8.33 | 10.24 | 4.86 | 8.56 | 10.29 | 14.63 | 60.58 | 84.96 | 82.46 | 7.41 | 9.62 | 10.2 | 4.85
FOSSIL Coal Primary 300-399 | 2020 | 2020 | 43 | 43.42 | 333 | 332 | 13.96 | 13.59 | 4411.09 | 2537.66 | 10.64 | 0 | 0 | 6948.75 | 439.64 | 5.8 | 694.99 | 0.99 | 37.28 | 0.12 | 255.35 | 2.69 | 2.14 | 0.09 | 1429.41 | 8378.15 | 201.07 | 63.03 | 43.92 | 264.1 | 8.74 | 3.07 | 324.58 | 97.35 | 34.08 | 64.49 | 52.65 | 82.94 | 79.6 | 9.06 | 13.09 | 10.55 | 11.81 | 5.25 | 8.32 | 11.16 | 17.98 | 52.84 | 82.84 | 79.64 | 9.02 | 13.03 | 11.92 | 5.24
FOSSIL Coal Primary 400-599 | 2020 | 2020 | 104 | 103.67 | 483 | 482 | 11.15 | 10.94 | 5450.52 | 1504.82 | 6.28 | 0 | 0 | 6955.34 | 561.24 | 6.03 | 616.04 | 1.12 | 55.3 | 0.14 | 295.28 | 2.56 | 3.99 | 0.03 | 1531.85 | 8487.19 | 117.34 | 56.08 | 8.42 | 173.42 | 7.91 | 3.53 | 498.22 | 98.12 | 42.58 | 66.03 | 64.22 | 81.95 | 79.68 | 9.34 | 11.27 | 10.03 | 11.44 | 6.61 | 10.14 | 11.72 | 15.73 | 64.48 | 82.25 | 80 | 8.9 | 10.83 | 11.45 | 6.3
FOSSIL Coal Primary 600-799 | 2020 | 2020 | 90 | 89.67 | 663 | 661 | 10.22 | 9.95 | 5605.7 | 1634.86 | 6.43 | 0 | 0 | 7240.56 | 389.47 | 5.43 | 683.5 | 1.05 | 25.65 | 0.1 | 290.69 | 2.67 | 10.79 | 0.07 | 1400.09 | 8640.65 | 137.57 | 54.37 | 7.11 | 191.94 | 8.21 | 3.49 | 563.39 | 97.36 | 45.68 | 70.5 | 64.88 | 83.8 | 81.27 | 6.5 | 8.78 | 7.79 | 11.7 | 4.51 | 8 | 9.8 | 13.43 | 64.79 | 83.64 | 81.1 | 6.57 | 8.86 | 11.8 | 4.56
FOSSIL Coal Primary 800-999 | 2020 | 2020 | 36 | 36 | 835 | 834 | 8.75 | 8.47 | 5020.94 | 1971.69 | 5.53 | 0 | 0 | 6992.63 | 565.38 | 4.94 | 698.76 | 1.22 | 43.05 | 0.22 | 341.48 | 2.69 | 0 | 0 | 1648.68 | 8641.31 | 89.87 | 40.28 | 13.78 | 130.15 | 8.58 | 3.95 | 592.79 | 96.8 | 37.09 | 63.61 | 58.1 | 80.92 | 79.41 | 10.12 | 11.7 | 10.25 | 12.54 | 6.54 | 10.49 | 11.99 | 17.44 | 58.3 | 81.34 | 79.85 | 9.7 | 11.26 | 12.4 | 6.26
FOSSIL Coal Primary 1000 Plus | 2020 | 2020 | 7 | 7 | 1321 | 1321 | 9 | 8.57 | 5321.85 | 861.09 | 5.86 | 0 | 0 | 6182.94 | 610.56 | 5.57 | 799.44 | 1 | 0 | 0 | 1191.06 | 5.86 | 0 | 0 | 2601.06 | 8784 | 117.25 | 45.57 | 4.69 | 162.82 | 9.1 | 13.56 | 620.99 | 95.22 | 41.13 | 67.73 | 60.59 | 70.39 | 68.5 | 10.29 | 12.26 | 11.3 | 22.66 | 6.95 | 20.51 | 22.35 | 27.54 | 60.72 | 70.51 | 68.61 | 10.25 | 12.22 | 22.56 | 6.93
FOSSIL Oil Primary All Sizes | 2020 | 2020 | 45 | 43.17 | 294 | 293 | 16.31 | 16.24 | 1734.14 | 4235.43 | 18.6 | 0 | 0 | 5969.58 | 743.8 | 2.08 | 589.92 | 1 | 20.42 | 0.09 | 400.04 | 1.55 | 26.13 | 0.05 | 1780.32 | 7749.89 | 194.39 | 5.8 | 72.14 | 200.19 | 7.88 | 5.5 | 106.78 | 99.57 | 4.42 | 40.9 | 22.38 | 77.03 | 74.35 | 30.02 | 36.79 | 17.88 | 13.37 | 9.6 | 15.1 | 17.67 | 46 | 10.81 | 80.85 | 79.62 | 26.93 | 32.65 | 15.17 | 3.98
FOSSIL Oil Primary 001-099 | 2020 | 2020 | 15 | 15 | 65 | 65 | 36.67 | 36.53 | 3101.47 | 1136.63 | 35.33 | 0 | 0 | 4238.1 | 1285.54 | 2.4 | 374.09 | 0.07 | 0 | 0 | 543.87 | 1.2 | 0 | 0 | 2203.5 | 6441.6 | 454.44 | 11.47 | 164.85 | 465.91 | 5.81 | 8.44 | 84.9 | 99.62 | 28.47 | 49.3 | 48.15 | 65.79 | 58.56 | 29.3 | 38.23 | 31.75 | 14.25 | 19.96 | 28.4 | 35.62 | 45.03 | 57.75 | 71.43 | 63.84 | 17.84 | 27.56 | 16.03 | 12.54
FOSSIL Oil Primary 100-199 | 2020 | 2020 | 8 | 6.42 | 122 | 122 | 3.74 | 3.74 | 2268.61 | 4958.74 | 6.55 | 0 | 0 | 7227.35 | 970.64 | 1.4 | 182.4 | 0.62 | 0 | 0 | 289.52 | 1.56 | 0 | 0 | 1442.57 | 8669.92 | 128.45 | 7.19 | 30.16 | 135.63 | 2.1 | 3.34 | 606.58 | 100 | 17.67 | 58.74 | 26.17 | 83.36 | 81.8 | 29.96 | 33.62 | 21.07 | 5.44 | 11.2 | 14.53 | 16.09 | 39.2 | 30.09 | 83.54 | 81.69 | 26.18 | 30.15 | 5.8 | 10.67
FOSSIL Oil Primary 200-299 | 2020 | 2020 | **** | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [10 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: POF to FOR
FOSSIL Oil Primary 300-399 | 2020 | 2020 | 9 | 9 | 364 | 364 | 6.44 | 6.44 | 1377.27 | 4654.28 | 11.44 | 0 | 0 | 6031.55 | 522.23 | 2.22 | 975.53 | 1.56 | 0 | 0 | 278.68 | 1.89 | 0 | 0 | 1776.45 | 7808 | 33.39 | 0 | 1.98 | 33.39 | 12.49 | 3.57 | 213.86 | 100 | 5.07 | 28.09 | 17.64 | 77.25 | 76.82 | 27.49 | 29.22 | 17.62 | 16.06 | 6.69 | 10.26 | 10.69 | 38.27 | 18.05 | 77.55 | 77.12 | 25.71 | 27.44 | 16.2 | 6.25
FOSSIL Oil Primary 400-599 | 2020 | 2020 | 6 | 6 | 462 | 462 | 4.33 | 4.33 | 54.46 | 7441.36 | 9.17 | 0 | 0 | 7495.82 | 217.01 | 1.17 | 936.39 | 2 | 0 | 0 | 134.79 | 1.67 | 0 | 0 | 1288.19 | 8784 | 15.26 | 2.14 | 14.55 | 17.4 | 10.66 | 1.53 | 12.58 | 100 | 0.05 | 8.19 | 0.62 | 85.33 | 85.12 | 79.94 | 81.21 | 21.94 | 12.19 | 2.47 | 4.01 | 4.18 | 87.23 | 0.59 | 84.85 | 84.64 | 83.06 | 83.93 | 12.26 | 2.89
FOSSIL Oil Primary 600-799 | 2020 | 2020 | 4 | 3.75 | 600 | 594 | 8.8 | 8.8 | 146.21 | 7009.85 | 12.53 | 0 | 0 | 7156.05 | 152.71 | 3.73 | 642.61 | 1.87 | 32 | 0.27 | 503.29 | 1.07 | 300.81 | 0.53 | 1631.41 | 8787.47 | 1.51 | 0 | 0 | 1.51 | 7.68 | 9.15 | 16.61 | 100 | 0.63 | 36.99 | 1.66 | 81.43 | 80.74 | 51.09 | 51.59 | 23.82 | 16.83 | 1.74 | 10.89 | 10.91 | 86.88 | 1.69 | 81.21 | 80.48 | 51.07 | 51.58 | 17.02 | 1.77
FOSSIL Oil Primary 800-999 | 2020 | 2020 | **** | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [10 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: POF to FOR
FOSSIL Gas Primary All Sizes | 2020 | 2020 | 253 | 246.92 | 239 | 239 | 38.1 | 37.77 | 2386.28 | 4195.71 | 23.66 | 0 | 0 | 6581.99 | 527.18 | 4.25 | 769.2 | 1.6 | 49.05 | 0.12 | 423.13 | 2.64 | 10.13 | 0.02 | 1778.7 | 8360.68 | 157.3 | 34.08 | 79.86 | 191.37 | 9.79 | 5.18 | 63.18 | 99.13 | 14.67 | 45.48 | 28.54 | 78.73 | 76.2 | 18.09 | 22.87 | 12.45 | 14.97 | 6.31 | 11.49 | 13.57 | 32.96 | 32.26 | 77.66 | 74.77 | 16.18 | 21.4 | 16.11 | 6.23
FOSSIL Gas Primary 001-099 | 2020 | 2020 | 68 | 65.67 | 52 | 52 | 37.13 | 37.04 | 1234.04 | 4596.12 | 15.3 | 0 | 0 | 5830.16 | 608.96 | 2.25 | 463.45 | 1.02 | 68.29 | 0.06 | 532.63 | 1.48 | 0 | 0 | 1673.33 | 7503.49 | 74.45 | 5.09 | 31.83 | 79.54 | 7.09 | 7.1 | 33.32 | 99.76 | 10.42 | 51.41 | 16.45 | 77.7 | 75.82 | 33.04 | 36.45 | 13.34 | 14.18 | 8.12 | 15.21 | 16.26 | 50.62 | 20.26 | 78.1 | 76.03 | 29.82 | 33.47 | 13.29 | 8.61
FOSSIL Gas Primary 100-199 | 2020 | 2020 | 75 | 73.08 | 130 | 130 | 55.92 | 55.79 | 2497.99 | 4507.65 | 26.08 | 0 | 0 | 7005.64 | 449.47 | 4.17 | 815.83 | 1.57 | 7.87 | 0.07 | 374.99 | 2.22 | 0 | 0 | 1648.15 | 8653.79 | 165.28 | 35.12 | 98.82 | 200.4 | 9.52 | 4.33 | 44.77 | 99.77 | 13.76 | 46.63 | 28.87 | 80.95 | 78.59 | 15.25 | 20.18 | 10.31 | 13.85 | 5.19 | 9.53 | 11.81 | 29.54 | 29.5 | 80.75 | 78.29 | 15.32 | 19.99 | 13.92 | 5.34
FOSSIL Gas Primary 200-299 | 2020 | 2020 | 23 | 23 | 234 | 234 | 25.83 | 25.22 | 3811.78 | 3593.26 | 27.39 | 0 | 0 | 7405.04 | 298.9 | 4.43 | 767.79 | 1.26 | 34.17 | 0.13 | 278.1 | 3.61 | 0 | 0 | 1378.96 | 8784 | 172.02 | 41.74 | 62.01 | 213.76 | 9.13 | 3.17 | 151.14 | 97.64 | 22.54 | 51.25 | 43.39 | 84.3 | 81.82 | 7.27 | 11.29 | 7.88 | 12.3 | 3.4 | 6.57 | 9 | 17.66 | 43.98 | 84.41 | 82.09 | 6.94 | 10.7 | 12.3 | 3.28
FOSSIL Gas Primary 300-399 | 2020 | 2020 | 28 | 27.25 | 337 | 337 | 29.39 | 28.48 | 2991.26 | 3765.4 | 29.58 | 0 | 0 | 6756.66 | 436.79 | 5.58 | 1098.33 | 2.24 | 94.19 | 0.26 | 286.21 | 3.3 | 57.62 | 0.07 | 1973.14 | 8729.8 | 116.63 | 34.58 | 41.82 | 151.22 | 13.66 | 3.94 | 105.03 | 96.9 | 14.77 | 42.24 | 34.26 | 77.4 | 75.57 | 12.74 | 15.95 | 10.65 | 17.6 | 5 | 8.94 | 10.45 | 23.86 | 34.96 | 77.31 | 75.62 | 12.53 | 15.63 | 17.68 | 5.01
FOSSIL Gas Primary 400-599 | 2020 | 2020 | 43 | 42.08 | 479 | 479 | 25.62 | 25.21 | 2823.28 | 3708.04 | 25.28 | 0 | 0 | 6531.32 | 661 | 6.15 | 814.6 | 2.33 | 45.28 | 0.14 | 504.58 | 3.97 | 1.09 | 0.02 | 2026.56 | 8557.88 | 266.76 | 72.43 | 141.34 | 339.18 | 10.05 | 5.91 | 111.99 | 98.4 | 14.85 | 44.61 | 32.99 | 76.32 | 72.3 | 18.97 | 25.59 | 16.67 | 15.96 | 7.72 | 13.63 | 16.8 | 34.76 | 33.29 | 77.12 | 73.16 | 16.86 | 23.37 | 16.13 | 6.75
FOSSIL Gas Primary 600-799 | 2020 | 2020 | 10 | 9.83 | 681 | 681 | 15.36 | 14.44 | 2397.51 | 3583.36 | 15.97 | 0 | 0 | 5980.87 | 603.7 | 6.2 | 1518.35 | 2.03 | 182.49 | 0.51 | 415.9 | 3.05 | 90.01 | 0.31 | 2810.46 | 8791.32 | 322.32 | 53.65 | 189.17 | 375.97 | 19.35 | 5.75 | 166.03 | 94.01 | 15.43 | 52.02 | 27.27 | 68.03 | 63.75 | 20.12 | 29.03 | 19.7 | 25.1 | 6.87 | 12.62 | 16.29 | 38.74 | 29.67 | 68.42 | 64.04 | 18.06 | 27.26 | 25.04 | 6.54
FOSSIL Gas Primary 800-999 | 2020 | 2020 | 6 | 6 | 795 | 795 | 43.17 | 43 | 2340.56 | 4701.66 | 45.83 | 0 | 0 | 7042.22 | 800.11 | 3.83 | 512.13 | 0.67 | 0 | 0 | 429.54 | 3.67 | 0 | 0 | 1741.78 | 8784 | 56.86 | 5.84 | 5.27 | 62.7 | 5.83 | 4.89 | 54.43 | 99.61 | 8.3 | 31.6 | 26.65 | 80.17 | 79.46 | 25.48 | 27.24 | 13.57 | 10.72 | 9.11 | 14 | 14.71 | 36.04 | 26.27 | 79.57 | 78.89 | 26.66 | 28.33 | 10.88 | 9.55
FOSSIL Lignite Primary All Sizes | 2020 | 2020 | 18 | 17.08 | 506 | 505 | 11.53 | 11.36 | 7278.55 | 723.9 | 4.8 | 0 | 0 | 8002.44 | 353.94 | 6.38 | 265.69 | 0.94 | 3.87 | 0.12 | 158.7 | 1.7 | 0 | 0 | 782.2 | 8784.64 | 274.5 | 74.88 | 3.86 | 349.38 | 3.07 | 1.81 | 640.72 | 98.53 | 62.25 | 74.94 | 82.86 | 91.1 | 86.03 | 4.64 | 8.23 | 7.72 | 4.88 | 4.03 | 5.84 | 9.48 | 10.69 | 83.06 | 91.59 | 87.28 | 3.93 | 7.58 | 5.01 | 3.4
FOSSIL Oil/Gas Primary 001-099 | 2020 | 2020 | 83 | 80.67 | 55 | 54 | 37.04 | 36.94 | 1581.29 | 3952.82 | 19.03 | 0 | 0 | 5534.12 | 734.77 | 2.28 | 446.83 | 0.84 | 55.59 | 0.05 | 534.72 | 1.43 | 0 | 0 | 1771.92 | 7306.03 | 145.11 | 6.28 | 56.57 | 151.38 | 6.88 | 7.32 | 42.81 | 99.73 | 14.09 | 50.52 | 21.64 | 75.75 | 72.99 | 31.72 | 37.08 | 16.17 | 14.2 | 10.06 | 17.38 | 19.44 | 48.8 | 27.89 | 76.74 | 73.55 | 25.23 | 31.19 | 13.85 | 9.41
FOSSIL Oil/Gas Primary 100-199 | 2020 | 2020 | 82 | 79.5 | 129 | 129 | 51.71 | 51.58 | 2479.47 | 4544.06 | 24.5 | 0 | 0 | 7023.54 | 491.54 | 3.95 | 764.7 | 1.5 | 7.23 | 0.06 | 368.09 | 2.16 | 0 | 0 | 1631.56 | 8655.09 | 162.3 | 32.87 | 93.28 | 195.17 | 8.92 | 4.25 | 48.07 | 99.75 | 14.05 | 47.57 | 28.65 | 81.15 | 78.85 | 16.54 | 21.34 | 10.85 | 13.17 | 5.68 | 9.93 | 12.15 | 30.34 | 29.54 | 80.96 | 78.55 | 16.28 | 20.87 | 13.3 | 5.74
FOSSIL Oil/Gas Primary 200-299 | 2020 | 2020 | 23 | 23 | 234 | 234 | 25.83 | 25.22 | 3811.78 | 3593.26 | 27.39 | 0 | 0 | 7405.04 | 298.9 | 4.43 | 767.79 | 1.26 | 34.17 | 0.13 | 278.1 | 3.61 | 0 | 0 | 1378.96 | 8784 | 172.02 | 41.74 | 62.01 | 213.76 | 9.13 | 3.17 | 151.14 | 97.64 | 22.54 | 51.25 | 43.39 | 84.3 | 81.82 | 7.27 | 11.29 | 7.88 | 12.3 | 3.4 | 6.57 | 9 | 17.66 | 43.98 | 84.41 | 82.09 | 6.94 | 10.7 | 12.3 | 3.28
FOSSIL Oil/Gas Primary 300-399 | 2020 | 2020 | 37 | 36.25 | 344 | 344 | 23.7 | 23.01 | 2590.55 | 3986.09 | 25.08 | 0 | 0 | 6576.63 | 458 | 4.74 | 1067.84 | 2.07 | 70.81 | 0.19 | 284.34 | 2.95 | 43.31 | 0.06 | 1924.31 | 8500.94 | 95.96 | 26 | 31.93 | 121.96 | 13.39 | 3.85 | 112.58 | 97.09 | 12.43 | 40.25 | 30.47 | 77.36 | 75.85 | 15.02 | 17.98 | 11.58 | 17.25 | 5.39 | 9.24 | 10.5 | 26.14 | 30.89 | 77.37 | 75.98 | 14.66 | 17.52 | 17.33 | 5.31
FOSSIL Oil/Gas Primary 400-599 | 2020 | 2020 | 49 | 48.08 | 477 | 477 | 22.96 | 22.61 | 2477.78 | 4173.89 | 23.27 | 0 | 0 | 6651.67 | 605.6 | 5.53 | 829.8 | 2.29 | 39.63 | 0.12 | 458.43 | 3.68 | 0.95 | 0.02 | 1934.42 | 8586.09 | 235.37 | 63.66 | 125.51 | 299.03 | 10.13 | 5.35 | 109.59 | 98.48 | 13.02 | 44.52 | 28.86 | 77.47 | 73.94 | 19.64 | 26.21 | 16.16 | 15.48 | 7.05 | 12.4 | 15.19 | 35.51 | 29.24 | 78.08 | 74.58 | 17.66 | 24.11 | 15.65 | 6.27
FOSSIL Oil/Gas Primary 600-799 | 2020 | 2020 | 14 | 13.58 | 659 | 657 | 13.55 | 12.88 | 1775.98 | 4529.32 | 15.02 | 0 | 0 | 6305.3 | 479.19 | 5.52 | 1276.58 | 1.99 | 140.95 | 0.44 | 440.03 | 2.5 | 148.21 | 0.37 | 2484.95 | 8790.26 | 233.76 | 38.84 | 136.95 | 272.59 | 16.13 | 6.69 | 137.89 | 95.06 | 11.71 | 51.74 | 20.2 | 71.73 | 68.44 | 21.25 | 29.8 | 18.39 | 22.82 | 5.45 | 12.14 | 14.8 | 43.66 | 22.64 | 71.63 | 68.17 | 19.09 | 27.98 | 23.03 | 5.34
FOSSIL Oil/Gas Primary 800-999 | 2020 | 2020 | 8 | 8 | 801 | 800 | 33.5 | 33.25 | 1770.1 | 5354.07 | 36.25 | 0 | 0 | 7124.18 | 602.72 | 3.38 | 618.49 | 1.13 | 95.19 | 0.38 | 343.43 | 3.25 | 0 | 0 | 1659.82 | 8784 | 82.88 | 4.38 | 43.51 | 87.26 | 8.12 | 3.91 | 53.24 | 99.25 | 6.22 | 31.53 | 20.15 | 81.1 | 80.01 | 25.4 | 28.37 | 12.67 | 12.03 | 6.86 | 10.77 | 11.76 | 37.34 | 19.71 | 80.69 | 79.61 | 26.57 | 29.47 | 12.18 | 7.13
FOSSIL Oil/Gas Primary All Sizes | 2020 | 2020 | 297 | 290.08 | 248 | 247 | 34.86 | 34.57 | 2289.23 | 4201.62 | 22.91 | 0 | 0 | 6490.86 | 559.41 | 3.93 | 742.53 | 1.51 | 44.79 | 0.12 | 419.7 | 2.48 | 12.51 | 0.03 | 1778.94 | 8269.79 | 162.82 | 29.87 | 78.71 | 192.69 | 9.52 | 5.23 | 66.22 | 99.17 | 12.91 | 45.18 | 27.68 | 78.49 | 75.94 | 19.64 | 24.67 | 13.19 | 14.75 | 6.76 | 11.99 | 14.14 | 34.67 | 28.57 | 78.21 | 75.61 | 16.97 | 22.24 | 15.95 | 5.84
NUCLEAR All Types All Sizes | 2020 | 2020 | 78 | 78 | 1015 | 1011 | 1.5 | 1.45 | 8011.46 | 0.53 | 0.01 | 0 | 0 | 8011.99 | 150.22 | 0.86 | 493.12 | 0.92 | 12.1 | 0.06 | 22.4 | 0.13 | 0 | 0 | 677.83 | 8689.82 | 40.65 | 81.02 | 0 | 121.67 | 5.81 | 0.26 | 5525.14 | 96.67 | 91.23 | 99.16 | 92.19 | 92.2 | 90.41 | 1.84 | 2.34 | 2.34 | 6.07 | 1.73 | 1.99 | 2.8 | 2.98 | 92 | 92.01 | 90.25 | 1.91 | 2.41 | 6.2 | 1.79
NUCLEAR All Types 400-799 | 2020 | 2020 | 10 | 10 | 620 | 614 | 0.7 | 0.7 | 7904.05 | 0 | 0 | 0 | 0 | 7904.05 | 209.28 | 0.5 | 463.87 | 0.8 | 0 | 0 | 60.3 | 0.1 | 0 | 0 | 733.45 | 8637.5 | 44.76 | 80.45 | 0 | 125.21 | 5.37 | 0.7 | 11291.5 | 100 | 89.79 | 98.22 | 91.51 | 91.51 | 89.14 | 2.58 | 3.13 | 3.13 | 6.07 | 2.42 | 3.12 | 3.74 | 3.95 | 91.42 | 91.42 | 89.1 | 2.57 | 3.12 | 6.17 | 2.41
NUCLEAR All Types 800-999 | 2020 | 2020 | 26 | 26 | 893 | 890 | 1.62 | 1.54 | 8199.87 | 0 | 0 | 0 | 0 | 8199.87 | 99.42 | 0.92 | 451.31 | 0.85 | 4.16 | 0.08 | 29.23 | 0.19 | 0 | 0 | 584.13 | 8784 | 43.58 | 83.5 | 0 | 127.08 | 5.19 | 0.33 | 5324.59 | 95.06 | 93.1 | 99.71 | 93.35 | 93.35 | 91.68 | 1.2 | 1.72 | 1.72 | 5.52 | 1.13 | 1.46 | 2.33 | 2.46 | 93.38 | 93.38 | 91.72 | 1.22 | 1.75 | 5.47 | 1.15
NUCLEAR All Types 1000 Plus | 2020 | 2020 | 42 | 42 | 1185 | 1180 | 1.62 | 1.57 | 7920.4 | 0.98 | 0.02 | 0 | 0 | 7921.39 | 167.6 | 0.9 | 525.96 | 1 | 19.89 | 0.07 | 9.14 | 0.1 | 0 | 0 | 722.59 | 8643.98 | 37.87 | 79.62 | 0 | 117.49 | 6.31 | 0.11 | 5044.84 | 96.91 | 90.52 | 99.01 | 91.63 | 91.64 | 89.92 | 2.07 | 2.54 | 2.54 | 6.42 | 1.94 | 2.04 | 2.87 | 3.07 | 91.43 | 91.44 | 89.69 | 2.16 | 2.64 | 6.54 | 2.02
NUCLEAR PWR All Sizes | 2020 | 2020 | 46 | 46 | 1042 | 1037 | 1.61 | 1.54 | 7955.8 | 0 | 0 | 0 | 0 | 7955.8 | 136.93 | 0.91 | 538.67 | 0.96 | 19.95 | 0.09 | 4.8 | 0.04 | 0 | 0 | 700.35 | 8656.15 | 28.67 | 48.89 | 0 | 77.56 | 6.45 | 0.06 | 5166.1 | 95.65 | 91.49 | 99.73 | 91.91 | 91.91 | 90.59 | 1.69 | 2.05 | 2.05 | 6.51 | 1.58 | 1.64 | 2.12 | 2.27 | 91.73 | 91.73 | 90.44 | 1.8 | 2.15 | 6.59 | 1.68
NUCLEAR PWR 400-799 | 2020 | 2020 | 4 | 4 | 608 | 601 | 1 | 1 | 8111.17 | 0 | 0 | 0 | 0 | 8111.17 | 28.41 | 0.5 | 644.42 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 672.83 | 8784 | 8.45 | 95.83 | 0 | 104.27 | 7.34 | 0 | 8111.17 | 100 | 91.52 | 99.33 | 92.34 | 92.34 | 90.05 | 0.35 | 0.45 | 0.45 | 7.34 | 0.32 | 0.32 | 0.49 | 0.53 | 92.14 | 92.14 | 89.94 | 0.33 | 0.42 | 7.56 | 0.31
NUCLEAR PWR 800-999 | 2020 | 2020 | 14 | 14 | 898 | 897 | 1.71 | 1.57 | 8159.97 | 0 | 0 | 0 | 0 | 8159.97 | 93.05 | 0.86 | 523.39 | 1 | 5.87 | 0.07 | 1.72 | 0.07 | 0 | 0 | 624.03 | 8784 | 43.78 | 42.65 | 0 | 86.44 | 6.03 | 0.02 | 5197.43 | 91.81 | 93.16 | 100.3 | 92.9 | 92.9 | 91.8 | 1.13 | 1.66 | 1.66 | 6.04 | 1.06 | 1.08 | 1.82 | 1.94 | 92.88 | 92.88 | 91.77 | 1.13 | 1.66 | 6.06 | 1.06
NUCLEAR PWR 1000 Plus | 2020 | 2020 | 28 | 28 | 1176 | 1170 | 1.64 | 1.61 | 7831.52 | 0 | 0 | 0 | 0 | 7831.52 | 174.38 | 1 | 531.2 | 0.93 | 29.83 | 0.11 | 7.04 | 0.04 | 0 | 0 | 742.45 | 8573.96 | 24.01 | 45.3 | 0 | 69.31 | 6.54 | 0.08 | 4864.3 | 98.17 | 90.84 | 99.54 | 91.34 | 91.34 | 90.05 | 2.18 | 2.48 | 2.48 | 6.63 | 2.03 | 2.12 | 2.51 | 2.69 | 91.26 | 91.26 | 89.96 | 2.17 | 2.47 | 6.72 | 2.02
NUCLEAR BWR All Sizes | 2020 | 2020 | 25 | 25 | 1045 | 1042 | 1.44 | 1.4 | 8214 | 1.65 | 0.04 | 0 | 0 | 8215.66 | 115.18 | 0.64 | 415.21 | 0.92 | 1.05 | 0.04 | 36.92 | 0.28 | 0 | 0 | 568.34 | 8784 | 57.35 | 116.65 | 0 | 174 | 4.74 | 0.42 | 5867.14 | 97.22 | 91.69 | 98.72 | 93.51 | 93.53 | 91.23 | 1.38 | 2.07 | 2.07 | 5.16 | 1.31 | 1.73 | 3.13 | 3.28 | 92.88 | 92.91 | 90.53 | 1.68 | 2.42 | 5.51 | 1.59
NUCLEAR BWR 400-799 | 2020 | 2020 | **** | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [10 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: POF to FOR
NUCLEAR BWR 800-999 | 2020 | 2020 | 9 | 9 | 890 | 886 | 1.56 | 1.56 | 8267.52 | 0 | 0 | 0 | 0 | 8267.52 | 80.29 | 0.67 | 351.51 | 0.78 | 2.9 | 0.11 | 81.77 | 0.44 | 0 | 0 | 516.48 | 8784 | 52.53 | 85.76 | 0 | 138.29 | 4.03 | 0.93 | 5299.69 | 100 | 94.28 | 100.16 | 94.12 | 94.12 | 92.09 | 0.96 | 1.59 | 1.59 | 4.97 | 0.91 | 1.84 | 2.98 | 3.1 | 94.14 | 94.14 | 92.15 | 0.99 | 1.63 | 4.92 | 0.94
NUCLEAR BWR 1000 Plus | 2020 | 2020 | 14 | 14 | 1203 | 1201 | 1.57 | 1.5 | 8098.17 | 2.95 | 0.07 | 0 | 0 | 8101.13 | 154.05 | 0.71 | 515.47 | 1.14 | 0 | 0 | 13.35 | 0.21 | 0 | 0 | 682.88 | 8784 | 65.58 | 148.26 | 0 | 213.84 | 5.87 | 0.15 | 5398.78 | 95.54 | 89.92 | 98 | 92.19 | 92.23 | 89.67 | 1.87 | 2.66 | 2.66 | 6.02 | 1.75 | 1.91 | 3.58 | 3.81 | 91.75 | 91.78 | 89.18 | 2.15 | 2.98 | 6.2 | 2.02
NUCLEAR CANDU All Sizes | 2020 | 2020 | **** | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [10 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: POF to FOR
JET ENGINE All Sizes | 2020 | 2020 | 193 | 193 | 41 | 39 | 82.5 | 81.81 | 403.02 | 7403.52 | 85.78 | 0 | 73.19 | 7879.73 | 291.61 | 4.57 | 322.63 | 2.58 | 3.2 | 0.03 | 161.78 | 3.73 | 3.4 | 0.02 | 782.62 | 8662.35 | 18.49 | 31.83 | 17.87 | 50.32 | 3.76 | 1.91 | 4.93 | 99.16 | 4.97 | 78.29 | 4.65 | 90.97 | 88 | 37.98 | 39.47 | 8 | 5.67 | 3.37 | 5.27 | 5.73 | 50.24 | 6.35 | 90.49 | 86.27 | 31.75 | 33.8 | 6.12 | 3.39
JET ENGINE 001-019 | 2020 | 2020 | 20 | 20 | 14 | 14 | 13.7 | 13.5 | 142.62 | 8112.59 | 19.5 | 0 | 0 | 8255.21 | 370.48 | 2.7 | 92.89 | 1.65 | 0 | 0 | 65.42 | 3.95 | 0 | 0 | 528.79 | 8784 | 0.01 | 0.14 | 0 | 0.15 | 1.06 | 0.74 | 10.56 | 98.54 | 0.05 | 3.4 | 1.62 | 93.98 | 93.98 | 72.2 | 72.21 | 18.37 | 1.8 | 4.22 | 4.96 | 4.96 | 75.37 | 1.49 | 93.53 | 93.53 | 75 | 75 | 2.02 | 4.45
JET ENGINE 20 Plus | 2020 | 2020 | 173 | 173 | 44 | 42 | 90.46 | 89.71 | 433.12 | 7321.54 | 93.45 | 0 | 81.66 | 7836.32 | 282.49 | 4.79 | 349.19 | 2.68 | 3.58 | 0.03 | 172.92 | 3.71 | 3.79 | 0.02 | 811.97 | 8648.29 | 20.62 | 35.49 | 19.94 | 56.12 | 4.08 | 2.04 | 4.83 | 99.17 | 5.17 | 78.95 | 5.01 | 90.61 | 87.29 | 35.43 | 37.09 | 7.72 | 6.12 | 3.27 | 5.31 | 5.82 | 48.61 | 6.54 | 90.37 | 85.98 | 30.83 | 32.94 | 6.28 | 3.34
GAS TURBINE All Sizes | 2020 | 2020 | 488 | 493 | 68 | 67 | 57.76 | 56.92 | 480.51 | 7055.44 | 55.51 | 0 | 0 | 7535.95 | 384.07 | 4.07 | 395.57 | 1.71 | 3.9 | 0.02 | 179.11 | 2.93 | 25.87 | 0.03 | 988.51 | 8524.46 | 15.6 | 5.47 | 14.08 | 21.08 | 4.69 | 2.4 | 8.44 | 98.55 | 5.16 | 69.58 | 5.64 | 88.4 | 85.79 | 44.42 | 45.49 | 10.05 | 7.09 | 4.51 | 6.91 | 7.1 | 55.82 | 7.42 | 89.61 | 86.88 | 30.39 | 31.47 | 7.15 | 3.24
GAS TURBINE 001-019 | 2020 | 2020 | 64 | 64 | 16 | 16 | 28.27 | 26.66 | 112.99 | 6594.31 | 32.08 | 0 | 0 | 6707.3 | 575.2 | 3.23 | 271.85 | 0.89 | 14.86 | 0.06 | 137.8 | 1.45 | 46.89 | 0.02 | 1046.61 | 7753.91 | 8.99 | 13.05 | 8.46 | 22.04 | 3.7 | 2.38 | 4.24 | 94.3 | 0.65 | 46.41 | 1.46 | 86.5 | 85.13 | 83.58 | 83.86 | 17.15 | 6.08 | 7.42 | 9.8 | 9.94 | 87.12 | 1.41 | 87.3 | 85.92 | 83.53 | 83.82 | 5.57 | 7.13
GAS TURBINE 020-049 | 2020 | 2020 | 91 | 91 | 33 | 31 | 108.89 | 107.88 | 648.47 | 6909.86 | 75.96 | 0 | 0 | 7558.33 | 588.81 | 5.13 | 264.01 | 1.68 | 1.64 | 0.02 | 269.67 | 3.65 | 0.24 | 0.01 | 1124.37 | 8682.7 | 18.53 | 0.42 | 17.21 | 18.95 | 3.06 | 3.11 | 6.01 | 99.07 | 6.58 | 67.77 | 7.47 | 87.05 | 83.34 | 47.59 | 48.41 | 10.65 | 6.17 | 6.78 | 9.89 | 10.11 | 57.57 | 9.71 | 88.39 | 84.99 | 33.99 | 34.87 | 6.62 | 5
GAS TURBINE 50 Plus | 2020 | 2020 | 333 | 338 | 88 | 86 | 49.57 | 48.93 | 504.88 | 7181.95 | 54.43 | 0 | 0 | 7686.83 | 292.75 | 3.94 | 454.41 | 1.87 | 2.43 | 0.02 | 162.54 | 3.01 | 28.79 | 0.03 | 940.93 | 8627.76 | 16.06 | 5.4 | 14.29 | 21.46 | 5.3 | 2.22 | 10.32 | 98.71 | 5.16 | 69.95 | 5.85 | 89.09 | 86.57 | 36.7 | 38.03 | 9.34 | 7.51 | 3.39 | 5.61 | 5.8 | 49.87 | 7.37 | 89.81 | 87.1 | 28.52 | 29.65 | 7.25 | 2.94
COMBINED CYCLE All Sizes | 2020 | 2020 | 266 | 266 | 298 | 291 | 60.78 | 60.24 | 4868.88 | 2819.46 | 54.27 | 0 | 0 | 7688.34 | 247.57 | 4.93 | 604.44 | 2.36 | 25.66 | 0.18 | 156.71 | 1.76 | 0.83 | 0.02 | 1035.21 | 8723.55 | 39.12 | 43.63 | 13.63 | 82.75 | 7.22 | 1.81 | 80.82 | 99.11 | 53.36 | 81.6 | 55.81 | 88.13 | 85.05 | 4.84 | 5.59 | 4.26 | 9.03 | 2.84 | 4.64 | 5.26 | 8.66 | 65.39 | 88.46 | 85.14 | 3.15 | 3.87 | 9.41 | 2.13
HYDRO All Sizes | 2020 | 2020 | 880 | 880 | 69 | 69 | 142.13 | 142.03 | 5340.15 | 1406.09 | 39.55 | 7.15 | 146.96 | 6900.35 | 698.41 | 3.4 | 911.63 | 2.72 | 31.3 | 0.05 | 150.29 | 2.08 | 12.18 | 0.01 | 1803.8 | 8704.15 | 7.45 | 12.59 | 0.67 | 20.04 | 10.83 | 1.87 | 37.6 | 99.93 | 37.71 | 61.78 | 61.35 | 79.28 | 78.73 | 11.28 | 11.4 | 9.56 | 12.7 | 8.02 | 9.89 | 9.98 | 13.66 | 61.04 | 80.68 | 80.25 | 5.04 | 5.1 | 15.98 | 3.34
HYDRO 001-029 | 2020 | 2020 | 320 | 320 | 11 | 11 | 36.4 | 36.33 | 5127.21 | 1088.13 | 13.45 | 15.31 | 93.13 | 6323.78 | 1296.54 | 5.08 | 682.6 | 1.45 | 41.08 | 0.09 | 215.06 | 2.08 | 5.37 | 0.02 | 2240.65 | 8564.43 | 15.87 | 7.34 | 0 | 23.21 | 8.45 | 2.57 | 141.13 | 99.81 | 35.2 | 55.17 | 59.87 | 73.84 | 73.45 | 19.85 | 20.09 | 17.74 | 11.02 | 15.14 | 17.71 | 17.9 | 22.7 | 63.81 | 79.19 | 78.83 | 12.74 | 13.12 | 11.25 | 9.56
HYDRO 30 Plus | 2020 | 2020 | 560 | 560 | 102 | 101 | 202.55 | 202.42 | 5461.83 | 1587.79 | 54.46 | 2.49 | 177.72 | 7229.82 | 356.63 | 2.43 | 1042.5 | 3.45 | 25.71 | 0.02 | 113.27 | 2.09 | 16.07 | 0.01 | 1554.18 | 8784 | 2.63 | 15.59 | 1.06 | 18.23 | 12.16 | 1.47 | 26.98 | 99.94 | 37.87 | 62.23 | 62.18 | 82.31 | 81.68 | 5.95 | 5.99 | 4.9 | 13.63 | 4.06 | 5.53 | 5.56 | 7.97 | 60.86 | 80.78 | 80.34 | 4.47 | 4.5 | 16.28 | 2.93
PUMPED STORAGE All Sizes | 2020 | 2020 | 101 | 101 | 114 | 113 | 217.65 | 217.57 | 2485.14 | 3840.48 | 177.22 | 868.93 | 161.24 | 7355.78 | 247.41 | 2.17 | 901.64 | 2.25 | 87.08 | 0.16 | 192 | 4.59 | 0.09 | 0.02 | 1428.22 | 8784 | 0.77 | 0.2 | 0.51 | 0.97 | 11.26 | 2.19 | 11.42 | 99.96 | 7.18 | 45.06 | 28.29 | 83.74 | 83.58 | 6.58 | 6.59 | 4.09 | 13.44 | 2.82 | 5 | 5.01 | 11.13 | 15.94 | 80.24 | 79.75 | 8.09 | 8.11 | 17.24 | 2.52
MULTIBOILER/MULTI-TURBINE All Sizes | 2020 | 2020 | 19 | 19 | 338 | 336 | 12.84 | 12.58 | 3941.56 | 2729.44 | 12.58 | 0 | 0 | 6671 | 198.7 | 3.11 | 958.33 | 1.53 | 1.2 | 0.05 | 566.44 | 3.47 | 1.8 | 0.05 | 1726.48 | 8397.47 | 345.45 | 158.85 | 40.86 | 504.3 | 11.43 | 6.77 | 313.32 | 97.98 | 16.52 | 52.34 | 46.94 | 79.44 | 72.51 | 4.8 | 13.01 | 9.14 | 18.19 | 2.37 | 9.13 | 13.87 | 24.47 | 31.56 | 74.98 | 70.64 | 4.32 | 13.15 | 23.59 | 1.42
DIESEL All Sizes | 2020 | 2020 | 115 | 115 | 9 | 9 | 84.97 | 84.54 | 1010.26 | 7075.72 | 83.69 | 0 | 0 | 8085.97 | 254.01 | 7.43 | 246.97 | 0.7 | 1.81 | 0.01 | 118.85 | 2.5 | 0 | 0 | 621.65 | 8707.62 | 35.97 | 18.86 | 30.14 | 54.83 | 2.86 | 1.36 | 11.95 | 99.49 | 11.64 | 61.86 | 11.6 | 92.86 | 92.11 | 20.09 | 22.4 | 8.08 | 4.22 | 2.92 | 4.28 | 4.78 | 29.35 | 18.81 | 94.35 | 92.61 | 9.51 | 12.66 | 3.67 | 1.98
* Column title definitions and calculations can be found in the GADS Data Reporting Instructsions - Appendix F Equations
**Caution: EFOR and WEFOR values may be low since deratings during reserve shutdown periods may not have been reported for a large number of these units.
*** The two methods for calculating combined cycle units is not available at this time.
**** Less than three generating companies are reporting this type of unit. To retain confidentiality of the data, no data is reported here.