## non-CIP SNOPs
Filed_Date | NOC_ID | Region | Registered_Entity_Name | NCR | Reliability_Functions | Notice_of_Confirmed_Violation_or_Settlement_Agreement | Admits_OR_Agrees_and_Stipulates_OR_Neither_Admits_nor_Denies_OR_Does_Not_Contest | Total_Penalty | NERC_Violation_ID | Reliability_Standard | Requirement | Risk_Assessment | Violation_Risk_Factor | Violation_Severity_Level | Discovery_Method | Reported_to_Region_Date | Noncompliance_Start_Date | Noncompliance_End_Date | Mitigation_Expected_Completion_Date | Mitigation_Completion_Date | Date_Regional_Entity_Verified_Completion_of_Mitigation | Description_of_Noncompliance | Description_of_Risk_Assessment | Description_of_Mitigation | Other_Factors_and_Compliance_History_Discussion
2024-03-28 | NOC-2828 | ReliabilityFirst Corporation (ReliabilityFirst) | Twin Ridges Wind Farm | NCR11280 | GOP | Settlement Agreement | Admits | $30,000 (for 2021-00498, 2021-00386, 2021-00514, 2021-00515, and 2021-00516) | 2021-00498 | COM-002-4 | R3 | Moderate | Lower | Severe | Self-Report | 2021-08-13 | 2016-07-01 | 2020-12-06 |  | 2021-02-04 | 2021-11-01 | On August 13, 2021, the entity submitted a Self-Report to ReliabilityFirst stating that, as a Generator Operator, it was in violation of COM-002-4 R3. The second Operations and Management (O&M) company discovered, amongst a litany of other deficiencies, that there was no formal program for communications training of the entity’s operating personnel under the previous ownership, or if existing, no records were provided to the second O&M. The root cause of this noncompliance was an inadequate transition of oversight and maintenance records between multiple owners and O&M companies. The violation began on July 1, 2016, the date the entity was required to comply with COM-002-4 R3. The violation ended on December 6, 2020, the date the entity completed COM-002 training. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Failing to train operators on predefined communication protocols increases the likelihood of a miscommunication that could lead to action or inaction harmful to the reliability of the BPS. The risk is not minimal because the violation has a significant duration of more than four years, increasing the probability that the entity would receive communications that staff would be unable to address appropriately. The site received operating instructions during the period of noncompliance, elevating the probability that the instructions would be mishandled and result in harm. The risk is not serious because the plant itself has limited BPS implications with a 149.6 MVA nameplate rating and is not designated as an Interconnection Reliability Operating Limit, reducing the potential magnitude of harm. | To mitigate this violation, the entity has performed the following actions: 1) trained the operating personnel in the three-part communication process as described in COM-002; and 2) integrated NERC tasks into centralized tracking software. This software solution tracks NERC compliance obligations and due dates. Additionally, the entity held a series of calls with their NERC consultant to discuss compliance training. | ReliabilityFirst reviewed Twin Ridges internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. Twin Ridges was cooperative throughout the entire enforcement process. Throughout the enforcement process, Twin Ridges voluntarily provided ReliabilityFirst with information regarding the violations in a manner that was detailed, thorough, organized, and prompt. Therefore, ReliabilityFirst awarded cooperation credit to encourage this sort of behavior by Twin Ridges and other Registered Entities in the future. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by Registered Entities. Twin Ridges identified and Self-Reported the violations disposed of herein. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by timely detection and correction unconnected to a pending regional compliance monitoring action, by reducing the monetary penalty. ReliabilityFirst notes that the entity has a nameplate rating of 149.6 MVA, limiting its overall BES impact and the potential magnitude of harm. However, an entity will not be excused from its compliance and reliability responsibilities and avoid potential sanctions merely because it is small. The penalty is limited, in part, due to proactive actions of new owners and a new O&M, including self-reporting the violations involved herein (2018 owner) and cooperative information exchange (2022 owner). While the owner bears responsibility for the violations associated with an asset, ReliabilityFirst also wishes to promote the transparent review and self-reporting seen here.
2024-03-28 | NOC-2828 | ReliabilityFirst Corporation (ReliabilityFirst) | Twin Ridges Wind Farm | NCR11280 | GO | Settlement Agreement | Admits | $30,000 (for 2021-00498, 2021-00386, 2021-00514, 2021-00515, and 2021-00516) | 2021-00386 | PRC-005-6 | R3 | Moderate | High | Severe | Self-Report | 2021-07-15 | 2016-01-01 | 2021-10-20 |  | 2021-10-20 | 2021-12-01 | On July 15, 2021, the entity submitted a Self-Report to ReliabilityFirst stating that, as a Generator Owner, it was in violation of PRC-005-6 R3. The entity had not performed the maintenance of the following Protection System components: (a) Sudden Pressure Relaying (One SPR on transformer T1); (b) Lockout relay testing (Five LOR - 86BFT, 86TS, 86TP, 86B, 86BFB); and (c) 18-month and 6-year battery maintenance activities (One VLA battery bank). This lack of maintenance affects a significant portion of PRC-005-6 R3 applicable elements. The entity failed to perform maintenance on its only Sudden Pressure Relay, failed to perform 18-month and six-year testing on the entity’s single battery bank (8-month duration on 18-month testing), and failed to perform maintenance on each of its Lockout Relays where PRC-005-6 R3 Table 1-5 row two was applicable (3-year duration). The root cause of this noncompliance was an inadequate transition of oversight and maintenance records between multiple owners and O&M companies. The violation began on January 1, 2016, the date the entity was required to comply with PRC-005-6 R3. The violation ended on October 20, 2021, the date the entity completed its Mitigating Activities. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by failing to maintain and test Protection System devices is that it could lead to device malfunction, premature or undetected device failure, and Protection System Misoperation. Protection System issues could have significant consequences related to equipment damage and power system performance (e.g., generating unit or system instability, unacceptable loss of load or generation, cascading, or uncontrolled system separation). The risk is not minimal because the violation impacts a significant portion of the entity’s in scope PRC-005-6 elements, elevating the probability that the lack of maintenance would result in harm. The risk is not serious based on the following factors impacting the potential magnitude of harm. First, the facility is limited to a 149.6 MVA facility. Second, the entity is not part of a designated Interconnection Reliability Operating Limit. | To mitigate this violation, the entity has performed the following actions: 1) implemented the practice of annually reviewing its Protection System inventory and maintenance activities due dates; and 2) performed Sudden Pressure relaying, Lockout relays, and battery maintenance activities. | ReliabilityFirst reviewed Twin Ridges internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. Twin Ridges was cooperative throughout the entire enforcement process. Throughout the enforcement process, Twin Ridges voluntarily provided ReliabilityFirst with information regarding the violations in a manner that was detailed, thorough, organized, and prompt. Therefore, ReliabilityFirst awarded cooperation credit to encourage this sort of behavior by Twin Ridges and other Registered Entities in the future. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by Registered Entities. Twin Ridges identified and Self-Reported the violations disposed of herein. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by timely detection and correction unconnected to a pending regional compliance monitoring action, by reducing the monetary penalty. ReliabilityFirst notes that the entity has a nameplate rating of 149.6 MVA, limiting its overall BES impact and the potential magnitude of harm. However, an entity will not be excused from its compliance and reliability responsibilities and avoid potential sanctions merely because it is small. The penalty is limited, in part, due to proactive actions of new owners and a new O&M, including self-reporting the violations involved herein (2018 owner) and cooperative information exchange (2022 owner). While the owner bears responsibility for the violations associated with an asset, ReliabilityFirst also wishes to promote the transparent review and self-reporting seen here.
2024-03-28 | NOC-2828 | ReliabilityFirst Corporation (ReliabilityFirst) | Twin Ridges Wind Farm | NCR11280 | GOP | Settlement Agreement | Admits | $30,000 (for 2021-00498, 2021-00386, 2021-00514, 2021-00515, and 2021-00516) | 2021-00514 | VAR-002-4.1 | R1 | Moderate | Medium | Severe | Self-Report | 2021-08-13 | 2017-12-22 | 2022-01-26 |  | 2022-01-26 | 2022-04-11 | On August 13, 2021, the entity submitted a Self-Report to ReliabilityFirst stating that, as a Generator Operator, it was in violation of VAR-002-4.1 R1. The second O&M determined that there is no evidence on file to demonstrate the generation was in the automatic voltage control mode (or if not, that the Transmission Operator (TOP) was notified of a status change). If compliance was maintained, records from the previous ownership were not available or at least not forwarded to the second O&M when the asset was purchased. The root cause of this noncompliance was an inadequate transition of oversight and maintenance records between multiple owners and O&M companies. The violation began on December 22, 2017, the date following the closing date of the ReliabilityFirst audit of Twin Ridges, including in scope VAR-002-4. The violation ended on January 26, 2022, the date the entity completed its Mitigating Activities. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by failing to notify the TOP of a change in the status of the Automatic Voltage Regulator (AVR) is that if deviations from the prescribed and coordinated scheduled voltage occurred, the TOP may be delayed in taking action in a timely manner to restore the system to the prescribed voltage levels. The risk posed by this violation was not minimal due to an extensive duration of more than 4 years. Extensive durations elevate the probability that the entity would have experienced or implemented a change in AVR status, failed to notify its TOP, and as a result, caused harm. The risk is not serious based on the following factors impacting the potential magnitude of harm. First, the facility is limited to a 149.6 MVA facility. Second the entity is not part of a designated Interconnection Reliability Operating Limit. | To mitigate this violation, the entity has performed the following actions: 1) implemented control room visual alarming capabilities for loss of AVR; 2) adopted a corporate-wide VAR-002 procedure which will document the requirements within the VAR-002 applicable to the entity; and 3) conducted training to ensure entity operations personnel understand the corporate-wide VAR-002 procedure. | ReliabilityFirst reviewed Twin Ridges internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. Twin Ridges was cooperative throughout the entire enforcement process. Throughout the enforcement process, Twin Ridges voluntarily provided ReliabilityFirst with information regarding the violations in a manner that was detailed, thorough, organized, and prompt. Therefore, ReliabilityFirst awarded cooperation credit to encourage this sort of behavior by Twin Ridges and other Registered Entities in the future. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by Registered Entities. Twin Ridges identified and Self-Reported the violations disposed of herein. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by timely detection and correction unconnected to a pending regional compliance monitoring action, by reducing the monetary penalty. ReliabilityFirst notes that the entity has a nameplate rating of 149.6 MVA, limiting its overall BES impact and the potential magnitude of harm. However, an entity will not be excused from its compliance and reliability responsibilities and avoid potential sanctions merely because it is small. The penalty is limited, in part, due to proactive actions of new owners and a new O&M, including self-reporting the violations involved herein (2018 owner) and cooperative information exchange (2022 owner). While the owner bears responsibility for the violations associated with an asset, ReliabilityFirst also wishes to promote the transparent review and self-reporting seen here.
2024-03-28 | NOC-2828 | ReliabilityFirst Corporation (ReliabilityFirst) | Twin Ridges Wind Farm | NCR11280 | GOP | Settlement Agreement | Admits | $30,000 (for 2021-00498, 2021-00386, 2021-00514, 2021-00515, and 2021-00516) | 2021-00515 | VAR-002-4.1 | R2 | Moderate | Medium | Severe | Self-Report | 2021-08-13 | 2017-12-22 | 2022-01-07 |  | 2022-01-07 | 2022-02-22 | On August 13, 2021, the entity submitted a Self-Report to ReliabilityFirst stating that, as a Generator Operator, it was in violation of VAR-002-4.1 R2. In the Self-Report, the new O&M determined that there is no evidence on file to demonstrate the generator maintained its voltage or Reactive Power schedule (or if not, that the Transmission Operator (TOP) was notified of a deviation). If compliance was maintained, records from the previous ownership were not available or at least not forwarded to the new O&M when the asset was purchased. The root cause of this noncompliance was centrally, a lack of oversight by former owners of Twin Ridges of its O&M company resulting in a lack of evidence of whether the site maintained its voltage and Reactive Power Schedule. The violation began on December 22, 2017, the date following the closing date of the ReliabilityFirst audit of Twin Ridges, including in scope VAR-002-4. The violation ended on January 7, 2022, the date the entity completed its Mitigating Activities. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance is a negative impact on the reliable operation of the BPS by allowing detrimental levels of generator voltage or Reactive Power output. The risk posed by this violation was not minimal due to an extensive duration of more than four years. Extensive durations elevate the probability that the entity would have deviated from its voltage schedule or reactive power schedule, and failed to notify its TOP, and as a result, caused harm. The risk is not serious based on the following factors impacting the potential magnitude of harm. First, the facility is limited to a 149.6 MVA facility. Second the entity is not part of a designated Interconnection Reliability Operating Limit. | To mitigate this violation, the entity has performed the following actions: 1) implemented control room visual alarming capabilities for loss of voltage schedule within tolerance; and 2) adopted a corporate-wide VAR-002 procedure which will document the requirements within the Standard applicable to the entity. | ReliabilityFirst reviewed Twin Ridges internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. Twin Ridges was cooperative throughout the entire enforcement process. Throughout the enforcement process, Twin Ridges voluntarily provided ReliabilityFirst with information regarding the violations in a manner that was detailed, thorough, organized, and prompt. Therefore, ReliabilityFirst awarded cooperation credit to encourage this sort of behavior by Twin Ridges and other Registered Entities in the future. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by Registered Entities. Twin Ridges identified and Self-Reported the violations disposed of herein. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by timely detection and correction unconnected to a pending regional compliance monitoring action, by reducing the monetary penalty. ReliabilityFirst notes that the entity has a nameplate rating of 149.6 MVA, limiting its overall BES impact and the potential magnitude of harm. However, an entity will not be excused from its compliance and reliability responsibilities and avoid potential sanctions merely because it is small. The penalty is limited, in part, due to proactive actions of new owners and a new O&M, including self-reporting the violations involved herein (2018 owner) and cooperative information exchange (2022 owner). While the owner bears responsibility for the violations associated with an asset, ReliabilityFirst also wishes to promote the transparent review and self-reporting seen here.
2024-03-28 | NOC-2828 | ReliabilityFirst Corporation (ReliabilityFirst) | Twin Ridges Wind Farm | NCR11280 | GOP | Settlement Agreement | Admits | $30,000 (for 2021-00498, 2021-00386, 2021-00514, 2021-00515, and 2021-00516) | 2021-00516 | VAR-002-4.1 | R3 | Moderate | Medium | Severe | Self-Report | 2021-08-13 | 2017-12-22 | 2022-01-07 |  | 2022-01-07 | 2022-02-22 | On August 13, 2021, the entity submitted a Self-Report to ReliabilityFirst stating that, as a Generator Operator, it was in violation of VAR-002-4.1 R3. The second O&M determined that there is no evidence on file to demonstrate notification within 30 minutes to its Transmission Operator (TOP) of a status change on its Automatic Voltage Regulator (AVR), power system stabilizer (PSS), or alternative voltage control device. If compliance was maintained, records from the previous ownership were not available or at least not forwarded when the asset was purchased. The root cause of this noncompliance was centrally, a lack of oversight by former owners of Twin Ridges of its O&M company resulting in a lack of evidence of whether the site monitored and communicated changes to its AVR, PSS, or alternate voltage controlling device. The violation began on December 22, 2017, the date following the closing date of the ReliabilityFirst audit of Twin Ridges, including in scope VAR-002-4. The violation ended on January 7, 2022, the date the entity completed its Mitigating Activities. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. An entity’s failure to notify the TOP of a status change on an AVR, PSS, or alternative voltage controlling device could lead to inappropriate voltage-control action by the TOP. The risk posed by this violation was not minimal due to an extensive duration of more than four years. Extensive durations, elevate the probability that the entity’s AVR, PSS, or alternative voltage controlling device would have experienced a status change and the entity would have failed to notify its TOP, and as a result, caused harm. The risk is not serious based on the following factors impacting the potential magnitude of harm. First, the facility is limited to a 149.6 MVA facility. Second the entity is not part of a designated Interconnection Reliability Operating Limit. | To mitigate this violation, the entity adopted a corporate-wide VAR-002 procedure which will document the requirements within the Standard applicable to the entity. | ReliabilityFirst reviewed Twin Ridges internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. Twin Ridges was cooperative throughout the entire enforcement process. Throughout the enforcement process, Twin Ridges voluntarily provided ReliabilityFirst with information regarding the violations in a manner that was detailed, thorough, organized, and prompt. Therefore, ReliabilityFirst awarded cooperation credit to encourage this sort of behavior by Twin Ridges and other Registered Entities in the future. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by Registered Entities. Twin Ridges identified and Self-Reported the violations disposed of herein. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by timely detection and correction unconnected to a pending regional compliance monitoring action, by reducing the monetary penalty. ReliabilityFirst notes that the entity has a nameplate rating of 149.6 MVA, limiting its overall BES impact and the potential magnitude of harm. However, an entity will not be excused from its compliance and reliability responsibilities and avoid potential sanctions merely because it is small. The penalty is limited, in part, due to proactive actions of new owners and a new O&M, including self-reporting the violations involved herein (2018 owner) and cooperative information exchange (2022 owner). While the owner bears responsibility for the violations associated with an asset, ReliabilityFirst also wishes to promote the transparent review and self-reporting seen here.