## non-CIP SNOPs
Filed_Date | NOC_ID | Region | Registered_Entity_Name | NCR | Reliability_Functions | Notice_of_Confirmed_Violation_or_Settlement_Agreement | Admits_OR_Agrees_and_Stipulates_OR_Neither_Admits_nor_Denies_OR_Does_Not_Contest | Total_Penalty | NERC_Violation_ID | Reliability_Standard | Requirement | Risk_Assessment | Violation_Risk_Factor | Violation_Severity_Level | Discovery_Method | Reported_to_Region_Date | Noncompliance_Start_Date | Noncompliance_End_Date | Mitigation_Expected_Completion_Date | Mitigation_Completion_Date | Date_Regional_Entity_Verified_Completion_of_Mitigation | Description_of_Noncompliance | Description_of_Risk_Assessment | Description_of_Mitigation | Other_Factors_and_Compliance_History_Discussion
2024-05-30 | NOC-2830 | Northeast Power Coordinating Council, Inc. (NPCC) | Long Island Power Authority (LIPA) | NCR07133 | TO | Settlement Agreement | Admits | 96000 | NPCC2020024201 | FAC-008-3 | R6 | Moderate | Medium | Severe | Self-Report | 2020-11-05 | 2016-07-01 | 2024-02-05 | 5/31/2024 (Expected Completion Date) | TBD | TBD | On November 5, 2020, LIPA submitted a Self-Report to NPCC stating that, as a Transmission Owner (TO), it was potentially in violation of FAC-008-3 R6 for failing to determine Facility Ratings consistent with its Facility Ratings Methodology (FRM). The Self-Report identified Facility Rating discrepancies impacting twenty-four (24) Facilities, equivalent to approximately 19% of LIPA’s 128 applicable Bulk Electric System (BES) Facilities. Of the twenty-four (24) total noncompliant Facilities, nine (9) 138 kV cables had incorrect seasonal Facility ratings. These cables require seasonal rating changes in the Energy Management System (EMS) based on their pump house field configurations. Specifically, the EMS Facility ratings did not match pump house field configurations, resulting in some limited overloading conditions relative to the cables’ correct ratings. LIPA conducted a review of its engineering drawings and a targeted walk down of its BES Facilities as part of its extent of condition review. This resulted in the identification of fifteen (15) 138 kV Facilities, comprised of nine (9) feeders and six (6) transformers, with Facility Ratings that did not consider the Most Limiting Element (MLE). The fifteen (15) Facilities were newly identified as BES Elements as a result of the revised BES definition effective on July 1, 2016. During a walk down conducted in October 2023, LIPA discovered an additional two (2) 138 kV cables were operating in the field in static mode, while circulate ratings were being utilized in the EMS for real-time system operation. Before LIPA could implement mitigation to prevent reoccurrences, on January 31, 2024, LIPA discovered one (1) of the two (2) 138 kV cables was once again operating in the field in static mode, while circulate ratings were being utilized in the EMS, bringing the total number of noncompliant Facilities to twenty-six (26) and the total number of instances to twenty-seven (27). The root cause for the fifteen (15) Facilities, where LIPA failed to determine Facility Ratings consistent with its FRM, was ineffective internal procedures for ensuring the accuracy of Facility Ratings, including ineffective interdepartmental coordination and an inadequate process for considering the MLE. The root cause for the nine (9) cables, where LIPA failed to set correct cable seasonal ratings, was a database transposition error. The root cause of the two (2) noncompliant cables found in 2023 and the additional instance that occurred in 2024 was an ineffective detective control to alert personnel of the pump house field configuration change and a lack of awareness that such a change would occur under the circumstances. The instance of violation pertaining to the fifteen (15) Facilities with incorrect MLEs started on July 1, 2016, the effective date of the new BES Definition, and when LIPA failed to determine Facility Ratings consistent with its FRM at that time. Each of these inconsistencies were corrected promptly after they were discovered, with the last being resolved when the extent of condition review was completed on May 20, 2021. The instance of violation regarding the nine (9) cables started on May 1, 2021, when the seasonal ratings for the cables were changed from Winter to Summer. The issue was identified by the System Operator and corrected on June 2, 2021. The instance of the two (2) noncompliant cables discovered in 2023 started October 15, 2023, when the pump house field configuration changed from circulate to static mode and applicable ratings were not adjusted in the EMS. The violation ended October 25, 2023, when the System Operator applied the static ratings in the EMS. The instance of the noncompliant cable discovered in 2024 started January 31, 2024, when the pump house field configuration was once again contradictory to the ratings used in the EMS. The violation ended February 5, 2024, when the System Operator applied the correct ratings in the EMS. | NPCC determined that the violation posed a moderate risk to the reliability of the BPS based on the following factors. A failure to have Facility Ratings that are consistent with the associated Facility Ratings methodology or documentation for determining Facility Ratings could lead to an incorrect Facility Rating if a missing, or incorrectly rated component turns out to be the MLE. In all cases of incorrect Facility Ratings, the System Operator is operating with a decreased level of situational awareness in real-time and is monitoring contingencies with reduced accuracy. Incorrect Facility Ratings also result in inaccurate system planning, including planning during short-term studies, long term-studies, seasonal assessments, capital project studies, and other studies. Incorrectly inflated ratings increase the likelihood of equipment damage or failure which could adversely affect the BPS. It also increases the risk that the System Operator is operating to incorrect System Operating Limits or Interconnection Reliability Operating Limits. If the Facility Rating was too low, it could have resulted in unnecessary reductions in transfer, or generator output, and/or a perception of congestion that did not really exist. Whether the incorrect ratings were too high or too low, System Operators could have been required to implement reliability actions that otherwise would not have been needed. LIPA’s peak load from 2020-2023 ranged from approximately 5,200 MW to 5,500 MW. Twenty-six (26) Facilities, equivalent to approximately 20% of LIPA’s 128 applicable BES Facilities, operated with incorrect Facility ratings during the period of noncompliance. Because LIPA is a summer peaking entity, its summer peak conditions are the most significant. With respect to Normal ratings for the summer peak load period, mitigation of the violation required an increased rating for one (1) 138 kV feeder by 19 MW (+9% change), a decreased rating for two (2) 138 kV feeders up to 98 MW (-20% change), and a decreased rating for four (4) transformers, up to 50 MW (-12% change). The nine (9) cables that had wrong seasonal ratings, all had higher Summer Normal ratings set than what should have been applied, up to 52 MW (-14% difference). Remediation of the two (2) additional noncompliant cables found in 2023 resulted in decreased ratings, up to 35 MW (-14% difference). However, the duration of this instance was short, and the two cables never exceeded their respective static ratings during the ten (10) days of noncompliance. The instance of the noncompliant cable discovered in 2024 occurred in the off-peak season, and therefore, had no impact on LIPA’s summer peak conditions. The remaining six (6) feeders and two (2) transformers experienced no change in their Summer Normal ratings. According to LIPA’s more comprehensive, year-round analysis of the historical performance of all twenty-six (26) noncompliant Facilities, six (6) Facilities comprising of two (2) 138 kV feeders and four (4) transformer banks exceeded the corrected ratings ninety-five (95) times in a five-year period. These exceedances did not affect any Critical Facilities, and all occurred during off-peak operating conditions except for one (1) exceedance that occurred on a high-load day during a Summer Dependable Maximum Net Capability test for the generating unit associated with the Bank. All exceedances were of the Facilities’ Normal ratings, with one (1) single exception where a Long-Term Emergency (LTE) rating was momentarily exceeded for 20 seconds. LIPA determined that the above Facilities have not been damaged by these exceedances and have not suffered a loss of service life. LIPA also reported that the Facilities have been operated for approximately 50 years without any identifiable damage or adverse effects. LIPA has operating controls in place to mitigate the effect of operational issues that may be caused by noncompliance with this Standard. The SCADA/EMS system used by its control center, provides real-time telemetry of power flow on monitored transmission lines and transformers for MW, MVAR, amperage and bus voltages in kV. SCADA will generate audible and visible alarms to System Operators when monitored system Facilities are being operated in excess of real-time limits. Additionally, LIPA’s Real-Time Network Analysis (RTNA)/Real-Time Contingency Analysis (RTCA) applications continuously run on a time trigger every 5 minutes, or every time a 69 kV or higher voltage breaker has been operated and evaluates LIPA’s system for N-1 Post-contingency violations. Under most circumstances, LIPA is able to resolve Real-time rating exceedances by modifying power flow distribution over its system via six (6) Phase-Angle-Regulators (PARs) and/or dispatch of interconnected generation resources. None of the noncompliant Facilities are part of IROLs or tie-lines with neighboring systems. The de-rated Facilities have not caused a decrease in overall system resources needed to reliably serve LIPA customer load. Furthermore, LIPA’s Reliability Coordinator, NYISO, carries required operating reserves of 1,965 MW and could have adequately addressed potential reliability gaps arising from this violation. No harm is known to have occurred. | To mitigate the violations, LIPA has or will complete the following actions: 1) Corrected ratings for all noncompliant Facilities, communicated them to its Reliability Coordinator and entered them into its EMS for use in actual operation. 2) Reviewed substation drawings for 138 kV BES line terminals into the bus connections. 3) Conducted a field review of 138 kV BES line terminals into the bus connections. 4) Reviewed overhead transmission drawings for the 138 kV BES lines. 5) Conducted a field review of all 138 kV BES Transmission support structures and conductor spans between overhead substation termination and first support structure. 6) Created an internal compliance control, by which documentation for new facilities, or changes/updates to existing facilities, will be peer-checked by a second engineer. 7) Enhanced an existing EMS/SCADA tool to facilitate the correct operation of cables requiring seasonal rating changes by hard-coding the full array of control points that system operators will need to select in order to populate the EMS with ratings that match pump house field configuration(s). 8) Provided formal review of the enhanced process for correctly operating cables with seasonal ratings to System Operators and Transmission Operations staff. 9) Conducted incident review with all operators in Transmission Control Center and all Multi-Station Operators. 10) Performed field check on other pumping plants that were utilizing circulate ratings. 11) Developed design drawings for multiple alarm scheme from the in-scope pump house to the control room. 12) Placed in-scope pump skids into Static Operation Mode with the intention to keep them in this default mode until mitigation is completed. 13) Installed the multiple alarm scheme at the in-scope pump house. 14) Will post additional signage on the Automatic Throw Overs located at all substations with pump houses to alert personnel of impact to pump house and cable mode of operation. This mitigating activity is expected to be completed by May 31, 2024. 15) Will prepare and distribute job aids to both field and operations personnel to provide awareness of the new pump house signage and notifications on circulation status. This mitigating activity is expected to be completed by May 31, 2024. In addition to the above mitigation measures to bring LIPA into compliance and reduce the likelihood of recurrence, LIPA implemented the following additional measures to further enhance FAC-008 compliance, protect Facility Ratings, and improve BES reliability: • LIPA is in the process of purchasing a Facility Ratings software called Cascade Facility Ratings (“CFR”) to enhance LIPA’s compliance with FAC-008. The CFR software solution will consolidate multiple Microsoft Access databases and Excel spreadsheets which currently contain LIPA Facility Ratings. The software will streamline the process by having all facility rating tables in one location and provide timely access to the latest facility ratings for other departments that utilize such facility ratings. The software is expected to be operational in 2025. • LIPA created a new dedicated group to lead and focus on FAC-008 Facility Ratings in November 2022. Currently, a manager and three engineers are assigned and/or hired for this group. Responsibilities include managing overall coordination of processes, procedures and documentation and planning strategic direction associated with NERC FAC-008 related compliance activities, including training of relevant employees on the CFR software. | NPCC considered the following factors in its penalty determination: When assessing the penalty for the violation at issue in this Agreement, NPCC considered whether the facts of the violation constitute repetitive infractions and determined that LIPA had no relevant prior noncompliance with FAC-008-3 R6. LIPA has been cooperative throughout the entire enforcement process for this violation. LIPA provided requested information to NPCC that was detailed, organized, and thorough. LIPA self-reported the violation described in this Agreement. Effective oversight of the BPS reliability depends on Registered Entities self-reporting. As such, NPCC seeks to encourage self-reporting of violations and, therefore, is applying mitigating credit in the instant case. LIPA agreed to settle the violation thereby avoiding a hearing on this matter. A willingness to resolve cases without the need for a trial-type hearing reduces the amount of time and resources that NPCC, NERC, and the FERC would otherwise expend to resolve this violation. Additionally, it is important to promote prompt resolution of enforcement actions so that LIPA can focus on mitigation and reducing risks to reliability.
2024-05-30 | NOC-2831 | SERC | Virginia Electric & Power Company d/b/a Dominion Energy Virginia – Nuclear (DEV-NUC) | NCR09006 | GOP | Settlement Agreement | Neither Admits nor denies | 150000 | 2022-00052 | VAR-002-4.1 | R2; R2.1, R2.2, R2.3 | Moderate | Medium | Severe | Self-Report | 2022-01-10 | 2007-06-18 | 2022-10-14 | 2024-07-18 |  | TBD | DEV-NUC notified SERC that it was noncompliant with VAR-002-4.1 R2. DEV-NUC failed to notify the Transmission Operator (TOP) when it could not continuously maintain its generator voltage schedule for 30 minutes. SERC determined that this issue began under VAR-002-1 and spanned to VAR-002-4.1 On December 14, 2021, while preparing for an upcoming audit, DEV-NUC discovered multiple occasions since 2020 where both of its power stations (four total units) operated outside the assigned voltage schedule for longer than 30 minutes and no notification was made to the TOP. The TOP’s procedure requires that a Generator Owner (GO) notify both the TOP and Transmission Owner (TO) when voltage cannot be maintained within the voltage schedule continuously for 30 minutes. Additionally, the TOP’s procedure requires that the TO assign either the TOP’s default voltage schedule or an alternative voltage schedule that the GO must comply with. The TOP’s default voltage schedule for 500 kV unit is 525 +/- 8 kV and the default voltage schedule for a 230 kV unit is 235 +/- 4 kV. However, in this case, before the Standard became mandatory and enforceable, the TO assigned the following more conservative voltage schedule: for a 500 kV unit 524 +/- 4kV, and for a 230 kV unit, 232 +/- 3 kV. During its audit preparations, DEV-NUC reviewed 2020 and 2021 voltage data from its Systems Operations Center (SOC), which serves as the TO. In this review, it discovered 1,421 instances where voltage exceeded the TO’s assigned schedule for longer than 30 minutes without the proper notifications being made. The SOC data reviewed showed that for DEV-NUC’s three 500 kV units, the maximum upper exceedance was 3.76 kV, and the maximum exceedance duration was 12.9 hours. For DEV-NUC’s one 230 kV unit, the maximum upper exceedance was 4.10 kV, and the maximum exceedance duration was 164.4 hours. Both the SOC and the GO’s power station control rooms independently receive voltage readings. While verifying the SOC voltage data, DEV-NUC compared the data with each power station’s control room voltage data and discovered a discrepancy in the parameters used to monitor the voltage data in the power station control rooms. This discrepancy resulted in the GO’s control room voltage data reading approximately 1-4 kV lower than the actual voltage, which was being correctly relayed to the SOC. As a result, during the voltage schedule exceedances discovered in the 2020 and 2021 SOC data, the power station’s control room operators did not recognize they were operating outside the assigned voltage schedules. After its initial review of the 2020 and 2021 operating data, DEV-NUC continued reviewing all the 2022 and Q1 2023 voltage data from the SOC. In this extended review, DEV-NUC discovered 86 additional voltage schedule exceedances that occurred for longer than 30 minutes without the proper notifications being made. As DEV-NUC began implementing its mitigating activities, it found there was a sharp decline in these additional instances of noncompliance. Specifically, 81 of the 86 additional exceedances occurred at the beginning of 2022, 1 instance occurred in April 2022, and the remaining 4 instances occurred from October 13 through 14, 2022. DEV-NUC did not perform an additional historical review of its voltage data prior to 2020, as it was focused on correcting and mitigating the noncompliance moving forward. However, since the TO’s voltage schedules had not changed for the generating units since the standard’s effective date of June 18, 2007, there was a historical parameter that incorrectly reported the voltage data to the power stations’ control room, there was a lack of controls for maintaining voltage within the voltage schedule, and there was a lack of procedural guidance informing personnel of the requirement to notify the TOP, it was conservatively concluded that the noncompliance began when the standard and requirement first became mandatory and enforceable. The causes of the noncompliance were deficient procedural guidance for the control room operators and deficient voltage monitoring controls. DEV-NUC’s procedural guidance included directions to notify the TO (the SOC) but did not include guidance to notify the TOP when operating outside the voltage schedule for longer than 30 minutes. Additionally, there were ineffective voltage monitoring controls because not only was there not a control to alert the operators when the voltage exceeded the TO's set voltage schedule, the degradation in the analog signal carrying the voltage data over a long distance back to each power station’s control room caused the voltage data to read approximately 1-4 kV lower than the actual voltage. Thus, the power station control rooms were monitoring inaccurate voltage data. This noncompliance started on June 18, 2007, when the standard became mandatory and enforceable and DEV-NUC failed to notify the TOP of voltage schedule exceedances lasting longer than 30 minutes, and ended on October 14, 2022, when DEV-NUC last operated outside the assigned voltage schedule for longer than 30 minutes without making the required notifications. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the BPS. The failure to maintain the set voltage schedule and to inform the TOP of voltage excursions within a timely manner could have delayed the TOP’s ability to respond to deviations in the voltage of the transmission system, potentially resulting in damage to the system or BPS instability. Additionally, the extended duration of the violation and the number of exceedances made without proper notification demonstrates ineffective procedural and detective controls necessary to maintain the required voltage schedule. This failure of its controls resulted in an increased risk to the BPS as DEV-NUC effectively relied on the TOP to notify them if voltage needed to be adjusted in order to maintain reliability. This violation did not pose a serious or substantial risk because although DEV-NUC frequently exceeded the upper bound of the voltage schedule set by the TO, DEV-NUC’s voltage excursions were typically very small and always within 2% of the nominal voltage. Furthermore, during the noncompliance, DEV-NUC was operating under a restrictive voltage schedule, and although it frequently exceed that restrictive voltage schedule, DEV-NUC would have consistently met the default TOP generator voltage if it were operating under that voltage schedule. As a mitigating measure, the TO reevaluated DEV-NUC’s voltage schedules and determined that it was appropriate to apply the TOP’s default voltage schedule. While this voltage schedule adjustment does not negate the historical exceedances of the restrictive schedule, it demonstrates the reduced impact the actual voltage operations over the period of noncompliance would have had on the operation of the BPS. Along with the TOP's backstop of independently monitoring the GO’s voltage and having the ability to request adjustments be made if needed, DEV-NUC and the TO had normal and emergency limit alarms in place to protect the stations’ nuclear safety-related buses from voltage levels that could present a challenge to the operability of equipment important to station nuclear safety. These limits provided a backup to the voltage schedule setpoints so that if the voltage continued to increase or decrease to an unsafe level, an alarm would alert the station operators to initiate action. No harm is known to have occurred. | To mitigate this violation, DEV-NUC has or will perform the following actions: 1) reviewed operational data for Q2 2022-Q1 2023 (all units) to determine adherence to the assigned voltage schedules; 2) developed a plan and scheduled for installation of generator output voltage indication into the nuclear control rooms (plant computer system (PCS)) that matches the SOC voltage indication, which will create a permanent resolution to having a continuously monitored voltage indication that matches the SOC; 3) revised the voltage schedule bandwidth for the 500 kV units from +/- 4 kV to match the PJM default (+/- 8 kV) and revised the voltage schedule bandwidth for the 230 kV unit from 232 +/- 3 kV to 234 +/- 4kV and revised station Operations procedures for the voltage schedule bandwidth changes; 4) installed Bus Voltage Indication Capabilities as a permanent fix that addresses the capability of the nuclear station control rooms to monitor output voltages, including bringing a digital bus voltage signal into the PCS in the control rooms at the nuclear power stations, and migration of the signal into the PCS to allow for user-defined alarms to give continual monitoring of bus voltages with alerts when deviating from the assigned voltage schedules. 5) implemented audio and visual user-defined alarms to alert power station control room personnel prior to the unit reaching the voltage schedule limits; 6) revised applicable site Operations procedures to provide guidance for notification to the TO and TOP and trained on the changes; 7) developed a corrective action to monitor compliance with VAR-002 R2 on a periodic basis, including submitting a condition report to the nuclear corrective action program to create an action for reviewing operational data for compliance with NERC Reliability Standard VAR-002 R2. The reviews will be performed on a quarterly basis until error-free performance has been achieved for one year for all units. After that milestone has been reached, the review will be conducted on one unit per quarter for two years (assuming no periods of operation outside the voltage schedule have been detected). If any period of operation outside the voltage schedule is detected for any unit, the quarterly review will restart from the beginning with an analysis of all units until the error free performance is achieved. The reviews will begin with operational data from Q2 2023; 8) developed VAR-002 R2 focused training to familiarize station Operations personnel, such as system operators, with VAR-002 R2 compliance requirements, including details on when notifications are required for periods of operation outside of the assigned voltage schedules. After initial delivery, this training will be delivered on a three-year basis; 9) developed VAR-002 R2 general awareness training that will familiarize personnel responsible for equipment related to VAR-002 compliance with VAR-002 compliance requirements. This training will be delivered to the target audience on an initial and/or as-needed basis; and 10) developed a process to deliver the voltage schedule and any changes to the generator operators and trained on the new process. | SERC considered DEV-NUC’s compliance history and determined there were no relevant instances of noncompliance. SERC reviewed DEV-NUC’s internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. DEV-NUC, as a Dominion Energy Virginia (DEV) registered entity, has a compliance document that follows guidance provided in the DEV corporate NERC ICP. The DEV ICP covers topics from internal controls, self-assessments, and tools for addressing root cause analysis and extent-of-condition. Although DEV-NUC’s document mentions performance of self-assessments, the actionable requirements for personnel to perform the self-assessment were not clearly defined or owned by responsible groups with adequate dedicated resources. Self-assessments are an important control to help reduce risks to the BPS as they provide a method for reducing the potential duration of a noncompliance and allow for prompt mitigation. However, in this instance, no periodic assessment was conducted for DEV-NUC’s VAR-002 compliance, which resulted in a lengthy duration. As a result, SERC determined that the ICP was not a mitigating factor in the penalty determination. SERC encourages DEV-NUC to review the implementation of self-assessments for its other mandatory compliance requirements as a way to help identify other long-standing historical deficiencies and ensure the controls outlined in the ICP are functioning as intended. DEV-NUC did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit.