## non-CIP SNOPs
Filed_Date | NOC_ID | Region | Registered_Entity_Name | NCR | Reliability_Functions | Notice_of_Confirmed_Violation_or_Settlement_Agreement | Admits_OR_Agrees_and_Stipulates_OR_Neither_Admits_nor_Denies_OR_Does_Not_Contest | Total_Penalty | NERC_Violation_ID | Reliability_Standard | Requirement | Risk_Assessment | Violation_Risk_Factor | Violation_Severity_Level | Discovery_Method | Reported_to_Region_Date | Noncompliance_Start_Date | Noncompliance_End_Date | Mitigation_Expected_Completion_Date | Mitigation_Completion_Date | Date_Regional_Entity_Verified_Completion_of_Mitigation | Description_of_Noncompliance | Description_of_Risk_Assessment | Description_of_Mitigation | Other_Factors_and_Compliance_History_Discussion
2024-07-31 | NOC-2834 | Northeast Power Coordinating Council, Inc. (NPCC) | New York State Electric & Gas Corporation (NYSEG) | NCR07181 | TOP | Settlement Agreement | Admits | 0 | NPCC2020023651 | EOP-008-2 | R6 | Moderate | Medium | Severe | Audit | 2020-07-14 | 2016-07-01 | 2022-12-21 |  | 2024-01-02 | 2024-05-23 | In 2020, NPCC conducted an off-site audit for the period of August 12, 2017, to January 28, 2020, and determined NYSEG was potentially in violation of EOP-008-2 R6 for failing to have Backup Control Center (“BCC”) functionality that was completely independent from the Primary Control Center (“PCC”). Both Control Centers had a shared communication path that a single point of failure at the PCC could have resulted in a significant loss of Remote Terminal Unit (“RTU”) data at both the PCC and BCC. A catastrophic event at the PCC would result in the loss of seven T1 communications lines terminating in a common communications room. This would result in the loss of data from approximately 150 RTUs, 62 of which are associated with Bulk Electric System ("BES") substations. NYSEG has 121 BES RTUs in total. Therefore, a loss of the T1 lines would represent a loss of more than 50% of NYSEG’s BES RTUs. A temporary solution with NYSEG’s telecommunication vendor was pursued but could not be implemented. Priority was not given to a permanent solution delaying the remediation of the noncompliance. The root cause of this violation was a failure to implement planned infrastructure changes in a timely manner. The issue was first discovered during the prior 2017 audit and identified as an Area of Concern (“AOC”). NYSEG developed a plan to address the AOC, by first pursuing a solution with its telecommunication vendor. However, the vendor first postponed implementation, and later advised NYSEG in December 2019 that the vendor could no longer support the solution as designed. Due to the vendor delay and failed execution of the temporary solution, NYSEG pivoted to planning and implementing a permanent solution, which was in the planning stages prior to the 2020 audit. However, effective internal controls were not in place to ensure the required work was given the priority or necessary management oversight to complete. As a result, priority was not given to the permanent solution, resulting in a longer violation duration. NPCC determined that this violation spans multiple versions of the Reliability Standard as follows: • EOP-008-1 R6, from July 1, 2016 (the date NYSEG registered as a Transmission Operator), until March 31, 2019 (Standard’s retirement date); • EOP-008-2 R6, from April 1, 2019, until December 21, 2022, when NYSEG completed its Optical Signal Generator Fiber replacement improvement project, which allowed the BCC to operate independently from the PCC. NPCC further determined that, for purposes of this violation, there was no substantive change in NYSEG’s compliance obligations under the two applicable Standards/Requirements. | NPCC determined that the violation posed a moderate risk to the reliability of the Bulk Power System (“BPS”) based on the following factors. Failure to have BCC functionality independent of the PCC increases the potential impact on the BPS by reducing NYSEG's situational awareness and removing its ability to operate remotely in the event a control center becomes inoperable. If the PCC were to suffer a catastrophic event, or otherwise become inoperable, it would likely be a long duration event and would impact data provided to both NYSEG and its RC, the New York Independent System Operator ("NYISO"). During this time, NYSEG would have no visibility of its system, potentially resulting in a complete loss of NYSEG’s BES. This is a long duration violation lasting approximately 6.5 years. The risk is reduced because the likelihood of a catastrophic event occurring at the PCC is low. If an event did happen in which the 62 BES RTUs went down, the impact would affect NYSEG’s operators’ ability to monitor the system. However, even if all seven T1 lines were lost as a part of NYISO’s area, NYISO and its neighboring TOPs/Balancing Authorities would retain the ability to monitor their respective systems. In addition, no Interconnection Reliability Operating Limits were impacted by this violation. The Violation Severity Level and Violation Risk Factor are severe and medium, respectively. No harm is known to have occurred as a result of this noncompliance. | To mitigate the violation, NYSEG has completed the following actions: 1) Migrated T1 circuits to remove the single point of failure; 2) Created a new NERC compliance solution tool to monitor compliance projects and help ensure schedules are maintained and potential roadblocks are appropriately mitigated; 3) Updated project management procedure to specify if changes to a project schedule are required, a documented review of the Project Management Plan must take place and the changes incorporated; and 4) Trained applicable personnel on new NERC compliance solution tool. | NPCC considered the following factors in its penalty determination: 1) Compliance History When assessing the penalty for the violation at issue in this Agreement, NPCC considered whether the facts of the violation constitute repetitive infractions and determined that NYSEG had no relevant prior noncompliance with EOP-008-2 and no other aggravating prior noncompliance. 2) Cooperation NYSEG was cooperative throughout the entire enforcement process and provided requested information to NPCC that was detailed, organized, and thorough. 3) Settlement NYSEG agreed to settle this matter. A willingness to resolve cases without the need for a trial-type hearing reduces the amount of time and resources that NPCC, NERC, and the Federal Energy Regulatory Commission would otherwise expend to resolve the violation. Additionally, it is important to promote prompt resolution of enforcement actions so that NYSEG can focus on mitigation and reducing risks to reliability. 4) Other Factors NPCC elevated the disposition of this moderate risk violation to a Spreadsheet Notice of Penalty (SNOP) due to the discovery method and length of time NYSEG took to come into compliance after it became aware of the issue in 2017. However, due to the factors above and the risk assessment, NPCC determined that a $0 penalty was appropriate for this violation.