## non-CIP SNOPs
Filed_Date | NOC_ID | Region | Registered_Entity_Name | NCR | Reliability_Functions | Notice_of_Confirmed_Violation_or_Settlement_Agreement | Admits_OR_Agrees_and_Stipulates_OR_Neither_Admits_nor_Denies_OR_Does_Not_Contest | Total_Penalty | NERC_Violation_ID | Reliability_Standard | Requirement | Risk_Assessment | Violation_Risk_Factor | Violation_Severity_Level | Discovery_Method | Reported_to_Region_Date | Noncompliance_Start_Date | Noncompliance_End_Date | Mitigation_Expected_Completion_Date | Mitigation_Completion_Date | Date_Regional_Entity_Verified_Completion_of_Mitigation | Description_of_Noncompliance | Description_of_Risk_Assessment | Description_of_Mitigation | Other_Factors_and_Compliance_History_Discussion
2025-03-31 | NOC-2845 | SERC | Georgia Transmission Corporation (GTC) | NCR01249 | TO | Settlement Agreement | Admits | $0 | 2022-01538 | FAC-008-5 | R6 | Moderate | Medium | Lower | Self-Report | 2022-10-12 | 2007-06-18 | Present | 2025-12-31 | TBD | TBD | GTC notified SERC that it was noncompliant with FAC-008-5 R6. GTC failed to have Facility Ratings that are consistent with the associated Facility Ratings methodology (FRM). SERC determined that this noncompliance began under FAC-009-1 R1 and spanned to FAC-008-5 R6. On July 21, 2022, during an internal verification of equipment rating information for all Bulk Electric System (BES) substation equipment in accordance with the NATF Ratings Practices recommendations, GTC identified an incorrect Facility Rating. During a review of verified drawings and equipment logs for the Bolingbroke substation, a looped through substation on the Forrest Road-Rumble Road 115kV line, GTC discovered that the Line Elements Database (LED), owned and maintained by another registered entity, did not have the correct jumpers or bus listed. In 1999, Bolingbroke was converted from 68 kV to 115 kV as part of a transmission line conversion. GTC determined that the bus and jumpers were likely installed during that project. GTC notified the other entity (Georgia Power Company or GPC) of the incorrect equipment and when this listing in the LED was corrected, the Forrest Road – Rumble Road 115 kV line was de-rated by 30% on July 21, 2022. On August 12, 2022, the Bolingbroke bus and jumpers were replaced with higher capacity conductor and the previous line rating was subsequently restored. As a result of this finding, GPC initiated a walk-down of all 77 GTC owned Transmission Substations, and a review of an additional 622 BES stations which includes distribution stations that are part of the continuous BES path due to transmission lines being looped into the stations, distribution stations with BES-level capacitor banks, and approximately 150 non-BES radial stations. At the time of the Self-Report, GTC had completed the walk-down of the 77 Transmission Substations. As of July 1, 2024, GTC has completed a desktop review of all 622 BES stations and follow-up field verifications for 13 of the stations where the desktop review identified possible documentation discrepancies. In total, GTC identified 10 incorrect Facility Ratings. All incorrect ratings resulted in derates between 1% and 32%. Some incorrect ratings began June 18, 2007, the effective date of the Standard. Nine of the derates were on the 115 kV system and one of the derates was on the 230 kV system. In all instances, there were inconsistencies between GTC’s internal drawings, equipment databases, and the LED related to certain line termination equipment. GTC did not operate above the correct Facility Rating in any of the instances. In addition to GTC’s assessments, the SERC audit team conducted a FAC-008-5 audit in 2023 that included a walk-down assessment of two 500 kV substations. The audit team did not identify any instances of noncompliance. The cause of this noncompliance was ineffective controls. Procedures used in the past to communicate Facility Ratings were insufficient to ensure clear communications. Communication of BES sheets did not exist at the time of the noncompliance. Ratings were communicated via project drawings. This noncompliance started on June 18, 2007, when FAC-009-1 R1 became enforceable on GTC and will end on December 31, 2025, when GTC completes its verification of the circuit breaker CT ratios at the transmission substations. | This noncompliance posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System. GTC’s failure to determine the correct Facility Rating increased the potential for it to operate the Facility in excess of its capacity rating, thereby creating the opportunity for equipment damage and Facility outages. However, the risk from the noncompliance was reduced because GTC identified only 10 incorrect Facility Ratings. All incorrect ratings resulted in derates between 1% and 32% with nine of the derates on the 115 kV system and only one of the derates was on the 230 kV system. GTC did not operate above the correct Facility Rating in any of the instances. No harm is known to have occurred. | To mitigate this noncompliance, GTC has or will perform the following actions: 1) updated GTC's Project Review Checklist to include the Physical Design group verifying that the Transmission Line sizes on the drawings match the actual sizes verified by the Transmission Line group; 2) completed Extent of Condition. There are 13 substations identified to conduct field audits before completion of the BES baseline effort; 3) revised the BES Substation Ratings Verification Procedure to incorporate the creation of a BES substation database that records and verifies the transmission elements of a substation; 4) will verify circuit breaker CT ratios at transmission substations. The status and results of the verifications will be submitted to SERC on a quarterly basis; 5) corrected its internal records, as necessary, and notified Georgia Power of the actual element rating in order for them to update the Line Element Database. All identified discrepancies have been updated; 6) developed process to create and communicate BES Sheets. GTC developed a procedure used to create new and modified BES Substation Spreadsheets that track the equipment ratings of the elements within the substation along with how the sheet is included in the drawing packages and submitted to Georgia Power Company. This new process provides a more concise summary of equipment ratings that will help minimize data errors in the Line Element Database that impact planning and operational models; and 7) trained on processes to create and communicate BES sheets. | GTC self-reported the violation. Effective oversight of the reliability and resilience of the BES depends upon self-reporting by Registered Entities. SERC seeks to encourage self-reporting of offenses and, therefore, applied mitigating credit. GTC has been highly cooperative throughout the entire enforcement process relating to this violation. Throughout the enforcement process, GTC voluntarily provided SERC with information that was timely, detailed, thoughtful, organized, and thorough. GTC fully cooperated in SERC’s investigation of the violation and all associated mitigating activities and openly shared information regarding its processes, procedures, internal controls, assets, systems, and organization. Therefore, SERC applied mitigating credit. SERC considered the GTC’s compliance history and determined that there were no relevant instances of noncompliance.
2025-03-31 | NOC-2846 | SERC | Municipal Electric Authority of Georgia (MEAG_Power) | NCR01278 | TO | Settlement Agreement | Admits | $0 | 2022-50001 | FAC-008-5 | R6 | Minimal | Medium | Lower | Compliance Audit | 2022-06-16 | 2007-06-18 | 2022-10-25 | 2025-12-31 | TBD | TBD | SERC determined that MEAG_Power was noncompliant with FAC-009-1 R1. MEAG_Power failed to have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology (FRM). SERC submitted the noncompliance under FAC-008-5 R6 due to Align requirements. SERC determined that this noncompliance started under FAC-009-1 R1 and spanned to FAC-008-5 R6. On March 4, 2022, SERC sent MEAG_Power an audit notification letter notifying it of a compliance audit scheduled for June 20, 2022 through June 24, 2022 covering the period of September 29, 2020 through March 4, 2022. During a walk down of MEAG_Power’s facilities, the SERC audit team observed installed equipment in the field that was not included in the MEAG_Power Facility Ratings table provided and not considered in the Facility Rating in accordance with the MEAG_Power FRM. The audit team determined that MEAG_Power omitted all the jumpers, single conductor, and name plate size of a switch at Wansley 230 kV #9A, Wansley 230 kV #9B, and Wansley 230 kV #9ST. The omitted transmission elements were above the Facility Rating limit, and therefore, they did not impact the Facility Rating. The audit team determined that the Wansley 230 KV station was the only MEAG_Power location where transmission elements were omitted, and all other evidence reviewed for the sampled locations were accurate. Following the audit, SERC issued a request for information (RFI) which required MEAG_Power to conduct a walk-down assessment of eight additional Transmission stations. During this assessment, MEAG_Power evaluated 387 elements and identified one additional incorrect rating which did impact the Facility Rating and one incorrect element which did not impact the Facility Rating. The incorrect rating resulted in a 10% derate on a 115 kV line. MEAG_Power did not exceed the correct rating in real-time operation. In 2017, as in internal control, MEAG_Power completed a walk-down of Facilities, which did not include the substations in question, which the audit team identified as a positive audit observation and an industry best practice. The cause of this noncompliance was ineffective controls. For the audit finding, the internal control established was not followed to ensure all applicable elements were included in the Facility Rating database. For the RFI finding, MEAG_Power had incorrect ratings on the diagrams that MEAG_Power used to rate the switches for the element rating determination. The nameplates for the switches were located on the switch frame above the 115 kV bus and due to the location and age, the nameplates could not be read with binoculars from the ground and the 2017 walk-down did not include the substation in question. For the 2022 walk-down, MEAG_Power attached a camera to a hot stick to capture the nameplate data. This noncompliance started on June 18, 2007, when MEAG_Power failed to rate its Facilities in accordance with its FRM and ended on October 25, 2022, when MEAG_Power rated its Facilities in accordance with its FRM. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System. MEAG_Power’s failure to establish Facility Ratings consistent with its FRM could result in violations of System Operating Limits, unnecessary facility trips, damage to facilities, and erroneous planning. However, the risk from the noncompliance was reduced because the incorrect rating was limited to a single 115 kV Facility that required a 10% derate. The correct Facility Rating was 1,284 amps and the maximum loading within the last year was 764 amps. In addition, on August 17, 2021, MEAG_Power implemented a process documented in its Procedure for Updating the Facility Ratings Database internal control which requires a substation walk-down prior to close-out for any project in a substation containing Bulk Electric System equipment. Also, in 2017, as in internal control, MEAG_Power completed a walk-down of certain Facilities, which the audit team identified as a positive audit observation and an industry best practice. No harm is known to have occurred. | To mitigate this noncompliance, MEAG_Power has or will perform the following actions: 1) informed the System Operator regarding the missing elements and added Wansley #9 jumpers and conductors to the “MEAG Power’s Facility Ratings Database” and the System Operator updated the "Integrated Transmission System (ITS) Line Ratings Database". The System Operator also updated their "Static Rating Table" to include the missing jumper type. The "Static Rating Table" is an element rating library maintained by the System Operator (TCC). MEAG_Power verified that all of the applicable elements at Wansley #9 were captured in its Facility Ratings Database; 2) updated the "MEAG Power Facility Ratings Database" and informed the System Operator to update the "ITS Line Ratings Database". The System Operator acknowledged the new ratings and communicated the changes to the Georgia ITS owners via the "System Operator Memo No. 42"; 3) participated in "Facility Ratings (NERC FAC-008) Change Management" training by the System Operator on the method of informing the TCC when a BES element has been replaced as a result of a planned, unplanned, or emergency work. The training outlines the workflow for requesting system changes and approval activity needed by the TCC before releasing a work request for a project. This process ensures accurate and proper coordination of facility ratings on the ITS. On an ongoing basis, MEAG_Power participates in the FAC-008 Facility Rating Working Group of the ITS which develops best practices for the NERC compliance regarding facility ratings; and 4) will develop a checklist (Field Visual Rating Verification for BES Elements - breakers, bus work, line traps, switches, and transformers) which includes FAC-008 elements. This checklist will be developed to prevent instances such as Wansley #9 and Marietta #10 from reoccurring. This checklist will require visual inspections as well as digital imagery evidence of the nameplates, and the elements. The checklist will be used to insure: a) Engineering department is notified of the proper changes needed to update engineering drawings. b) There are no missing elements or discrepancies between the checklist and "MEAG Power Facility Database". c) The System Operator has been updated with the corrected or added element ratings. Beginning in the third quarter of 2024, with an expected completion date of December 31, 2025, MEAG_Power will perform walkdowns of all its BES elements (74 locations) applicable to FAC-008 using this checklist and MEAG_Power will report any discrepancies it discovers to SERC on a quarterly basis using the format requested by SERC and will indicate whether or not the discrepancies impacted the Most Limiting Element (MLE) or Facility Rating and will report discrepancies where elements were not rated in accordance with the Facility Ratings methodology but did not impact the MLE or Facility Rating. | MEAG_Power has been highly cooperative throughout the entire enforcement process relating to these violations. Throughout the enforcement process, MEAG_Power voluntarily provided SERC with information that was timely, detailed, thoughtful, organized, and thorough. MEAG_Power fully cooperated in SERC’s investigation of the violations and all associated mitigating activities and openly shared information regarding its processes, procedures, internal controls, assets, systems, and organization. Therefore, SERC is applying mitigating credit. SERC considered MEAG_Power’s compliance history and determined there were no relevant instances of noncompliance.