## Redacted for Public Posting
Reported Quarter and Year | Regional Entity | Registered Function(s) | Nominal Voltage Rating of the Circuit (kV) | Has the reported circuit experienced a previous vegetation-related transmission outage within the last eight reporting quarters? | Element of IROL or Major WECC Transfer Path? | Outage Start Date | Outage Duration (mins) | Detailed Description of the Cause of the Outage | Category Associated with the Sustained Outage | If the vegetation causing the outage was located outside of the ROW, provide the horizontal distance to the edge of the ROW. | If the vegetation causing the outage was located outside of the ROW, provide the horizontal distance to the nearest conductor. | Tree Type | Tree Height (ft) | Tree Condition | Mitigation/remediation actions taken by Registered Entity to address recurrence of the contact/encroachment.
Q3 2024 | SERC | GO, TO | 230 | no | no | 2024-08-26 | 709 | A healthy red oak uprooted during a high wind event and fell onto the line from outside the right of way. | 3 | 17 | 54 | Red Oak | 92 | Healthy | Adjacent trees were inspected and no additional concerns were found.
Q3 2024 | SERC | GO, TO | 230 | no | no | 2024-09-27 | 16812 | A healthy red oak uprooted during Storm Helene and fell on the outside conductor resulting in line locking out. | 3 | 20 | 55 | Red Oak | 86 | Healthy | Location was inspected to identify/mitigate any vegetation concerns
Q3 2024 | SERC | GO, TO | 230 | no | no | 2024-08-13 | 642 | An off the right-of-way an alive pine tree with root rot made contact and hung on the line. The tree was removed and the line was returned to service. The soil conditions were dry. | 3 | 4 | 46 | Sweetgum | 82 | Alive | Removed one dead pine and spot trimmed 2 hardwoods
Q3 2024 | SERC | GO, TO | 230 | no | no | 2024-08-17 | 3699 | An off the right-of-way alive and healthy oak tree made contact and hung on the line. The tree was removed and the line was returned to service. Soil condition were wet and thunderstorms were in the area. | 3 | 21 | 56 | Oak | 98 | Alive | The tree was in a recent cut over. The remaining residual trees, left by the loggers, were cut so they would not fall and hit the line.
Q3 2024 | SERC | GO, TO | 230 | no | no | 2024-09-17 | 550 | A 100-foot healthy pine tree fell from 29 feet off right-of-way. | 3 | 29 | 89 | Pine | 100 | Healthy | Patrolled and found no other trees that required work at this time.
Q3 2024 | SERC | GO, TO | 230 | no | no | 2024-08-19 | 963 | A healthy willow tree was struck by lightning in a storm fracturing the tree trunk. A limb leaned toward the conductor and made contact due to the high wind. | 3 | 7 | 39 | Willow | 50 | Healthy | The tree was removed and the grounds were patrolled
Q2 2024 | SERC | GO, TO | 230 | no | no | 2024-04-10 | 432 | A 20" diameter red oak split and uprooted fell into a three-phase distribution circuit and the top of the tree rested in the line across the outside conductor. The tree was a 3-stem codominant trunk, with the codominant union orignating at just below the ground level and extending up to about 3-4 feet above ground. The three stems were each approximatley 20"+ and approximatly 90-100 feet tall. All 3 stems at the codominant union, with the one trunk that was facing the right of way, falling at a 90-degree angle to the link. There were visable broken roots below the ground. | 3 | 43 | 78 | Red Oak | 100 | Co-Dominant stem | DEV-ET personnel walked adjoining spans on same side of the ROW to inspect the trees. The area is in a residential neighborhood resulting in a lminted woodline in that area. Six additional trees have been marked as potential hazard trees and will be taken down.
Q2 2024 | SERC | GO, TO | 230 | no | no | 2024-05-27 | 960 | A 22" diameter red oak approximatly 85 feet tall failed at roughly 35 feet from the ground fell across the line pinning both phases to the ground. This area experienced sustained and heavy wind for several days leading to several uprooted trees in the surrounding area. The tree was a healthy and full crown and no visible defects from the groun. | 3 | 1 | 36 | Red Oak | 85 | This tree had minor fungal growth about 35 feet up the main stem where it browk and fell into the ROW. Within the tree rot was visible only after the tree broke in half. | DEV-ET personnel performed a visiual insepction of the surrounding spans in this area. A tree crew was sent to the area to clean up the fall in, remove a dead tree located outside the ROW, and remove a Virgina Pine that was leaning due to the same wind storm.
Q2 2024 | SERC | GO, TO | 345 | no | no | 2024-05-28 | 93 | A 92ft oak tree fell from outside the right of way (ROW) due to erosion around the roots. | 3 | 17 | 68 | OAK | 92 | Erosion around the root | NA
Q2 2024 | SERC | GO, TO | 230 | no | no | 2024-04-03 | 839.53 | A live tree uprooted off right of way (ROW) causing damage to outside conductor. There was storms and high winds 24 hours prior to tree failure. | 3 | 15 | 62.5 | sweet gum | 85 | live, sound | Performed vegetation patrol of the immediate area.
Q2 2024 | SERC | GO, TO | 230 | no | no | 2024-05-10 | 12 | A tall oak tree, approximately 100', fell at an angle toward the line in a low area due to the wind and rain from a storm. The tree top brushed against "A" and "C" phase conductors causing the line to trip and lock out. The tree was located approximatly 35' off the right of way (ROW) and 100' south of the structure. | 3 | 35 | 61 | Oak | 100 | live and healthy | Lidar and ground expections performed per Transmission Vegetation Management Plan (TVMP). Additional ground inspection performed for this section of line to identify any additonal vegetation concerns.
Q2 2024 | SERC | GO, TO | 230 | no | no | 2024-05-30 | 902 | A dead oak tree fell during a thunderstorm with high winds. | 3 | 8 | 40 | Oak | 70 | dead oak tree | Foot patrol the area and no findings
Q2 2024 | SERC | GO, TO | 230 | no | no | 2024-06-01 | 735 | A healthy pine tree fell due to high winds in a thunder storm | 3 | 15 | 47 | Pine | 85 | healthy pine tree | Foot patrol the area and no findings
Q2 2024 | SERC | GO, TO | 230 | no | no | 2024-04-11 | 1026 | A small green pine tree with an unhealthy hollow base fell on the conductor in a thunderstorm event. | 3 | 8.5 | 50.5 | Pine | 75 | unhealthy pine tree with hollow base | Foot patrol the area and no findings
Q2 2024 | WECC | GO, TO | 230 | no | no | 2024-06-27 | 273 | A live spruce tree fell into the line during thunderstorm with heavy rains and winds. That cleared itself. The line was tested and returned to service. | 3 | 1 | 41 | Spruce | 110 | Live | Crew investigated the area. This section of the line in on the national forest. The entity plans to work with the authorities to plan for mechanical re-treatment in 2025 or 2026.
Q2 2024 | RF | TO | 345 | no | no | 2024-06-25 | 1650 | Severe thunderstorm knocked down the tree from outside the ROW | 3 | 30 | 80 | Shagbark Hickory (Deciduous, hardwood) | 90 | healthy | Removed tree. The entity's TVMP includes budget for danger tree removal. The entity expects to remove danger trees when they are found during inspections.
Q1 2024 | SERC | GO, TO | 500 | No | yes | 2024-03-20 | 24430 | During a period of sustained wind, a contact between the conductor and a Hickory tree located 23 feet outside of the ROW has occurred. | 3 | 23 | 61 | Hickory | 49 | Healthy | Tree was removed and surrounding area inspected.
Q1 2024 | SERC | GO, TO | 230 | No | No | 2024-01-14 | 199 | A healthy Pine tree 31 feet outside of the ROW made contact with a 230 kV line. The tree was removed and the line was returned to service. Soil conditions were wet and rain and high winds were in the area. | 3 | 31 | 36 | Pine | 87 | Alive | Two trees next to the tree in question were cut down due to cankers.
Q1 2024 | SERC | GO, TO | 230 | No | No | 2024-02-28 | 1138 | A live Hickory tree with root rot made contact a 230 kV line. The tree was removed and the line was returned to service. Soil conditions were wet and storms and strong winds were in the area. | 3 | 10 | 53 | Hickory | 80 | Alive | No additional issues observed.
Q1 2024 | SERC | GO, TO | 230 | No | No | 2024-02-11 | 326 | As a result of winds and saturated soil conditions, several large hardwood trees uprooted and fell on a 40 foot tall hardwood tree located 3 feet outside of the ROW, causing it to uproot and contact the conductor. | 3 | 3 | 31 | Maple | 50 | Healthy | Tree was removed and surrounding area inspected.
Q1 2024 | SERC | GO, TO | 230 | No | No | 2024-03-17 | 154 | A dead Virginia pine broke about 4 feet from the base and contacted the line. | 3 | 6 | 61 | Virginia pine | 85 | External decay | Tree was removed and surrounding area inspected.
Q1 2024 | SERC | GO, TO | 230 | No | No | 2024-01-09 | 420 | During thunderstorm and high winds, a pine tree between broke off during a thunderstorm and fell into the transmission line. The three was removed off the line. Neither the conductor or structures sustained any damage. | 3 | 8 | 42 | Pine | 74 | The roots of the pine tree showed sign of deterioration due to an old injury at the ground line | Surrounding area was foot patrolled. No findings.
Q1 2024 | WECC | GO, TO | 230 | Yes | No | 2024-01-10 | 480 | A Douglas fir tree uprooted due to high wind and soft soil and fell into the line. | 3 | 20 | 40 | Douglas Fir | 155 | Alive | No additional issues observed.
Q1 2024 | WECC | GO, TO | 230 | Yes | No | 2024-01-13 | 1431 | A Western hemlock uprooted due to high wind and soft soil and fell into the line. | 3 | 23 | 43 | Western Hemlock | 68 | Alive | No additional issues observed.
Q1 2024 | WECC | GO, TO | 230 | Yes | No | 2024-02-16 | 3060 | During high winds. a large cottonwood tree broke off and fell into a Douglas fir, causing it to break off and contact a line. | 3 | 7 | 27 | Douglas Fir | 85 | Alive | No additional issues observed.
Q1 2024 | WECC | GO, TO | 60 | No | Yes | 2024-03-01 | 2981 | During heavy snow, a pine tree broke off and struck line. | 3 | 33 | 43 | Lodgepole pine | 100 | Healthy | Inspection completed. No additional issue was identified.
Q1 2024 | WECC | GO, TO | 230 | No | No | 2024-03-05 | 1 | During heavy snow, a large cedar tree uprooted from outside of the ROW and struck line. | 3 | 53 | 97 | Incense Cedar | 114 | Live and healthy | Inspection conducted to in vicinity of impacted tree to identify any additional trees.
Q1 2024 | WECC | GO, TO | 230 | No | N0 | 2024-01-08 | 630 | During high wind and heavy rain, a hemlock tree 35 feet off the ROW broke and fell into the line. | 3 | 35 | 35 | Western Hemlock | 117 | Good | Surrounding area was inspected for signs of forest decline.
Q4 2023 | SERC | TO | 230 | No | No | 2023-10-14 | 3862 | The top portion of a dead Sweetgum tree that was outside the right-of-way fell into the line. | 3 | 12 | 52 | Sweetgum | 70 | Dead | Tree was removed and surrounding area inspected.
Q3 2023 | NPCC | TO | 115 | No | Yes | 2023-07-15 | 8 | A healthy Cottonwood tree was uprooted on the south side of the right-of-way during a thunderstorm. The saturated ground surrounding the tree and the added wind caused the tree to fall. | 3 | 41 | 78 | Cottonwood | 99 | Healthy | Tree was removed and surrounding area inspected.
Q3 2023 | NPCC | TO | 345 | No | No | 2023-09-07 | 1413 | A Locust tree from outside the right-of-way fell into the conductor during a severe wind and rain storm. | 3 | 10 | 60 | Locust | 80 | Healthy | The tree was removed. No damage was done to the conductor. The entire line was patrolled with no additional issues identified prior to restoring.
Q3 2023 | RF | TO | 230 | No | No | 2023-09-24 | 2928 | An outwardly healthy Virginia Pine tree uprooted during a wind event and fell into the line. Upon further examination, the roots showed signs of potential root decay and may have contributed to the fall. | 3 | 39 | 115 | Virginia Pine | 103 | Outwardly healthy | When investigating the fault, surrounding spans were reviewed to ensure there were no other existing tree conditions related to this incident. No other vegetation concerns were identified.
Q3 2023 | RF | TO | 230 | No | No | 2023-07-22 | 234 | A Hickory tree from outside the right-of-way split out and fell into the conductor. It made contact but self-cleared from the line. | 3 | 30 | 65 | Hickory | 100 | Healthy | Tree was removed and surrounding area inspected.
Q3 2023 | SERC | TO | 230 | No | No | 2023-07-14 | 461 | An oak tree from outside the right-of-way fell into the line during a storm. The tree's root system was damaged when the property owner logged the surrounding area, leavening nothing to sustain the tree's roots during the storm. | 3 | 14 | 60 | Oak | 75 | Good | Two adjacent trees in the same wet area were cut down to avoid similar falls into the right-of-way.
Q3 2023 | SERC | TO | 230 | No | No | 2023-07-30 | 150 | A Pine tree from outside the right-of-way fell into the line during stormy weather conditions. | 3 | 16 | 46 | Pine | 93 | Living and otherwise healthy | Tree was removed and surrounding area inspected.
Q3 2023 | SERC | TO | 230 | No | No | 2023-08-07 | 243 | A Pine tree from outside the right-of-way fell into the line during stormy weather conditions. | 3 | 7 | 45 | Pine | 75 | Green | Tree was removed and surrounding area inspected.
Q2 2023 | SERC | GO, TO | 230 | No | No | 2023-06-03 | 371 | A Hackberry tree from off the right-of-way broke in a thunderstorm and fell into the line. Neither the conductor nor the structures sustained any damage. | 3 | 7 | 39 | Hackberry | 55 | Healthy | The tree was removed off the line. A patrol of the area did not find any other damaged trees.
Q2 2023 | SERC | GO, TO | 230 | Yes | No | 2023-05-27 | 283 | An alive and healthy Sweetgum tree from off the right-of-way made contact and hung on the line during a thunderstorm. | 3 | 24 | 58 | Sweetgum | 86 | Alive and healthy | No additional vegetation issues were observed. The tree was removed and the line returned to service.
Q2 2023 | SERC | TO | 230 | No | No | 2023-04-30 | 200 | A live Northern Red Oak with internal decay fell from off the right-of-way and pinned the line to the ground during a high wind event. | 3 | 1 | 43 | Northern Red Oak | 102 | Live, internal decay not visible from outside | The surrounding area was patrolled for other storm-related hazards.
Q2 2023 | SERC | TO | 230 | No | No | 2023-04-01 | 260 | A Sweetgum tree with decay on the backside of tree fell onto the line from off the right-of-way during a thunderstorm. | 3 | 8 | 39 | Sweetgum | 65 | Decay on backside | The immediate area was patrolled to identify any additional hazardous trees.
Q2 2023 | SERC | TO | 230 | No | No | 2023-04-01 | 275 | A Hickory tree with root decay and a light systemic fungal infection from off the right-of-way fell into the line. | 3 | 25 | 70 | Hickory | 91 | Root decay and a light systemic fungal infection | The line crew patrolled the area and followed up by performing an aerial patrol. No hazards were observed during the patrols.
Q1 2023 | RF | TO | 230 | No | No | 2023-03-03 | 1564 | An off-corridor, outwardly healthy, White Pine tree broke at the trunk 12' from the ground. The tree appeared healthy externally, but upon examination after failure, the tree was found to have some internal decay; however, no internal decay was observed at the point of failure. The tree failed during a high wind weather event and subsequently fell into the ROW contacting the conductor. Radar indicates that the outage location experienced high winds in the range of 41-44 mph at the time of the outage, which exceeds the threshold for the high wind weather exclusion. | 3 | 11 | 65 | White Pine | 94 | Healthy | During the investigation, surrounding spans were reviewed, but no further vegetation threats were identified.
Q1 2023 | WECC | GO, TO | 230 | Yes | No | 2023-01-04 | 1465 | During a high wind event, a healthy Douglas Fir was uprooted and blown into the line. | 3 | 18 | 38 | Douglas Fir | 85 | Alive | Tree was removed and surrounding area inspected.
Q1 2023 | WECC | GO, TO | 230 | Yes | No | 2023-01-09 | 1916 | During a high wind event, a Douglas Fir with root rot was uprooted and blown into the line. | 3 | 30 | 50 | Douglas Fir | 75 | Alive with root rot | Tree was removed and surrounding area inspected.
Q1 2023 | WECC | TO | 230 | No | No | 2023-03-28 | 1346 | A Ponderosa Pine was snow loaded and fell into the line due to a recent atmospheric river event. | 3 | 8 | 60 | Ponderosa Pine | 75 | Healthy | Tree was removed and surrounding area inspected with LiDAR.
Q1 2023 | WECC | TO | 230 | No | No | 2023-03-28 | 373 | A dead Lodgepole Pine off the right-of-way in saturated soil conditions with tree leaning resulted in the roots breaking and the tree landing on the conductor. | 3 | 5 | 38 | Lodgepole Pine | 70 | Dead | The dead tree, as well as an additional tree at the site, were removed The surrounding area was survey for other potential hazards.
Q4 2022 | NPCC | TO | 115 | No | Yes | 2022-12-03 | 1486 | An Ash tree that was dead from the effects of Emerald Ash Borers was uprooted during high winds and fell into the line from outside the right-of-way. | 3 | 18 | 58 | Ash | 80 | Dead from Emerald Ash Borers | Tree was removed and area inspected for other dead trees.
Q4 2022 | SERC | TO | 230 | No | No | 2022-12-23 | 268 | During a thunderstorm, a Red Oak fell onto a conductor from outside the right-of-way. | 3 | 1 | 43 | Red Oak | 90 | Alive and healthy | Tree was removed and surrounding area inspected for other storm-related hazards.
Q4 2022 | SERC | GO, TO | 230 | No | No | 2022-10-18 | 499 | During a thunderstorm, a Red Oak fell into the line from outside the right-of-way. Upon investigation, it was the determined there was internal decay. | 3 | 59 | 99 | Red Oak | 110 | Internal decay | Tree was removed and surrounding area inspected.
Q4 2022 | WECC | GO, TO | 230 | Yes | No | 2022-11-04 | 2768 | During a high wind event, a healthy Western Hemlock was blown into the line. | 3 | 25 | 50 | Western Hemlock | 90 | Alive and healthy | Tree was removed and area inspected, at which time a separate 60-foot-tall Western Hemlock also outside the right-of-way was discovered on the line.
Q4 2022 | WECC | GO, TO | 230 | No | No | 2022-11-04 | 2755 | During a high wind event, a healthy Douglas Fir was blown into the line. | 3 | 15 | 36 | Douglas Fir | 120 | Alive and healthy | Tree was removed and area inspected, at which time a separate 110-foot-tall Western Red Cedar also outside the right-of-way was discovered on the line.
Q4 2022 | WECC | GO, TO | 230 | Yes | No | 2022-12-08 | 1303 | Heavy snow load caused a tree to break off at the base and fall into the line. | 3 | 10 | 35 | Western Hemlock | 65 | Alive and healthy | Tree was removed and surrounding area inspected.
Q4 2022 | WECC | GO, TO | 230 | Yes | No | 2022-11-17 | 1183 | A large Douglas Fir at the edge of the right-of-way lost its codominant tops in gale force winds, one of which made contact with and pinned down the line. | 3 | 1 | 28 | Douglas Fir | 110 | Codominant tops 67 feet up the trunk, otherwise alive and healthy | Tree was removed and surrounding area inspected.
Q4 2022 | WECC | GO, TO | 230 | Yes | No | 2022-12-22 | 1419 | A healthy Douglas Fir tree standing on the uphill side of a creek blew over in high gusty winds, compromising two Alder trees. All three trees struck the line. | 3 | 55 | 73.5 | Douglas Fir | 124 | Alive and healthy | Tree was removed. An annual inspection conducted earlier in the year showed no other signs of concern.
Q4 2022 | WECC | GO, TO | 230 | Yes | No | 2022-12-27 | 1623 | A healthy Alder tree in sandy soil on a steep hillside was uprooted in heavy rains and gusty winds and fell into the line. | 3 | 19 | 55 | Red Alder | 80 | Alive and healthy | Tree was removed. An inspection occurs on this line every year.
Q4 2022 | WECC | GO, TO | 230 | Yes | No | 2022-11-04 | 631 | The soil around a Douglas Fir became saturated from a wind and rain storm and fell into the line from outside the right-of-way. | 3 | 58 | 95 | Douglas Fir | 110 | Alive and healthy | Tree was removed and surrounding area inspected.
Q3 2022 | SERC | GO, TO | 230 | No | No | 2022-09-03 | 406 | A dead oak tree broke in a storm and fell through the transmission line. Neither the conductor nor the structures sustained any damage. | 3 | 7 | 40 | Oak | 65 | Dead and decaying (broke into pieces when tree hit the ground) | Tree identified in line patrol and removed. Thorough line patrol to identify potential hazard trees. None identified.
Q3 2022 | SERC | GO, TO | 230 | Yes | No | 2022-07-06 | 473 | A live Loblolly Pine with canker on the trunk made contact with the line. The tree was removed and the line returned to service. The tree was removed and the line returned to service. The soil condition was dry. Thunderstorms and a possible tornado were in the area. | 3 | 24 | 54 | Loblolly Pine | 78 | Alive with canker on trunk | The tree was removed and the line returned to service.
Q3 2022 | SERC | GO, TO | 230 | No | No | 2022-07-25 | 146 | A live and healthy Sweetgum tree made contact with the line. The tree was cut to ground and removed and the line returned to service. The soil condition was wet. Strong winds and rain was in the area. | 3 | 15 | 47 | Sweetgum | 75 | Alive and healthy | The tree was cut to ground and removed and the line returned to service.
Q3 2022 | SERC | GO, TO | 230 | No | No | 2022-08-11 | 518 | A live Loblolly Pine tree with some root rot made contact with the line. The tree was removed and the line returned to service. The soil condition was dry. Thunderstorms were in the area. | 3 | 27 | 56 | Loblolly Pine | 80 | Alive with some root rot | The tree was removed and the line returned to service.
Q3 2022 | SERC | GO, TO | 230 | No | No | 2022-08-10 | 53 | A dead and decaying Hackberry tree fell through the line. | 3 | 10 | 40 | Hackberry | 60 | Dead and decaying | Tree was removed.
Q3 2022 | SERC | GO, TO | 230 | No | No | 2022-07-15 | 174 | Adverse weather from the night before caused a large Red Oak tree with internal decay - possibly due to a lightning strike in the past - to fall into a Pine tree, which fell into the line. | 3 | 22 | 69 | Red Oak, Pine | 73 | Healthy | Tree was removed.
Q3 2022 | SERC | TO | 230 | No | No | 2022-09-30 | 164 | Strong winds from Hurricane Ian caused a live Loblolly Pine tree to break six feet above the base and fall into the line. | 3 | 10 | 40 | Loblolly Pine | 83 | Live | Tree was removed.
Q3 2022 | SERC | TO | 230 | No | No | 2022-09-30 | 325 | Strong winds from Hurricane Ian uprooted a live Loblolly Pine and it fell into the line. | 3 | 2 | 32 | Loblolly Pine | 72 | Live | Tree was removed.
Q2 2022 | NPCC | TO | 115 | No | Yes | 2022-06-17 | 595 | A healthy basswood tree uprooted and fell at an angle toward the line. | 3 | 12 | 68 | Basswood | 79 | Healthy | A small oak tree that was bent over by the fallen basswood is being removed.
Q2 2022 | SERC | GO, TO | 230 | Yes | No | 2022-06-16 | 195 | A tree uprooted and fell on to the northern base of the line pinning it to the ground. The soil was saturated due to recent heavy rains. | 3 | 35 | 47 | Pine | 85 | Healthy | A ground visual inspection of trees in the area didn’t find any others that posed a danger to the line. No further action was required.
Q2 2022 | SERC | GO, TO | 230 | No | No | 2022-06-08 | 148 | A large poplar tree broke off three feet from ground level and fell into another large polar tree that was uprooted and fell into the line. | 3 | 50 | 69 | Poplar | 98 | Healthy | Significant storm came through the area, producing very high wind gusts and rainfall within a matter of an hour.
Q2 2022 | SERC | GO, TO | 230 | No | No | 2022-05-29 | 1 | A palm tree off the right-of-way failed at the base of the tree and made contact with the conductor. | 3 | 19 | 27 | Washingtonian Palm | 53 | Dead | Tree was removed and area inspected.
Q2 2022 | SERC | GO, TO | 230 | No | No | 2022-06-25 | 417.07 | A water oak failed during a major storm event, falling on the outside of the conductor. | 3 | 3 | 38 | Water oak | 66 | Live, internal decay not visible from outside | Local storm event, patrolled area for other storm-related hazards.
Q2 2022 | WECC | TO | 60 | Yes | Yes | 2022-04-04 | 213 | A healthy sugar pine with no visual defects completely uprooted and made contact with the line after the ground became saturated with snow melt. | 3 | 20 | 40 | Sugar Pine | 60 | Healthy | Site inspection that will address high risk trees based on poor taper condition of tree or site conditions identified by LiDAR along the adjacent spans in either direction to the outage span.
Q1 2022 | SERC | GO, TO | 230 | No | No | 2022-01-18 | 1414.57 | A tree uprooted and fell into the line causing an outage, caused by strong winds after an ice storm. | 3 | 2 | 46 | Water oak | 69 | Live tree with internal decay | Tree was removed from line and line was patrolled for any other tree issue.
Q1 2022 | SERC | GO, TO | 230 | Yes | No | 2022-01-12 | 109 | A tree from outside the right-of-way fell into the line, caused by the back side of the trunk base being burned through after a controlled burn. | 3 | 10 | 40 | Pine | 88 | Healthy tree but was still smoldering from a controlled burn the previous day and had a large wound on the base of the trunk at ground level that had burned through | A foot patrol was conducted along the ROW of the controlled burn area to identify other trees that exhibited a similar condition. One live pine was identified as leaning and a canker was noted on another live pine. Both pines were removed.
Q1 2022 | SERC | GO, TO | 230 | No | No | 2022-01-17 | 122 | A tree fell into the line from outside the right-of-way during Winter Storm Izzy. | 3 | 6 | 39 | Pine | 60 | Live | The entire area was air-patrolled and the immediate surrounding area was ground-patrolled to identify any additional threats.
Q1 2022 | SERC | GO, TO | 230 | Yes | No | 2022-01-03 | 3130 | A red oak uprooted and made contact with the line, pinning it to the ground, caused by wet snow built up from the previous day's winter storm. | 3 | 11 | 58 | Red Oak | 85 | Healthy | Line corridor ground was patrolled by line crew and followed up with an aerial patrol. No hazards were observed during the patrols.
Q1 2022 | WECC | GO, TO | 230 | Yes | No | 2022-01-07 | 1562 | A large Douglas Fir from outside the right-of-way uprooted during gusty winds and made contact with the line. | 3 | 100 | 132 | Western Hemlock and Douglas Fir | 155 | Healthy | Annual inspection conducted in spring of 2021. Other trees in the area inspected, but no others showed signs for concern of failure.
Q1 2022 | WECC | GO, TO | 230 | No | No | 2022-01-02 | 1050 | A Douglas Fir was uprooted in a storm with heavy winds and precipitation and fell into the line. | 3 | 19 | 51 | Douglas Fir | 107 | Healthy | Tree was removed.
Q1 2022 | WECC | GO, TO | 230 | Yes | No | 2022-01-06 | 49808 | Heavy snow and high winds caused four trees in separate locations to fall into the line from outside the right-of-way. | 3 | 25 | 35 | Douglas Fir | 80 | Healthy | Additional damaged trees were removed.
Q4 2021 | SERC | TO | 230 | No | No | 2021-12-07 | 222 | A dead pine fell from off the right-of-way into the line. Tree height is estimated because it broke into multiple pieces. | 3 | 5 | 35 | Pine | 65 | Dead, tree height is estimated because it broke into multiple pieces. | The surrounding area was patrolled to determine if any additional threats existed. None were found.
Q4 2021 | WECC | TO | 60 | No | Yes | 2021-12-14 | 1210 | A tall Lodgepole pine with poor taper was snow loaded and bent over the line due to heavy storm and a recent atmospheric river event. | 3 | 3 | 23 | Lodgepole Pine | 65 | Healthy | Tree was removed and area inspected.
Q4 2021 | WECC | TO | 115 | No | Yes | 2021-12-14 | 2136 | A tall lodgepole pine broke off during a heavy snow storm and fell into the line. | 3 | 17 | 32 | Lodgepole Pine | 100 | Healthy | Tree was removed and area inspected.
Q4 2021 | WECC | GO, TO | 230 | NO | No | 2021-10-24 | 586 | A healthy Douglas Fir with no outward signs of failure fell into the line from outside the right-of-way during high winds. | 3 | 35 | 60 | Douglas Fir | 100 | Healthy | Tree was removed and area inspected.
Q4 2021 | WECC | GO, TO | 230 | Yes | No | 2021-11-01 | 2381 | High wind/rain created saturated soils causing whole tree to uproot. | 3 | 20 | 45 | Western Hemlock | 95 | Healthy | Tree was removed.
Q4 2021 | WECC | GO, TO | 230 | Yes | No | 2021-11-15 | 2877 | High wind/rain created saturated soils causing whole tree to uproot. | 3 | 10 | 30 | Douglas Fir | 55 | Healthy | Tree was removed.
Q4 2021 | WECC | GO, TO | 230 | No | No | 2021-12-25 | 4019 | Heavy snow/strong winds caused whole tree to fall. | 3 | 25 | 55 | Douglas Fir | 120 | Healthy | Tree was removed.
Q3 2021 | SERC | GO, TO | 230 | No | No | 2021-07-14 | 108 | An isolated, severe thunderstorm impacted the area immediately surrounding the outage that included high winds, lightning and heavy rains resulting in many customer outages. A large oak tree from off the right-of-way fell into the line. | 3 | 35 | 86 | Oak | 111 | Live tree before storm damages. Growth defects included rotten center visible after all/split | Area was inspected for other danger trees. None identified.
Q3 2021 | SERC | GO, TO | 230 | No | No | 2021-08-23 | 615 | During a severe thunderstorm, lightning struck a green slash pine. The tee failed at the base where the sap become overheated and blew out the structure of the tree base. The pine tree fell into the right-of-way and made contact with the conductor. | 3 | 15 | 52 | Slash Pine | 72 | Green, live tree | Tree was removed and area inspected.
Q3 2021 | SERC | GO, TO | 230 | No | No | 2021-07-19 | 236 | A living pine tree from off the right-of-way broke 20 feet up and fell diagonally towards the line and landed on the line. No visible signs of decay were observed at the breakpoint. Weather at the time of outage was a passing though afternoon thunderstorm. | 3 | 9 | 76 | Pine | 90 | Live, sound | Tree was removed and area inspected.
Q3 2021 | SERC | GO, TO | 230 | No | No | 2021-08-24 | 25 | A tall gum tree fell at the an angle toward the line in a swampy area due to the wind and rain from summer storms. | 3 | 16 | 42 | Sweet gum | 90 | Live | Area was inspected
Q3 2021 | SERC | TO | 230 | No | No | 2021-07-28 | 7929 | A strong storm passed through part the corridor, and strong winds brought a 100 foot tall Sycamore tree down on the line. | 3 | 0 | 43 | American Sycamore | 100 | Tree was sheared 15 foot up the trunk by the wind, no noted damage to remainder of tree | Tree was removed and area inspected.
Q3 2021 | SERC | TO | 230 | No | No | 2021-08-10 | 413 | Extensive decay at the base of and back side of the tree caused the tree to split during the wind load of the storm and fall onto the line. | 3 | 16 | 59 | Red Maple | 75 | Extensive decay at the base of and on the back side of the tree | Tree was removed and area inspected.
Q3 2021 | SERC | TO | 230 | No | No | 2021-08-13 | 410 | The area experienced localized thunderstorms. A small grouping of 3-4 trees that were entangled in vines were uprooted in saturated soil and fell at a 90 degree angle onto the line. | 3 | 12 | 42 | Basswood | 70 | Entangled in vines in saturated soil | Tree was removed and area inspected.
Q3 2021 | SERC | TO | 230 | No | No | 2021-08-22 | 533 | A 75-foot-tall red oak, located off the right-of-way, fell onto the line. It had a crack up and down the main stem. The main stem failed six feet from the ground. | 3 | 11 | 44 | Red Oak | 75 | The tree had a crack up and down the main stem, rot was only visible after the tree fell | Tree was removed and area inspected.
Q3 2021 | WECC | GO, TO | 230 | No | No | 2021-09-18 | 165 | Declining Douglas Fir tree that was outside of the ROW fell onto the line. | 3 | 15 | 77 | Douglas Fir | 85 | Dying | Tree was removed and area inspected.
Q2 2021 | SERC | GO, TO | 230 | No | No | 2021-05-05 | 702 | A tree uprooted and fell onto the line. The tree fell as a result of strong gusty winds and saturated soil due to thunderstorms. There was no damage to either the wires or conductors. | 3 | 7 | 45 | Sweetgum | 65 | Healthy tree with no apparent wounds or insect issues | A ground visual inspection of trees in the area didn’t find any others that pose a danger to the line. No further action was required.
Q2 2021 | SERC | GO, TO | 230 | Yes | No | 2021-06-11 | 289 | A live sycamore tree with rot on the back side broke off and fell onto the line from outside the right-of-way. The tree fell to the ground and damaged the line conductors. The soil condition was dry. The line was repaired and restored to service. | 3 | 14 | 46 | Sycamore | 75 | Alive with rot on the back side (woods side) of the trunk where the tree broke off | No mitigation/remediation actions taken because tree fell to ground and no additional vegetation issues were observed.
Q2 2021 | SERC | GO, TO | 230 | Yes | No | 2021-06-15 | 234 | A live maple tree that appeared healthy fell into the line from outside the right-of-way. The top of the tree broke and made contact with the middle and outside phases, pulling them to the ground and damaging the line conductor. The soil condition was wet. The tree was removed from the line, and the line was returned to service. The damaged wire was later repaired. Storms and high winds were reported in the area. | 3 | 9 | 32 | Maple | 30 | Alive and healthy | Flight patrol was conducted as well as a foot patrol in vicinity of the outage.
Q2 2021 | SERC | TO | 230 | No | No | 2021-06-15 | 383 | A sweet bay magnolia fell onto the transmission conductor from outside the right-of-way. The tree was found to have decay at the base of the trunk causing the failure. | 3 | 2 | 32 | Sweet Bay Magnolia | 60 | Internal decay at base of trunk | Tree fell into the clear and no longer a threat. Surrounding area was patrolled and no other issues were identified.
Q2 2021 | SERC | TO | 500 | No | No | 2021-06-15 | 1149 | Due to local storms and wind conditions, a mature oak tree up-rooted and fell onto the outside conductor causing a transmission line outage. | 3 | 20 | 49 | Water Oak | 96 | Healthy and live with a rotten core that was discovered after tree fell and split | Transmission Vegetation inspected the area of storm impact and no other trees were identified to need maintenance
Q2 2021 | SERC | TO | 230 | No | No | 2021-05-04 | 193 | During a thunderstorm in area, a large hardwood tree uprooted and fell into the transmission line. | 3 | 6 | 40 | Hardwood | 65 | Healthy | An inspection of the area where the outage occurred was performed and no other hazard tree related issues were identified.
Q2 2021 | SERC | TO | 230 | Yes | No | 2021-04-30 | 299 | An 85-foot-tall hickory tree fell over into line 2010 and lodged on a single phase distribution pole. | 3 | 5 | 30 | Hickory | 85 | The tree had a 2 foot area of decay below ground level. No decay was visible above grade. The tree appeared healthy - good leaf flush with good color. The tree did not uproot in the typical manner. Essentially, the tree separated from what should have been the root system. There was a single large root on one side of the stump providing nutrients. | A nearby white oak tree was removed the following day.
Q1 2021 | SERC | GO, TO | 230 | No | No | 2021-02-12 | 308 | A tree uprooted and fell onto the line pinning it to the ground. The soil was saturated due to recent heavy rains. There was no damage to either the wires or conductors. | 3 | 41.5 | 73 | Pine | 109 | Tree was healthy and had a wound approximately 15 feet from the ground with DBH of 23 inches. | A ground visual inspection of trees in the area didn’t find any others that pose a danger to the line. No further action was required.
Q1 2021 | SERC | GO, TO | 230 | Yes | No | 2021-02-16 | 192 | A living loblolly pine tree located outside the right-of-way fell to ground and made contact with the line. The tree had root rot-below grade and strong thunderstorms/winds were in the area. The tree was removed and the line was restored to service. | 3 | 4 | 36 | Loblolly Pine | 80 | Alive, but functional issue included: root rot - below grade | No mitigation/remediation actions taken because tree fell to ground and no additional vegetation issues were observed.
Q1 2021 | SERC | TO | 230 | No | No | 2021-01-26 | 825 | A tree from off the right-of-way fell onto the line. It was very windy and rainy that day. The soil was saturated and the root system appeared to have been damaged by Hurricane Zeta. | 3 | 15 | 59 | Pine | 85 | Healthy, but root system appears to have been weekend by Hurricane Zeta. | We performed an aerial patrol of the area to identify any other trees that appeared to be prone to falling on the line. We sent a vegetation crew to cut all identified trees.
Q1 2021 | SERC | TO | 230 | Yes | No | 2021-01-31 | 267 | Pine tree had been damaged during Hurricane Zeta and was leaning/lodged in another tree. During a thunderstorm, the other tree fell under the strain, and the leaning pine tree fell onto the transmission line. | 3 | 31 | 69 | Pine | 85 | Damaged - leaning on and lodged in another tree. | We performed an aerial patrol to identify danger trees. We then sent a vegetation crew in to remove the identified trees. Due to weather, we were unable to patrol the line until after this incident.
Q1 2021 | SERC | TO | 230 | No | No | 2021-02-18 | 924 | Heavy rainfall in the region associated with the flooding of the Great Pee Dee River swamp undermined a cluster of sycamore trees which floated into the line. | 3 | 5 | 39 | Sycamore | 55 | Healthy | An inspection of the area where the outage occurred was performed and no other hazard tree related issues were identified.
Q1 2021 | WECC | TO | 230 | No | No | 2021-01-14 | 5211 | A healthy Douglas Fir tree fell into the right-of-way during a high wind event. | 3 | 6.5 | 52 | Alder | 71 | Healthy | The tree was removed. A site inspection will be conducted to address high-risk trees in the area using LiDAR.
Q1 2021 | WECC | TO | 230 | No | No | 2021-01-19 | 5185 | A healthy Douglas Fir tree fell into the right-of-way during a high wind event. | 3 | 58 | 98 | Douglas Fir | 137 | Healthy | The tree was removed. A site inspection will be conducted to address high-risk trees in the area using LiDAR.
Q1 2021 | WECC | TO | 230 | No | No | 2021-01-19 | 2926 | A healthy Alder tree from outside the right-of-way during a high wind event. | 3 | 58 | 98 | Douglas Fir | 137 | Healthy | The tree was removed.
Q1 2021 | WECC | TO | 230 | Yes | No | 2021-01-13 | 9509 | During a storm with strong winds, a Douglas Fir tree snapped and fell into the right-of-way. Restricted access and crew availability led to the extended outage. | 3 | 40 | 60 | Douglas Fir | 95 | Damaged | The tree was removed.
Q1 2021 | WECC | TO | 230 | Yes | No | 2021-01-13 | 3679 | A Western Hemlock tree with root decay fell into the right-of-way during a storm with high winds. | 3 | 20 | 45 | Western Hemlock | 75 | Root Decay | The tree was removed.
Q1 2021 | WECC | TO | 230 | Yes | No | 2021-01-13 | 3679 | A Douglas Fir tree with root decay fell into the right-of-way during a storm with high winds. | 3 | 45 | 65 | Douglas Fir | 104 | Root Decay | The tree was removed.
Q1 2021 | WECC | TO | 230 | Yes | No | 2021-01-26 | 1026 | During a high wind event, a Hemlock tree with root rot broke off at ground level and fell into the right-of-way. | 3 | 26 | 46 | Western Hemlock | 65 | Root Rot | The tree was removed.
Q1 2021 | WECC | TO | 230 | Yes | No | 2021-02-13 | 1620 | During a high wind event, a healthy Douglas Fir tree fell into the right-of-way. | 3 | 65 | 90 | Douglas Fir | 145 | Healthy | The tree was removed.
Q1 2021 | WECC | TO | 230 | No | No | 2021-01-13 | 1127 | A healthy Douglas Fir tree fell into the right-of-way. | 3 | 71 | 105 | Douglas Fir | 135 | Healthy | The tree was removed. The surrounding property will continue to be monitored for signs of forest decline.
Q1 2021 | WECC | TO | 230 | No | No | 2021-01-13 | 588 | A damaged Douglas Fir tree fell into the right-of-way. | 3 | 25 | 80 | Douglas Fir | 150 | Damaged | The tree was removed. The surrounding property will continue to be monitored for signs of forest decline.
Q1 2021 | WECC | TO | 230 | No | No | 2021-01-13 | 396 | A damaged Douglas Fir tree fell into the right-of-way. | 3 | 25 | 80 | Douglas Fir | 150 | Damaged | The tree was removed. The surrounding property will continue to be monitored for signs of forest decline.
Q1 2021 | WECC | TO | 230 | Yes | No | 2021-01-13 | 475 | A damaged Douglas Fir tree fell into the right-of-way. | 3 | 25 | 80 | Douglas Fir | 150 | Damaged | The tree was removed. The surrounding property will continue to be monitored for signs of forest decline.
Q4 2020 | NPCC | TO | 230 | No | Yes | 2020-11-15 | 1105 | A wind event caused two outage events due to a fall-in from outside the right-of-way by one tree at the same location. | 3 | 7 | 31 | White Pine | 99 | Healthy | The tree lot adjacent to the right-of-way had been partially cleared for a new development. Following the event, the entity received permission to remove additional trees that may be susceptible to wind due to the recent clearing on the adjacent lot.
Q4 2020 | NPCC | TO | 115 | No | Yes | 2020-11-15 | 1119 | A wind event caused two outage events due to a fall-in from outside the right-of-way by one tree at the same location. | 3 | 7 | 31 | White Pine | 99 | Healthy | The tree lot adjacent to the right-of-way had been partially cleared for a new development. Following the event, the entity received permission to remove additional trees that may be susceptible to wind due to the recent clearing on the adjacent lot.
Q4 2020 | WECC | TO | 115 | Yes | Yes | 2020-11-08 | 434 | A dead Lodgepole Pine tree fell into the line from outside the right-of-way. | 3 | 10 | 40 | Lodgepole Pine | 75 | Dead | Constant proactive analysis of vegetation on this line along with continuing coordination with the local Forest Service to remove appropriate trees outside of the cleared right-of-way.
Q4 2020 | WECC | TO | 230 | Yes | No | 2020-10-11 | 2547 | During a storm with high winds, a healthy Western Hemlock tree broke at 15' above the ground and fell from the edge of the right-of-way into the line. | 3 | 32 | 54 | Western Hemlock | 85 | Healthy | Tree was removed.
Q4 2020 | WECC | TO | 230 | Yes | No | 2020-11-25 | 918 | A healthy Birch tree fell into the right-of-way after a beaver gnawed the base of the tree. | 3 | 17.5 | 37.5 | Birch | 85 | Healthy | Continue to monitor surrounding property for signs of forest decline.
Q3 2020 | NPCC | GO | 345 | No | No | 2020-08-30 | 333 | A tree fell from outside the ROW and contacted the line. | 3 | 10 | 60 | Ash | 110 | Healthy appearance, interior rot | Inspection of the area of concern identified additional trees outside ROW but potential hazards; these trees are to be removed.
Q3 2020 | RF | TO | 230 | No | No | 2020-08-04 | 4561 | An off-corridor healthy White Pine tree approximately 71’ tall and 23” diameter at breast height uprooted due to high winds during Tropical Storm Isaias, and subsequently fell into the ROW, coming to rest approximately 7" from the conductor. Upon investigation, the tree was still leaning on fencing and suspended by distribution and communication wires. The White Pine tree was located approximately 9’ from the edge of the maintained ROW. No other trees in the surrounding spans uprooted during the tropical storm, but substantial damage was observed throughout. Radar indicates that the outage location experienced high winds in excess of 50 mph at the time of the outage. The National Weather Service issued a tropical storm warning for Tropical Storm Isaias that was travelling over the outage area, which indicated the storm may contain high winds in excess of 60 mph. | 3 | 9 | 59 | White Pine | 71 | Healthy | After the contact, surrounding spans were reviewed to ensure there were no other existing tree conditions.
Q3 2020 | RF | TO | 230 | No | No | 2020-08-27 | 284 | An off-corridor healthy Red Oak tree approximately 98’ tall and 29.4” diameter at breast height uprooted due to high winds and subsequently fell into the ROW contacting the conductor. The Red Oak tree was located approximately 20’ from the edge of the maintained ROW. Radar indicates that the outage location experienced high winds in excess of 50-60 mph at the time of the outage. National Weather Service had issued a severe thunderstorm warning for the outage area, which indicated the storm may contain high winds in excess of 55 mph. | 3 | 20 | 75 | Red Oak | 98 | Healthy | After the contact, surrounding spans were reviewed to ensure there were no other existing tree conditions. As information, three large trees, broken at base, were encountered on the access road and had to be removed to reach outage location.
Q3 2020 | RF | TO | 345 | No | No | 2020-07-12 | 5 | Fall-in from outside the ROW. An off-corridor healthy Red Oak tree approximately 91’ tall and 22” diameter at breast height uprooted due to saturated soil and a root system insufficient for the size of the tree, and subsequently fell into the ROW contacting the line. The Red Oak tree was located approximately 40’ from the edge of the maintained ROW. | 3 | 40 | 80 | Red Oak | 91 | Healthy | After the contact, surrounding spans were reviewed to ensure there were no other existing tree conditions; one tree was struck by the Red Oak and fell at the time of the outage, and one other tree was identified for removal in the span.
Q3 2020 | SERC | GO, TO | 230 | No | No | 2020-08-06 | 243 | A Loblolly Pine tree from off the ROW, which appeared to be healthy, made contact with the 230 kV line. No damage to facilities. Strong thunderstorms were in the area at the time of event. | 3 | 10 | 42 | Loblolly Pine | 83 | Healthy, no visible signs of decay | Vines were cut and removed and area was sprayed.
Q3 2020 | SERC | TO | 230 | No | No | 2020-07-23 | 990 | A healthy Poplar Tree 90' off the ROW broke off about 8-10 feet up the tree. | 3 | 1 | 43 | Poplar | 74 | Healthy tree sheared off 8-10 feet up tree. | Tree was cut down. Adjacent spans in both directions were evaluated and additional potential danger trees were also mitigated and cut.
Q3 2020 | SERC | TO | 230 | No | No | 2020-07-13 | 56 | Oak tree with root decay fell 35 feet from off the right-of-way. | 3 | 35 | 65 | Oak | 87 | Evidence of root decay. | Tree was cut down and other trees in the adjacent spans were evaluated for potential risk to facilities and cut down as needed.
Q3 2020 | SERC | DP, TO | 230 | No | No | 2020-07-28 | 551 | An 86 foot tall red oak tree uprooted during a storm and hit the line. The tree was outside the right of way, 4 feet from the ROW edge, and 38 feet from the nearest conductor. The tree was a hazard tree, with a small defect on the backside that might have affected root growth and might have contributed to the uprooting. | 3 | 4 | 38 | Red Oak | 86 | The tree had a small defect on the backside at the bottom that might have affected root growth and might have contributed to the uprooting. | Adjacent areas were patrolled for other trees with visible damage. None were found.
Q3 2020 | WECC | TO | 230 | No | No | 2020-08-09 | 474 | A dead Douglas fir tree back in the stand broke about 12 feet from ground level and hit the line. The tree broke from a healthy, unmanaged stand of Douglas firs and big leaf maples. | 3 | 41.5 | 61 | Douglas Fir | 65 | dead | The stand was surveyed and 6 small, suppressed dead Douglas firs were felled.
Q3 2020 | WECC | TO | 230 | Yes | No | 2020-09-08 | 3791 | 24" Hemlock was alive, root failure due to root rot with strong wind out of east. Tree is located on the south side of the ROW, sitting on the west bank of a steep uphill section | 3 | 32 | 52 | Western Hemlock | 124 | Healthy | Tree was removed.
Q3 2020 | WECC | TO | 230 | Yes | No | 2020-09-23 | 401 | Hemlock Tree fell through and contacted the line. | 3 | 27 | 47 | Hemlock | 110 | Healthy | Tree was removed. Continue to monitor surrounding property for signs of forest decline.
Q2 2020 | NPCC | TO | <200 | No | Yes | 2020-06-06 | 1416 | During a strong wind event, a healthy Red Oak tree snapped 6 feet up from the base of the trunk, falling into the transmission line. | 3 | 14 | 62 | Red Oak | 70 | Healthy tree with no evidence of internal decay | The tree was removed and the area was inspected with no findings of additional vegetation issues identified.
Q2 2020 | RF | TO | 345 | No | No | 2020-05-29 | 183 | During a high wind in excess of 55 mph weather condition, a healthy Tulip Poplar tree approximately 20” diameter at breast height (DBH) uprooted, falling into the transmission line and contacting a conductor. | 3 | 8 | 53 | Tulip Poplar | 95 | Healthy | The surrounding spans were reviewed to ensure there were no other existing tree conditions. A total of 20 trees were uprooted or damaged as a result of the severe thunderstorm and high winds. The Tulip Poplar tree and 7 other trees were uprooted. Due to the severity of the storm and winds, an aerial saw was brought in to remove 12 additional trees which were unsafe to climb.
Q2 2020 | SERC | GO, TO | 230 | No | No | 2020-06-27 | 855 | During a strong thunderstorms, a live healthy loblolly pine from outside of the ROW fell and made contact with the transmission line. There was no damage to the facilities. | 3 | 4 | 36 | Loblolly Pine | 84 | Healthy, no visible signs of decay | Tree was removed from area and right of way was inspected for any other hazards.
Q2 2020 | SERC | GO, TO | 230 | No | No | 2020-05-27 | 297 | During strong thunderstorm event, a tree off the ROW broke and pushed a healthy pine tree into the transmission lines. There were no damages to the facilities. | 3 | 22 | 54 | Pine | 86 | Healthy, no visible signs of decay. | Tree was removed from area and right of way was inspected for any other hazards.
Q2 2020 | SERC | GO, TO | 230 | No | No | 2020-06-30 | 329 | An off right-of-way live water oak tree with internal decay broke at base and made contact with the transmission line. Tree had signs of internal decay and root rot, but signs were not externally visible. Strong thunderstorms were in the area at the time of event. | 3 | 10 | 31 | Water Oak | 76 | Tree was alive with root rot | Tree was removed from area and right of way was inspected for any other hazards. There were no damages to the facilities.
Q2 2020 | SERC | TO | 230 | Yes | No | 2020-05-16 | 565 | A 103 feet tall oak tree , 28 feet off the ROW split 10 feet from the ground, making contact with the line and causing an outage. | 3 | 28 | 61 | Oak | 103 | Tree appeared healthy from an aerial inspection during the spring helicopter patrol. The large tree had 2 codominant stems that split 10’ from the ground. Age of the tree and the weight of the stem facing the conductor caused the tree to fail. The tree showed signs of internal rot at the split that could not be seen during a visual inspection. | A tree crew was called to site to remove the tree from the conductors and line was restored. Additional off right of way danger trees have been identified and scheduled for removal during the routine vegetation maintenance of this section of line.
Q2 2020 | SERC | TO | 230 | Yes | No | 2020-05-01 | 953 | A 115 ft. maple tree fell into 62 ft. sweetgum making the sweetgum to fall on the conductor. | 3 | 12 | 44 | Maple/Sweetgum | 62 | Healthy | Tree cut from conductor and other trees evaluated for condition with additional tree work completed the next day.
Q2 2020 | SERC | TO | 230 | Yes | No | 2020-06-22 | 1025 | Off right-of-way poplar tree fell on the conductor during thunderstorm. | 3 | 23 | 55 | Poplar | 98 | Healthy | Tree was cut off the line. The area was inspected and other trees and vegetation observed in the immediate area for additional vegetation threats were removed.
Q2 2020 | WECC | TO | 230 | No | No | 2020-06-01 | 197 | A hemlock tree fell into the transmission line due to laminated root rot disease. | 3 | 26 | 46 | Hemlock | 75 | Dying | Tree was removed off the line. The entity will continue to monitor vegetation for signs of rot.
Q2 2020 | WECC | TO | 230 | No | No | 2020-06-01 | 329 | A cottonwood tree fell from outside of the ROW and made contact with conductor. | 3 | 19 | 60 | Cottonwood | 70 | Healthy | Tree was removed off the line. The entity will continue to monitor surrounding property for signs of forest decline.
Q1 2020 | WECC | TO | 230 | Yes | Yes | 2020-01-12 | 7636 | A Douglas fir tree back in the stand uprooted and fell into the trunk/base of another Douglas fir tree closer to the edge of the ROW, causing this tree to uproot and hit the line. The tree was alive but the now-exposed roots showed evidence of a possible root rot. This occurred during a snow event with an accumulation of approximately 30 inches in 72 hours with sustained winds of 15 to 18 mph and gusts of 35 to 40 mph. | 3 | 8 | 36 | Douglas Fir | 84 | Alive, but some rot present in the roots | The adjacent trees were surveyed for removal.
Q1 2020 | WECC | TO | 230 | Yes | Yes | 2020-01-22 | 17355 | A Douglas fir tree back in the stand uprooted and fell onto the line. The tree was alive and healthy. This occurred during a period in which the area received over 2 inches of rain in a 72 hour period and experienced sustained winds of 13-17mph and gusts of 32mph. | 3 | 34.5 | 83 | Douglas Fir | 95 | Alive/healthy | An adjacent, uprooted tree was removed and the stand surveyed.
Q1 2020 | WECC | TO | 230 | Yes | No | 2020-01-12 | 3058 | A Douglas Fir tree fell into the line due to root failure caused by high water flow undermining the bank. | 3 | 22 | 42 | Douglas Fir | 124 | Healthy | None
Q1 2020 | WECC | TO | 230 | Yes | No | 2020-03-15 | 580 | Large dead tree fell from outside ROW and brushed through circuit and fell to ground. | 3 | 62 | 90 | Western Hemlock | 100 | Dead | Continue to monitor surrounding property for signs of forest decline.
Q4 2019 | SERC | TO | 230 | No | No | 2019-12-22 | 3267 | During a weather event a pine tree located 35 feet off the ROW fell into two structures, breaking insulators and conductors. | 3 | 35 | 77 | Loblolly Pine | 93 | Tree was still green in the top but had beetle damage and was rotten at the trunk. | Forester and contract tree crew checked the area and removed any other danger trees. The line was also patrolled for any other potential danger trees.
Q4 2019 | SERC | TO | 230 | No | No | 2019-10-19 | 583 | During a tropical storm, a live red oak tree located 26 feet off the ROW fell on a transmission structure breaking a cross arm and insulators. The tree had root rot that was not visible during routine inspections. | 3 | 26 | 74 | Red Oak | 94 | The tree had root damage that was not visible during routine inspections | Tree was removed from area and right of way was inspected for any other hazards.
Q4 2019 | WECC | TO | 230 | Yes | Yes | 2019-10-29 | 2109 | A healthy Douglas fir tree on a steep slope that was located nearly 30 feet off the ROW was uprooted and fell into the line during a wind storm. | 3 | 29.5 | 66 | Douglas Fir | 88 | Alive healthy tree with no visible defects | The entity surveyed the outage site and took corrective action the following day to remove 2 additional trees that potentially could fall into the line.
Q3 2019 | RF | TO | 345 | No | Yes | 2019-07-20 | 1621 | A large tree was uprooted by strong wind moving through the area. | 3 | 2 | 40 | Ash | 88 | Live, healthy | Ground patrol was conducted to identify any hazards. The tree was safely removed to remediate the situation.
Q3 2019 | SERC | GO, TO | 230 | No | No | 2019-08-24 | 919 | During a thunderstorm, an off right-of-way live pine tree with internal decay at the base of the trunk broke at base and fell from outside ROW. | 3 | 6 | 38 | Loblolly Pine | 94 | Alive, but with decay at base of trunk. | None
Q2 2019 | RF | TO | 230 | No | No | 2019-06-29 | 1.63 | A healthy Red Oak tree was uprooted due to high winds in the area and subsequently falling into the ROW contacting the conductor, causing two sustained outages. | 3 | 8 | 41 | Red Oak | 65 | Healthy | The surrounding spans were reviewed to ensure there were no other existing tree conditions; no other issues were identified. This corridor is currently being worked for 2019 Maintenance.
Q2 2019 | SERC | TO | 230 | No | No | 2019-06-20 | 1077 | During a thundershower, a live pine tree broke approximately 14' above the ground contacting the transmission line. There were no damages to the facilities. | 3 | 5 | 58 | Pine | 78 | Healthy with no visible internal decay. | Tree was removed from area and right of way was inspected for any other hazards.
Q2 2019 | SERC | TO | 230 | Yes | No | 2019-04-19 | 6 | During a weather event, a healthy oak tree fell into the line making contact long enough to cause a sustained outage. | 3 | 30 | 66 | Oak | 86 | Healthy | Checked several spans adjacent to tree location for additional vegetation issues and none were found.
Q2 2019 | SERC | TO | 230 | Yes | No | 2019-05-30 | 892 | A double-stemmed poplar tree fell onto the line causing the outage. Tree was found in a wetland area on a section of line where a strip of danger trees adjacent to the right-of-way was left by a logging operation months after routine utility vegetation maintenance had occurred. Area of right-of-way had been previously maintained using side-trimming aerial saw. | 3 | 4 | 38 | Poplar | 68 | Healthy | Tree was cut off of line and several spans adjacent to the location was patrolled for any additional vegetation issues. Additional potential danger trees were found and removed. The removed trees were prone to future wind damage that had been previously left adjacent to the right-of-way by outside logging operations.
Q2 2019 | SERC | TO | 230 | No | No | 2019-06-27 | 158 | Recent storms caused the tree to lean towards the line. The tree broke approximately 40’ high resulting in the top falling into the line. | 3 | 1 | 30 | Green Pine | 51 | Healthy green Pine | An inspection of the area was performed and no other hazard tree related issues were identified.
Q2 2019 | SERC | TO | 230 | Yes | No | 2019-06-20 | 1 | Tree fell onto the line and fell in the clear during a thunderstorm weather event causing an approximate one-minute outage. | 3 | 27 | 77 | Maple | 95 | Healthy | Line was patrolled for additional vegetation issues in several adjacent spans. No issues were found.
Q2 2019 | SERC | TO | 230 | No | No | 2019-06-22 | 411 | A loblolly pine tree fell into the line during thunder storm. | 3 | 2 | 45 | Loblolly Pine | 65 | Dead | Tree was removed from the line. Forester inspected the area and removed other trees as needed.
Q2 2019 | SERC | TO | 230 | No | No | 2019-06-22 | 860 | During a thunderstorms in the area, a healthy Sweet Gum tree broke off about six feet from the ground and fell on the conductor. Tree had no visible issues. | 3 | 14 | 57 | Sweet Gum | 85 | Green tree broke with no visible issues. | Forester inspected the area and removed other trees as well.
Q2 2019 | SERC | TO | 230 | No | No | 2019-05-14 | 275 | A Red Oak with root rot uprooted hitting the conductor, causing the outage. | 3 | 30 | 75 | Red Oak | 98 | Tree had root rot causing the failure. | Tree did not have to be removed from the line it brushed the conductor and fell to the ground. Forester inspected the area and removed diseased trees.
Q2 2019 | SERC | TO | 230 | No | Yes | 2019-06-20 | 103 | Strong winds in the area caused green pine tree to break off approximately 10 ft. up from ground falling onto outside conductor closest to edge of right of way. | 3 | 10 | 35 | Pine | 70 | Healthy green pine | An inspection of the area was performed. No other hazard tree were identified.
Q2 2019 | SERC | TO | 230 | No | Yes | 2019-06-22 | 470 | Strong winds in the area caused green oak to be uprooted, falling into the conductor closest to the edge of the right of way. | 3 | 8 | 32 | Oak | 78 | Healthy green oak | An inspection of the area where the outage occurred was performed and no other hazard tree related issues were identified.
Q2 2019 | WECC | TO | 230 | Yes | No | 2019-06-06 | 621 | Wet soils in area caused a cedar tree to be uprooted, falling into a Hemlock and push it into line. | 3 | 25 | 45 | Western Hemlock | 60 | Healthy | An inspection of the area was performed.
Q2 2019 | MRO | TO | 345 | No | No | 2019-05-18 | 6919 | During strong wind gust in the area, an oak tree fell into the line. The tree appeared to be healthy with a dense green canopy and showed no signs of distress such as included bark, disease or decay that would lead to its failure. The area has also experienced tornadoes and record rainfall during the previous months. | 3 | 16 | 76 | Swamp Laurel Oak | 90 | Healthy | Other identified hazard trees off the ROW were removed.
Q2 2019 | MRO | TO | 345 | No | No | 2019-06-03 | 743 | Strong winds caused an oak tree to fall into the line. The area had received nearly 23 inches of rain prior to this event. | 3 | 9 | 60 | Southern Red Oak | 64 | Healthy | Other identified hazard trees off the ROW were removed.
Q2 2019 | MRO | TO | 345 | No | No | 2019-05-26 | 1094 | During severe thunderstorm with wind gust of over 40 mph a healthy oak tree fell into the line causing a sustained outage. The tree was standing in over 12 inches of water due to recent flooding in the area. | 3 | 10 | 47 | Red Oak | 90 | Healthy | Other identified hazard trees off the ROW were removed.
Q1 2019 | WECC | TO | 230 | No | No | 2019-02-15 | 10980 | Due to a 3 days of heavy rain and wind storm in the area, a large healthy tree located 30 feet outside of the ROW fell into the transmission line. The tree was located on property owned by the county. The maintenance crew removed the tree, assessed the area and determined that no further work is necessary. | 3 | 30 | 111 | Ponderosa Pine | 158 | Healthy | None
Q1 2019 | WECC | GO, TO | 230 | Yes | No | 2019-01-06 | 3494 | A healthy tree broke off 18 feet above the ground during high winds and freezing rain-snow, falling into the transmission line. | 3 | 12 | 32 | Western Hemlock | 100 | Healthy | None
Q1 2019 | SERC | TO | 230 | No | No | 2019-01-20 | 1415 | An off right-of-way live pine tree with internal decay at the base of the trunk broke at base and made contact with the 230 kV line. There was no damage to the facilities. Tree had signs of internal decay, but signs were not externally visible. The soil condition was wet. Storms and high winds were recorded in the area. | 3 | 27 | 57 | Loblolly Pine | 81 | Alive with visible signs of decay at the root | None
Q1 2019 | SERC | TO | 230 | No | No | 2019-01-19 | 556 | A healthy tree uprooted and fell onto the east phase of the line pinning it to the ground between two structures. The soil was saturated due to recent heavy rains. There was no damage to either the wires or conductors. A strong storm front was passing though at the time of the outage. | 3 | 31 | 63 | Oak | 93 | Healthy | None